## data
edb | disc_yr | subnetwork | row_num | interruption_identifier | circuit_location | feeder | start_datetime | end_datetime | saidi_value | saifi_value | number_of_icps_interrupted | icp_interruption_minutes | planned_or_unplanned | cause | explanation | section | sect_no | source | schedule
Alpine Energy | 2025 |  | 9 | JDJ060 | CB W465 | Otaio | 2024-04-02 04:37 | 2024-04-02 04:43 | 0.014857 | 0.0024761 | 84 | 504 | Planned | Planned interruption | Red tag pole replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 10 | JDJ060 | CB W685 | Otaio | 2024-04-02 04:37 | 2024-04-02 04:42 | 0.0092855 | 0.0018571 | 63 | 315 | Planned | Planned interruption | Red tag pole replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 11 | JDJ060 | ABS W306-CB W465-CB W685 | Otaio | 2024-04-02 04:39 | 2024-04-02 04:41 | 0.0076052 | 0.0038026 | 129 | 258 | Planned | Planned interruption | Red tag pole replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 12 | JDJ060 | Links W571-ABS W306 | Otaio | 2024-04-02 11:00 | 2024-04-02 14:22 | 0.27391 | 0.001356 | 46 | 9292 | Planned | Planned interruption | Red tag pole replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 13 | JDJ060 | CB W465 | Otaio | 2024-04-02 18:30 | 2024-04-02 18:35 | 0.012381 | 0.0024761 | 84 | 420 | Planned | Planned interruption | Red tag pole replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 14 | JDJ060 | CB W685 | Otaio | 2024-04-02 18:31 | 2024-04-02 18:35 | 0.0074284 | 0.0018571 | 63 | 252 | Planned | Planned interruption | Red tag pole replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 15 | JDJ060 | ABS W306-CB W465-CB W685 | Otaio | 2024-04-02 18:33 | 2024-04-02 18:34 | 0.0038026 | 0.0038026 | 129 | 129 | Planned | Planned interruption | Red tag pole replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 16 | SKE1415 | TX A790 CCT2 | Waimate | 2024-04-03 08:32 | 2024-04-03 18:03 | 0.48812 | 0.00085485 | 29 | 16559 | Planned | Planned interruption | TX Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 17 | SKE1415 | TX A790-TX A790 CCT2 | Waimate | 2024-04-03 08:32 | 2024-04-03 17:56 | 0.49876 | 0.00088433 | 30 | 16920 | Planned | Planned interruption | TX Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 18 | SKE1415 | TX A789-TX A789 CCT2 | Waimate | 2024-04-03 08:32 | 2024-04-03 17:47 | 0.45808 | 0.00082537 | 28 | 15540 | Planned | Planned interruption | TX Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 19 | SKE1415 | TX A798 CCT2 | Waimate | 2024-04-03 08:32 | 2024-04-03 17:38 | 0.64379 | 0.0011791 | 40 | 21840 | Planned | Planned interruption | TX Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 20 | SKE1415 | TX A546 CCT3 | Waimate | 2024-04-03 08:32 | 2024-04-03 17:45 | 0.50534 | 0.00091381 | 31 | 17143 | Planned | Planned interruption | TX Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 21 | SKE1415 | TX A546 CCT2 | Waimate | 2024-04-03 08:32 | 2024-04-03 17:43 | 0.24363 | 0.00044216 | 15 | 8265 | Planned | Planned interruption | TX Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 22 | SKE1415 | Pole 20795 Links W749-TX A546 CCT3-TX A546 CCT2-TX A790-TX789 | Waimate | 2024-04-03 08:32 | 2024-04-03 17:33 | 0.68574 | 0.0012675 | 43 | 23263 | Planned | Planned interruption | TX Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 23 | GWM1138 | Fuses L305 | Waipopo | 2024-04-03 09:00 | 2024-04-03 10:14 | 0.034902 | 0.00047164 | 16 | 1184 | Planned | Planned interruption | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 24 | JJV135 | Services 76, 76a & 80 Wai-iti Rd | Nile Street | 2024-04-03 09:00 | 2024-04-03 15:52 | 0.036434 | 8.8433e-05 | 3 | 1236 | Planned | Planned interruption | Sub Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 25 | JJV135 | DB Q43 | Nile Street | 2024-04-03 09:00 | 2024-04-03 15:48 | 0.10824 | 0.0002653 | 9 | 3672 | Planned | Planned interruption | Sub Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 26 | JJV135 | GRM CB5-RMU E14-DB Q43-Services 76, 76a & 80 Wai-iti Rd | Nile Street | 2024-04-03 09:00 | 2024-04-03 15:35 | 1.9212 | 0.0048638 | 165 | 65175 | Planned | Planned interruption | Sub Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 27 | JDJ074 | TX D1064 | Winchester | 2024-04-03 09:48 | 2024-04-03 15:03 | 0.018571 | 5.8955e-05 | 2 | 630 | Planned | Planned interruption | DDE connection | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 28 | SKE1416 | TX A546 CCT3 | Waimate | 2024-04-04 08:31 | 2024-04-04 16:33 | 0.44046 | 0.00091381 | 31 | 14942 | Planned | Planned interruption | TX Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 29 | SKE1416 | TX A546 CCT2 | Waimate | 2024-04-04 08:31 | 2024-04-04 16:22 | 0.20826 | 0.00044216 | 15 | 7065 | Planned | Planned interruption | TX Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 30 | SKE1416 | Pole 20795 Links W749-TX A546 CCT3-TX A546 CCT2-TX A790 CCT2 | Waimate | 2024-04-04 08:31 | 2024-04-04 16:05 | 1.887 | 0.0041563 | 141 | 64014 | Planned | Planned interruption | TX Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 31 | RAK137 | TX E311 CCT2 | Lakeside Drive | 2024-04-04 13:09 | 2024-04-04 15:17 | 0.0075463 | 5.8955e-05 | 2 | 256 | Planned | Planned interruption | TX Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 32 | RAK137 | TX E311 CCT3 | Lakeside Drive | 2024-04-04 13:09 | 2024-04-04 15:22 | 0.0039205 | 2.9478e-05 | 1 | 133 | Planned | Planned interruption | TX Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 33 | 3866 | CB G297 to ABS G173 & ABS G170 | Winchester | 2024-04-06 00:32 | 2024-04-06 13:00 | 1.0363 | 0.0013854 | 47 | 35156 | Unplanned | Adverse environment | Fire In hedge Line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 34 | 3866 | ABS G173 to end | Winchester | 2024-04-06 00:32 | 2024-04-06 03:08 | 0.087372 | 0.00056008 | 19 | 2964 | Unplanned | Adverse environment | Fire In hedge Line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 35 | 3866 | ABS G170 to end minus ABS G160 | Winchester | 2024-04-06 00:32 | 2024-04-06 03:08 | 0.77715 | 0.0049817 | 169 | 26364 | Unplanned | Adverse environment | Fire In hedge Line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 36 | 3866 | ABS G160 to end | Winchester | 2024-04-06 00:32 | 2024-04-06 01:35 | 0.18942 | 0.0030067 | 102 | 6426 | Unplanned | Adverse environment | Fire In hedge Line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 37 | 5031 | Fuses L707 to end | Hadlow | 2024-04-09 06:28 | 2024-04-09 08:09 | 0.068477 | 0.00067799 | 23 | 2323 | Unplanned | Unknown | 2x Blown drop outs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 38 | GWM1129 | ABS F277 | Fairlie Rural | 2024-04-09 09:00 | 2024-04-09 12:43 | 0.18406 | 0.00082537 | 28 | 6244 | Planned | Planned interruption | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 39 | 4307 | M338 less M452 (pole #55422) | Simons | 2024-04-09 19:23 | 2024-04-09 20:20 | 0.031924 | 0.00056008 | 19 | 1083 | Unplanned | Defective equipment | Burnt jumper pole #51666 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 40 | 4307 | M452 (pole #55422) end | Simons | 2024-04-09 19:23 | 2024-04-09 21:40 | 0.084807 | 0.00061903 | 21 | 2877 | Unplanned | Defective equipment | Burnt jumper pole #51666 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 41 | ACD115 | Switch W556 to end minus ICP #0006650232AL652 minus ICP #0006650155AL76B | Tawai | 2024-04-10 08:00 | 2024-04-10 17:03 | 0.48019 | 0.00088433 | 30 | 16290 | Planned | Planned interruption | Pole replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 42 | ACD115 | ICP #0006650232AL652 | Tawai | 2024-04-10 08:00 | 2024-04-10 17:16 | 0.01639 | 2.9478e-05 | 1 | 556 | Planned | Planned interruption | Pole replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 43 | ACD115 | ICP #0006650155AL76B | Tawai | 2024-04-10 08:00 | 2024-04-10 17:10 | 0.016213 | 2.9478e-05 | 1 | 550 | Planned | Planned interruption | Pole replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 44 | 5061 | Tripsavers W308 | Otaio | 2024-04-10 13:27 | 2024-04-10 16:16 | 0.059781 | 0.00035373 | 12 | 2028 | Unplanned | Defective equipment | Broken Jumper | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 45 | ACD116 | ABS W555-A1365-A311-A1559-A1300 | Tawai | 2024-04-11 08:00 | 2024-04-11 16:19 | 0.13238 | 0.0002653 | 9 | 4491 | Planned | Planned interruption | Pole replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 46 | ACD116 | TX A1365 | Tawai | 2024-04-11 08:00 | 2024-04-11 16:52 | 0.062728 | 0.00011791 | 4 | 2128 | Planned | Planned interruption | Pole replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 47 | ACD116 | TX A311 | Tawai | 2024-04-11 08:00 | 2024-04-11 16:44 | 0.061785 | 0.00011791 | 4 | 2096 | Planned | Planned interruption | Pole replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 48 | ACD116 | TX A1559 | Tawai | 2024-04-11 08:00 | 2024-04-11 16:38 | 0.015269 | 2.9478e-05 | 1 | 518 | Planned | Planned interruption | Pole replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 49 | ACD116 | TX A1300 | Tawai | 2024-04-11 08:00 | 2024-04-11 16:30 | 0.015034 | 2.9478e-05 | 1 | 510 | Planned | Planned interruption | Pole replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 50 | JJV138 | Fuses B1916 to end | Hadlow | 2024-04-11 10:05 | 2024-04-11 13:20 | 0.017244 | 8.8433e-05 | 3 | 585 | Planned | Planned interruption | Liven DB4828 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 51 | 164 | STU CB1 (Otaio) to end | Otaio | 2024-04-12 01:34 | 2024-04-12 02:23 | 0.50554 | 0.010317 | 350 | 17150 | Unplanned | Vegetation | Bark on line pole 31701 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 52 | 164 | STU CB8 (Mt Studholme) to end | Mt Studholme | 2024-04-12 01:34 | 2024-04-12 02:25 | 0.51565 | 0.010111 | 343 | 17493 | Unplanned | Vegetation | Bark on line pole 31701 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 53 | 3011 | STU CB1 (Otaio) to end | Otaio | 2024-04-12 03:03 | 2024-04-12 06:34 | 2.1769 | 0.010317 | 350 | 73850 | Unplanned | Defective equipment | Burnt jumper pole 31678 due to fault current from the bark | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 54 | 3011 | STU CB8 (Mt Studholme) to end | Mt Studholme | 2024-04-12 04:49 | 2024-04-12 06:35 | 1.0717 | 0.010111 | 343 | 36358 | Unplanned | Defective equipment | Burnt jumper pole 31678 due to fault current from the bark | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 55 | 3011 | W100 to end | Morven | 2024-04-12 04:50 | 2024-04-12 06:18 | 0.028534 | 0.00032425 | 11 | 968 | Unplanned | Defective equipment | Burnt jumper pole 31678 due to fault current from the bark | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 56 | ACD117 | TX A311 | Tawai | 2024-04-12 08:00 | 2024-04-12 15:53 | 0.055772 | 0.00011791 | 4 | 1892 | Planned | Planned interruption | Pole replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 57 | ACD117 | ABS W555-TX A311 | Tawai | 2024-04-12 08:00 | 2024-04-12 15:16 | 0.19278 | 0.00044216 | 15 | 6540 | Planned | Planned interruption | Pole replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 58 | SLA547 | Fuses A387 to end | Waikakahi | 2024-04-12 09:15 | 2024-04-12 10:03 | 0.0042448 | 8.8433e-05 | 3 | 144 | Unplanned | Third party interference | Tx maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 59 | 3012 | CB T127 to end less T404, TX62, T667 & TX66 | Rangitata | 2024-04-13 03:18 | 2024-04-13 05:57 | 0.14998 | 0.00094328 | 32 | 5088 | Unplanned | Wildlife | Possum at pole #06748 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 60 | 3012 | T404 to end | Rangitata | 2024-04-13 03:18 | 2024-04-13 06:06 | 0.064379 | 0.00038321 | 13 | 2184 | Unplanned | Wildlife | Possum at pole #06748 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 61 | 3012 | T667 to end | Rangitata | 2024-04-13 03:18 | 2024-04-13 06:13 | 0.041269 | 0.00023582 | 8 | 1400 | Unplanned | Wildlife | Possum at pole #06748 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 62 | 3012 | TX62 to end | Rangitata | 2024-04-13 03:18 | 2024-04-13 06:17 | 0.047489 | 0.0002653 | 9 | 1611 | Unplanned | Wildlife | Possum at pole #06748 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 63 | 3012 | TX66 to end | Rangitata | 2024-04-13 03:18 | 2024-04-13 06:11 | 0.061196 | 0.00035373 | 12 | 2076 | Unplanned | Wildlife | Possum at pole #06748 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 64 | SKE1727 | TX B1245 CCT4 | Levels Plain | 2024-04-14 08:00 | 2024-04-14 14:46 | 0.15558 | 0.00038321 | 13 | 5278 | Planned | Planned interruption | Removal of redundant 33kV lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 65 | SKE1727 | RMU L1264-CB L876-RMU L1140-TX B1245 CCT4 | Levels Plain | 2024-04-14 08:00 | 2024-04-14 14:44 | 0.29772 | 0.00073694 | 25 | 10100 | Planned | Planned interruption | Removal of redundant 33kV lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 66 | GWM1141 | Fuses T119 | Milford | 2024-04-15 09:01 | 2024-04-15 12:20 | 0.19945 | 0.0010022 | 34 | 6766 | Planned | Planned interruption | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 67 | 4401 | M346 - M318 | TEK-UHT 33kV | 2024-04-15 18:35 | 2024-04-15 20:30 | 0.033899 | 0.00029478 | 10 | 1150 | Unplanned | Unknown | Unknown - possible bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 68 | 4401 | M73 - M272 - M24 | TEK-UHT 33kV | 2024-04-15 18:35 | 2024-04-15 22:04 | 0.07393 | 0.00035373 | 12 | 2508 | Unplanned | Unknown | Unknown - possible bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 69 | 4401 | M272 | TEK-UHT 33kV | 2024-04-15 18:35 | 2024-04-15 22:06 | 0.031099 | 0.00014739 | 5 | 1055 | Unplanned | Unknown | Unknown - possible bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 70 | 4401 | M158 | M158 | 2024-04-15 18:35 | 2024-04-15 22:06 | 0.099517 | 0.00047164 | 16 | 3376 | Unplanned | Unknown | Unknown - possible bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 71 | 4401 | M159 | M159 | 2024-04-15 18:35 | 2024-04-15 22:06 | 0.43538 | 0.0020634 | 70 | 14770 | Unplanned | Unknown | Unknown - possible bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 72 | 4401 | M24 | TEK-UHT 33kV | 2024-04-15 18:35 | 2024-04-15 22:08 | 0.087902 | 0.00041269 | 14 | 2982 | Unplanned | Unknown | Unknown - possible bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 73 | RAK136 | TE12-TE12 CCT11-TE12 CCT18 | Hayes Street | 2024-04-15 22:00 | 2024-04-15 22:32 | 0.016979 | 0.0005306 | 18 | 576 | Planned | Planned interruption | Pre work for planned outage for Lucy box replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 74 | SLA542A | Fuses TO C356 | Fairlie Rural | 2024-04-16 09:00 | 2024-04-16 11:46 | 0.048933 | 0.00029478 | 10 | 1660 | Planned | Planned interruption | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 75 | ACD125 | TX B1073-3ph ICP from p#28301-other ICPs fed from P#28301 | Hadlow | 2024-04-16 09:00 | 2024-04-16 14:23 | 0.0095213 | 2.9478e-05 | 1 | 323 | Planned | Planned interruption | Red Tag pole replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 76 | ACD125 | 3ph ICP fed from p#28301 | Hadlow | 2024-04-16 09:00 | 2024-04-16 14:32 | 0.0097866 | 2.9478e-05 | 1 | 332 | Planned | Planned interruption | Red Tag pole replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 77 | ACD125 | ICPs fed from P#28301-3ph ICP fed from pole #28301 | Hadlow | 2024-04-16 09:00 | 2024-04-16 14:50 | 0.020634 | 5.8955e-05 | 2 | 700 | Planned | Planned interruption | Red Tag pole replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 78 | 5062 | RGA CB4-ABS T415 | Old Main South Road | 2024-04-16 15:55 | 2024-04-16 16:33 | 0.082891 | 0.0021813 | 74 | 2812 | Unplanned | Defective equipment | Fault - Broken conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 79 | 5062 | ABS T415 | Old Main South Road | 2024-04-16 15:55 | 2024-04-16 19:12 | 0.11614 | 0.00058955 | 20 | 3940 | Unplanned | Defective equipment | Fault Broken conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 80 | HTR001 | ABS G204-ABS TX38 | Speechley | 2024-04-17 08:00 | 2024-04-17 13:11 | 0.38504 | 0.0012381 | 42 | 13062 | Planned | Planned interruption | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 81 | ACD118 | TX A1038 | Morven | 2024-04-17 08:05 | 2024-04-17 17:11 | 0.016095 | 2.9478e-05 | 1 | 546 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 82 | ACD118 | TX A297 | Morven | 2024-04-17 08:05 | 2024-04-17 17:22 | 0.032838 | 5.8955e-05 | 2 | 1114 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 83 | ACD118 | TX A531 | Morven | 2024-04-17 08:05 | 2024-04-17 17:12 | 0.016124 | 2.9478e-05 | 1 | 547 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 84 | ACD118 | ABS W112-Temp links pole 54387-TX A1038-TX A297-TX A531 | Morven | 2024-04-17 08:05 | 2024-04-17 16:49 | 0.13902 | 0.0002653 | 9 | 4716 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 85 | HTR003 | Fuses T217 | Waitohi | 2024-04-18 08:00 | 2024-04-18 09:54 | 0.07057 | 0.00061903 | 21 | 2394 | Planned | Planned interruption | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 86 | ACD123 | TX A94 | Otaio | 2024-04-18 08:30 | 2024-04-18 16:55 | 0.029772 | 5.8955e-05 | 2 | 1010 | Planned | Planned interruption | Red Tag Pole replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 87 | ACD123 | Fuses W316-TX A94 | Otaio | 2024-04-18 08:30 | 2024-04-18 16:37 | 0.15791 | 0.00032425 | 11 | 5357 | Planned | Planned interruption | Red Tag Pole replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 88 | SKE1684 | TX B992 | Morgans Rd | 2024-04-18 09:00 | 2024-04-18 15:54 | 0.085426 | 0.00020634 | 7 | 2898 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 89 | SKE1684 | B960 CCT3 | Morgans Rd | 2024-04-18 09:00 | 2024-04-18 15:43 | 0.11879 | 0.00029478 | 10 | 4030 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 90 | SKE1684 | B960 CCT2 | Morgans Rd | 2024-04-18 09:00 | 2024-04-18 15:43 | 0.10692 | 0.0002653 | 9 | 3627 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 91 | SKE1684 | B1021 CCT5 | Morgans Rd | 2024-04-18 09:00 | 2024-04-18 15:43 | 0.15443 | 0.00038321 | 13 | 5239 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 92 | SKE1684 | B1021 CCT4 | Morgans Rd | 2024-04-18 09:00 | 2024-04-18 15:43 | 0.16631 | 0.00041269 | 14 | 5642 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 93 | SKE1684 | B1021 CCT3 | Morgans Rd | 2024-04-18 09:00 | 2024-04-18 15:42 | 0.2133 | 0.0005306 | 18 | 7236 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 94 | SKE1684 | B1097 CCT5 | Morgans Rd | 2024-04-18 09:00 | 2024-04-18 15:50 | 0.24172 | 0.00058955 | 20 | 8200 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 95 | SKE1684 | B1097 CCT3 | Morgans Rd | 2024-04-18 09:00 | 2024-04-18 15:50 | 0.1692 | 0.00041269 | 14 | 5740 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 96 | SKE1684 | B1097 CCT4 | Morgans Rd | 2024-04-18 09:00 | 2024-04-18 15:50 | 0.15712 | 0.00038321 | 13 | 5330 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 97 | 5032 | T325 | Speechley | 2024-04-18 12:30 | 2024-04-18 14:20 | 0.058366 | 0.0005306 | 18 | 1980 | Unplanned | Defective equipment | Conductor Repairs at Pole #09713 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 98 | HTR004 | Fuses T309 | Waitohi | 2024-04-18 13:00 | 2024-04-18 14:55 | 0.071189 | 0.00061903 | 21 | 2415 | Planned | Planned interruption | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 99 | 4402 | T127 | Rangitata | 2024-04-18 17:00 | 2024-04-18 19:09 | 0.28139 | 0.0021813 | 74 | 9546 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 100 | 5063 | TX B1553 | Arowhenua | 2024-04-19 08:13 | 2024-04-19 15:42 | 0.026471 | 5.8955e-05 | 2 | 898 | Unplanned | Defective equipment | Faulty TX replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 101 | ACD124 | Links W440 | Otaio | 2024-04-19 08:30 | 2024-04-19 14:03 | 0.098161 | 0.00029478 | 10 | 3330 | Planned | Planned interruption | Red Tag Pole replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 102 | 5063 | Fuses L879-TX B1553 | Arowhenua | 2024-04-19 13:53 | 2024-04-19 15:34 | 0.026795 | 0.0002653 | 9 | 909 | Unplanned | Defective equipment | Faulty TX replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 103 | 4403 | W527 - TO A969 | Waikakahi | 2024-04-21 15:40 | 2024-04-21 16:52 | 0.0084896 | 0.00011791 | 4 | 288 | Unplanned | Defective equipment | Replace Faulty Tx A969 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 104 | 4403 | TO A969 | Waikakahi | 2024-04-21 15:40 | 2024-04-21 17:17 | 0.0028593 | 2.9478e-05 | 1 | 97 | Unplanned | Defective equipment | Replace Faulty Tx A969 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 105 | 5038 | Fuses TO C464 | Fairlie Rural | 2024-04-22 15:57 | 2024-04-22 17:03 | 0.0019455 | 2.9478e-05 | 1 | 66 | Unplanned | Defective equipment | Broken Stay | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 106 | ACD119 | Pole 54387 temp links-Links W363-TX A483 | Morven | 2024-04-23 08:00 | 2024-04-23 16:37 | 0.74676 | 0.0014444 | 49 | 25333 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 107 | ACD119 | TX A483 | Morven | 2024-04-23 08:00 | 2024-04-23 17:00 | 0.063672 | 0.00011791 | 4 | 2160 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 108 | GWM1148 | Fuses L827 | Hadlow | 2024-04-23 09:00 | 2024-04-23 11:53 | 0.18869 | 0.0010907 | 37 | 6401 | Planned | Planned interruption | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 109 | SRT200 | Fuses G245 | Speechley | 2024-04-24 08:30 | 2024-04-24 14:28 | 0.1583 | 0.00044216 | 15 | 5370 | Planned | Planned interruption | New TX | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 110 | 5035 | F179 | Fairlie Rural | 2024-04-24 16:55 | 2024-04-24 17:35 | 0.0058955 | 0.00014739 | 5 | 200 | Unplanned | Defective equipment | Replace missing nut on P#10916 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 111 | 5037 | Fuses F220 | Fairlie Rural | 2024-04-25 10:39 | 2024-04-25 13:49 | 0.12322 | 0.00064851 | 22 | 4180 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 112 | 5036 | W664 - W263 | Waihaorunga | 2024-04-25 11:15 | 2024-04-25 11:36 | 0.095331 | 0.0045396 | 154 | 3234 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 113 | 5036 | W263 - W258 | Waihaorunga | 2024-04-25 11:15 | 2024-04-25 11:45 | 0.29537 | 0.0098455 | 334 | 10020 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 114 | 5036 | W258 - W708 | Waihaorunga | 2024-04-25 11:15 | 2024-04-25 11:54 | 0.067828 | 0.0017392 | 59 | 2301 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 115 | 5036 | W708 | Waihaorunga | 2024-04-25 11:15 | 2024-04-25 12:05 | 0.37142 | 0.0074284 | 252 | 12600 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 116 | 5034 | T598 | Speechley | 2024-04-25 13:12 | 2024-04-25 16:21 | 0.011143 | 5.8955e-05 | 2 | 378 | Unplanned | Adverse weather | Strong Wind - Part of roof on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 117 | 5033 | W674 | Otaio | 2024-04-25 15:00 | 2024-04-25 16:04 | 0.018866 | 0.00029478 | 10 | 640 | Unplanned | Adverse weather | Strong Wind - Tree branch on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 118 | 4404 | W291 - W653 | Morven | 2024-04-26 14:43 | 2024-04-26 16:06 | 0.10031 | 0.0012086 | 41 | 3403 | Unplanned | Defective equipment | Broken Jumper @ Links W742 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 119 | SKE1731 | DB H107 | Church Street South Side | 2024-04-30 07:30 | 2024-04-30 18:44 | 0.35762 | 0.0005306 | 18 | 12132 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 120 | SKE1731 | DB H95 | Church Street South Side | 2024-04-30 07:30 | 2024-04-30 19:07 | 0.12328 | 0.00017687 | 6 | 4182 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 121 | SKE1731 | DB H94 | Church Street South Side | 2024-04-30 07:30 | 2024-04-30 18:55 | 0.080769 | 0.00011791 | 4 | 2740 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 122 | SKE1731 | TE87 CCT17 | Church Street South Side | 2024-04-30 07:30 | 2024-04-30 18:33 | 0.42996 | 0.00064851 | 22 | 14586 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 123 | SKE1731 | TE87-TE87 CCT17-DB H94-DB H95-DB H107 | Church Street South Side | 2024-04-30 07:30 | 2024-04-30 18:05 | 0.7113 | 0.0011202 | 38 | 24130 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 124 | SKE1731 | 24 BRUNSWICK ST | Church Street South Side | 2024-04-30 07:30 | 2024-04-30 18:08 | 0.018807 | 2.9478e-05 | 1 | 638 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 125 | SKE1731 | 24 GIBSON ST | Church Street South Side | 2024-04-30 07:30 | 2024-04-30 18:07 | 0.018777 | 2.9478e-05 | 1 | 637 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 126 | SKE1731 | 82 CHURCH ST | Church Street South Side | 2024-04-30 07:30 | 2024-04-30 18:04 | 0.018689 | 2.9478e-05 | 1 | 634 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 127 | SKE1731 | HNT CB7-82 CHURCH-24 GIBSON-24 BRUNSWICK-TE87-TE20 | Church Street South Side | 2024-04-30 07:30 | 2024-04-30 17:56 | 2.3066 | 0.0036847 | 125 | 78250 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 128 | SRT201 | Temp links pole 26443 | Sutherland | 2024-04-30 09:00 | 2024-04-30 15:08 | 0.065087 | 0.00017687 | 6 | 2208 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 129 | 5064 | TX D1067 | Woodbury | 2024-04-30 09:11 | 2024-04-30 09:18 | 0.0022698 | 0.00032425 | 11 | 77 | Unplanned | Vegetation | Branch on LV line removal | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 130 | ACD121 | TX A296 | Morven | 2024-05-01 08:00 | 2024-05-01 17:40 | 0.017097 | 2.9478e-05 | 1 | 580 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 131 | ACD121 | Fuses W656 | Morven | 2024-05-01 08:00 | 2024-05-01 17:41 | 0.23977 | 0.00041269 | 14 | 8134 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 132 | ACD121 | Fuses W655 | Morven | 2024-05-01 08:00 | 2024-05-01 17:37 | 0.23812 | 0.00041269 | 14 | 8078 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 133 | ACD121 | ABS W496 | Morven | 2024-05-01 08:00 | 2024-05-01 17:35 | 0.033899 | 5.8955e-05 | 2 | 1150 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 134 | ACD121 | TX A552 | Morven | 2024-05-01 08:00 | 2024-05-01 17:32 | 0.016861 | 2.9478e-05 | 1 | 572 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 135 | ACD121 | TX A529 | Morven | 2024-05-01 08:00 | 2024-05-01 17:45 | 0.18969 | 0.00032425 | 11 | 6435 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 136 | ACD121 | TX A283 | Morven | 2024-05-01 08:00 | 2024-05-01 17:41 | 0.068506 | 0.00011791 | 4 | 2324 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 137 | ACD121 | Fuses W164 | Morven | 2024-05-01 08:00 | 2024-05-01 17:36 | 0.3226 | 0.00056008 | 19 | 10944 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 138 | ACD121 | ABS W299 | Morven | 2024-05-01 08:00 | 2024-05-01 17:30 | 0.033605 | 5.8955e-05 | 2 | 1140 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 139 | ACD121 | TX A803 | Morven | 2024-05-01 08:00 | 2024-05-01 17:25 | 0.016655 | 2.9478e-05 | 1 | 565 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 140 | ACD121 | Links W279-Temp Links Pole 38954-TX A803-ABS W299-Fuses W164-TX A283-TX A529-TX A552-ABS W496-Fuses W655-Fuses W656-TX A296 | Morven | 2024-05-01 08:00 | 2024-05-01 17:21 | 0.049611 | 8.8433e-05 | 3 | 1683 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 141 | SKE1732 | DB H93 | Church Street South Side | 2024-05-01 08:00 | 2024-05-01 17:20 | 0.14857 | 0.0002653 | 9 | 5040 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 142 | SKE1732 | DB H92 | Church Street South Side | 2024-05-01 08:00 | 2024-05-01 17:08 | 0.14538 | 0.0002653 | 9 | 4932 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 143 | SKE1732 | DB H108 service | Church Street South Side | 2024-05-01 08:00 | 2024-05-01 17:13 | 0.016301 | 2.9478e-05 | 1 | 553 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 144 | SKE1732 | TE87 CCT15 | Church Street South Side | 2024-05-01 08:00 | 2024-05-01 16:57 | 0.17412 | 0.00032425 | 11 | 5907 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 145 | 5065 | ABS T493 | Rolleston Road | 2024-05-01 09:44 | 2024-05-01 12:53 | 0.87469 | 0.004628 | 157 | 29673 | Unplanned | Defective equipment | ABS Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 146 | 5066 | TMK CB2-ABS T116-ABS T125 | Milford | 2024-05-01 15:11 | 2024-05-01 17:36 | 0.29065 | 0.0020045 | 68 | 9860 | Unplanned | Defective equipment | ABS Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 147 | ACD120 | TX A892 | Morven | 2024-05-02 08:00 | 2024-05-02 16:25 | 0.029772 | 5.8955e-05 | 2 | 1010 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 148 | ACD120 | ABS W112-Temp links pole 54387-TX A892 | Morven | 2024-05-02 08:00 | 2024-05-02 16:20 | 0.16213 | 0.00032425 | 11 | 5500 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 149 | JDJ080 | TX B260-233 Kerrytown Rd-240 Kerrytown Rd | Waitawa | 2024-05-02 08:33 | 2024-05-02 10:26 | 0.003331 | 2.9478e-05 | 1 | 113 | Planned | Planned interruption | Change TX from 1ph to 2ph | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 150 | JDJ080 | 233 Kerrytown Rd | Waitawa | 2024-05-02 08:33 | 2024-05-02 10:28 | 0.0033899 | 2.9478e-05 | 1 | 115 | Planned | Planned interruption | Change TX from 1ph to 2ph | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 151 | JDJ080 | 240 Kerrytown Rd | Waitawa | 2024-05-02 08:33 | 2024-05-02 11:10 | 0.004628 | 2.9478e-05 | 1 | 157 | Planned | Planned interruption | Change TX from 1ph to 2ph | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 152 | ACD122/GWM1144 | TX A1038 | Morven | 2024-05-03 08:00 | 2024-05-03 17:46 | 0.017274 | 2.9478e-05 | 1 | 586 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 153 | ACD122/GWM1144 | TX A1539 | Morven | 2024-05-03 08:00 | 2024-05-03 17:40 | 0.017097 | 2.9478e-05 | 1 | 580 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 154 | ACD122/GWM1144 | TX A835 | Morven | 2024-05-03 08:00 | 2024-05-03 17:36 | 0.033958 | 5.8955e-05 | 2 | 1152 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 155 | ACD122/GWM1144 | Fuses W656 | Morven | 2024-05-03 08:00 | 2024-05-03 17:47 | 0.24225 | 0.00041269 | 14 | 8218 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 156 | ACD122/GWM1144 | Fuses W655 | Morven | 2024-05-03 08:00 | 2024-05-03 17:44 | 0.24101 | 0.00041269 | 14 | 8176 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 157 | ACD122/GWM1144 | ABS W496 | Morven | 2024-05-03 08:00 | 2024-05-03 17:42 | 0.034312 | 5.8955e-05 | 2 | 1164 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 158 | ACD122/GWM1144 | TX A552 | Morven | 2024-05-03 08:00 | 2024-05-03 17:36 | 0.033958 | 5.8955e-05 | 2 | 1152 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 159 | ACD122/GWM1144 | TX A529 | Morven | 2024-05-03 08:00 | 2024-05-03 17:47 | 0.19034 | 0.00032425 | 11 | 6457 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 160 | ACD122/GWM1144 | TX A283 | Morven | 2024-05-03 08:00 | 2024-05-03 17:45 | 0.068978 | 0.00011791 | 4 | 2340 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 161 | ACD122/GWM1144 | Fuses W164 | Morven | 2024-05-03 08:00 | 2024-05-03 17:43 | 0.32652 | 0.00056008 | 19 | 11077 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 162 | ACD122/GWM1144 | ABS W299 | Morven | 2024-05-03 08:00 | 2024-05-03 17:40 | 0.034194 | 5.8955e-05 | 2 | 1160 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 163 | ACD122/GWM1144 | TX A803 | Morven | 2024-05-03 08:00 | 2024-05-03 17:35 | 0.01695 | 2.9478e-05 | 1 | 575 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 164 | ACD122/GWM1144 | ABS W190-CB W245-TX A803-ABS W299-Fuses W164-TX A283-TX A529-TX A552-ABS W496-Fuses W655-Fuses W656-TX A835-TX A1539-TX A1038 | Morven | 2024-05-03 08:00 | 2024-05-03 17:32 | 1.1971 | 0.0020929 | 71 | 40612 | Planned | Planned interruption | Crowes Rd Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 165 | SRT202/GWM1152 | ABS W264 | Morven | 2024-05-03 09:00 | 2024-05-03 13:58 | 0.24596 | 0.00082537 | 28 | 8344 | Planned | Planned interruption | Red tag pole replacement & Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 166 | 5119 | CB T127 to end minus T404, TX62, T667 & TX62 | Rangitata | 2024-05-05 20:53 | 2024-05-05 22:18 | 0.080179 | 0.00094328 | 32 | 2720 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 167 | 5119 | TX62 to end | Rangitata | 2024-05-05 20:53 | 2024-05-05 22:34 | 0.026795 | 0.0002653 | 9 | 909 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 168 | 5119 | TX66 to end | Rangitata | 2024-05-05 20:53 | 2024-05-05 22:39 | 0.037496 | 0.00035373 | 12 | 1272 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 169 | 5119 | T667 to end | Rangitata | 2024-05-05 20:53 | 2024-05-05 22:52 | 0.028063 | 0.00023582 | 8 | 952 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 170 | 5119 | T404 to end | Rangitata | 2024-05-05 20:53 | 2024-05-05 23:23 | 0.057481 | 0.00038321 | 13 | 1950 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 171 | ACD126 | TX D217 | Rolleston Road | 2024-05-06 09:40 | 2024-05-06 14:30 | 0.017097 | 5.8955e-05 | 2 | 580 | Planned | Planned interruption | Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 172 | JDJ073 | TX D899 CCT3 | Temuka East | 2024-05-06 10:44 | 2024-05-06 16:29 | 0.37628 | 0.0010907 | 37 | 12765 | Planned | Planned interruption | LV Fuse work | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 173 | JDJ073 | TX D899 CCT2 | Temuka East | 2024-05-06 10:44 | 2024-05-06 15:57 | 0.1384 | 0.00044216 | 15 | 4695 | Planned | Planned interruption | LV fuse work | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 174 | JDJ081 | TX D142 | Waitohi | 2024-05-07 08:30 | 2024-05-07 16:53 | 0.014827 | 2.9478e-05 | 1 | 503 | Planned | Planned interruption | Red Tagged Pole replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 175 | JDJ081 | Fuses T305-TX D142 | Waitohi | 2024-05-07 08:30 | 2024-05-07 16:38 | 0.14385 | 0.00029478 | 10 | 4880 | Planned | Planned interruption | Red Tagged Pole replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 176 | SKE1626 | TX D1393 | Old Main South Road | 2024-05-07 09:18 | 2024-05-07 17:10 | 0.04174 | 8.8433e-05 | 3 | 1416 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 177 | 4405 | TO A1419 | St Andrews | 2024-05-07 11:13 | 2024-05-07 15:58 | 0.0084011 | 2.9478e-05 | 1 | 285 | Unplanned | Third party interference | Lines down - caused by logger truck | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 178 | ACD127 | TX A65 | St Andrews | 2024-05-08 09:00 | 2024-05-08 16:55 | 0.014002 | 2.9478e-05 | 1 | 475 | Planned | Planned interruption | Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 179 | ACD127 | Fuses W460-TX A65 | St Andrews | 2024-05-08 09:00 | 2024-05-08 16:35 | 0.040237 | 8.8433e-05 | 3 | 1365 | Planned | Planned interruption | Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 180 | SKE1671 | TX B1348 | Mountainview | 2024-05-08 09:02 | 2024-05-08 14:10 | 0.29053 | 0.00094328 | 32 | 9856 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 181 | 5039 | TO A48 | St Andrews | 2024-05-08 14:57 | 2024-05-08 15:02 | 0.00029478 | 5.8955e-05 | 2 | 10 | Unplanned | Defective equipment | Remove broken Stay @ P#29044 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 182 | 988 | CB F295 | Cave | 2024-05-08 15:46 | 2024-05-08 16:58 | 0.070039 | 0.00097276 | 33 | 2376 | Unplanned | Adverse weather | Strong winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 183 | 989 | Fuses G174 | Winchester | 2024-05-08 16:17 | 2024-05-08 17:40 | 0.046486 | 0.00056008 | 19 | 1577 | Unplanned | Vegetation | Branch on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 184 | SKE1687 | TX D1274 | Milford | 2024-05-09 09:32 | 2024-05-09 15:06 | 0.039382 | 0.00011791 | 4 | 1336 | Planned | Planned interruption | Defect repairs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 185 | RAK138 | ABS T234 | Temuka West | 2024-05-11 08:04 | 2024-05-11 17:08 | 0.016036 | 2.9478e-05 | 1 | 544 | Planned | Planned interruption | NZI Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 186 | 5018 | ABS M26 | Haldon-Lilybank 22kV | 2024-05-11 12:10 | 2024-05-11 13:54 | 0.076642 | 0.00073694 | 25 | 2600 | Unplanned | Third party interference | Broken Pole #23795 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 187 | ACD128 | ABS F273 | Fairlie Rural | 2024-05-13 08:00 | 2024-05-13 08:03 | 0.0014149 | 0.00047164 | 16 | 48 | Planned | Planned interruption | Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 188 | ACD128 | ABS F255-ABS F277-ABS F273-TX C100 | Fairlie Rural | 2024-05-13 08:30 | 2024-05-13 14:22 | 0.22827 | 0.00064851 | 22 | 7744 | Planned | Planned interruption | Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 189 | ACD128 | TX C100 | Fairlie Rural | 2024-05-13 08:30 | 2024-05-13 14:33 | 0.032101 | 8.8433e-05 | 3 | 1089 | Planned | Planned interruption | Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 190 | ACD128 | ABS F273 | Fairlie Rural | 2024-05-13 17:15 | 2024-05-13 17:17 | 0.00094328 | 0.00047164 | 16 | 32 | Planned | Planned interruption | Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 191 | 4406 | CB11 - T586 | Belfield | 2024-05-14 15:17 | 2024-05-14 16:25 | 0.13831 | 0.002034 | 69 | 4692 | Unplanned | Third party interference | Car v Pole #10556 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 192 | 4406 | T585 | Belfield | 2024-05-14 15:17 | 2024-05-14 16:33 | 0.087372 | 0.0011496 | 39 | 2964 | Unplanned | Third party interference | Car v Pole #10556 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 193 | 4406 | T584 | Belfield | 2024-05-14 15:17 | 2024-05-14 16:45 | 0.046693 | 0.0005306 | 18 | 1584 | Unplanned | Third party interference | Car v Pole #10556 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 194 | 4406 | T586 - T585 - T584 | Belfield | 2024-05-14 15:17 | 2024-05-14 18:39 | 0.047636 | 0.00023582 | 8 | 1616 | Unplanned | Third party interference | Car v Pole #10556 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 195 | 4406 | T584 | Belfield | 2024-05-14 19:10 | 2024-05-14 19:12 | 0.0010612 | 0.0005306 | 18 | 36 | Unplanned | Third party interference | Car v Pole #10556 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 196 | 4407 | W685 | Otaio | 2024-05-15 07:35 | 2024-05-15 07:36 | 0.0018571 | 0.0018571 | 63 | 63 | Unplanned | Unknown | Load transfer from STU to PAR | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 197 | 4407 | W315 - W685 | Otaio | 2024-05-15 07:43 | 2024-05-15 07:43 | 0 | 0.0010317 | 35 | 0 | Unplanned | Unknown | Load transfer from STU to PAR | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 198 | SKE1664A | TX B1046 CCT6 | Mountainview | 2024-05-15 09:00 | 2024-05-15 15:27 | 0.13689 | 0.00035373 | 12 | 4644 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 199 | SKE1664A | TX B1046 CCT5-LB29 | Mountainview | 2024-05-15 09:00 | 2024-05-15 15:26 | 0.091027 | 0.00023582 | 8 | 3088 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 200 | SKE1664A | TX B1046 CCT4 | Mountainview | 2024-05-15 09:00 | 2024-05-15 15:26 | 0.1593 | 0.00041269 | 14 | 5404 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 201 | SKE1664A | TX B1046 CCT3 | Mountainview | 2024-05-15 09:00 | 2024-05-15 15:25 | 0.23833 | 0.00061903 | 21 | 8085 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 202 | SKE1664A | TX B1046 CCT2 | Mountainview | 2024-05-15 09:00 | 2024-05-15 15:17 | 0.14447 | 0.00038321 | 13 | 4901 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 203 | ACD132 | TX C116 | Cave | 2024-05-15 09:31 | 2024-05-15 13:38 | 0.014562 | 5.8955e-05 | 2 | 494 | Planned | Planned interruption | TX Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 204 | ACD132 | Fuses F130 | Cave | 2024-05-15 09:31 | 2024-05-15 13:00 | 0.067769 | 0.00032425 | 11 | 2299 | Planned | Planned interruption | TX Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 205 | JDJ084 | TX A515 | Mt Studholme | 2024-05-16 10:00 | 2024-05-16 11:23 | 0.0024466 | 2.9478e-05 | 1 | 83 | Planned | Planned interruption | TX Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 206 | 3790 | T644 | Arundel | 2024-05-16 19:57 | 2024-05-16 21:41 | 0.009197 | 8.8433e-05 | 3 | 312 | Unplanned | Defective equipment | Broken jumper to Fuses T644 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 207 | 3790 | T448 - T644 | Arundel | 2024-05-16 21:08 | 2024-05-16 21:41 | 0.041829 | 0.0012675 | 43 | 1419 | Unplanned | Defective equipment | Broken jumper to Fuses T644 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 208 | 5019 | CB T626 | Rolleston Road | 2024-05-17 19:14 | 2024-05-17 20:43 | 0.4906 | 0.0055123 | 187 | 16643 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 209 | ACD129 | TX B1994 | Holme Station | 2024-05-20 08:30 | 2024-05-20 15:58 | 0.013206 | 2.9478e-05 | 1 | 448 | Planned | Planned interruption | Red Tag Pole replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 210 | ACD129 | ABS L123-ABS L126-TX B1994 | Holme Station | 2024-05-20 08:30 | 2024-05-20 15:50 | 0.33722 | 0.00076642 | 26 | 11440 | Planned | Planned interruption | Red Tag Pole replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 211 | SKE1755 | TE140 CCT15-LB H24 to H253 | Le Cren Street | 2024-05-20 18:15 | 2024-05-20 18:21 | 0.0005306 | 8.8433e-05 | 3 | 18 | Planned | Planned interruption | TE140 Maintenenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 212 | SKE1755 | TE149 CCT14 | Le Cren Street | 2024-05-20 18:15 | 2024-05-20 18:26 | 0.0022698 | 0.00020634 | 7 | 77 | Planned | Planned interruption | TE140 Maintenenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 213 | SKE1755 | TE140 CCT18-DB H27 | Le Cren Street | 2024-05-20 18:15 | 2024-05-20 18:24 | 0.0015918 | 0.00017687 | 6 | 54 | Planned | Planned interruption | TE140 Maintenenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 214 | SKE1755 | TE140 CCT17 | Le Cren Street | 2024-05-20 18:15 | 2024-05-20 18:29 | 0.0016507 | 0.00011791 | 4 | 56 | Planned | Planned interruption | TE140 Maintenenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 215 | SKE1755 | TE140 CCT14 | Le Cren Street | 2024-05-20 18:15 | 2024-05-20 23:46 | 0.029271 | 8.8433e-05 | 3 | 993 | Planned | Planned interruption | TE140 Maintenenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 216 | SKE1755 | TE140 CCT18-DB H27 | Le Cren Street | 2024-05-20 23:33 | 2024-05-20 23:46 | 0.0022993 | 0.00017687 | 6 | 78 | Planned | Planned interruption | TE140 Maintenenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 217 | SKE1755 | TE140 CCT17 | Le Cren Street | 2024-05-20 23:34 | 2024-05-20 23:46 | 0.0014149 | 0.00011791 | 4 | 48 | Planned | Planned interruption | TE140 Maintenenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 218 | SKE1755 | TE140 CCT14 | Le Cren Street | 2024-05-20 23:38 | 2024-05-20 23:46 | 0.00070746 | 8.8433e-05 | 3 | 24 | Planned | Planned interruption | TE140 Maintenenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 219 | SKE1755 | TE140 CCT15-LB H24 to H253 | Le Cren Street | 2024-05-20 23:39 | 2024-05-20 23:46 | 0.00061903 | 8.8433e-05 | 3 | 21 | Planned | Planned interruption | TE140 Maintenenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 220 | SKE1735 | 69 The Avenue | Normanby | 2024-05-21 08:30 | 2024-05-21 15:57 | 0.013177 | 2.9478e-05 | 1 | 447 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 221 | SKE1735 | 70 The Avenue | Normanby | 2024-05-21 08:30 | 2024-05-21 15:48 | 0.012911 | 2.9478e-05 | 1 | 438 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 222 | SKE1735 | 72 The Avenue | Normanby | 2024-05-21 08:30 | 2024-05-21 15:47 | 0.012882 | 2.9478e-05 | 1 | 437 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 223 | SKE1735 | 74 The Avenue | Normanby | 2024-05-21 08:30 | 2024-05-21 15:34 | 0.012499 | 2.9478e-05 | 1 | 424 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 224 | SKE1735 | TX B45 CCT2-69,70,72,74 The Avenue | Normanby | 2024-05-21 08:30 | 2024-05-21 15:27 | 0.086045 | 0.00020634 | 7 | 2919 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 225 | SKE1735 | 12 Abbott Street | Normanby | 2024-05-21 08:30 | 2024-05-21 15:48 | 0.012911 | 2.9478e-05 | 1 | 438 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 226 | SKE1735 | TX B45 CCT4-12 Abbott Street | Normanby | 2024-05-21 08:30 | 2024-05-21 15:46 | 0.025705 | 5.8955e-05 | 2 | 872 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 227 | SKE1735 | 60 The Avenue | Normanby | 2024-05-21 08:30 | 2024-05-21 15:42 | 0.012734 | 2.9478e-05 | 1 | 432 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 228 | SKE1735 | 61 The Avenue | Normanby | 2024-05-21 08:30 | 2024-05-21 15:40 | 0.012675 | 2.9478e-05 | 1 | 430 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 229 | SKE1735 | 63 The Avenue | Normanby | 2024-05-21 08:30 | 2024-05-21 15:38 | 0.012616 | 2.9478e-05 | 1 | 428 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 230 | SKE1735 | TX B45 CCT3-60,61,63 The Avenue | Normanby | 2024-05-21 08:30 | 2024-05-21 15:35 | 0.78926 | 0.0018571 | 63 | 26775 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 231 | SKE1735 | Links L112-Links LL063-TX B45 | Normanby | 2024-05-21 08:30 | 2024-05-21 15:17 | 0.14397 | 0.00035373 | 12 | 4884 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 232 | GWM1160 | ABS G116 | Winchester | 2024-05-21 09:00 | 2024-05-21 11:53 | 0.16829 | 0.00097276 | 33 | 5709 | Planned | Planned interruption | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 233 | 4408 | F203 | Raincliff | 2024-05-21 10:54 | 2024-05-21 11:45 | 0.015034 | 0.00029478 | 10 | 510 | Unplanned | Defective equipment | Broken surge arrestor @ P#51963 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 234 | SKE1736 | Links L112-Links LL063-74,75,76,77,78,79,82,83 The Avenue | Normanby | 2024-05-22 08:30 | 2024-05-22 15:24 | 1.0129 | 0.0024466 | 83 | 34362 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 235 | SKE1736 | 74 The Avenue | Normanby | 2024-05-22 08:30 | 2024-05-22 15:38 | 0.012616 | 2.9478e-05 | 1 | 428 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 236 | SKE1736 | 75 The Avenue | Normanby | 2024-05-22 08:30 | 2024-05-22 15:41 | 0.012705 | 2.9478e-05 | 1 | 431 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 237 | SKE1736 | 76 The Avenue | Normanby | 2024-05-22 08:30 | 2024-05-22 15:40 | 0.012675 | 2.9478e-05 | 1 | 430 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 238 | SKE1736 | 77 The Avenue | Normanby | 2024-05-22 08:30 | 2024-05-22 15:42 | 0.012734 | 2.9478e-05 | 1 | 432 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 239 | SKE1736 | 78 The Avenue | Normanby | 2024-05-22 08:30 | 2024-05-22 15:41 | 0.012705 | 2.9478e-05 | 1 | 431 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 240 | SKE1736 | 79 The Avenue | Normanby | 2024-05-22 08:30 | 2024-05-22 15:48 | 0.012911 | 2.9478e-05 | 1 | 438 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 241 | SKE1736 | 82 The Avenue | Normanby | 2024-05-22 08:30 | 2024-05-22 15:32 | 0.01244 | 2.9478e-05 | 1 | 422 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 242 | SKE1736 | 83 The Avenue | Normanby | 2024-05-22 08:30 | 2024-05-22 15:36 | 0.012557 | 2.9478e-05 | 1 | 426 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 243 | SKE1736 | 73 The Avenue | Normanby | 2024-05-22 08:30 | 2024-05-22 15:35 | 0.012528 | 2.9478e-05 | 1 | 425 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 244 | 5020 | Fuses W266 | Morven | 2024-05-23 19:00 | 2024-05-23 21:44 | 0.043509 | 0.0002653 | 9 | 1476 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 245 | 5068 | W307 | Otaio | 2024-05-25 17:56 | 2024-05-25 19:37 | 0.020841 | 0.00020634 | 7 | 707 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 246 | SKE1757 | TX D1705 | Temuka East | 2024-05-26 09:00 | 2024-05-26 14:43 | 0.010111 | 2.9478e-05 | 1 | 343 | Planned | Planned interruption | Repair TX oil leak | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 247 | SKE1753 | TX B2119 CCT2 | Levels Plain | 2024-05-26 09:00 | 2024-05-26 14:11 | 0.091676 | 0.00029478 | 10 | 3110 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 248 | SKE1753 | TX B2119 CCT3 | Levels Plain | 2024-05-26 09:00 | 2024-05-26 14:11 | 0.055005 | 0.00017687 | 6 | 1866 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 249 | SKE1753 | TX B2119 CCT4 | Levels Plain | 2024-05-26 09:00 | 2024-05-26 14:11 | 0.0091676 | 2.9478e-05 | 1 | 311 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 250 | SKE1753 | TX B2119 ICP | Levels Plain | 2024-05-26 09:00 | 2024-05-26 14:12 | 0.009197 | 2.9478e-05 | 1 | 312 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 251 | 5067 | W101 | Morven | 2024-05-26 17:52 | 2024-05-26 19:12 | 0.018866 | 0.00023582 | 8 | 640 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 252 | 5041 | W742 | Morven | 2024-05-27 06:32 | 2024-05-27 11:17 | 0.10921 | 0.00038321 | 13 | 3705 | Unplanned | Defective equipment | Broken Jumper @ Links W742 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 253 | 5041 | W291 - W653 - W742 | Morven | 2024-05-27 09:49 | 2024-05-27 11:17 | 0.072633 | 0.00082537 | 28 | 2464 | Unplanned | Defective equipment | Broken Jumper @ Links W742 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 254 | HTR009 | ABS W482 | Morven | 2024-05-28 08:00 | 2024-05-28 16:19 | 0.29419 | 0.00058955 | 20 | 9980 | Planned | Planned interruption | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 255 | SKE1738 | Links L112-Links LL063-60,61,63 The Avenue | Normanby | 2024-05-28 08:41 | 2024-05-28 13:07 | 0.20387 | 0.00076642 | 26 | 6916 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 256 | SKE1738 | 60 The Avenue | Normanby | 2024-05-28 08:41 | 2024-05-28 14:02 | 0.0094623 | 2.9478e-05 | 1 | 321 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 257 | SKE1738 | 61 The Avenue | Normanby | 2024-05-28 08:41 | 2024-05-28 14:01 | 0.0094328 | 2.9478e-05 | 1 | 320 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 258 | SKE1738 | 63 The Avenue | Normanby | 2024-05-28 08:41 | 2024-05-28 13:15 | 0.0080769 | 2.9478e-05 | 1 | 274 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 259 | SKE1738 | TX B45 CCT3-60,61,63 The Avenue | Normanby | 2024-05-28 08:41 | 2024-05-28 13:13 | 0.50513 | 0.0018571 | 63 | 17136 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 260 | HTR007 | Fuses F145 | Cave | 2024-05-28 09:00 | 2024-05-28 13:07 | 0.12378 | 0.00050112 | 17 | 4199 | Planned | Planned interruption | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 261 | SKE1739 | Links L112-Links LL063-69,70,71,72,73,74,75,76,77,78 The Avenue | Normanby | 2024-05-29 08:33 | 2024-05-29 14:55 | 0.92336 | 0.0024172 | 82 | 31324 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 262 | SKE1739 | 69 The Avenue | Normanby | 2024-05-29 08:33 | 2024-05-29 15:08 | 0.011644 | 2.9478e-05 | 1 | 395 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 263 | SKE1739 | 70 The Avenue | Normanby | 2024-05-29 08:33 | 2024-05-29 15:09 | 0.011673 | 2.9478e-05 | 1 | 396 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 264 | SKE1739 | 71 The Avenue | Normanby | 2024-05-29 08:33 | 2024-05-29 15:12 | 0.011762 | 2.9478e-05 | 1 | 399 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 265 | SKE1739 | 72 The Avenue | Normanby | 2024-05-29 08:33 | 2024-05-29 15:10 | 0.011703 | 2.9478e-05 | 1 | 397 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 266 | SKE1739 | 73 The Avenue | Normanby | 2024-05-29 08:33 | 2024-05-29 15:19 | 0.011968 | 2.9478e-05 | 1 | 406 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 267 | SKE1739 | 74 The Avenue | Normanby | 2024-05-29 08:33 | 2024-05-29 15:12 | 0.011762 | 2.9478e-05 | 1 | 399 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 268 | SKE1739 | 75 The Avenue | Normanby | 2024-05-29 08:33 | 2024-05-29 15:20 | 0.011997 | 2.9478e-05 | 1 | 407 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 269 | SKE1739 | 76 The Avenue | Normanby | 2024-05-29 08:33 | 2024-05-29 15:29 | 0.012263 | 2.9478e-05 | 1 | 416 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 270 | SKE1739 | 77 The Avenue | Normanby | 2024-05-29 08:33 | 2024-05-29 15:09 | 0.011673 | 2.9478e-05 | 1 | 396 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 271 | SKE1739 | 78 The Avenue | Normanby | 2024-05-29 08:33 | 2024-05-29 15:13 | 0.011791 | 2.9478e-05 | 1 | 400 | Planned | Planned interruption | Pareora Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 272 | SKE1751 | TX A1092 | Waihaorunga | 2024-05-29 09:02 | 2024-05-29 13:45 | 0.0083422 | 2.9478e-05 | 1 | 283 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 273 | 5121 | Fuses T317 to end | Waitohi | 2024-05-30 03:01 | 2024-05-30 04:30 | 0.047223 | 0.0005306 | 18 | 1602 | Unplanned | Unknown | Unknown - 1x Blown DO | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 274 | 5120 | Fuses T317 to end | Waitohi | 2024-05-30 06:22 | 2024-05-30 07:49 | 0.046162 | 0.0005306 | 18 | 1566 | Unplanned | Unknown | Unknown - 2x Blown DO's | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 275 | ACD134 | RMU L1130 FS-43,47,31,37,35,33,19,20,21,4,23,25,24,26 Balmoral St | Highfield | 2024-05-31 08:32 | 2024-05-31 14:54 | 0.52924 | 0.0013854 | 47 | 17954 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 276 | ACD134 | 43 Balmoral St | Highfield | 2024-05-31 08:32 | 2024-05-31 15:42 | 0.012675 | 2.9478e-05 | 1 | 430 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 277 | ACD134 | 47 Balmoral St | Highfield | 2024-05-31 08:32 | 2024-05-31 15:50 | 0.012911 | 2.9478e-05 | 1 | 438 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 278 | ACD134 | 31 Balmoral St | Highfield | 2024-05-31 08:32 | 2024-05-31 15:03 | 0.011526 | 2.9478e-05 | 1 | 391 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 279 | ACD134 | 37 Balmoral St | Highfield | 2024-05-31 08:32 | 2024-05-31 15:08 | 0.011673 | 2.9478e-05 | 1 | 396 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 280 | ACD134 | 35 Balmoral St | Highfield | 2024-05-31 08:32 | 2024-05-31 15:11 | 0.011762 | 2.9478e-05 | 1 | 399 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 281 | ACD134 | 33 Balmoral St | Highfield | 2024-05-31 08:32 | 2024-05-31 15:15 | 0.011879 | 2.9478e-05 | 1 | 403 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 282 | ACD134 | 19 Balmoral St | Highfield | 2024-05-31 08:32 | 2024-05-31 15:04 | 0.011555 | 2.9478e-05 | 1 | 392 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 283 | ACD134 | 20 Balmoral St | Highfield | 2024-05-31 08:32 | 2024-05-31 15:13 | 0.011821 | 2.9478e-05 | 1 | 401 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 284 | ACD134 | 21 Balmoral St | Highfield | 2024-05-31 08:32 | 2024-05-31 15:09 | 0.011703 | 2.9478e-05 | 1 | 397 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 285 | ACD134 | 4 Balmoral St | Highfield | 2024-05-31 08:32 | 2024-05-31 15:11 | 0.011762 | 2.9478e-05 | 1 | 399 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 286 | ACD134 | 23 Balmoral St | Highfield | 2024-05-31 08:32 | 2024-05-31 15:04 | 0.011555 | 2.9478e-05 | 1 | 392 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 287 | ACD134 | 25 Balmoral St | Highfield | 2024-05-31 08:32 | 2024-05-31 15:09 | 0.011703 | 2.9478e-05 | 1 | 397 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 288 | ACD134 | 24 Balmoral St | Highfield | 2024-05-31 08:32 | 2024-05-31 15:13 | 0.011821 | 2.9478e-05 | 1 | 401 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 289 | ACD134 | 26 Balmoral St | Highfield | 2024-05-31 08:32 | 2024-05-31 15:19 | 0.011997 | 2.9478e-05 | 1 | 407 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 290 | SKE1756 | RMU R55 MS | Port Services | 2024-05-31 09:10 | 2024-05-31 14:19 | 0.0091086 | 2.9478e-05 | 1 | 309 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 291 | 5070 | Fuses TOC497 | Raincliff | 2024-05-31 10:00 | 2024-06-10 16:53 | 0.43665 | 2.9478e-05 | 1 | 14813 | Unplanned | Third party interference | Digger V Cable | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 292 | 3867 | CB M338 to end | Simons | 2024-06-01 06:19 | 2024-06-01 09:44 | 0.24172 | 0.0011791 | 40 | 8200 | Unplanned | Adverse weather | High Wind, Tree on line, Broken Conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 293 | 3868 | Fuses F428 to end | Cave | 2024-06-01 08:27 | 2024-06-01 10:13 | 0.084365 | 0.0007959 | 27 | 2862 | Unplanned | Adverse weather | High Wind . Branch on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 294 | 3869 | TX Fuses TO A389 | Waikakahi | 2024-06-01 09:26 | 2024-06-01 11:16 | 0.0032425 | 2.9478e-05 | 1 | 110 | Unplanned | Adverse weather | High Wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 295 | 3871 | CB F138 to Links F140 | Cave | 2024-06-01 10:24 | 2024-06-01 12:28 | 0.036552 | 0.00029478 | 10 | 1240 | Unplanned | Adverse weather | High Wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 296 | 3871 | Links F140 to Links F141 | Cave | 2024-06-01 10:24 | 2024-06-01 12:51 | 0.069331 | 0.00047164 | 16 | 2352 | Unplanned | Adverse weather | High Wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 297 | 3871 | Links F141 to end minus F157 - F142 - F144 & F145 | Cave | 2024-06-01 10:24 | 2024-06-01 13:35 | 0.028151 | 0.00014739 | 5 | 955 | Unplanned | Adverse weather | High Wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 298 | 3871 | Fuses F157 to end | Cave | 2024-06-01 10:24 | 2024-06-01 13:46 | 0.047636 | 0.00023582 | 8 | 1616 | Unplanned | Adverse weather | High Wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 299 | 3871 | Fuses F145 to end | Cave | 2024-06-01 10:24 | 2024-06-01 13:42 | 0.099222 | 0.00050112 | 17 | 3366 | Unplanned | Adverse weather | High Wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 300 | 3871 | Links F144 to end | Cave | 2024-06-01 10:24 | 2024-06-01 13:40 | 0.14444 | 0.00073694 | 25 | 4900 | Unplanned | Adverse weather | High Wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 301 | 3871 | Links F142 to end minus F191 - F171 - F143 - F174 | Cave | 2024-06-01 10:24 | 2024-06-01 15:05 | 0.091115 | 0.00032425 | 11 | 3091 | Unplanned | Adverse weather | High Wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 302 | 3871 | Fuses F191 to end | Cave | 2024-06-01 10:24 | 2024-06-01 15:12 | 0.033958 | 0.00011791 | 4 | 1152 | Unplanned | Adverse weather | High Wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 303 | 3871 | Fuses F171 to end | Cave | 2024-06-01 10:24 | 2024-06-01 15:20 | 0.026176 | 8.8433e-05 | 3 | 888 | Unplanned | Adverse weather | High Wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 304 | 3871 | Fuses F143 to end | Cave | 2024-06-01 10:24 | 2024-06-01 15:16 | 0.14633 | 0.00050112 | 17 | 4964 | Unplanned | Adverse weather | High Wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 305 | 3871 | Fuses F174 to end | Cave | 2024-06-01 10:24 | 2024-06-01 15:08 | 0.058602 | 0.00020634 | 7 | 1988 | Unplanned | Adverse weather | High Wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 306 | 3870 | CB W515 to end | Waikakahi | 2024-06-01 11:30 | 2024-06-01 11:37 | 0.035697 | 0.0050996 | 173 | 1211 | Unplanned | Adverse weather | High wind - Bark removal | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 307 | 3871 | CB F138 to Links F140 | Cave | 2024-06-01 13:26 | 2024-06-01 13:35 | 0.002653 | 0.00029478 | 10 | 90 | Unplanned | Adverse weather | High Wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 308 | 3871 | Links F140 to Links F141 | Cave | 2024-06-01 13:26 | 2024-06-01 13:35 | 0.0042448 | 0.00047164 | 16 | 144 | Unplanned | Adverse weather | High Wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 309 | 4057 | Fuses L827 | Hadlow | 2024-06-01 14:29 | 2024-06-01 16:54 | 0.15815 | 0.0010907 | 37 | 5365 | Unplanned | Adverse weather | High Winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 310 | 3872 | PLP CB1 (Waitawa) to end | Waitawa | 2024-06-01 16:48 | 2024-06-01 17:00 | 0.096569 | 0.0080474 | 273 | 3276 | Unplanned | Adverse weather | Emergency Trip to remove burning branch - Connells Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 311 | 4309 | F138 to end less F142 | Cave | 2024-06-01 18:25 | 2024-06-01 19:46 | 0.1934 | 0.0023877 | 81 | 6561 | Unplanned | Adverse weather | Conductor on x arm #14053 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 312 | 4309 | F142 to end | Cave | 2024-06-01 18:25 | 2024-06-02 11:05 | 1.2381 | 0.0012381 | 42 | 42000 | Unplanned | Adverse weather | Conductor on x arm #14053 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 313 | 4308 | Fuses TO D404 to the end | Winchester | 2024-06-01 18:34 | 2024-06-02 | 0.028829 | 8.8433e-05 | 3 | 978 | Unplanned | Adverse weather | Repair LV conductor beyond D404 Tx | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 314 | 4058 | ABS T306 | Waitohi | 2024-06-01 21:31 | 2024-06-01 21:46 | 0.021224 | 0.0014149 | 48 | 720 | Unplanned | Adverse weather | High Winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 315 | 4058 | TMK CB9-ABS T306 | Waitohi | 2024-06-01 21:31 | 2024-06-01 21:34 | 0.022727 | 0.0075758 | 257 | 771 | Unplanned | Adverse weather | High Winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 316 | ACD130 | ABS W174-TX A688 | Tawai | 2024-06-04 09:18 | 2024-06-04 16:11 | 0.23131 | 0.00056008 | 19 | 7847 | Planned | Planned interruption | TX Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 317 | ACD130 | TX A688 | Tawai | 2024-06-04 09:18 | 2024-06-04 16:22 | 0.049994 | 0.00011791 | 4 | 1696 | Planned | Planned interruption | TX Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 318 | ACD131 | ABS G107-Links G197- Pole 09047-TX D170 01 | Winchester | 2024-06-05 09:00 | 2024-06-05 15:33 | 0.35913 | 0.00091381 | 31 | 12183 | Planned | Planned interruption | Red Tag Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 319 | ACD131 | Pole 09047 | Winchester | 2024-06-05 09:00 | 2024-06-05 16:18 | 0.012911 | 2.9478e-05 | 1 | 438 | Planned | Planned interruption | Red Tag Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 320 | ACD131 | Pole 09032 | Winchester | 2024-06-05 09:00 | 2024-06-05 16:35 | 0.013412 | 2.9478e-05 | 1 | 455 | Planned | Planned interruption | Red Tag Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 321 | ACD131 | Pole 09029 | Winchester | 2024-06-05 09:00 | 2024-06-05 16:25 | 0.013118 | 2.9478e-05 | 1 | 445 | Planned | Planned interruption | Red Tag Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 322 | ACD131 | TX D170 01-Pole 09032- Pole 09029 | Winchester | 2024-06-05 09:00 | 2024-06-05 15:50 | 0.20546 | 0.00050112 | 17 | 6970 | Planned | Planned interruption | Red Tag Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 323 | JJV149 | Fuses F232 | Fairlie Rural | 2024-06-05 09:02 | 2024-06-05 13:15 | 0.49222 | 0.0019455 | 66 | 16698 | Planned | Planned interruption | New TX | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 324 | ACD143 | Fuses F179 | Fairlie Rural | 2024-06-07 09:00 | 2024-06-07 11:09 | 0.019013 | 0.00014739 | 5 | 645 | Planned | Planned interruption | Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 325 | 3801 | TMK CB9-ABS T313 | Waitohi | 2024-06-07 09:00 | 2024-06-07 10:54 | 0.28564 | 0.0025056 | 85 | 9690 | Unplanned | Defective equipment | Repair broken jumper at ABS T306 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 326 | ACD144 | Fuses F108 | Cave | 2024-06-07 09:12 | 2024-06-07 11:57 | 0.0097276 | 5.8955e-05 | 2 | 330 | Planned | Planned interruption | Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 327 | SKE1773 | DB C39 | Hayes Street | 2024-06-09 08:30 | 2024-06-09 16:27 | 0.042183 | 8.8433e-05 | 3 | 1431 | Planned | Planned interruption | TE12 UG Sub replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 328 | SKE1773 | TE12 CCT16 | Hayes Street | 2024-06-09 08:30 | 2024-06-09 16:41 | 0.057894 | 0.00011791 | 4 | 1964 | Planned | Planned interruption | TE12 UG Sub replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 329 | SKE1773 | TE12 CCT15 | Hayes Street | 2024-06-09 08:30 | 2024-06-09 16:49 | 0.14709 | 0.00029478 | 10 | 4990 | Planned | Planned interruption | TE12 UG Sub replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 330 | JJV148 | TX B1775 | Redruth 2 | 2024-06-09 09:00 | 2024-06-09 17:17 | 0.01465 | 2.9478e-05 | 1 | 497 | Planned | Planned interruption | New TX & RMU | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 331 | JJV148 | ABS L283-Links L500-LV links LL084-TX B1775 | Redruth 2 | 2024-06-09 09:00 | 2024-06-09 16:00 | 0.4457 | 0.0010612 | 36 | 15120 | Planned | Planned interruption | New TX & RMU | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 332 | OS KCK678 | CB W685 | Otaio | 2024-06-09 10:00 | 2024-06-09 10:04 | 0.0074284 | 0.0018571 | 63 | 252 | Planned | Planned interruption | Reconfiguring Network | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 333 | OS KCK678 | LB ABS W315-CB W685 | Otaio | 2024-06-09 10:02 | 2024-06-09 10:03 | 0.0010317 | 0.0010317 | 35 | 35 | Planned | Planned interruption | Reconfiguring Network | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 334 | ACD142 | ABS L878 | Normanby | 2024-06-10 09:00 | 2024-06-10 15:03 | 0.19261 | 0.0005306 | 18 | 6534 | Planned | Planned interruption | Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 335 | 5044 | F287 - F250 | Fairlie Rural | 2024-06-10 11:27 | 2024-06-10 12:19 | 0.26365 | 0.0050702 | 172 | 8944 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 336 | 5044 | F250 - End | Fairlie Rural | 2024-06-10 11:27 | 2024-06-10 12:31 | 0.092442 | 0.0014444 | 49 | 3136 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 337 | 3791 | CB G251 - T325 | Speechley | 2024-06-10 14:19 | 2024-06-10 15:22 | 0.23214 | 0.0036847 | 125 | 7875 | Unplanned | Third party interference | Truck with trees hit lines @ P#10490 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 338 | 3791 | T325 | Speechley | 2024-06-10 14:19 | 2024-06-10 18:32 | 0.13424 | 0.0005306 | 18 | 4554 | Unplanned | Third party interference | Truck with trees hit lines @ P#10490 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 339 | JDJ088 | ABS W560-Pole 43056 | Otaio | 2024-06-11 08:45 | 2024-06-11 14:12 | 0.11567 | 0.00035373 | 12 | 3924 | Planned | Planned interruption | Red Tag Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 340 | JDJ088 | Pole 43056 | Otaio | 2024-06-11 08:45 | 2024-06-11 14:14 | 0.0096981 | 2.9478e-05 | 1 | 329 | Planned | Planned interruption | Red Tag Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 341 | 5042 | F306 to end | Totara Valley | 2024-06-11 14:10 | 2024-06-11 15:13 | 0.0055713 | 8.8433e-05 | 3 | 189 | Unplanned | Defective equipment | Tipped crossarm at pole #18247 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 342 | JDJ107 | TX D85 | Rangitata | 2024-06-12 09:54 | 2024-06-12 14:00 | 0.014503 | 5.8955e-05 | 2 | 492 | Planned | Planned interruption | Replace standoff insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 343 | JDJ107UP | TX D85 | Rangitata | 2024-06-12 14:00 | 2024-06-14 16:05 | 0.17716 | 5.8955e-05 | 2 | 6010 | Unplanned | Defective equipment | Repair cable | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 344 | 5045 | L643 - L164 | Normanby | 2024-06-13 12:43 | 2024-06-13 13:16 | 0.10798 | 0.003272 | 111 | 3663 | Unplanned | Third party interference | Tree on line @ P#42035 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 345 | 5045 | L164 | Normanby | 2024-06-13 12:43 | 2024-06-13 18:19 | 0.12876 | 0.00038321 | 13 | 4368 | Unplanned | Third party interference | Tree on line @ P#42035 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 346 | 4410 | L243 | Waitawa | 2024-06-16 14:38 | 2024-06-16 15:58 | 0.099045 | 0.0012381 | 42 | 3360 | Unplanned | Third party interference | Car v Pole #19581 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 347 | 4410 | L347 + L244 | Waitawa | 2024-06-16 14:38 | 2024-06-16 16:07 | 0.26235 | 0.0029478 | 100 | 8900 | Unplanned | Third party interference | Car v Pole #19581 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 348 | 4410 | L211 - L347 | Waitawa | 2024-06-16 14:38 | 2024-06-16 16:07 | 0.049847 | 0.00056008 | 19 | 1691 | Unplanned | Third party interference | Car v Pole #19581 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 349 | 4410 | PLP CB1 - L246 - L211 - L244 - L243 | Waitawa | 2024-06-16 14:38 | 2024-06-16 19:18 | 0.89966 | 0.0032131 | 109 | 30520 | Unplanned | Third party interference | Car v Pole #19581 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 350 | 4410 | PLP CB2 - L240 | Sutherland | 2024-06-16 14:38 | 2024-06-16 16:39 | 0.13911 | 0.0011496 | 39 | 4719 | Unplanned | Third party interference | Car v Pole #19581 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 351 | 4410 | L246 | Waitawa | 2024-06-16 14:38 | 2024-06-16 16:42 | 0.010966 | 8.8433e-05 | 3 | 372 | Unplanned | Third party interference | Car v Pole #19581 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 352 | 4410 | PLP CB5 - L231 | Pleasant Point Township | 2024-06-16 14:38 | 2024-06-16 16:42 | 0.73105 | 0.0058955 | 200 | 24800 | Unplanned | Third party interference | Car v Pole #19581 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 353 | 4410 | PLP CB4 - L232 | Totara Valley | 2024-06-16 14:38 | 2024-06-16 16:46 | 0.84518 | 0.006603 | 224 | 28672 | Unplanned | Third party interference | Car v Pole #19581 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 354 | 4410 | L1239 - L820 | Sutherland | 2024-06-16 14:38 | 2024-06-16 16:49 | 0.065647 | 0.00050112 | 17 | 2227 | Unplanned | Third party interference | Car v Pole #19581 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 355 | 4410 | L820 | Sutherland | 2024-06-16 14:38 | 2024-06-16 16:49 | 0.038616 | 0.00029478 | 10 | 1310 | Unplanned | Third party interference | Car v Pole #19581 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 356 | 4410 | L240 - L1239 | Sutherland | 2024-06-16 14:38 | 2024-06-16 16:49 | 0.22397 | 0.0017097 | 58 | 7598 | Unplanned | Third party interference | Car v Pole #19581 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 357 | 4410 | L232 - L109 | Totara Valley | 2024-06-16 14:38 | 2024-06-16 17:09 | 1.1484 | 0.0076052 | 258 | 38958 | Unplanned | Third party interference | Car v Pole #19581 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 358 | 4410 | L109 | Totara Valley | 2024-06-16 14:38 | 2024-06-16 17:44 | 0.52087 | 0.0028004 | 95 | 17670 | Unplanned | Third party interference | Car v Pole #19581 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 359 | 4410 | L1159 | Pleasant Point Township | 2024-06-16 14:38 | 2024-06-16 16:57 | 0.23765 | 0.0017097 | 58 | 8062 | Unplanned | Third party interference | Car v Pole #19581 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 360 | 4410 | L231 - L1159 | Pleasant Point Township | 2024-06-16 14:38 | 2024-06-16 16:57 | 0.32779 | 0.0023582 | 80 | 11120 | Unplanned | Third party interference | Car v Pole #19581 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 361 | 4410 | PLP CB5 - L231 | Pleasant Point Township | 2024-06-16 17:17 | 2024-06-16 17:19 | 0.011791 | 0.0058955 | 200 | 400 | Unplanned | Third party interference | Car v Pole #19581 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 362 | 4410 | PLP CB5 - L231 | Pleasant Point Township | 2024-06-16 19:58 | 2024-06-16 20:01 | 0.017687 | 0.0058955 | 200 | 600 | Unplanned | Third party interference | Car v Pole #19581 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 363 | 4410 | L1159 | Pleasant Point Township | 2024-06-16 19:58 | 2024-06-16 20:01 | 0.0051291 | 0.0017097 | 58 | 174 | Unplanned | Third party interference | Car v Pole #19581 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 364 | 4410 | L231 - L1159 | Pleasant Point Township | 2024-06-16 19:58 | 2024-06-16 20:01 | 0.0070746 | 0.0023582 | 80 | 240 | Unplanned | Third party interference | Car v Pole #19581 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 365 | 4410 | L1239 - L820 | Sutherland | 2024-06-16 20:25 | 2024-06-17 00:15 | 0.11526 | 0.00050112 | 17 | 3910 | Unplanned | Defective equipment | Faulty LB ABS L639 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 366 | 4410 | L820 | Sutherland | 2024-06-16 20:25 | 2024-06-16 21:36 | 0.020929 | 0.00029478 | 10 | 710 | Unplanned | Defective equipment | Faulty LB ABS L639 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 367 | 4410 | L240 - L1239 | Sutherland | 2024-06-16 20:25 | 2024-06-16 20:40 | 0.025646 | 0.0017097 | 58 | 870 | Unplanned | Third party interference | Car v Pole #19581 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 368 | 4410 | L232 - L109 | Totara Valley | 2024-06-16 20:25 | 2024-06-16 20:40 | 0.11408 | 0.0076052 | 258 | 3870 | Unplanned | Third party interference | Car v Pole #19581 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 369 | 4410 | CB2742 - F293 + F298 | Cave | 2024-06-16 20:25 | 2024-06-16 21:12 | 0.51816 | 0.011025 | 374 | 17578 | Unplanned | Defective equipment | Faulty LB ABS L639 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 370 | 4410 | FX17 | Cave | 2024-06-16 20:25 | 2024-06-16 21:59 | 0.096981 | 0.0010317 | 35 | 3290 | Unplanned | Defective equipment | Faulty LB ABS L639 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 371 | 4410 | F293 - F298 - FX17 | Cave | 2024-06-16 20:25 | 2024-06-16 23:36 | 0.033781 | 0.00017687 | 6 | 1146 | Unplanned | Defective equipment | Faulty LB ABS L639 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 372 | 4410 | L109 | Totara Valley | 2024-06-16 21:48 | 2024-06-16 21:49 | 0.0028004 | 0.0028004 | 95 | 95 | Unplanned | Third party interference | Car v Pole #19581 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 373 | 4410 | L211 - L347 | Waitawa | 2024-06-16 22:31 | 2024-06-16 22:34 | 0.0016802 | 0.00056008 | 19 | 57 | Unplanned | Third party interference | Car v Pole #19581 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 374 | 4410 | FX17 | Cave | 2024-06-17 | 2024-06-17 00:03 | 0.0030952 | 0.0010317 | 35 | 105 | Unplanned | Defective equipment | Faulty LB ABS L639 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 375 | 4410 | L820 | Sutherland | 2024-06-17 00:18 | 2024-06-17 00:20 | 0.00058955 | 0.00029478 | 10 | 20 | Unplanned | Defective equipment | Faulty LB ABS L639 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 376 | 5139 | PAR CB6 - ABS L166 | Normanby | 2024-06-18 07:02 | 2024-06-18 08:29 | 0.91298 | 0.010494 | 356 | 30972 | Unplanned | Defective equipment | Broken ABS L166 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 377 | 5139 | ABS L145 | Normanby | 2024-06-18 07:02 | 2024-06-18 10:05 | 1.0303 | 0.0056302 | 191 | 34953 | Unplanned | Defective equipment | Broken ABS L166 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 378 | 5139 | ABS L878 | Normanby | 2024-06-18 07:02 | 2024-06-18 10:21 | 0.10559 | 0.0005306 | 18 | 3582 | Unplanned | Defective equipment | Broken ABS L166 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 379 | 5139 | ABS L166-ABS L145-L878 | Normanby | 2024-06-18 07:02 | 2024-06-18 13:09 | 0.06491 | 0.00017687 | 6 | 2202 | Unplanned | Defective equipment | Broken ABS L166 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 380 | 5139 | ABS L141-ABS L166 | Normanby | 2024-06-18 10:11 | 2024-06-18 13:11 | 0.068978 | 0.00038321 | 13 | 2340 | Unplanned | Defective equipment | Broken ABS L166 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 381 | HTR021 | Fuses G101 | Winchester | 2024-06-19 08:09 | 2024-06-19 13:05 | 0.20068 | 0.00067799 | 23 | 6808 | Planned | Planned interruption | Tree Trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 382 | BDS001 | ABS F154-ABS F156-Pole 47950 | Cave | 2024-06-20 09:10 | 2024-06-20 17:45 | 0.68314 | 0.0013265 | 45 | 23175 | Planned | Planned interruption | ABY Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 383 | BDS001 | Pole 47950 | Cave | 2024-06-20 09:10 | 2024-06-20 17:51 | 0.015358 | 2.9478e-05 | 1 | 521 | Planned | Planned interruption | ABY Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 384 | 5046 | TOA382 | Morven | 2024-06-21 13:20 | 2024-06-21 15:12 | 0.0033015 | 2.9478e-05 | 1 | 112 | Unplanned | Unknown | Blown fuse 11kV pole TOA382 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 385 | 5049 | CB L839 to End | Hadlow | 2024-06-23 13:02 | 2024-06-23 15:14 | 0.96498 | 0.0073105 | 248 | 32736 | Unplanned | Defective equipment | Blown Arrestors at Pole #35228 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 386 | 5049 | L798 - L839 | Hadlow | 2024-06-23 13:02 | 2024-06-23 15:14 | 0.015564 | 0.00011791 | 4 | 528 | Unplanned | Defective equipment | Blown Arrestors at Pole #35228 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 387 | 5049 | L812 to End | Hadlow | 2024-06-23 13:02 | 2024-06-23 15:38 | 0.43686 | 0.0028004 | 95 | 14820 | Unplanned | Defective equipment | Blown Arrestors at Pole #35228 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 388 | 5049 | L799 - L812 | Hadlow | 2024-06-23 13:02 | 2024-06-23 15:52 | 2.8564 | 0.016802 | 570 | 96900 | Unplanned | Defective equipment | Blown Arrestors at Pole #35228 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 389 | 5049 | Pole #35218 - L798 | Hadlow | 2024-06-23 13:02 | 2024-06-23 23:38 | 0.18748 | 0.00029478 | 10 | 6360 | Unplanned | Defective equipment | Blown Arrestors at Pole #35228 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 390 | 5049 | Pole #35227 - L799 | Hadlow | 2024-06-23 13:02 | 2024-06-23 23:27 | 0.6264 | 0.0010022 | 34 | 21250 | Unplanned | Defective equipment | Blown Arrestors at Pole #35228 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 391 | 5049 | L812 to End (2) | Hadlow | 2024-06-23 17:40 | 2024-06-23 18:37 | 0.15962 | 0.0028004 | 95 | 5415 | Unplanned | Defective equipment | Blown Arrestors at Pole #35228 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 392 | 5049 | L798 - L839 (2) | Hadlow | 2024-06-23 23:35 | 2024-06-23 23:38 | 0.00035373 | 0.00011791 | 4 | 12 | Unplanned | Defective equipment | Blown Arrestors at Pole #35228 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 393 | 5122 | Pole #35288 to links L797 minus TX B2078 - B119 - B1588 | Hadlow | 2024-06-24 11:52 | 2024-06-24 17:10 | 0.037496 | 0.00011791 | 4 | 1272 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 394 | 5122 | TX B2078 | Hadlow | 2024-06-24 11:52 | 2024-06-24 17:21 | 0.0096981 | 2.9478e-05 | 1 | 329 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 395 | 5122 | TX B119 | Hadlow | 2024-06-24 11:52 | 2024-06-24 17:26 | 0.039382 | 0.00011791 | 4 | 1336 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 396 | 5122 | TX B1588 | Hadlow | 2024-06-24 11:52 | 2024-06-24 17:30 | 0.0099634 | 2.9478e-05 | 1 | 338 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 397 | 5047 | TOE208 | TEK-UHT 33kV | 2024-06-24 14:17 | 2024-06-24 14:42 | 0.0014739 | 5.8955e-05 | 2 | 50 | Unplanned | Defective equipment | Broken binder / tie @ P#21895 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 398 | 5122 | Pole #35288 to Links L286 | Hadlow | 2024-06-24 15:10 | 2024-06-24 17:10 | 0.12027 | 0.0010022 | 34 | 4080 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 399 | HTR016 | Links G342 | Winchester | 2024-06-25 08:00 | 2024-06-25 13:21 | 0.0094623 | 2.9478e-05 | 1 | 321 | Planned | Planned interruption | Tree Trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 400 | HTR016 | RMU G313 MS | Geraldine Township | 2024-06-25 08:00 | 2024-06-25 13:18 | 0.37496 | 0.0011791 | 40 | 12720 | Planned | Planned interruption | Tree Trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 401 | BDS002 | ABS F154-ABS F156-17 Station St | Cave | 2024-06-25 08:36 | 2024-06-25 18:04 | 0.75345 | 0.0013265 | 45 | 25560 | Planned | Planned interruption | ABY Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 402 | BDS002 | 17 Station St | Cave | 2024-06-25 08:36 | 2024-06-25 18:25 | 0.017362 | 2.9478e-05 | 1 | 589 | Planned | Planned interruption | ABY Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 403 | HTR027 | Fuses T112 | Milford | 2024-06-25 09:00 | 2024-06-25 10:33 | 0.052087 | 0.00056008 | 19 | 1767 | Planned | Planned interruption | Tree Trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 404 | SKE1502 | ABS T690 | Rangitata | 2024-06-25 09:37 | 2024-06-25 13:01 | 0.01804 | 8.8433e-05 | 3 | 612 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 405 | HTR017 | ABS T497 | Rangitata Island | 2024-06-26 08:00 | 2024-06-26 14:29 | 0.72241 | 0.0018571 | 63 | 24507 | Planned | Planned interruption | Tree Trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 406 | ACD153 | TX E207 | TEK-UHT 33kV | 2024-06-26 09:16 | 2024-06-26 16:28 | 0.050937 | 0.00011791 | 4 | 1728 | Planned | Planned interruption | Red Tag Pole replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 407 | ACD153 | ABS M61-TX E207 | TEK-UHT 33kV | 2024-06-26 09:16 | 2024-06-26 16:07 | 0.18173 | 0.00044216 | 15 | 6165 | Planned | Planned interruption | Red Tag Pole replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 408 | BDS003 | ABS F154-ABS F156-2 x ICPs | Cave | 2024-06-27 08:33 | 2024-06-27 14:45 | 0.48249 | 0.001297 | 44 | 16368 | Planned | Planned interruption | ABY Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 409 | BDS003 | 2x ICPs | Cave | 2024-06-27 08:33 | 2024-06-27 14:54 | 0.022462 | 5.8955e-05 | 2 | 762 | Planned | Planned interruption | ABY Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 410 | JMR676 | Beyond CB T626 Rolleston Rd | Rolleston Road | 2024-06-27 09:07 | 2024-06-27 10:33 | 0.47406 | 0.0055123 | 187 | 16082 | Unplanned | Wildlife | Swann found between poles #07207 & #51490 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 411 | JRM010 | TX D1286 | Mahan Road | 2024-06-27 09:28 | 2024-06-27 14:56 | 0.0096687 | 2.9478e-05 | 1 | 328 | Planned | Planned interruption | TX Repairs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 412 | 3873 | Fuses L208 to end | Levels Plain | 2024-06-28 04:07 | 2024-06-28 06:23 | 0.072161 | 0.0005306 | 18 | 2448 | Unplanned | Unknown | Blown DO's - Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 413 | 3874 | TMK CB2 to ABS T116 and T125 | Milford | 2024-06-28 06:00 | 2024-06-28 07:27 | 0.17439 | 0.0020045 | 68 | 5916 | Unplanned | Wildlife | Conductors Down - Bird Strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 414 | 3874 | ABS T125 to end | Milford | 2024-06-28 06:00 | 2024-06-28 07:37 | 0.26592 | 0.0027414 | 93 | 9021 | Unplanned | Wildlife | Conductors Down - Bird Strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 415 | 3874 | ABS T116 to fuses T119 | Milford | 2024-06-28 06:00 | 2024-06-28 11:44 | 0.83151 | 0.0024172 | 82 | 28208 | Unplanned | Wildlife | Conductors Down - Bird Strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 416 | 3874 | Fuses T119 to end | Milford | 2024-06-28 06:00 | 2024-06-28 08:09 | 0.12929 | 0.0010022 | 34 | 4386 | Unplanned | Wildlife | Conductors Down - Bird Strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 417 | 3875 | CB L839 to ABS L836 & ABS L834 | Hadlow | 2024-06-29 10:25 | 2024-06-29 11:15 | 0.038321 | 0.00076642 | 26 | 1300 | Unplanned | Defective equipment | Faulty CB L839 Controller | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 418 | 3875 | ABS L834 to LBS L1401 | Hadlow | 2024-06-29 10:25 | 2024-06-29 11:27 | 0.11331 | 0.0018276 | 62 | 3844 | Unplanned | Defective equipment | Faulty CB L839 Controller | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 419 | 3875 | LBS L1401 to end | Hadlow | 2024-06-29 10:25 | 2024-06-29 11:29 | 0.20941 | 0.003272 | 111 | 7104 | Unplanned | Defective equipment | Faulty CB L839 Controller | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 420 | 3875 | ABS L836 to end | Hadlow | 2024-06-29 10:25 | 2024-06-29 11:32 | 0.09875 | 0.0014739 | 50 | 3350 | Unplanned | Defective equipment | Faulty CB L839 Controller | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 421 | GWM1162 | ABS TX20 - ABS TX62 - Links T458 | Rangitata | 2024-07-01 09:24 | 2024-07-01 11:27 | 0.14503 | 0.0011791 | 40 | 4920 | Planned | Planned interruption | Tree Cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 422 | HTR018 | T460 | Mahan Road | 2024-07-02 08:26 | 2024-07-02 15:27 | 0.2482 | 0.00058955 | 20 | 8420 | Planned | Planned interruption | Tree Cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 423 | ACD145 | L601 - L1472 - 121, 123, 124 & 133 Luxmoore Rd | Grants Road | 2024-07-02 08:30 | 2024-07-02 14:23 | 0.31217 | 0.00088433 | 30 | 10590 | Planned | Planned interruption | Isolate & Earth ABS L601 for Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 424 | ACD145 | 133 Luxmoore Road | Grants Road | 2024-07-02 08:30 | 2024-07-02 14:27 | 0.010524 | 2.9478e-05 | 1 | 357 | Planned | Planned interruption | Isolate & Earth ABS L601 for Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 425 | ACD145 | 121 + 133 Luxmoore Road | Grants Road | 2024-07-02 08:30 | 2024-07-02 14:33 | 0.021401 | 5.8955e-05 | 2 | 726 | Planned | Planned interruption | Isolate & Earth ABS L601 for Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 426 | ACD145 | 124 Luxmoore Road | Grants Road | 2024-07-02 08:30 | 2024-07-02 14:35 | 0.010759 | 2.9478e-05 | 1 | 365 | Planned | Planned interruption | Isolate & Earth ABS L601 for Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 427 | HTR006 | Fuses F180 | Cave | 2024-07-02 09:00 | 2024-07-02 14:48 | 0.071808 | 0.00020634 | 7 | 2436 | Planned | Planned interruption | Tree Cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 428 | JRM017 | Fuses TO C423 | Fairlie Rural | 2024-07-02 09:49 | 2024-07-02 14:47 | 0.017569 | 5.8955e-05 | 2 | 596 | Planned | Planned interruption | Isolation for repairs to TX C423 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 429 | HTR030 | ABS F101 | Cave | 2024-07-03 08:00 | 2024-07-03 13:45 | 0.35594 | 0.0010317 | 35 | 12075 | Planned | Planned interruption | Tree Cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 430 | 5048 | Fuses TO B731 to end | Hadlow | 2024-07-03 13:47 | 2024-07-03 14:27 | 0.0035373 | 8.8433e-05 | 3 | 120 | Unplanned | Wildlife | Remove birds Nests | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 431 | JMR672 | Fuses TO A705 | Tawai | 2024-07-08 10:00 | 2024-07-08 10:10 | 0.018866 | 0.0018866 | 64 | 640 | Planned | Planned interruption | Transformer Tap Change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 432 | 5050 | W308 to end at pole #06007 | Otaio | 2024-07-09 14:57 | 2024-07-09 15:39 | 0.014857 | 0.00035373 | 12 | 504 | Unplanned | Defective equipment | Broken 11kV jumper at pole #06007 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 433 | 5123 | BPD CB13 to ABS W117, ABS W138 & ABS W133 | Waikakahi | 2024-07-11 01:58 | 2024-07-11 04:27 | 0.25475 | 0.0017097 | 58 | 8642 | Unplanned | Wildlife | Possum at pole #33049 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 434 | 5123 | ABS W133 to end | Waikakahi | 2024-07-11 01:58 | 2024-07-11 04:58 | 0.058366 | 0.00032425 | 11 | 1980 | Unplanned | Wildlife | Possum at pole #33049 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 435 | 5123 | ABS W138 to end | Waikakahi | 2024-07-11 01:58 | 2024-07-11 04:59 | 0.090703 | 0.00050112 | 17 | 3077 | Unplanned | Wildlife | Possum at pole #33049 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 436 | 5123 | ABS W117 to end | Waikakahi | 2024-07-11 01:58 | 2024-07-11 05:15 | 1.0801 | 0.0054828 | 186 | 36642 | Unplanned | Wildlife | Possum at pole #33049 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 437 | 3803 | Fuses TOD324 to end | Woodbury | 2024-07-11 12:06 | 2024-07-11 12:58 | 0.0015328 | 2.9478e-05 | 1 | 52 | Unplanned | Defective equipment | Broken insulator pole #51954 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 438 | 3804 | CB7 open to Q44 | Church Street South Side | 2024-07-12 11:41 | 2024-07-12 11:48 | 0.022079 | 0.0031541 | 107 | 749 | Unplanned | Third party interference | UG sub isolate to open LV circuit for DB Q17 replace | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 439 | 3804 | TE102-17 | Church Street South Side | 2024-07-12 11:41 | 2024-07-12 14:01 | 0.1073 | 0.00076642 | 26 | 3640 | Unplanned | Third party interference | UG sub isolate to open LV circuit for DB Q17 replace | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 440 | 3804 | ICPs Q17 | Church Street South Side | 2024-07-12 11:41 | 2024-07-12 14:20 | 0.0093739 | 5.8955e-05 | 2 | 318 | Unplanned | Third party interference | UG sub isolate to open LV circuit for DB Q17 replace | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 441 | 3804 | CB7 to Q44 | Church Street South Side | 2024-07-12 13:54 | 2024-07-12 14:01 | 0.022079 | 0.0031541 | 107 | 749 | Unplanned | Third party interference | UG sub isolate to open LV circuit for DB Q17 replace | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 442 | ACD137 | Pole 29730-L607-B694 CCT3-B203 CCT2-Pole 29757-B917-37, 28D Kent-50 Kelvin-19, 18, 20, 15 Kent | Grants Road | 2024-07-15 08:30 | 2024-07-15 16:00 | 1.3132 | 0.0029183 | 99 | 44550 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 443 | ACD137 | B917 CCT2-2 Usk St-6 Usk St | Grants Road | 2024-07-15 08:30 | 2024-07-15 16:05 | 0.54991 | 0.0012086 | 41 | 18655 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 444 | ACD137 | 2 Usk St | Grants Road | 2024-07-15 08:30 | 2024-07-15 16:33 | 0.014238 | 2.9478e-05 | 1 | 483 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 445 | ACD137 | 6 Usk St | Grants Road | 2024-07-15 08:30 | 2024-07-15 17:18 | 0.015564 | 2.9478e-05 | 1 | 528 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 446 | ACD137 | B917-B917 CCT2-87 Kent | Grants Road | 2024-07-15 08:30 | 2024-07-15 16:11 | 0.23102 | 0.00050112 | 17 | 7837 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 447 | ACD137 | 87 Kent St | Grants Road | 2024-07-15 08:30 | 2024-07-15 16:38 | 0.014385 | 2.9478e-05 | 1 | 488 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 448 | ACD137 | 37 Kent | Grants Road | 2024-07-15 08:30 | 2024-07-15 17:06 | 0.01521 | 2.9478e-05 | 1 | 516 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 449 | ACD137 | 28D Kent St | Grants Road | 2024-07-15 08:30 | 2024-07-15 16:54 | 0.014857 | 2.9478e-05 | 1 | 504 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 450 | ACD137 | 50 Kelvin St | Grants Road | 2024-07-15 08:30 | 2024-07-15 17:00 | 0.015034 | 2.9478e-05 | 1 | 510 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 451 | ACD137 | 18 Kent St | Grants Road | 2024-07-15 08:30 | 2024-07-15 16:42 | 0.014503 | 2.9478e-05 | 1 | 492 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 452 | ACD137 | 19 Kent St | Grants Road | 2024-07-15 08:30 | 2024-07-15 16:42 | 0.014503 | 2.9478e-05 | 1 | 492 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 453 | ACD137 | 20 Kent St | Grants Road | 2024-07-15 08:30 | 2024-07-15 17:18 | 0.015564 | 2.9478e-05 | 1 | 528 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 454 | ACD137 | 15 Kent St | Grants Road | 2024-07-15 08:30 | 2024-07-15 17:18 | 0.015564 | 2.9478e-05 | 1 | 528 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 455 | GWM1167 | TX Fuses TO B1443 | Hadlow | 2024-07-15 09:00 | 2024-07-15 15:42 | 0.0237 | 5.8955e-05 | 2 | 804 | Planned | Planned interruption | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 456 | 3915 | Fuses TO A234 | Morven | 2024-07-15 15:38 | 2024-07-15 21:34 | 0.010494 | 2.9478e-05 | 1 | 356 | Unplanned | Third party interference | Truck vs Pole #32093 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 457 | ACD140 | TX B204-19,20,17,40,42,44,46,48,39,28,30,31 Kelvin St | Grants Road | 2024-07-16 08:30 | 2024-07-16 15:34 | 0.72491 | 0.0017097 | 58 | 24592 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 458 | ACD140 | 19 Kelvin St | Grants Road | 2024-07-16 08:30 | 2024-07-16 15:38 | 0.012616 | 2.9478e-05 | 1 | 428 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 459 | ACD140 | 20 Kelvin St | Grants Road | 2024-07-16 08:30 | 2024-07-16 15:42 | 0.012734 | 2.9478e-05 | 1 | 432 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 460 | ACD140 | 17 Kelvin St | Grants Road | 2024-07-16 08:30 | 2024-07-16 15:48 | 0.012911 | 2.9478e-05 | 1 | 438 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 461 | ACD140 | 40 Kelvin St | Grants Road | 2024-07-16 08:30 | 2024-07-16 15:45 | 0.012823 | 2.9478e-05 | 1 | 435 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 462 | ACD140 | 42 Kelvin St | Grants Road | 2024-07-16 08:30 | 2024-07-16 15:50 | 0.01297 | 2.9478e-05 | 1 | 440 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 463 | ACD140 | 44 Kelvin St | Grants Road | 2024-07-16 08:30 | 2024-07-16 15:51 | 0.013 | 2.9478e-05 | 1 | 441 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 464 | ACD140 | 46 Kelvin St | Grants Road | 2024-07-16 08:30 | 2024-07-16 15:39 | 0.012646 | 2.9478e-05 | 1 | 429 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 465 | ACD140 | 48 Kelvin St | Grants Road | 2024-07-16 08:30 | 2024-07-16 15:44 | 0.012793 | 2.9478e-05 | 1 | 434 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 466 | ACD140 | 39 Kelvin St | Grants Road | 2024-07-16 08:30 | 2024-07-16 15:36 | 0.012557 | 2.9478e-05 | 1 | 426 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 467 | ACD140 | 28 Kelvin St | Grants Road | 2024-07-16 08:30 | 2024-07-16 15:46 | 0.012852 | 2.9478e-05 | 1 | 436 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 468 | ACD140 | 30 Kelvin St | Grants Road | 2024-07-16 08:30 | 2024-07-16 15:42 | 0.012734 | 2.9478e-05 | 1 | 432 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 469 | ACD140 | 31 Kelvin St | Grants Road | 2024-07-16 08:30 | 2024-07-16 15:52 | 0.013029 | 2.9478e-05 | 1 | 442 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 470 | ACD138A | 11kV Break Pole #29714-44,38,23,25,8 Arun St | Grants Road | 2024-07-17 08:30 | 2024-07-17 15:54 | 0.62823 | 0.0014149 | 48 | 21312 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 471 | ACD138A | LV Break Pole #29714-5,3,17 Arun St | Grants Road | 2024-07-17 08:30 | 2024-07-17 15:57 | 0.092236 | 0.00020634 | 7 | 3129 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 472 | ACD138A | 44 Arun St | Grants Road | 2024-07-17 08:30 | 2024-07-17 15:59 | 0.013235 | 2.9478e-05 | 1 | 449 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 473 | ACD138A | 38 Arun St | Grants Road | 2024-07-17 08:30 | 2024-07-17 16:01 | 0.013294 | 2.9478e-05 | 1 | 451 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 474 | ACD138A | 23 Arun St | Grants Road | 2024-07-17 08:30 | 2024-07-17 16:03 | 0.013353 | 2.9478e-05 | 1 | 453 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 475 | ACD138A | 25 Arun St | Grants Road | 2024-07-17 08:30 | 2024-07-17 16:08 | 0.013501 | 2.9478e-05 | 1 | 458 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 476 | ACD138A | 8 Arun St | Grants Road | 2024-07-17 08:30 | 2024-07-17 16:02 | 0.013324 | 2.9478e-05 | 1 | 452 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 477 | ACD138A | 5 Arun St | Grants Road | 2024-07-17 08:30 | 2024-07-17 16:02 | 0.013324 | 2.9478e-05 | 1 | 452 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 478 | ACD138A | 3 Arun St | Grants Road | 2024-07-17 08:30 | 2024-07-17 16:00 | 0.013265 | 2.9478e-05 | 1 | 450 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 479 | ACD138A | 17 Arun St | Grants Road | 2024-07-17 08:30 | 2024-07-17 16:08 | 0.013501 | 2.9478e-05 | 1 | 458 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 480 | BDS004 | TX D1067-17.12,11,7 Church St-16 Burdon Rd | Woodbury | 2024-07-17 08:36 | 2024-07-17 16:05 | 0.079413 | 0.00017687 | 6 | 2694 | Planned | Planned interruption | GLD Township Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 481 | BDS004 | Fuses G161-20,14 Church-18,3 High St | Woodbury | 2024-07-17 08:36 | 2024-07-17 16:14 | 0.24301 | 0.0005306 | 18 | 8244 | Planned | Planned interruption | GLD Township Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 482 | BDS004 | 20 Church St | Woodbury | 2024-07-17 08:36 | 2024-07-17 16:37 | 0.014179 | 2.9478e-05 | 1 | 481 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 483 | BDS004 | 14 Church St | Woodbury | 2024-07-17 08:36 | 2024-07-17 16:49 | 0.014532 | 2.9478e-05 | 1 | 493 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 484 | BDS004 | 18 High St | Woodbury | 2024-07-17 08:36 | 2024-07-17 16:24 | 0.013796 | 2.9478e-05 | 1 | 468 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 485 | BDS004 | 17 Church St | Woodbury | 2024-07-17 08:36 | 2024-07-17 16:50 | 0.014562 | 2.9478e-05 | 1 | 494 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 486 | BDS004 | 12 Church St | Woodbury | 2024-07-17 08:36 | 2024-07-17 16:40 | 0.014267 | 2.9478e-05 | 1 | 484 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 487 | BDS004 | 11 Church St | Woodbury | 2024-07-17 08:36 | 2024-07-17 16:45 | 0.014415 | 2.9478e-05 | 1 | 489 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 488 | BDS004 | 3 High St | Woodbury | 2024-07-17 08:36 | 2024-07-17 16:55 | 0.014709 | 2.9478e-05 | 1 | 499 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 489 | BDS004 | 7 Church St | Woodbury | 2024-07-17 08:36 | 2024-07-17 16:32 | 0.014031 | 2.9478e-05 | 1 | 476 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 490 | BDS004 | 16 Burdon St | Woodbury | 2024-07-17 08:36 | 2024-07-17 16:40 | 0.014267 | 2.9478e-05 | 1 | 484 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 491 | SKE1771 | Fuses L316-ABS L769 | Elginshire | 2024-07-17 09:02 | 2024-07-17 17:09 | 0.028711 | 5.8955e-05 | 2 | 974 | Planned | Planned interruption | TX Replacement / Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 492 | SKE1771 | ABS L769 | Elginshire | 2024-07-17 09:02 | 2024-07-17 17:28 | 0.014916 | 2.9478e-05 | 1 | 506 | Planned | Planned interruption | TX Replacement / Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 493 | ACD138B | 11kV Break Pole #29714-44A,52,50,48,35,41,39,35A,37,41A,45,47,43 Arun St-7,5,2,15,11 Killick Place | Grants Road | 2024-07-18 08:30 | 2024-07-18 15:57 | 0.46118 | 0.0010317 | 35 | 15645 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 494 | ACD138B | 44A Arun St | Grants Road | 2024-07-18 08:30 | 2024-07-18 16:03 | 0.013353 | 2.9478e-05 | 1 | 453 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 495 | ACD138B | 52 Arun St | Grants Road | 2024-07-18 08:30 | 2024-07-18 16:05 | 0.013412 | 2.9478e-05 | 1 | 455 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 496 | ACD138B | 50 Arun St | Grants Road | 2024-07-18 08:30 | 2024-07-18 16:10 | 0.01356 | 2.9478e-05 | 1 | 460 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 497 | ACD138B | 48 Arun St | Grants Road | 2024-07-18 08:30 | 2024-07-18 16:51 | 0.014768 | 2.9478e-05 | 1 | 501 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 498 | ACD138B | 35 Arun St | Grants Road | 2024-07-18 08:30 | 2024-07-18 16:21 | 0.013884 | 2.9478e-05 | 1 | 471 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 499 | ACD138B | 41 Arun St | Grants Road | 2024-07-18 08:30 | 2024-07-18 16:05 | 0.013412 | 2.9478e-05 | 1 | 455 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 500 | ACD138B | 39 Arun St | Grants Road | 2024-07-18 08:30 | 2024-07-18 16:16 | 0.013737 | 2.9478e-05 | 1 | 466 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 501 | ACD138B | 35A Arun St | Grants Road | 2024-07-18 08:30 | 2024-07-18 16:22 | 0.013913 | 2.9478e-05 | 1 | 472 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 502 | ACD138B | 37 Arun St | Grants Road | 2024-07-18 08:30 | 2024-07-18 16:25 | 0.014002 | 2.9478e-05 | 1 | 475 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 503 | ACD138B | 41A Arun St | Grants Road | 2024-07-18 08:30 | 2024-07-18 16:30 | 0.014149 | 2.9478e-05 | 1 | 480 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 504 | ACD138B | 45 Arun St | Grants Road | 2024-07-18 08:30 | 2024-07-18 16:30 | 0.014149 | 2.9478e-05 | 1 | 480 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 505 | ACD138B | 47 Arun St | Grants Road | 2024-07-18 08:30 | 2024-07-18 16:25 | 0.014002 | 2.9478e-05 | 1 | 475 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 506 | ACD138B | 43 Arun St | Grants Road | 2024-07-18 08:30 | 2024-07-18 16:20 | 0.013854 | 2.9478e-05 | 1 | 470 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 507 | ACD138B | 7 Killick Pl | Grants Road | 2024-07-18 08:30 | 2024-07-18 16:04 | 0.013383 | 2.9478e-05 | 1 | 454 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 508 | ACD138B | 5 Killick Pl | Grants Road | 2024-07-18 08:30 | 2024-07-18 16:09 | 0.01353 | 2.9478e-05 | 1 | 459 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 509 | ACD138B | 2 Killick Pl | Grants Road | 2024-07-18 08:30 | 2024-07-18 16:13 | 0.013648 | 2.9478e-05 | 1 | 463 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 510 | ACD138B | 15 Killick Pl | Grants Road | 2024-07-18 08:30 | 2024-07-18 16:20 | 0.013854 | 2.9478e-05 | 1 | 470 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 511 | ACD138B | 11 Killick Pl | Grants Road | 2024-07-18 08:30 | 2024-07-18 16:25 | 0.014002 | 2.9478e-05 | 1 | 475 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 512 | ACD138B | LV Break Pole #29714-11,9,10 Arun St | Grants Road | 2024-07-18 08:32 | 2024-07-18 15:59 | 0.092236 | 0.00020634 | 7 | 3129 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 513 | ACD138B | 11 Arun St | Grants Road | 2024-07-18 08:32 | 2024-07-18 16:02 | 0.013265 | 2.9478e-05 | 1 | 450 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 514 | ACD138B | 9 Arun St | Grants Road | 2024-07-18 08:32 | 2024-07-18 16:05 | 0.013353 | 2.9478e-05 | 1 | 453 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 515 | ACD138B | 10 Arun St | Grants Road | 2024-07-18 08:32 | 2024-07-18 16:15 | 0.013648 | 2.9478e-05 | 1 | 463 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 516 | BDS005 | G326 to end - G154 to end | Woodbury | 2024-07-18 08:46 | 2024-07-18 17:37 | 1.534 | 0.0028888 | 98 | 52038 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 517 | SRT226 | Fuses TO C205 | Fairlie Rural | 2024-07-19 09:00 | 2024-07-19 09:37 | 0.0010907 | 2.9478e-05 | 1 | 37 | Planned | Planned interruption | Pole Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 518 | SKE1692 | TE31 | North Mole | 2024-07-21 08:26 | 2024-07-21 12:10 | 0.006603 | 2.9478e-05 | 1 | 224 | Planned | Planned interruption | RMU & TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 519 | 5022 | Fuses TO D1391 | Geraldine Township | 2024-07-21 11:30 | 2024-07-21 16:36 | 0.0090202 | 2.9478e-05 | 1 | 306 | Unplanned | Third party interference | Digger Broke Conductor between Pole #35167 and Pole #35168 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 520 | 3805 | W461 to end | Morven | 2024-07-22 06:52 | 2024-07-22 09:40 | 0.0049522 | 2.9478e-05 | 1 | 168 | Unplanned | Wildlife | Broken conductor due to goose vs line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 521 | 3805 | W742 to end - W461 to end | Morven | 2024-07-22 06:52 | 2024-07-22 09:35 | 0.057658 | 0.00035373 | 12 | 1956 | Unplanned | Wildlife | Broken conductor due to goose vs line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 522 | 3809 | TX D1391 | Geraldine Township | 2024-07-22 11:09 | 2024-07-22 14:05 | 0.0051881 | 2.9478e-05 | 1 | 176 | Unplanned | Third party interference | Tractor V Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 523 | 5140 | CB W103-ABS W461-TX A1154- TX A1157-TX A1158 | Morven | 2024-07-23 05:54 | 2024-07-23 13:50 | 0.12628 | 0.0002653 | 9 | 4284 | Unplanned | Wildlife | Goose V Lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 524 | 5140 | ABS W461 | Morven | 2024-07-23 05:54 | 2024-07-23 13:55 | 0.014179 | 2.9478e-05 | 1 | 481 | Unplanned | Wildlife | Goose V Lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 525 | 5140 | TX A1154 | Morven | 2024-07-23 05:54 | 2024-07-23 14:00 | 0.014326 | 2.9478e-05 | 1 | 486 | Unplanned | Wildlife | Goose V Lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 526 | 5140 | TX A1157 | Morven | 2024-07-23 05:54 | 2024-07-23 14:09 | 0.014591 | 2.9478e-05 | 1 | 495 | Unplanned | Wildlife | Goose V Lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 527 | 5140 | TX A1158 | Morven | 2024-07-23 05:54 | 2024-07-23 14:14 | 0.014739 | 2.9478e-05 | 1 | 500 | Unplanned | Wildlife | Goose V Lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 528 | ACD152 | TX B203 CCT2-84 & 86 Glen St | Grants Road | 2024-07-23 08:30 | 2024-07-23 16:45 | 0.23346 | 0.00047164 | 16 | 7920 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 529 | ACD152 | 84 Glen St | Grants Road | 2024-07-23 08:30 | 2024-07-23 16:50 | 0.014739 | 2.9478e-05 | 1 | 500 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 530 | ACD152 | 86 Glen St | Grants Road | 2024-07-23 08:30 | 2024-07-23 16:51 | 0.014768 | 2.9478e-05 | 1 | 501 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 531 | BDS006 | G152 to end - Tx D661 - 15 Burdon Rd - 16 Burdon Rd | Woodbury | 2024-07-23 08:40 | 2024-07-23 16:24 | 0.20516 | 0.00044216 | 15 | 6960 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 532 | BDS006 | Tx D661 - 36 Burdon Rd | Woodbury | 2024-07-23 08:40 | 2024-07-23 16:35 | 0.070009 | 0.00014739 | 5 | 2375 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 533 | BDS006 | 36 Burdon Rd | Woodbury | 2024-07-23 08:40 | 2024-07-23 16:37 | 0.014061 | 2.9478e-05 | 1 | 477 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 534 | BDS006 | 16 Burdon Rd | Woodbury | 2024-07-23 08:40 | 2024-07-23 16:38 | 0.01409 | 2.9478e-05 | 1 | 478 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 535 | BDS006 | 15 Burdon Rd | Woodbury | 2024-07-23 08:40 | 2024-07-23 16:45 | 0.014297 | 2.9478e-05 | 1 | 485 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 536 | ACD152 | TX B972-8,10,14,16,18 Ayr St | Grants Road | 2024-07-23 08:42 | 2024-07-23 16:41 | 0.52243 | 0.0010907 | 37 | 17723 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 537 | ACD152 | 8 Ayr St | Grants Road | 2024-07-23 08:42 | 2024-07-23 16:51 | 0.014415 | 2.9478e-05 | 1 | 489 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 538 | ACD152 | 10 Ayr St | Grants Road | 2024-07-23 08:42 | 2024-07-23 16:53 | 0.014474 | 2.9478e-05 | 1 | 491 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 539 | ACD152 | 14 Ayr St | Grants Road | 2024-07-23 08:42 | 2024-07-23 16:54 | 0.014503 | 2.9478e-05 | 1 | 492 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 540 | ACD152 | 16 Ayr St | Grants Road | 2024-07-23 08:42 | 2024-07-23 16:57 | 0.014591 | 2.9478e-05 | 1 | 495 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 541 | ACD152 | 18 Ayr St | Grants Road | 2024-07-23 08:42 | 2024-07-23 16:55 | 0.014532 | 2.9478e-05 | 1 | 493 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 542 | PJD1605 | TX E356 CCT2-DB4461 | Tekapo | 2024-07-23 10:05 | 2024-07-23 13:37 | 0.062493 | 0.00029478 | 10 | 2120 | Planned | Planned interruption | TX Replacement / Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 543 | PJD1605 | TX E356 CCT3 | Tekapo | 2024-07-23 10:05 | 2024-07-23 13:51 | 0.1399 | 0.00061903 | 21 | 4746 | Planned | Planned interruption | TX Replacement / Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 544 | PJD1605 | TX E356 CCT4 | Tekapo | 2024-07-23 10:05 | 2024-07-23 14:16 | 0.096186 | 0.00038321 | 13 | 3263 | Planned | Planned interruption | TX Replacement / Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 545 | PJD1605 | DB4461 | Tekapo | 2024-07-23 10:05 | 2024-07-23 13:47 | 0.006544 | 2.9478e-05 | 1 | 222 | Planned | Planned interruption | TX Replacement / Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 546 | ACD155 | TX B972-31,40,38,51,49,25,21,17,20,24,16 Glen St-38,40 Athol Place-9,21,19 Ayr St | Grants Road | 2024-07-24 08:30 | 2024-07-24 16:13 | 0.35485 | 0.00076642 | 26 | 12038 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 547 | ACD155 | 31 Glen St | Grants Road | 2024-07-24 08:30 | 2024-07-24 16:16 | 0.013737 | 2.9478e-05 | 1 | 466 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 548 | ACD155 | 40 Glen St | Grants Road | 2024-07-24 08:30 | 2024-07-24 16:16 | 0.013737 | 2.9478e-05 | 1 | 466 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 549 | ACD155 | 38 Glen St | Grants Road | 2024-07-24 08:30 | 2024-07-24 16:19 | 0.013825 | 2.9478e-05 | 1 | 469 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 550 | ACD155 | 51 Glen St | Grants Road | 2024-07-24 08:30 | 2024-07-24 16:16 | 0.013737 | 2.9478e-05 | 1 | 466 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 551 | ACD155 | 49 Glen St | Grants Road | 2024-07-24 08:30 | 2024-07-24 16:20 | 0.013854 | 2.9478e-05 | 1 | 470 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 552 | ACD155 | 25 Glen St | Grants Road | 2024-07-24 08:30 | 2024-07-24 16:23 | 0.013943 | 2.9478e-05 | 1 | 473 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 553 | ACD155 | 21 Glen St | Grants Road | 2024-07-24 08:30 | 2024-07-24 16:33 | 0.014238 | 2.9478e-05 | 1 | 483 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 554 | ACD155 | 17 Glen St | Grants Road | 2024-07-24 08:30 | 2024-07-24 16:36 | 0.014326 | 2.9478e-05 | 1 | 486 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 555 | ACD155 | 20 Glen St | Grants Road | 2024-07-24 08:30 | 2024-07-24 16:43 | 0.014532 | 2.9478e-05 | 1 | 493 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 556 | ACD155 | 24 Glen St | Grants Road | 2024-07-24 08:30 | 2024-07-24 16:45 | 0.014591 | 2.9478e-05 | 1 | 495 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 557 | ACD155 | 16 Glen St | Grants Road | 2024-07-24 08:30 | 2024-07-24 16:50 | 0.014739 | 2.9478e-05 | 1 | 500 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 558 | ACD155 | 38 Athol Place | Grants Road | 2024-07-24 08:30 | 2024-07-24 16:22 | 0.013913 | 2.9478e-05 | 1 | 472 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 559 | ACD155 | 40 Athol Place | Grants Road | 2024-07-24 08:30 | 2024-07-24 16:30 | 0.014149 | 2.9478e-05 | 1 | 480 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 560 | ACD155 | 9 Ayr St | Grants Road | 2024-07-24 08:30 | 2024-07-24 16:48 | 0.01468 | 2.9478e-05 | 1 | 498 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 561 | ACD155 | 21 Ayr St | Grants Road | 2024-07-24 08:30 | 2024-07-24 16:44 | 0.014562 | 2.9478e-05 | 1 | 494 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 562 | ACD155 | 19 Ayr St | Grants Road | 2024-07-24 08:30 | 2024-07-24 16:56 | 0.014916 | 2.9478e-05 | 1 | 506 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 563 | HTR042 | Fuses W236-1 ICP | Glenavy | 2024-07-24 08:30 | 2024-07-24 17:39 | 0.032366 | 5.8955e-05 | 2 | 1098 | Planned | Planned interruption | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 564 | HTR042 | 1 ICP | Glenavy | 2024-07-24 08:30 | 2024-07-24 17:46 | 0.01639 | 2.9478e-05 | 1 | 556 | Planned | Planned interruption | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 565 | BDS007 | ABS G154-Fuses G326 | Woodbury | 2024-07-24 08:43 | 2024-07-24 15:54 | 1.2451 | 0.0028888 | 98 | 42238 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 566 | BDS008 | Fuses G152-TX D890-TXD330-TX D1470-TX D1526 | Woodbury | 2024-07-25 08:31 | 2024-07-25 16:52 | 0.26583 | 0.0005306 | 18 | 9018 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 567 | BDS008 | TX D890 | Woodbury | 2024-07-25 08:31 | 2024-07-25 16:59 | 0.029949 | 5.8955e-05 | 2 | 1016 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 568 | BDS008 | TX D330 | Woodbury | 2024-07-25 08:31 | 2024-07-25 17:11 | 0.015328 | 2.9478e-05 | 1 | 520 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 569 | BDS008 | TX D1470 | Woodbury | 2024-07-25 08:31 | 2024-07-25 17:37 | 0.016095 | 2.9478e-05 | 1 | 546 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 570 | BDS008 | TX D1526 | Woodbury | 2024-07-25 08:31 | 2024-07-25 17:40 | 0.016183 | 2.9478e-05 | 1 | 549 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 571 | 3807 | Beyond CB W590 | Tawai | 2024-07-26 10:52 | 2024-07-26 12:38 | 0.53744 | 0.0050702 | 172 | 18232 | Unplanned | Wildlife | Phase to Phase after Goose flew into lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 572 | 3807 | Beyond ABS W494 | Tawai | 2024-07-26 10:52 | 2024-07-26 13:56 | 0.499 | 0.0027119 | 92 | 16928 | Unplanned | Wildlife | Phase to Phase after Goose flew into lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 573 | 3876 | CB W664 to RMU W699 | Waihaorunga | 2024-07-28 04:21 | 2024-07-28 04:57 | 0.83728 | 0.023258 | 789 | 28404 | Unplanned | Wildlife | Possum at pole #20944 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 574 | 3876 | RMU W699 to end | Waihaorunga | 2024-07-28 04:21 | 2024-07-28 06:30 | 0.038026 | 0.00029478 | 10 | 1290 | Unplanned | Wildlife | Possum at pole #20944 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 575 | 4414 | PAR CB6 to end - L162 | Normanby | 2024-07-28 14:36 | 2024-07-28 15:30 | 0.86116 | 0.015947 | 541 | 29214 | Unplanned | Third party interference | Tree on line @ Tx B1417 caused by farmer cutting trees | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 576 | 4414 | L162 | Normanby | 2024-07-28 14:36 | 2024-07-28 17:50 | 0.17156 | 0.00088433 | 30 | 5820 | Unplanned | Third party interference | Tree on line @ Tx B1417 caused by farmer cutting trees | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 577 | ACD157 | ABS F273 | Fairlie Rural | 2024-07-29 08:40 | 2024-07-29 08:44 | 0.0018866 | 0.00047164 | 16 | 64 | Planned | Planned interruption | Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 578 | ACD156 | D335-02-5 Darby St | Geraldine Township | 2024-07-29 09:00 | 2024-07-29 18:37 | 0.085043 | 0.00014739 | 5 | 2885 | Planned | Planned interruption | TX Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 579 | ACD156 | D335-03-27 Hewlings St | Geraldine Township | 2024-07-29 09:00 | 2024-07-29 19:04 | 0.28487 | 0.00047164 | 16 | 9664 | Planned | Planned interruption | TX Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 580 | ACD156 | 5 Darby St | Geraldine Township | 2024-07-29 09:00 | 2024-07-29 19:04 | 0.017805 | 2.9478e-05 | 1 | 604 | Planned | Planned interruption | TX Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 581 | ACD156 | 27 Hewlings St | Geraldine Township | 2024-07-29 09:00 | 2024-07-29 19:26 | 0.018453 | 2.9478e-05 | 1 | 626 | Planned | Planned interruption | TX Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 582 | ACD156 | D335-04 | Geraldine Township | 2024-07-29 09:00 | 2024-07-29 18:41 | 0.30828 | 0.0005306 | 18 | 10458 | Planned | Planned interruption | TX Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 583 | ACD157 | ABS F255-ABS F277-ABS F273-TX C291 | Fairlie Rural | 2024-07-29 09:03 | 2024-07-29 14:07 | 0.21507 | 0.00070746 | 24 | 7296 | Planned | Planned interruption | Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 584 | ACD157 | TX C291 | Fairlie Rural | 2024-07-29 09:03 | 2024-07-29 14:48 | 0.01017 | 2.9478e-05 | 1 | 345 | Planned | Planned interruption | Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 585 | 3806 | Beyond F284 | Fairlie Rural | 2024-07-29 13:02 | 2024-07-29 13:57 | 0.0064851 | 0.00011791 | 4 | 220 | Unplanned | Defective equipment | Broken binder wire & insulator at pole #10742 & pole #10743 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 586 | ACD157 | ABS F273 | Fairlie Rural | 2024-07-29 14:35 | 2024-07-29 14:41 | 0.0028299 | 0.00047164 | 16 | 96 | Planned | Planned interruption | Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 587 | JJV151 | TE140 CCT17 | Le Cren Street | 2024-07-29 18:20 | 2024-07-29 18:30 | 0.0011791 | 0.00011791 | 4 | 40 | Planned | Planned interruption | Lucy Box replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 588 | JJV151 | TE140 CCT15-LB H24 to H253 | Le Cren Street | 2024-07-29 18:20 | 2024-07-29 18:41 | 0.0018571 | 8.8433e-05 | 3 | 63 | Planned | Planned interruption | Lucy Box replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 589 | JJV151 | TE140 CCT16 | Le Cren Street | 2024-07-29 18:20 | 2024-07-29 19:19 | 0.012174 | 0.00020634 | 7 | 413 | Planned | Planned interruption | Lucy Box replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 590 | JJV151 | TE140 CCT14 | Le Cren Street | 2024-07-29 18:20 | 2024-07-29 19:19 | 0.0052175 | 8.8433e-05 | 3 | 177 | Planned | Planned interruption | Lucy Box replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 591 | JJV151 | TE140 CCT18-H337 CCT1-26 Canon St (2 ICPs) - 32 Canon St - 79 Sophia St | Le Cren Street | 2024-07-29 18:20 | 2024-07-30 06:19 | 0.042389 | 5.8955e-05 | 2 | 1438 | Planned | Planned interruption | Lucy Box replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 592 | JJV151 | 26 Canon St | Le Cren Street | 2024-07-29 18:20 | 2024-07-30 08:00 | 0.048343 | 5.8955e-05 | 2 | 1640 | Planned | Planned interruption | Lucy Box replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 593 | JJV151 | 32 Canon St | Le Cren Street | 2024-07-29 18:20 | 2024-07-30 08:20 | 0.024761 | 2.9478e-05 | 1 | 840 | Planned | Planned interruption | Lucy Box replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 594 | JJV151 | 79 Sophia St | Le Cren Street | 2024-07-29 18:20 | 2024-07-30 08:10 | 0.024466 | 2.9478e-05 | 1 | 830 | Planned | Planned interruption | Lucy Box replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 595 | JJV151 | TE140 CCT15-LB H24 to H253 | Le Cren Street | 2024-07-29 18:56 | 2024-07-29 19:03 | 0.00061903 | 8.8433e-05 | 3 | 21 | Planned | Planned interruption | Lucy Box replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 596 | JJV151 | TE140 CCT16 | Le Cren Street | 2024-07-30 06:00 | 2024-07-30 06:19 | 0.0039205 | 0.00020634 | 7 | 133 | Planned | Planned interruption | Lucy Box replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 597 | JJV151 | TE140 CCT14 | Le Cren Street | 2024-07-30 06:00 | 2024-07-30 06:19 | 0.0016802 | 8.8433e-05 | 3 | 57 | Planned | Planned interruption | Lucy Box replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 598 | JJV151 | TE140 CCT17 | Le Cren Street | 2024-07-30 06:02 | 2024-07-30 06:19 | 0.0020045 | 0.00011791 | 4 | 68 | Planned | Planned interruption | Lucy Box replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 599 | RAK147 | ABS L817 | Hadlow | 2024-07-31 09:00 | 2024-07-31 14:24 | 0.31518 | 0.00097276 | 33 | 10692 | Planned | Planned interruption | New ABS and removal of fuses L819 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 600 | RAK146 | Links L286-ABS L802 | Hadlow | 2024-07-31 09:17 | 2024-07-31 12:40 | 0.053856 | 0.0002653 | 9 | 1827 | Planned | Planned interruption | CB L287 Settings changes | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 601 | PJD1623 | Fuses B1078 cct 06 | Highfield | 2024-08-01 09:00 | 2024-08-01 13:05 | 0.057776 | 0.00023582 | 8 | 1960 | Planned | Planned interruption | DB Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 602 | PJD1623 | Fuses B1078 cct 05 | Highfield | 2024-08-01 09:02 | 2024-08-01 13:03 | 0.099458 | 0.00041269 | 14 | 3374 | Planned | Planned interruption | DB Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 603 | PJD1623 | Fuses B1078 cct 03 | Highfield | 2024-08-01 09:03 | 2024-08-01 13:02 | 0.17613 | 0.00073694 | 25 | 5975 | Planned | Planned interruption | DB Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 604 | PJD1623 | LB458 cct 04 | Highfield | 2024-08-01 09:14 | 2024-08-01 13:11 | 0.069862 | 0.00029478 | 10 | 2370 | Planned | Planned interruption | DB Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 605 | PJD1623 | DB2845 | Highfield | 2024-08-01 09:14 | 2024-08-01 13:44 | 0.023877 | 8.8433e-05 | 3 | 810 | Planned | Planned interruption | DB Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 606 | PJD1623 | CB B899 cct 03 - LB458 cct 04 - DB2845 | Highfield | 2024-08-01 09:14 | 2024-08-01 13:15 | 0.078145 | 0.00032425 | 11 | 2651 | Planned | Planned interruption | DB Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 607 | PJD1623 | CB B899 cct 02 | Highfield | 2024-08-01 09:17 | 2024-08-01 12:51 | 0.2334 | 0.0010907 | 37 | 7918 | Planned | Planned interruption | DB Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 608 | PJD1623 | CB B899 cct 04 | Highfield | 2024-08-01 09:17 | 2024-08-01 12:51 | 0.018925 | 8.8433e-05 | 3 | 642 | Planned | Planned interruption | DB Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 609 | PJD1625 | Beyond ABS L328 | Arowhenua | 2024-08-01 17:05 | 2024-08-01 18:31 | 0.020281 | 0.00023582 | 8 | 688 | Unplanned | Defective equipment | Broken binder wire & insulator at pole #35549 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 610 | ACD158 | F295 to End | Cave | 2024-08-05 08:08 | 2024-08-05 08:11 | 0.0029183 | 0.00097276 | 33 | 99 | Planned | Planned interruption | Albury Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 611 | ACD158 | ABS FX17 | Cave | 2024-08-05 08:09 | 2024-08-05 08:27 | 0.0010612 | 5.8955e-05 | 2 | 36 | Planned | Planned interruption | Albury Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 612 | ACD158 | LB ABS F293 | Cave | 2024-08-05 08:30 | 2024-08-05 16:13 | 0.027296 | 5.8955e-05 | 2 | 926 | Planned | Planned interruption | Albury Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 613 | ACD158 | TX B1963 | Cave | 2024-08-05 08:30 | 2024-08-05 16:48 | 0.01468 | 2.9478e-05 | 1 | 498 | Planned | Planned interruption | Albury Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 614 | ACD158 | TX B1957 | Cave | 2024-08-05 08:30 | 2024-08-05 16:47 | 0.01465 | 2.9478e-05 | 1 | 497 | Planned | Planned interruption | Albury Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 615 | ACD158 | TX B1263 | Cave | 2024-08-05 08:30 | 2024-08-05 16:46 | 0.014621 | 2.9478e-05 | 1 | 496 | Planned | Planned interruption | Albury Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 616 | ACD158 | TX B1704 | Cave | 2024-08-05 08:30 | 2024-08-05 16:43 | 0.014532 | 2.9478e-05 | 1 | 493 | Planned | Planned interruption | Albury Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 617 | ACD158 | ABS L1239 | Sutherland | 2024-08-05 08:32 | 2024-08-05 16:13 | 0.23102 | 0.00050112 | 17 | 7837 | Planned | Planned interruption | Albury Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 618 | ACD159 | F298 - TOB1034 - TOB1033 - B335'01' | Cave | 2024-08-06 08:33 | 2024-08-06 16:47 | 1.9659 | 0.0039795 | 135 | 66690 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 619 | ACD159 | B335 '01' | Cave | 2024-08-06 08:33 | 2024-08-06 16:54 | 0.59073 | 0.0011791 | 40 | 20040 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 620 | ACD159 | Fuses TOB1034 | Cave | 2024-08-06 08:33 | 2024-08-06 16:52 | 0.10297 | 0.00020634 | 7 | 3493 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 621 | ACD159 | Fuses TOB1033 | Cave | 2024-08-06 08:33 | 2024-08-06 17:11 | 0.030539 | 5.8955e-05 | 2 | 1036 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 622 | ACD159 | 20 Charles St | Cave | 2024-08-06 08:33 | 2024-08-06 17:01 | 0.014975 | 2.9478e-05 | 1 | 508 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 623 | ACD159 | 28 Charles St | Cave | 2024-08-06 08:33 | 2024-08-06 16:58 | 0.014886 | 2.9478e-05 | 1 | 505 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 624 | ACD159 | 1383 SH8 Albury Cave Road | Cave | 2024-08-06 08:33 | 2024-08-06 17:03 | 0.015034 | 2.9478e-05 | 1 | 510 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 625 | SKE1741 | TX TE72 | June Street | 2024-08-06 09:00 | 2024-08-06 15:41 | 0.27187 | 0.00067799 | 23 | 9223 | Planned | Planned interruption | RMU & TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 626 | SKE1741 | TX TE72 | June Street | 2024-08-06 09:00 | 2024-08-06 15:53 | 0.048697 | 0.00011791 | 4 | 1652 | Planned | Planned interruption | RMU & TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 627 | SKE1741 | TX TE72 | June Street | 2024-08-06 09:00 | 2024-08-06 16:03 | 0.22444 | 0.0005306 | 18 | 7614 | Planned | Planned interruption | RMU & TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 628 | SKE1741 | TX TE72 | June Street | 2024-08-06 09:00 | 2024-08-06 16:14 | 0.29425 | 0.00067799 | 23 | 9982 | Planned | Planned interruption | RMU & TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 629 | SKE1741 | TX TE72 | June Street | 2024-08-06 09:00 | 2024-08-06 16:19 | 0.18117 | 0.00041269 | 14 | 6146 | Planned | Planned interruption | RMU & TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 630 | SKE1741 | TX TE72 | June Street | 2024-08-06 09:00 | 2024-08-06 16:28 | 0.13206 | 0.00029478 | 10 | 4480 | Planned | Planned interruption | RMU & TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 631 | ACD159 | LB ABSF293 - ABS F298 | Cave | 2024-08-06 17:34 | 2024-08-06 17:36 | 0.0024172 | 0.0012086 | 41 | 82 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 632 | ACD160 | Fuses F136 | Cave | 2024-08-07 08:30 | 2024-08-07 16:05 | 0.013412 | 2.9478e-05 | 1 | 455 | Planned | Planned interruption | Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 633 | ACD160 | Fuses F136 | Cave | 2024-08-07 08:30 | 2024-08-07 16:07 | 0.013471 | 2.9478e-05 | 1 | 457 | Planned | Planned interruption | Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 634 | ACD160 | Fuses F136 | Cave | 2024-08-07 08:30 | 2024-08-07 16:30 | 0.014149 | 2.9478e-05 | 1 | 480 | Planned | Planned interruption | Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 635 | ACD160 | Fuses F136 | Cave | 2024-08-07 08:30 | 2024-08-07 16:40 | 0.014444 | 2.9478e-05 | 1 | 490 | Planned | Planned interruption | Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 636 | ACD160 | Fuses F136 | Cave | 2024-08-07 08:30 | 2024-08-07 15:55 | 0.013118 | 2.9478e-05 | 1 | 445 | Planned | Planned interruption | Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 637 | ACD161 | TX B1034 | Cave | 2024-08-08 09:15 | 2024-08-08 11:50 | 0.027414 | 0.00017687 | 6 | 930 | Planned | Planned interruption | Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 638 | ACD161 | TX B1034 | Cave | 2024-08-08 09:15 | 2024-08-08 11:51 | 0.0045985 | 2.9478e-05 | 1 | 156 | Planned | Planned interruption | Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 639 | ACD161 | TX B1034 | Cave | 2024-08-08 09:15 | 2024-08-08 11:56 | 0.0047459 | 2.9478e-05 | 1 | 161 | Planned | Planned interruption | Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 640 | ACD162 | TX B1673 | Cave | 2024-08-08 09:20 | 2024-08-08 12:27 | 0.0055123 | 2.9478e-05 | 1 | 187 | Planned | Planned interruption | Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 641 | SKE1831 | TX E224 | Urban #2 | 2024-08-09 09:00 | 2024-08-09 16:00 | 0.049522 | 0.00011791 | 4 | 1680 | Planned | Planned interruption | RMU & TX Maintenanace | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 642 | SKE1831 | TX E223 | Urban #2 | 2024-08-09 09:00 | 2024-08-09 15:55 | 0.061166 | 0.00014739 | 5 | 2075 | Planned | Planned interruption | RMU & TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 643 | SKE1831 | TX E222 | Urban #2 | 2024-08-09 09:00 | 2024-08-09 15:50 | 0.048343 | 0.00011791 | 4 | 1640 | Planned | Planned interruption | RMU & TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 644 | SKE1831 | TX E187 | Urban #2 | 2024-08-09 09:00 | 2024-08-09 16:15 | 0.025646 | 5.8955e-05 | 2 | 870 | Planned | Planned interruption | RMU & TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 645 | SKE1831 | TX E149 | Urban #2 | 2024-08-09 09:00 | 2024-08-09 16:21 | 0.025999 | 5.8955e-05 | 2 | 882 | Planned | Planned interruption | RMU & TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 646 | SRT240 | TX B373 | Hadlow | 2024-08-09 09:00 | 2024-08-09 13:58 | 0.0087843 | 2.9478e-05 | 1 | 298 | Planned | Planned interruption | TX Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 647 | 3811 | Orakipaoa Island Road Fuse T122 | Milford | 2024-08-09 09:06 | 2024-08-09 10:11 | 0.028741 | 0.00044216 | 15 | 975 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 648 | 3877 | CB L1220 to end minus ABS L156 | Normanby | 2024-08-10 10:04 | 2024-08-10 11:57 | 0.25982 | 0.0022993 | 78 | 8814 | Unplanned | Third party interference | Digger VS Lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 649 | 3877 | ABS L156 to end | Normanby | 2024-08-10 10:04 | 2024-08-10 13:59 | 0.33251 | 0.0014149 | 48 | 11280 | Unplanned | Third party interference | Digger VS Lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 650 | SEM014 | Fuses W510 | Ikawai | 2024-08-12 10:04 | 2024-08-12 11:19 | 0.019897 | 0.0002653 | 9 | 675 | Unplanned | Defective equipment | Missing nuts on Insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 651 | 4718 | CB L876 (Racecourse Rd) | Levels Plain | 2024-08-12 11:01 | 2024-08-12 11:46 | 0.23744 | 0.0052765 | 179 | 8055 | Unplanned | Vegetation | Tree fell on lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 652 | 4718 | Fuses L195 | Levels Plain | 2024-08-12 11:01 | 2024-08-12 14:25 | 0.030067 | 0.00014739 | 5 | 1020 | Unplanned | Vegetation | Tree fell on lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 653 | 4719 | CB F107 (Totara Valley Rd) | Totara Valley | 2024-08-12 11:10 | 2024-08-12 12:31 | 0.37726 | 0.0046575 | 158 | 12798 | Unplanned | Defective equipment | Broken pole #40354 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 654 | 3813 | G295 to End | Woodbury | 2024-08-12 11:23 | 2024-08-12 12:28 | 0.12071 | 0.0018571 | 63 | 4095 | Unplanned | Vegetation | Branches at Pole #11033 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 655 | 4719 | CB F107 (Totara Valley Rd) | Totara Valley | 2024-08-12 12:31 | 2024-08-12 17:36 | 0.56641 | 0.0018571 | 63 | 19215 | Unplanned | Defective equipment | Broken pole #40354 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 656 | 4719 | CB F107 (Totara Valley Rd) | Totara Valley | 2024-08-12 17:33 | 2024-08-12 17:36 | 0.0084011 | 0.0028004 | 95 | 285 | Unplanned | Defective equipment | Broken pole #40354 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 657 | 4719 | CB F150 (Langley Downs Rd) | Raincliff | 2024-08-12 17:33 | 2024-08-12 17:36 | 0.0068093 | 0.0022698 | 77 | 231 | Unplanned | Defective equipment | Broken pole #40354 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 658 | HTR054 | Links at pole #27513 | Mountainview | 2024-08-13 08:00 | 2024-08-13 11:55 | 0.048491 | 0.00020634 | 7 | 1645 | Planned | Planned interruption | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 659 | RAK151A JMR691 | LB262 | Urban #2 | 2024-08-13 09:02 | 2024-08-13 14:44 | 0.020163 | 5.8955e-05 | 2 | 684 | Planned | Planned interruption | PD Defect | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 660 | RAK151A JMR691 | E249-02 | Urban #2 | 2024-08-13 09:02 | 2024-08-13 15:18 | 0.011084 | 2.9478e-05 | 1 | 376 | Planned | Planned interruption | PD Defect | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 661 | RAK151A JMR691 | E249-03 | Urban #2 | 2024-08-13 09:02 | 2024-08-13 15:18 | 0.055418 | 0.00014739 | 5 | 1880 | Planned | Planned interruption | PD Defect | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 662 | RAK151A JMR691 | E249-06 | Urban #2 | 2024-08-13 09:02 | 2024-08-13 15:18 | 0.088669 | 0.00023582 | 8 | 3008 | Planned | Planned interruption | PD Defect | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 663 | RAK151A JMR691 | DB1501 | Urban #2 | 2024-08-13 09:02 | 2024-08-13 15:23 | 0.033693 | 8.8433e-05 | 3 | 1143 | Planned | Planned interruption | PD Defect | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 664 | RAK151A JMR691 | DB1492 | Urban #2 | 2024-08-13 09:02 | 2024-08-13 15:32 | 0.022993 | 5.8955e-05 | 2 | 780 | Planned | Planned interruption | PD Defect | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 665 | RAK151A JMR691 | DB1499 | Urban #2 | 2024-08-13 09:02 | 2024-08-13 15:26 | 0.022639 | 5.8955e-05 | 2 | 768 | Planned | Planned interruption | PD Defect | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 666 | SRS002 | ABS T499 (Rolleston Rd) | Rolleston Road | 2024-08-13 09:40 | 2024-08-13 11:58 | 0.0040679 | 2.9478e-05 | 1 | 138 | Unplanned | Defective equipment | Transformer repairs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 667 | SRS002 | TX D1488 | Rolleston Road | 2024-08-13 09:40 | 2024-08-13 12:00 | 0.0041269 | 2.9478e-05 | 1 | 140 | Unplanned | Defective equipment | Transformer repairs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 668 | 00002 | LBS T541 | Orton | 2024-08-13 14:11 | 2024-08-13 14:25 | 0.0012381 | 8.8433e-05 | 3 | 42 | Unplanned | Wildlife | Duck in TX DO Fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 669 | HTR056 | ABS F168 - ABS F170 - ABS F169 | Cave | 2024-08-20 09:08 | 2024-08-20 15:36 | 0.057187 | 0.00014739 | 5 | 1940 | Planned | Planned interruption | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 670 | 3810 | CB W308 | Otaio | 2024-08-20 09:40 | 2024-08-20 10:53 | 0.025822 | 0.00035373 | 12 | 876 | Unplanned | Unknown | Broken Jumper | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 671 | JJV152 | ABS W345 | Otaio | 2024-08-21 08:00 | 2024-08-21 15:28 | 0.039618 | 8.8433e-05 | 3 | 1344 | Planned | Planned interruption | Transformer Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 672 | JJV152 | 8 Murray St | Otaio | 2024-08-21 08:00 | 2024-08-21 15:42 | 0.013619 | 2.9478e-05 | 1 | 462 | Planned | Planned interruption | Transformer Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 673 | 4720 | Fuses W127 | Morven | 2024-08-21 22:05 | 2024-08-22 00:03 | 0.052175 | 0.00044216 | 15 | 1770 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 674 | 00003 | CB T626-ABS T675 | Rolleston Road | 2024-08-22 07:47 | 2024-08-22 08:56 | 0.36611 | 0.005306 | 180 | 12420 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 675 | 00003 | ABS T675 | Rolleston Road | 2024-08-22 07:47 | 2024-08-22 09:14 | 0.012823 | 0.00014739 | 5 | 435 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 676 | SKE1762 | RMU L489 | Old North Road | 2024-08-22 08:31 | 2024-08-22 16:38 | 0.014356 | 2.9478e-05 | 1 | 487 | Planned | Planned interruption | Transformer Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 677 | CWL027 | TOA1539 | Morven | 2024-08-23 08:00 | 2024-08-23 10:05 | 0.0036847 | 2.9478e-05 | 1 | 125 | Planned | Planned interruption | Upgrade Disconnect | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 678 | HTR049 & SKE1787 | ABS T462 - D1403 '01' - D1402'01' | Mahan Road | 2024-08-23 09:00 | 2024-08-23 13:56 | 0.20068 | 0.00067799 | 23 | 6808 | Planned | Planned interruption | Replace Red Tag Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 679 | HTR049 & SKE1787 | D1403'01' | Mahan Road | 2024-08-23 09:00 | 2024-08-23 14:13 | 0.0092265 | 2.9478e-05 | 1 | 313 | Planned | Planned interruption | Replace Red Tag Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 680 | HTR049 & SKE1787 | D1402'01' | Mahan Road | 2024-08-23 09:00 | 2024-08-23 14:05 | 0.026972 | 8.8433e-05 | 3 | 915 | Planned | Planned interruption | Replace Red Tag Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 681 | SKE1761 | RMU L427 - RMU L481 | Old North Road | 2024-08-23 09:00 | 2024-08-23 15:30 | 0.022993 | 5.8955e-05 | 2 | 780 | Planned | Planned interruption | Transformer Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 682 | SRS003 | B871 LV OH - 7 Shaw St - 11 Shaw St - 14 Shaw St | Redruth 2 | 2024-08-25 08:09 | 2024-08-25 17:20 | 0.097453 | 0.00017687 | 6 | 3306 | Planned | Planned interruption | Tx B871 upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 683 | SRS003 | 7 Shaw St + 11 Shaw St + 14 Shaw St | Redruth 2 | 2024-08-25 08:09 | 2024-08-25 17:29 | 0.049522 | 8.8433e-05 | 3 | 1680 | Planned | Planned interruption | Tx B871 upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 684 | SRS003 | DB4038 | Redruth 2 | 2024-08-25 08:09 | 2024-08-25 17:45 | 0.050937 | 8.8433e-05 | 3 | 1728 | Planned | Planned interruption | Tx B871 upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 685 | SRS003 | DB4773 | Redruth 2 | 2024-08-25 08:09 | 2024-08-25 18:00 | 0.034843 | 5.8955e-05 | 2 | 1182 | Planned | Planned interruption | Tx B871 upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 686 | SRS003 | Compactor Shed | Redruth 2 | 2024-08-25 08:09 | 2024-08-25 18:12 | 0.017775 | 2.9478e-05 | 1 | 603 | Planned | Planned interruption | Tx B871 upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 687 | SKE1782 | ABS T165 | Pleasant Point Township | 2024-08-26 08:15 | 2024-08-26 08:20 | 0.0030952 | 0.00061903 | 21 | 105 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 688 | SKE1782 | CB L1159 - ABS T165 -B755'01' - B756'01' - B1133'01' - B1197'01' - D104'01' - B130'01' - B1503'01' | Pleasant Point Township | 2024-08-26 08:37 | 2024-08-26 16:53 | 0.39476 | 0.0007959 | 27 | 13392 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 689 | SKE1782 | TX B755'01' | Pleasant Point Township | 2024-08-26 08:37 | 2024-08-26 17:09 | 0.015093 | 2.9478e-05 | 1 | 512 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 690 | SKE1782 | TX B756'01' | Pleasant Point Township | 2024-08-26 08:37 | 2024-08-26 17:18 | 0.015358 | 2.9478e-05 | 1 | 521 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 691 | SKE1782 | TX B1133'01' | Pleasant Point Township | 2024-08-26 08:37 | 2024-08-26 17:09 | 0.015093 | 2.9478e-05 | 1 | 512 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 692 | SKE1782 | TX B1197'01' | Pleasant Point Township | 2024-08-26 08:37 | 2024-08-26 17:12 | 0.030362 | 5.8955e-05 | 2 | 1030 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 693 | SKE1782 | TX D104'01' | Pleasant Point Township | 2024-08-26 08:37 | 2024-08-26 17:32 | 0.031541 | 5.8955e-05 | 2 | 1070 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 694 | SKE1782 | TX B1305'01' | Pleasant Point Township | 2024-08-26 08:37 | 2024-08-26 17:32 | 0.015771 | 2.9478e-05 | 1 | 535 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 695 | SKE1782 | TX B1503'01' | Pleasant Point Township | 2024-08-26 08:37 | 2024-08-26 17:21 | 0.030893 | 5.8955e-05 | 2 | 1048 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 696 | 4721 | Fuses TOB749 | Hadlow | 2024-08-26 09:00 | 2024-08-26 09:12 | 0.00035373 | 2.9478e-05 | 1 | 12 | Unplanned | Wildlife | Nest on HV Bushings | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 697 | SKE1783 &GWM1178 | TX B756'01' | Pleasant Point Township | 2024-08-27 08:31 | 2024-08-27 16:38 | 0.014356 | 2.9478e-05 | 1 | 487 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 698 | SKE1783 &GWM1178 | TX B1197'01' | Pleasant Point Township | 2024-08-27 08:31 | 2024-08-27 16:49 | 0.02936 | 5.8955e-05 | 2 | 996 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 699 | SKE1783 &GWM1178 | TX B1503'01' | Pleasant Point Township | 2024-08-27 08:31 | 2024-08-27 16:55 | 0.029713 | 5.8955e-05 | 2 | 1008 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 700 | SKE1783 &GWM1178 | TX B1305'01' | Pleasant Point Township | 2024-08-27 08:31 | 2024-08-27 17:06 | 0.015181 | 2.9478e-05 | 1 | 515 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 701 | SKE1783 &GWM1178 | TX D104'01' | Pleasant Point Township | 2024-08-27 08:31 | 2024-08-27 17:18 | 0.031069 | 5.8955e-05 | 2 | 1054 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 702 | SKE1783 &GWM1178 | CB L1159 - ABS T165 - B756'01' - B1197'01' - D104'01' - B130'01' - B1503'01' | Pleasant Point Township | 2024-08-27 08:31 | 2024-08-27 16:26 | 0.40605 | 0.00085485 | 29 | 13775 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 703 | SKE1784 | ABS T165-205 Young Rd | Pleasant Point Township | 2024-08-28 08:58 | 2024-08-28 16:25 | 0.26353 | 0.00058955 | 20 | 8940 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 704 | SKE1784 | 205 Young Rd | Pleasant Point Township | 2024-08-28 08:58 | 2024-08-28 16:28 | 0.013265 | 2.9478e-05 | 1 | 450 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 705 | HTR055 | Fuses F167 TO END | Cave | 2024-08-29 09:00 | 2024-08-29 10:30 | 0.015918 | 0.00017687 | 6 | 540 | Planned | Planned interruption | Tree Trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 706 | 00004 | ABS T224 | Temuka East | 2024-08-29 13:39 | 2024-08-29 16:47 | 1.8565 | 0.009875 | 335 | 62980 | Unplanned | Defective equipment | HV line broken | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 707 | 00004 | TMK CB8-ABS T224 | Temuka East | 2024-08-29 13:39 | 2024-08-29 15:30 | 3.6843 | 0.033192 | 1126 | 124986 | Unplanned | Defective equipment | HV line broken | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 708 | SKE1763 | ABS L456 ICP 1 | Waipopo | 2024-08-30 08:43 | 2024-08-30 14:31 | 0.010258 | 2.9478e-05 | 1 | 348 | Planned | Planned interruption | RMU & TX Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 709 | SKE1763 | ABS L456 ICP 2 | Waipopo | 2024-08-30 08:43 | 2024-08-30 14:39 | 0.010494 | 2.9478e-05 | 1 | 356 | Planned | Planned interruption | RMU & TX Maint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 710 | JRM030 | Fuses To A1424 | Otaio | 2024-08-30 09:14 | 2024-08-30 11:20 | 0.0037142 | 2.9478e-05 | 1 | 126 | Planned | Planned interruption | Transformer repairs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 711 | WMR081 | Fuses F284 | Fairlie Rural | 2024-08-30 10:22 | 2024-08-30 11:02 | 0.0047164 | 0.00011791 | 4 | 160 | Unplanned | Defective equipment | Binder Repairs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 712 | 3817 | ABY CB2742-ABS FX17 | Cave | 2024-09-01 15:35 | 2024-09-01 16:49 | 0.82673 | 0.011172 | 379 | 28046 | Unplanned | Adverse weather | Broken conductor due to wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 713 | 3817 | ABS FX17-CB F295 | Cave | 2024-09-01 15:35 | 2024-09-01 20:50 | 0.018571 | 5.8955e-05 | 2 | 630 | Unplanned | Adverse weather | Broken conductor due to wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 714 | 3817 | CB F295 | Cave | 2024-09-01 15:35 | 2024-09-01 17:12 | 0.094358 | 0.00097276 | 33 | 3201 | Unplanned | Adverse weather | Broken conductor due to wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 715 | 3814 | CB T565 to ABS T422 | Woodbury | 2024-09-01 18:36 | 2024-09-02 08:31 | 1.1569 | 0.0013854 | 47 | 39245 | Unplanned | Adverse weather | High Winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 716 | 3814 | ABS T422 to ABS T426 | Woodbury | 2024-09-01 18:36 | 2024-09-02 09:04 | 0.61408 | 0.00070746 | 24 | 20832 | Unplanned | Adverse weather | High Winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 717 | 3814 | ABS T426 to end | Woodbury | 2024-09-01 18:36 | 2024-09-02 09:26 | 3.2007 | 0.0035963 | 122 | 108580 | Unplanned | Adverse weather | High Winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 718 | 3817 | CB L107 | Totara Valley | 2024-09-01 20:54 | 2024-09-01 20:56 | 0.0093149 | 0.0046575 | 158 | 316 | Unplanned | Adverse weather | Broken conductor due to wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 719 | 3817 | CB F295 | Cave | 2024-09-01 20:55 | 2024-09-01 21:06 | 0.0107 | 0.00097276 | 33 | 363 | Unplanned | Adverse weather | Broken conductor due to wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 720 | SKE1786 | Fuses D822 | Totara Valley | 2024-09-02 08:57 | 2024-09-02 15:42 | 0.023877 | 5.8955e-05 | 2 | 810 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 721 | SKE1786 | ABS T165 - ABS T316 | Totara Valley | 2024-09-02 08:57 | 2024-09-02 15:21 | 0.21507 | 0.00056008 | 19 | 7296 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 722 | 3815 | Fuses T489 to end | Woodbury | 2024-09-02 10:02 | 2024-09-02 12:12 | 0.030657 | 0.00023582 | 8 | 1040 | Unplanned | Adverse weather | High Winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 723 | 3812 | Fuses TO A115 | Otaio | 2024-09-02 10:46 | 2024-09-02 15:27 | 0.0082832 | 2.9478e-05 | 1 | 281 | Unplanned | Defective equipment | Broken Pole #40795 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 724 | 3819 | RGA 11- ABS T585 | Belfield | 2024-09-03 02:50 | 2024-09-03 04:07 | 0.21563 | 0.0028004 | 95 | 7315 | Unplanned | Adverse weather | Broken conductor due to wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 725 | 3819 | ABS T585-ABS T643 | Belfield | 2024-09-03 02:50 | 2024-09-03 04:48 | 0.097394 | 0.00082537 | 28 | 3304 | Unplanned | Adverse weather | Broken conductor due to wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 726 | 3819 | ABS T643 | Belfield | 2024-09-03 02:50 | 2024-09-03 09:50 | 0.13619 | 0.00032425 | 11 | 4620 | Unplanned | Adverse weather | Broken conductor due to wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 727 | 3823 | CB T127-ABS TX20 | Rangitata | 2024-09-03 02:56 | 2024-09-03 04:11 | 0.015476 | 0.00020634 | 7 | 525 | Unplanned | Adverse weather | Broken pole - wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 728 | 3823 | ABS TX20-ABS TX62-Links T458 | Rangitata | 2024-09-03 02:56 | 2024-09-03 06:28 | 0.24997 | 0.0011791 | 40 | 8480 | Unplanned | Adverse weather | broken pole - wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 729 | 3823 | ABS TX62 | Rangitata | 2024-09-03 02:56 | 2024-09-03 04:30 | 0.024938 | 0.0002653 | 9 | 846 | Unplanned | Adverse weather | Broken pole wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 730 | 3823 | Links T458 | Rangitata | 2024-09-03 02:56 | 2024-09-03 05:08 | 0.070039 | 0.0005306 | 18 | 2376 | Unplanned | Adverse weather | Broken pole wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 731 | 3822 | Fuses L195 | Levels Plain | 2024-09-03 07:06 | 2024-09-03 14:54 | 0.068978 | 0.00014739 | 5 | 2340 | Unplanned | Adverse weather | Broken Pole & conductor due to wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 732 | 3820 | Fuses T488 | Rolleston Road | 2024-09-03 09:27 | 2024-09-03 10:52 | 0.29316 | 0.0034489 | 117 | 9945 | Unplanned | Adverse weather | Tree on lines and line repair due to wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 733 | 991 | Fuses L164 | Normanby | 2024-09-03 14:19 | 2024-09-03 14:28 | 0.0034489 | 0.00038321 | 13 | 117 | Unplanned | Adverse weather | Fencing wire on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 734 | 3821 | Links T421 | Woodbury | 2024-09-03 19:14 | 2024-09-03 20:38 | 0.039618 | 0.00047164 | 16 | 1344 | Unplanned | Adverse weather | Broken conductor due to wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 735 | SRT243 | B678-02 | Grants Road | 2024-09-04 08:30 | 2024-09-04 17:30 | 0.14326 | 0.0002653 | 9 | 4860 | Planned | Planned interruption | Tim Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 736 | SRT243 | ABS L601 | Grants Road | 2024-09-04 08:30 | 2024-09-04 17:27 | 1.2347 | 0.0022993 | 78 | 41886 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 737 | SRT243 | B696-06 FUSES | Grants Road | 2024-09-04 08:30 | 2024-09-04 18:24 | 0.15759 | 0.0002653 | 9 | 5346 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 738 | SRT243 | B696-05 FUSES | Grants Road | 2024-09-04 08:30 | 2024-09-04 18:08 | 0.25557 | 0.00044216 | 15 | 8670 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 739 | SRT243 | LB460 | Grants Road | 2024-09-04 08:30 | 2024-09-04 18:12 | 0.034312 | 5.8955e-05 | 2 | 1164 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 740 | SRT243 | B696-03 FUSES | Grants Road | 2024-09-04 08:30 | 2024-09-04 17:48 | 0.13159 | 0.00023582 | 8 | 4464 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 741 | SRT243 | B696-04 FUSES | Grants Road | 2024-09-04 08:30 | 2024-09-04 17:48 | 0.39476 | 0.00070746 | 24 | 13392 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 742 | SRT243 | 41 Luxmoore Rd | Grants Road | 2024-09-04 08:30 | 2024-09-04 17:48 | 0.016449 | 2.9478e-05 | 1 | 558 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 743 | SRT243 | 39 Luxmoore Rd | Grants Road | 2024-09-04 08:30 | 2024-09-04 17:51 | 0.016537 | 2.9478e-05 | 1 | 561 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 744 | SRT243 | 42 Luxmoore Rd | Grants Road | 2024-09-04 08:30 | 2024-09-04 17:58 | 0.016743 | 2.9478e-05 | 1 | 568 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 745 | SRT243 | 46 Luxmoore Rd | Grants Road | 2024-09-04 08:30 | 2024-09-04 18:01 | 0.016832 | 2.9478e-05 | 1 | 571 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 746 | SRT243 | 48 Luxmoore Rd | Grants Road | 2024-09-04 08:30 | 2024-09-04 18:03 | 0.016891 | 2.9478e-05 | 1 | 573 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 747 | SRT243 | 97 Luxmoore Rd | Grants Road | 2024-09-04 08:30 | 2024-09-04 17:46 | 0.01639 | 2.9478e-05 | 1 | 556 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 748 | SRT243 | 95 Luxmoore Rd | Grants Road | 2024-09-04 08:30 | 2024-09-04 17:49 | 0.016478 | 2.9478e-05 | 1 | 559 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 749 | SRT243 | 94 Luxmoore Rd | Grants Road | 2024-09-04 08:30 | 2024-09-04 17:45 | 0.01636 | 2.9478e-05 | 1 | 555 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 750 | SRT243 | 93 Luxmoore Rd | Grants Road | 2024-09-04 08:30 | 2024-09-04 17:48 | 0.016449 | 2.9478e-05 | 1 | 558 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 751 | SRT243 | 75 Luxmoore Rd | Grants Road | 2024-09-04 08:30 | 2024-09-04 17:48 | 0.016449 | 2.9478e-05 | 1 | 558 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 752 | SRT243 | 77 Luxmoore Rd | Grants Road | 2024-09-04 08:30 | 2024-09-04 17:52 | 0.016566 | 2.9478e-05 | 1 | 562 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 753 | SRT243 | 81 Luxmoore Rd | Grants Road | 2024-09-04 08:30 | 2024-09-04 17:45 | 0.01636 | 2.9478e-05 | 1 | 555 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 754 | SRT243 | 84 Luxmoore Rd | Grants Road | 2024-09-04 08:30 | 2024-09-04 17:46 | 0.01639 | 2.9478e-05 | 1 | 556 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 755 | SRT243 | 86 Luxmoore Rd | Grants Road | 2024-09-04 08:30 | 2024-09-04 17:49 | 0.016478 | 2.9478e-05 | 1 | 559 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 756 | SRT243 | 88 Luxmoore Rd | Grants Road | 2024-09-04 08:30 | 2024-09-04 17:50 | 0.016507 | 2.9478e-05 | 1 | 560 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 757 | SRT243 | 83 Luxmoore Rd | Grants Road | 2024-09-04 08:30 | 2024-09-04 18:01 | 0.016832 | 2.9478e-05 | 1 | 571 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 758 | SRT243 | 28 Luxmoore Rd | Grants Road | 2024-09-04 08:30 | 2024-09-04 17:48 | 0.016449 | 2.9478e-05 | 1 | 558 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 759 | HTR057 | CB F295 | Cave | 2024-09-05 08:30 | 2024-09-05 08:33 | 0.0029183 | 0.00097276 | 33 | 99 | Planned | Planned interruption | Tree trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 760 | SKE1834 | FUSES E315-02 | Lakeside Drive | 2024-09-05 09:00 | 2024-09-05 14:42 | 0.030244 | 8.8433e-05 | 3 | 1026 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 761 | HTR057 | ABS FX17 | Cave | 2024-09-05 09:00 | 2024-09-05 14:58 | 0.021106 | 5.8955e-05 | 2 | 716 | Planned | Planned interruption | Tree trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 762 | SRS008 | ABS W262 | Waihaorunga | 2024-09-09 08:48 | 2024-09-11 17:38 | 0.10052 | 2.9478e-05 | 1 | 3410 | Planned | Planned interruption | Installing NEW RMU | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 763 | SRT233 SRT234 | Fuses TOD13 | Temuka East | 2024-09-09 09:28 | 2024-09-09 14:58 | 0.35019 | 0.0010612 | 36 | 11880 | Planned | Planned interruption | Replace Drop out Fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 764 | SRT233 SRT234 | 131 Richard Pearce Dr | Temuka East | 2024-09-09 09:28 | 2024-09-09 15:11 | 0.010111 | 2.9478e-05 | 1 | 343 | Planned | Planned interruption | Replace Drop out Fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 765 | JDJ125 | Fusesn TO D789 | Waitohi | 2024-09-09 09:53 | 2024-09-09 12:44 | 0.010081 | 5.8955e-05 | 2 | 342 | Planned | Planned interruption | Transformer Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 766 | JDJ125 | Fusesn TO D789 | Waitohi | 2024-09-09 09:53 | 2024-09-09 12:36 | 0.0048049 | 2.9478e-05 | 1 | 163 | Planned | Planned interruption | Transformer Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 767 | ACD165 | Fuses TOD857 | Belfield | 2024-09-10 09:00 | 2024-09-10 13:50 | 0.0085485 | 2.9478e-05 | 1 | 290 | Planned | Planned interruption | Replace Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 768 | HTR044 | Links F144 to end | Cave | 2024-09-10 09:00 | 2024-09-10 13:55 | 0.2174 | 0.00073694 | 25 | 7375 | Planned | Planned interruption | Tree trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 769 | SKE1758 | TE166-11 | June Street | 2024-09-10 09:00 | 2024-09-10 09:12 | 0.0099045 | 0.00082537 | 28 | 336 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 770 | SKE1758 | TE106-01 | June Street | 2024-09-10 09:00 | 2024-09-10 09:21 | 0.050141 | 0.0023877 | 81 | 1701 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 771 | SKE1758 | TE166-12 | June Street | 2024-09-10 09:00 | 2024-09-10 09:10 | 0.0041269 | 0.00041269 | 14 | 140 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 772 | SKE1758 | TE106-01 | June Street | 2024-09-10 15:30 | 2024-09-10 15:38 | 0.019102 | 0.0023877 | 81 | 648 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 773 | SKE1758 | TE166-12 | June Street | 2024-09-10 15:54 | 2024-09-10 16:25 | 0.012793 | 0.00041269 | 14 | 434 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 774 | SKE1758 | TE166-11 | June Street | 2024-09-10 16:00 | 2024-09-10 16:10 | 0.007959 | 0.0007959 | 27 | 270 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 775 | SKE1758 | 10a Brascombe Rd | June Street | 2024-09-10 16:00 | 2024-09-10 16:21 | 0.00061903 | 2.9478e-05 | 1 | 21 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 776 | SKE1788 | Fuses TO TE53 | Le Cren Street | 2024-09-11 08:30 | 2024-09-11 18:55 | 0.90275 | 0.0014444 | 49 | 30625 | Planned | Planned interruption | R&T Cable | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 777 | 2850 | TE135-14 ,15, 16 | Le Cren Street | 2024-09-12 08:08 | 2024-09-12 08:13 | 0.0047164 | 0.00094328 | 32 | 160 | Unplanned | Human error | Incorrect Switch Operated | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 778 | 2849 | Beyond CB T127 Badham Road | Rangitata | 2024-09-12 08:52 | 2024-09-12 09:57 | 0.017244 | 0.0002653 | 9 | 585 | Unplanned | Unknown | Lines Down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 779 | 2849 | Beyond CB T127 Badham Road | Rangitata | 2024-09-12 08:52 | 2024-09-12 10:03 | 0.037672 | 0.0005306 | 18 | 1278 | Unplanned | Unknown | Lines Down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 780 | 2849 | Beyond CB T127 Badham Road | Rangitata | 2024-09-12 08:52 | 2024-09-12 11:05 | 0.027444 | 0.00020634 | 7 | 931 | Unplanned | Unknown | Lines Down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 781 | 2849 | Beyond CB T127 Badham Road | Rangitata | 2024-09-12 08:52 | 2024-09-12 13:42 | 0.34194 | 0.0011791 | 40 | 11600 | Unplanned | Unknown | Lines Down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 782 | 4724 | Fuses L862 | Levels Plain | 2024-09-13 09:59 | 2024-09-13 10:21 | 0.0064851 | 0.00029478 | 10 | 220 | Unplanned | Defective equipment | Damaged Insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 783 | 4723 | Links W745 | Tawai | 2024-09-13 12:03 | 2024-09-13 13:09 | 0.011673 | 0.00017687 | 6 | 396 | Unplanned | Vegetation | Trees over line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 784 | 3818 | Fuses TOB460 | Cave | 2024-09-14 13:50 | 2024-09-14 16:40 | 0.015034 | 8.8433e-05 | 3 | 510 | Unplanned | Third party interference | LV lines broken by digger | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 785 | 3816 | CB W465 | Otaio | 2024-09-16 01:19 | 2024-09-16 05:56 | 0.68589 | 0.0024761 | 84 | 23268 | Unplanned | Wildlife | Possum on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 786 | 4725 | Fuses F252 | Fairlie Rural | 2024-09-17 06:50 | 2024-09-17 09:32 | 0.023877 | 0.00014739 | 5 | 810 | Planned | Planned interruption | Tree Branch on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 787 | 4726 | Links Z439 | Urban #2 | 2024-09-17 13:45 | 2024-09-17 14:58 | 0.13342 | 0.0018276 | 62 | 4526 | Unplanned | Defective equipment | Cracked insulators causing high PD Tx E130 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 788 | PJD1626 | ABY CB2742 minus LB ABS F402 | Cave | 2024-09-18 07:33 | 2024-09-18 09:35 | 0.21218 | 0.0017392 | 59 | 7198 | Planned | Planned interruption | ABY GXP Outage | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 789 | PJD1626 | ABY CB2722 (Fairlie) + ABY CB4242 | ABY-FLE 33kV | 2024-09-18 07:37 | 2024-09-18 09:35 | 0.010435 | 8.8433e-05 | 3 | 354 | Planned | Planned interruption | ABY GXP Outage | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 790 | PJD1626 | FLE CB F374 to end + ABS F212 to end | Cricklewood | 2024-09-18 07:37 | 2024-09-18 09:35 | 0.28175 | 0.0023877 | 81 | 9558 | Planned | Planned interruption | ABY GXP Outage | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 791 | PJD1626 | CB F380 (Fairlie Rural) to end | Fairlie Rural | 2024-09-18 07:37 | 2024-09-18 09:35 | 2.6853 | 0.022757 | 772 | 91096 | Planned | Planned interruption | ABY GXP Outage | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 792 | PJD1626 | FLE CB F383 (FLE TS) minus TX C269 Minus TX C308 | Fairlie Township | 2024-09-18 07:37 | 2024-09-18 09:35 | 0.99133 | 0.0084011 | 285 | 33630 | Planned | Planned interruption | ABY GXP Outage | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 793 | PJD1626 | TX C308 | Fairlie Township | 2024-09-18 07:37 | 2024-09-18 09:35 | 0.073046 | 0.00061903 | 21 | 2478 | Planned | Planned interruption | ABY GXP Outage | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 794 | PJD1626 | TX C308 minus LV Links at pole #15321 minus Gold Club | Fairlie Township | 2024-09-18 17:31 | 2024-09-18 17:45 | 0.0037142 | 0.0002653 | 9 | 126 | Planned | Planned interruption | ABY GXP Outage | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 795 | PJD1626 | Golf Club | Fairlie Township | 2024-09-18 17:31 | 2024-09-18 17:55 | 0.00070746 | 2.9478e-05 | 1 | 24 | Planned | Planned interruption | ABY GXP Outage | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 796 | PJD1626 | LV from Links at pole #15321 to end | Fairlie Township | 2024-09-18 17:31 | 2024-09-18 18:30 | 0.019131 | 0.00032425 | 11 | 649 | Planned | Planned interruption | ABY GXP Outage | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 797 | 5128 | TX Fuses TO A163 to end | Mt Studholme | 2024-09-18 17:34 | 2024-09-18 19:42 | 0.0075463 | 5.8955e-05 | 2 | 256 | Unplanned | Defective equipment | Broken Stay Wire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 798 | PJD1626 | PLP CB2 (Sutherlands) to end | Cave | 2024-09-18 18:03 | 2024-09-18 18:04 | 0.0036847 | 0.0036847 | 125 | 125 | Unplanned | Defective equipment | LB ABS Flickers not engaged | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 799 | 5128 | Fuses W312 to end minus TX fuses TO A163 | Mt Studholme | 2024-09-18 19:10 | 2024-09-18 19:42 | 0.0028299 | 8.8433e-05 | 3 | 96 | Unplanned | Defective equipment | Broken Stay Wire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 800 | 4727 | ABS T675 | Rolleston Road | 2024-09-18 23:50 | 2024-09-19 13:07 | 0.11747 | 0.00014739 | 5 | 3985 | Unplanned | Third party interference | Broken Pole and conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 801 | 4727 | ABS T490 - ABS T675 | Rolleston Road | 2024-09-18 23:50 | 2024-09-19 01:58 | 0.53201 | 0.0041563 | 141 | 18048 | Unplanned | Third party interference | Broken Pole and conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 802 | 4727 | CB T626-ABS T490 | Rolleston Road | 2024-09-18 23:50 | 2024-09-19 00:56 | 0.075875 | 0.0011496 | 39 | 2574 | Unplanned | Third party interference | Broken Pole and conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 803 | 4730 | Links W742 | Morven | 2024-09-19 07:46 | 2024-09-19 10:10 | 0.055182 | 0.00038321 | 13 | 1872 | Unplanned | Defective equipment | Broken Conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 804 | 994 | Fuses TOD214 | Rangitata | 2024-09-19 11:30 | 2024-09-19 11:38 | 0.00023582 | 2.9478e-05 | 1 | 8 | Unplanned | Wildlife | Bird's nest on Transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 805 | 5127 | RGA CB13 to ABS T497 | Rangitata Island | 2024-09-21 09:56 | 2024-09-21 13:44 | 0.013442 | 5.8955e-05 | 2 | 456 | Unplanned | Third party interference | Car Vs Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 806 | 5126 | Fusess L716 / ABS L717 to end | Hadlow | 2024-09-21 10:00 | 2024-09-21 12:35 | 0.68079 | 0.0043922 | 149 | 23095 | Unplanned | Unknown | Unkknown - Blown DO | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 807 | 5125 | Fuses G245 to end | Speechley | 2024-09-21 16:19 | 2024-09-21 17:47 | 0.038911 | 0.00044216 | 15 | 1320 | Unplanned | Unknown | Unknown - Blown DO's | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 808 | 5023 | CB T626 (Rolleston Rd) - ABS T675 | Rolleston Road | 2024-09-21 18:43 | 2024-09-21 19:44 | 0.32366 | 0.005306 | 180 | 10980 | Unplanned | Defective equipment | Damaged Conductor between Pole #07206 and Pole #488723 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 809 | 5023 | ABS T675 | Rolleston Road | 2024-09-21 18:43 | 2024-09-21 22:22 | 0.032278 | 0.00014739 | 5 | 1095 | Unplanned | Defective equipment | Damaged Conductor between Pole #07206 and Pole #488723 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 810 | HTR062 | Fuses W161 | Morven | 2024-09-25 08:30 | 2024-09-25 13:57 | 0.067474 | 0.00020634 | 7 | 2289 | Planned | Planned interruption | Tree trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 811 | HTR063A SRT263 | Links W134 - Links W601 - ABS W190 - Fuses W161 | Morven | 2024-09-25 08:30 | 2024-09-25 13:31 | 0.20407 | 0.00067799 | 23 | 6923 | Planned | Planned interruption | Tree trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 812 | 4728 | ABS L171 - ABS L169 | Normanby | 2024-09-25 14:03 | 2024-09-25 15:47 | 0.088905 | 0.00085485 | 29 | 3016 | Unplanned | Defective equipment | Rotten Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 813 | 4415 | TOD366 | Speechley | 2024-09-25 19:10 | 2024-09-25 20:33 | 0.0073399 | 8.8433e-05 | 3 | 249 | Unplanned | Unknown | Unknown -Bown Tx Fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 814 | RAK141 | Links G292 | Speechley | 2024-09-26 08:36 | 2024-09-26 09:19 | 0.0012675 | 2.9478e-05 | 1 | 43 | Planned | Planned interruption | Installing NEW RMU | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 815 | JDJ116 JDJ117 | TOD426 | Temuka East | 2024-09-26 09:00 | 2024-09-26 13:26 | 0.39205 | 0.0014739 | 50 | 13300 | Planned | Planned interruption | Replace Drop out Fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 816 | JDJ116 JDJ117 | 9 Hyahurst St | Temuka East | 2024-09-26 09:00 | 2024-09-26 13:41 | 0.0082832 | 2.9478e-05 | 1 | 281 | Planned | Planned interruption | Replace Drop out Fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 817 | JDJ116 JDJ117 | 36 Hayhurst St | Temuka East | 2024-09-26 09:00 | 2024-09-26 13:30 | 0.007959 | 2.9478e-05 | 1 | 270 | Planned | Planned interruption | Replace Drop out Fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 818 | JDJ116 JDJ117 | 44 Hayhurst St | Temuka East | 2024-09-26 09:00 | 2024-09-26 13:35 | 0.0081064 | 2.9478e-05 | 1 | 275 | Planned | Planned interruption | Replace Drop out Fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 819 | JDJ116 JDJ117 | 29 Denmark St | Temuka East | 2024-09-26 09:00 | 2024-09-26 13:44 | 0.0083717 | 2.9478e-05 | 1 | 284 | Planned | Planned interruption | Replace Drop out Fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 820 | JRM031 | Fuses TOB1996 | Cave | 2024-09-26 09:47 | 2024-09-26 12:10 | 0.0084306 | 5.8955e-05 | 2 | 286 | Planned | Planned interruption | LV earth bar rusting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 821 | RAK141 | DB4759 | Speechley | 2024-09-26 17:31 | 2024-09-26 17:41 | 0.00029478 | 2.9478e-05 | 1 | 10 | Planned | Planned interruption | Installing NEW RMU | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 822 | 4601 | Fuses W155 | Waikakahi | 2024-10-02 11:47 | 2024-10-02 12:19 | 0.006603 | 0.00020634 | 7 | 224 | Unplanned | Defective equipment | Remove wrap off crossarm pole #43887 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 823 | 4602 | ABS W309 to end | Otaio | 2024-10-02 14:49 | 2024-10-02 18:30 | 0.13029 | 0.00058955 | 20 | 4420 | Unplanned | Defective equipment | Red tagged Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 824 | 4742 | Fuses TOC276 | Fairlie Rural | 2024-10-04 10:25 | 2024-10-04 13:54 | 0.0061608 | 2.9478e-05 | 1 | 209 | Unplanned | Defective equipment | Defective Transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 825 | 4416 | TO C44 to end | Cave | 2024-10-06 22:26 | 2024-10-07 15:35 | 0.060665 | 5.8955e-05 | 2 | 2058 | Unplanned | Defective equipment | Replace faulty Tx C44 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 826 | JDJ126 | TO D850 to end | Temuka West | 2024-10-07 09:00 | 2024-10-07 11:00 | 0.13796 | 0.0011496 | 39 | 4680 | Planned | Planned interruption | Replace Drop out Fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 827 | SRT264 | W510 to end | Ikawai | 2024-10-07 09:21 | 2024-10-07 10:13 | 0.013796 | 0.0002653 | 9 | 468 | Planned | Planned interruption | Replace red tag pole - outgae cancelled | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 828 | JDJ133 | TO C323 to end | Fairlie Rural | 2024-10-07 10:02 | 2024-10-07 15:42 | 0.010022 | 2.9478e-05 | 1 | 340 | Planned | Planned interruption | Replace Red Tag Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 829 | SRS006 | TE61 cct 11 | Douglas Street | 2024-10-09 06:00 | 2024-10-09 07:23 | 0.061166 | 0.00073694 | 25 | 2075 | Planned | Planned interruption | RMU replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 830 | SRS006 | TE61 cct 12 | Douglas Street | 2024-10-09 06:00 | 2024-10-09 07:23 | 0.0097866 | 0.00011791 | 4 | 332 | Planned | Planned interruption | RMU replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 831 | SRS006 | TE61 cct 13 | Douglas Street | 2024-10-09 06:00 | 2024-10-09 07:23 | 0.085633 | 0.0010317 | 35 | 2905 | Planned | Planned interruption | RMU replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 832 | SRS006 | TE61 cct 14 | Douglas Street | 2024-10-09 06:00 | 2024-10-09 07:20 | 0.037731 | 0.00047164 | 16 | 1280 | Planned | Planned interruption | RMU replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 833 | SRS006 | TE61 cct 15 | Douglas Street | 2024-10-09 06:00 | 2024-10-09 07:23 | 0.04404 | 0.0005306 | 18 | 1494 | Planned | Planned interruption | RMU replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 834 | SRT265 & GWM1190 | W238 to end - A664 - A854 | Mt Studholme | 2024-10-09 08:32 | 2024-10-09 15:08 | 0.10506 | 0.0002653 | 9 | 3564 | Planned | Planned interruption | Tx upgrade and tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 835 | SRT265 & GWM1190 | A664 | Mt Studholme | 2024-10-09 08:32 | 2024-10-09 15:14 | 0.01185 | 2.9478e-05 | 1 | 402 | Planned | Planned interruption | Tx upgrade and tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 836 | SRT265 & GWM1190 | A854 | Mt Studholme | 2024-10-09 08:32 | 2024-10-09 15:29 | 0.012292 | 2.9478e-05 | 1 | 417 | Planned | Planned interruption | Tx upgrade and tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 837 | SRS006 | TE61 cct 11 | Douglas Street | 2024-10-09 19:00 | 2024-10-09 20:19 | 0.058218 | 0.00073694 | 25 | 1975 | Planned | Planned interruption | RMU replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 838 | SRS006 | TE61 cct 12 | Douglas Street | 2024-10-09 19:00 | 2024-10-09 20:29 | 0.010494 | 0.00011791 | 4 | 356 | Planned | Planned interruption | RMU replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 839 | SRS006 | TE61 cct 13 | Douglas Street | 2024-10-09 19:00 | 2024-10-09 20:29 | 0.091823 | 0.0010317 | 35 | 3115 | Planned | Planned interruption | RMU replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 840 | SRS006 | TE61 cct 14 | Douglas Street | 2024-10-09 19:00 | 2024-10-09 20:29 | 0.041976 | 0.00047164 | 16 | 1424 | Planned | Planned interruption | RMU replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 841 | SRS006 | TE61 cct 15 | Douglas Street | 2024-10-09 19:00 | 2024-10-09 20:29 | 0.047223 | 0.0005306 | 18 | 1602 | Planned | Planned interruption | RMU replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 842 | HTR066 | W190 - W279 | Morven | 2024-10-10 08:34 | 2024-10-10 09:44 | 0.012381 | 0.00017687 | 6 | 420 | Planned | Planned interruption | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 843 | GWM1191 | TO B505 | Normanby | 2024-10-10 09:00 | 2024-10-10 12:52 | 0.027355 | 0.00011791 | 4 | 928 | Planned | Planned interruption | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 844 | JDJ134 | F218 | Fairlie Rural | 2024-10-10 10:00 | 2024-10-10 12:25 | 0.038468 | 0.0002653 | 9 | 1305 | Planned | Planned interruption | Replace red tagged pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 845 | 5141 | Fuses G185 | Woodbury | 2024-10-12 07:20 | 2024-10-12 09:18 | 0.031305 | 0.0002653 | 9 | 1062 | Unplanned | Unknown | Blown Fuses Cause Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 846 | 5142 | Fuses w132 | Glenavy | 2024-10-14 05:58 | 2024-10-14 06:22 | 0.0063672 | 0.0002653 | 9 | 216 | Unplanned | Wildlife | Blown Fuses Bird V Lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 847 | 4603 | Fuses TOB972 | Grants Road | 2024-10-14 08:00 | 2024-10-14 14:11 | 0.42651 | 0.0011496 | 39 | 14469 | Unplanned | Third party interference | Truck vs pole #45941 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 848 | 4603 | Service Fuses from pole #45941/#488753 | Grants Road | 2024-10-14 08:00 | 2024-10-14 14:25 | 0.034047 | 8.8433e-05 | 3 | 1155 | Unplanned | Third party interference | Truck vs pole #45941 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 849 | SKE1795 | TX B1233 CCT4 to end (to DB2649) | Morgans Rd | 2024-10-15 08:30 | 2024-10-15 14:55 | 0.43126 | 0.0011202 | 38 | 14630 | Planned | Planned interruption | Sub Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 850 | SKE1795 | TX B1233 CCT5 to end (to Hockey South Canterbury) | Morgans Rd | 2024-10-15 08:30 | 2024-10-15 15:02 | 0.011555 | 2.9478e-05 | 1 | 392 | Planned | Planned interruption | Sub Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 851 | SKE1836 | ICP fed from LB161 | M158 | 2024-10-15 09:08 | 2024-10-15 14:37 | 0.0096981 | 2.9478e-05 | 1 | 329 | Planned | Planned interruption | RMU & TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 852 | SKE1836 | ICP's fed from DB1414 | M158 | 2024-10-15 09:08 | 2024-10-15 15:03 | 0.020929 | 5.8955e-05 | 2 | 710 | Planned | Planned interruption | RMU & TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 853 | JRM033 | CB M357 to end | TEK-UHT 33kV | 2024-10-15 10:03 | 2024-10-15 14:28 | 0.0078116 | 2.9478e-05 | 1 | 265 | Planned | Planned interruption | CB Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 854 | SKE1836 | ICP fed from LB161 | M158 | 2024-10-15 14:51 | 2024-10-15 14:54 | 8.8433e-05 | 2.9478e-05 | 1 | 3 | Planned | Planned interruption | RMU & TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 855 | HTR047 | Links W131 to ABS WX19 | Glenavy | 2024-10-16 08:30 | 2024-10-16 12:37 | 0.36405 | 0.0014739 | 50 | 12350 | Planned | Planned interruption | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 856 | SKE1901 | TX B992 to end | Morgans Rd | 2024-10-16 08:30 | 2024-10-16 16:42 | 0.10152 | 0.00020634 | 7 | 3444 | Planned | Planned interruption | Sub Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 857 | SRT266 | Fuses L189 to end | Holme Station | 2024-10-16 09:00 | 2024-10-16 14:50 | 0.041269 | 0.00011791 | 4 | 1400 | Planned | Planned interruption | TX Upgrade & O/H to U/G service conversion | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 858 | SKE1835 | DB1070 to end (UHT Lodge) | M158 | 2024-10-16 09:07 | 2024-10-16 14:18 | 0.0091676 | 2.9478e-05 | 1 | 311 | Planned | Planned interruption | RMU & TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 859 | SKE1835 | TX E179 to end | M158 | 2024-10-16 09:07 | 2024-10-16 14:32 | 0.028741 | 8.8433e-05 | 3 | 975 | Planned | Planned interruption | RMU & TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 860 | SKE1835 | TX E169 to end | M158 | 2024-10-16 09:07 | 2024-10-16 14:39 | 0.078293 | 0.00023582 | 8 | 2656 | Planned | Planned interruption | RMU & TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 861 | SKE1835 | TX E168 to end | M158 | 2024-10-16 09:07 | 2024-10-16 14:45 | 0.0099634 | 2.9478e-05 | 1 | 338 | Planned | Planned interruption | RMU & TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 862 | SRT267 | ABS M452 to end | Simons | 2024-10-17 10:00 | 2024-10-17 11:53 | 0.06995 | 0.00061903 | 21 | 2373 | Planned | Planned interruption | Replace connections | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 863 | LXL068 | TX E10 CCT 04 | Lakeside Drive | 2024-10-18 11:04 | 2024-10-18 14:26 | 0.071454 | 0.00035373 | 12 | 2424 | Planned | Planned interruption | TX E10 repairs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 864 | LXL068 | TX E10 CCT 02 | Lakeside Drive | 2024-10-18 11:04 | 2024-10-18 14:26 | 0.16077 | 0.0007959 | 27 | 5454 | Planned | Planned interruption | TX E10 repairs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 865 | LXL068 | TX E10 CCT 03 | Lakeside Drive | 2024-10-18 11:04 | 2024-10-18 14:26 | 0.11314 | 0.00056008 | 19 | 3838 | Planned | Planned interruption | TX E10 repairs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 866 | LXL068 | TX E10 CCT 045 | Lakeside Drive | 2024-10-18 11:04 | 2024-10-18 14:26 | 0.059545 | 0.00029478 | 10 | 2020 | Planned | Planned interruption | TX E10 repairs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 867 | LXL068 | TX E10 CCT 06 | Lakeside Drive | 2024-10-18 11:04 | 2024-10-18 14:26 | 0.11909 | 0.00058955 | 20 | 4040 | Planned | Planned interruption | TX E10 repairs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 868 | SKE1691 | Trace from RMU L759 | Washdyke | 2024-10-19 08:17 | 2024-10-19 13:47 | 0.0097276 | 2.9478e-05 | 1 | 330 | Planned | Planned interruption | RMU & TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 869 | HTR046 | ABS W121 | Glenavy | 2024-10-21 08:30 | 2024-10-21 15:47 | 0.48951 | 0.0011202 | 38 | 16606 | Planned | Planned interruption | Tree Cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 870 | DVE371 | T420 - D301 - D1174 - D1877 | Woodbury | 2024-10-22 08:30 | 2024-10-22 16:33 | 0.32747 | 0.00067799 | 23 | 11109 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 871 | DVE371 | D301 | Woodbury | 2024-10-22 08:30 | 2024-10-22 16:42 | 0.029006 | 5.8955e-05 | 2 | 984 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 872 | DVE371 | D1174 | Woodbury | 2024-10-22 08:30 | 2024-10-22 17:03 | 0.030244 | 5.8955e-05 | 2 | 1026 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 873 | DVE371 | D1877 | Woodbury | 2024-10-22 08:30 | 2024-10-22 17:13 | 0.015417 | 2.9478e-05 | 1 | 523 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 874 | SKE1833 | E252 Cct 4 | Tekapo | 2024-10-22 09:04 | 2024-10-22 14:57 | 0.39541 | 0.0011202 | 38 | 13414 | Planned | Planned interruption | RMU & Tx Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 875 | SKE1833 | M294 - E356-01 | Tekapo | 2024-10-22 09:15 | 2024-10-22 14:35 | 1.198 | 0.0037437 | 127 | 40640 | Planned | Planned interruption | RMU & Tx Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 876 | SKE1833 | E356-01 | Tekapo | 2024-10-22 09:15 | 2024-10-22 14:50 | 0.45425 | 0.001356 | 46 | 15410 | Planned | Planned interruption | RMU & Tx Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 877 | DVE372 | T420 | Woodbury | 2024-10-23 08:30 | 2024-10-23 16:59 | 0.42012 | 0.00082537 | 28 | 14252 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 878 | JRM041 | TX E366 CCT2 | Urban #2 | 2024-10-23 09:02 | 2024-10-23 13:02 | 0.0070746 | 2.9478e-05 | 1 | 240 | Planned | Planned interruption | Repair TX | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 879 | JRM041 | TX E366 CCT3 | Urban #2 | 2024-10-23 09:02 | 2024-10-23 13:11 | 0.02936 | 0.00011791 | 4 | 996 | Planned | Planned interruption | Repair TX | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 880 | JRM041 | TX E366 CCT5 | Urban #2 | 2024-10-23 09:02 | 2024-10-23 13:24 | 0.046339 | 0.00017687 | 6 | 1572 | Planned | Planned interruption | Repair TX | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 881 | DVE373 | Fuses T420 - Fuses T429 - TX D623 - TX D1687 - TX D673 - TX D1725 | Woodbury | 2024-10-24 08:30 | 2024-10-24 16:56 | 0.13424 | 0.0002653 | 9 | 4554 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 882 | DVE373 | TX T429 to end | Woodbury | 2024-10-24 08:30 | 2024-10-24 17:10 | 0.22993 | 0.00044216 | 15 | 7800 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 883 | DVE373 | TX D623 | Woodbury | 2024-10-24 08:30 | 2024-10-24 17:18 | 0.015564 | 2.9478e-05 | 1 | 528 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 884 | DVE373 | TX D1687 | Woodbury | 2024-10-24 08:30 | 2024-10-24 17:28 | 0.015859 | 2.9478e-05 | 1 | 538 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 885 | DVE373 | TX D673 | Woodbury | 2024-10-24 08:30 | 2024-10-24 17:39 | 0.016183 | 2.9478e-05 | 1 | 549 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 886 | DVE373 | TX D1725 | Woodbury | 2024-10-24 08:30 | 2024-10-24 17:05 | 0.015181 | 2.9478e-05 | 1 | 515 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 887 | GWM1194 | ABS T643 to end | Belfield | 2024-10-24 09:00 | 2024-10-24 17:44 | 0.16991 | 0.00032425 | 11 | 5764 | Planned | Planned interruption | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 888 | SRS017 | TX TE132-H341 CCT2- H339 CCT3 - LB B31 | Barnard Street | 2024-10-24 20:30 | 2024-10-25 04:04 | 0.25427 | 0.00056008 | 19 | 8626 | Planned | Planned interruption | Lucy Box H89 & B10 replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 889 | SRS017 | LB B31- DB B30 | Barnard Street | 2024-10-24 20:30 | 2024-10-25 04:46 | 0.029242 | 5.8955e-05 | 2 | 992 | Planned | Planned interruption | Lucy Box H89 & B10 replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 890 | SRS017 | DB B30 | Barnard Street | 2024-10-24 20:30 | 2024-10-25 05:01 | 0.015063 | 2.9478e-05 | 1 | 511 | Planned | Planned interruption | Lucy Box H89 & B10 replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 891 | 4604 | Fuses F108 to end | Cave | 2024-10-25 07:58 | 2024-10-25 10:55 | 0.010435 | 5.8955e-05 | 2 | 354 | Unplanned | Defective equipment | Broken Conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 892 | SKE1909 | TX65 - T430 - Trace from Pole #08381 | Woodbury | 2024-10-25 10:24 | 2024-10-25 15:49 | 0.15328 | 0.00047164 | 16 | 5200 | Planned | Planned interruption | Replace Pole and upgrade Transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 893 | SKE1909 | TX D299 - 3ph ICP Fed From Pole #09434 | Woodbury | 2024-10-25 10:24 | 2024-10-25 16:01 | 0.039736 | 0.00011791 | 4 | 1348 | Planned | Planned interruption | Replace Pole and upgrade Transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 894 | SKE1909 | 3ph ICP Fed From Pole #09434 | Woodbury | 2024-10-25 10:24 | 2024-10-25 16:10 | 0.010199 | 2.9478e-05 | 1 | 346 | Planned | Planned interruption | Replace Pole and upgrade Transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 895 | 3825 | HLB CB M82- LBS M441 | Haldon-Lilybank 22kV | 2024-10-26 12:54 | 2024-10-26 13:44 | 0.02653 | 0.0005306 | 18 | 900 | Unplanned | Adverse weather | Broken Conductor - Snow | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 896 | 3825 | LBS M441 | Haldon-Lilybank 22kV | 2024-10-26 12:54 | 2024-10-26 16:58 | 0.27332 | 0.0011202 | 38 | 9272 | Unplanned | Adverse weather | Broken Conductor -Snow | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 897 | 4606 | Tx C341 | Fairlie Rural | 2024-10-26 19:15 | 2024-10-27 13:32 | 0.032337 | 2.9478e-05 | 1 | 1097 | Unplanned | Defective equipment | Broken Jumper at Pole #54293 / #54294 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 898 | 3824 | Fuses F222-ABS F403 | Fairlie Rural | 2024-10-27 11:18 | 2024-10-27 15:21 | 0.028652 | 0.00011791 | 4 | 972 | Unplanned | Adverse weather | Broken Conductor - weather | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 899 | 3824 | ABS F403 | Fairlie Rural | 2024-10-27 11:18 | 2024-10-27 15:29 | 0.014798 | 5.8955e-05 | 2 | 502 | Unplanned | Adverse weather | Broken Conductor weather | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 900 | 4606 | F226 - Tx C341 | Fairlie Rural | 2024-10-27 11:48 | 2024-10-27 13:32 | 0.030657 | 0.00029478 | 10 | 1040 | Unplanned | Defective equipment | Broken Jumper at Pole #54293 / #54294 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 901 | 4607 | PAR CB4 - W470 - L998 - B1018 | St Andrews | 2024-10-27 16:27 | 2024-10-27 17:45 | 0.37248 | 0.0047754 | 162 | 12636 | Unplanned | Defective equipment | Faulty Tx B1018 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 902 | 4607 | W470 | St Andrews | 2024-10-27 16:27 | 2024-10-27 18:05 | 0.52576 | 0.0053649 | 182 | 17836 | Unplanned | Defective equipment | Faulty Tx B1018 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 903 | 4607 | L998 | St Andrews | 2024-10-27 16:27 | 2024-10-27 18:12 | 0.23214 | 0.0022108 | 75 | 7875 | Unplanned | Defective equipment | Faulty Tx B1018 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 904 | 4607 | Tx B1018 | St Andrews | 2024-10-27 16:27 | 2024-10-30 13:45 | 0.24514 | 5.8955e-05 | 2 | 8316 | Unplanned | Defective equipment | Faulty Tx B1018 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 905 | 3826 | CB F359-ABS F248-ABS F313 | Fairlie Rural | 2024-10-28 17:39 | 2024-10-28 18:48 | 0.1078 | 0.0015623 | 53 | 3657 | Unplanned | Third party interference | CB F359 Trip on EF - possible digger boom v lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 906 | 3826 | ABS F248 TO END | Fairlie Rural | 2024-10-28 17:39 | 2024-10-28 19:46 | 0.28452 | 0.0022403 | 76 | 9652 | Unplanned | Third party interference | CB F359 Trip on EF - possible digger boom v lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 907 | 3826 | ABS F313-ABS F225-ABS F355 | Fairlie Rural | 2024-10-28 17:39 | 2024-10-28 19:12 | 0.10692 | 0.0011496 | 39 | 3627 | Unplanned | Third party interference | CB F359 Trip on EF - possible digger boom v lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 908 | 3826 | ABS F355 | Fairlie Rural | 2024-10-28 17:39 | 2024-10-28 19:41 | 0.10789 | 0.00088433 | 30 | 3660 | Unplanned | Third party interference | CB F359 Trip on EF - possible digger boom v lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 909 | 3826 | ABS F225-Fuses F226 | Fairlie Rural | 2024-10-28 17:39 | 2024-10-28 20:29 | 0.19043 | 0.0011202 | 38 | 6460 | Unplanned | Third party interference | CB F359 Trip on EF - possible digger boom v lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 910 | 3826 | Fuses F226 | Fairlie Rural | 2024-10-28 17:39 | 2024-10-28 21:27 | 0.07393 | 0.00032425 | 11 | 2508 | Unplanned | Third party interference | CB F359 Trip on EF - possible digger boom v lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 911 | DVE374 | Links T421 to end minus Links T744 - TX D620 - TX D1211 - TX D2120 - TX D307 | Woodbury | 2024-10-29 08:30 | 2024-10-29 16:01 | 0.039883 | 8.8433e-05 | 3 | 1353 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 912 | DVE374 | Links T744 to end | Woodbury | 2024-10-29 08:30 | 2024-10-29 16:32 | 0.085249 | 0.00017687 | 6 | 2892 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 913 | DVE374 | TX D620 to end | Woodbury | 2024-10-29 08:30 | 2024-10-29 16:12 | 0.013619 | 2.9478e-05 | 1 | 462 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 914 | DVE374 | TX D1211 to end | Woodbury | 2024-10-29 08:30 | 2024-10-29 16:18 | 0.027591 | 5.8955e-05 | 2 | 936 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 915 | DVE374 | TX D2120 to end | Woodbury | 2024-10-29 08:30 | 2024-10-29 16:22 | 0.013913 | 2.9478e-05 | 1 | 472 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 916 | DVE374 | TX D307 to end | Woodbury | 2024-10-29 08:30 | 2024-10-29 16:45 | 0.043774 | 8.8433e-05 | 3 | 1485 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 917 | HTR043A | Fuses W504 to end | Glenavy | 2024-10-29 08:54 | 2024-10-29 15:21 | 0.045631 | 0.00011791 | 4 | 1548 | Planned | Planned interruption | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 918 | GWM1193 | ABS L221 to end | Totara Valley | 2024-10-29 09:00 | 2024-10-29 13:55 | 0.46958 | 0.0015918 | 54 | 15930 | Planned | Planned interruption | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 919 | SKE1898 | ABS T426 to end | Woodbury | 2024-10-29 10:05 | 2024-10-29 11:49 | 0.37401 | 0.0035963 | 122 | 12688 | Planned | Planned interruption | Connect WMG | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 920 | DVE375 | Fuses at pole #04780 to end | Woodbury | 2024-10-30 08:30 | 2024-10-30 12:17 | 0.0066914 | 2.9478e-05 | 1 | 227 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 921 | HTR043B | Fuses W504 to end | Glenavy | 2024-10-30 08:30 | 2024-10-30 15:07 | 0.046811 | 0.00011791 | 4 | 1588 | Planned | Planned interruption | Tree Cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 922 | SKE1845 | RMU L528 minus RMU L581 minus #20 Chaucer St | Highfield | 2024-10-30 09:00 | 2024-10-30 14:46 | 0.60176 | 0.0017392 | 59 | 20414 | Planned | Planned interruption | RMU & TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 923 | SKE1845 | RMU L581 to end | Highfield | 2024-10-30 09:00 | 2024-10-30 14:49 | 0.31892 | 0.00091381 | 31 | 10819 | Planned | Planned interruption | RMU & TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 924 | SKE1845 | #20 Chaucer Street | Highfield | 2024-10-30 09:00 | 2024-10-30 15:08 | 0.010848 | 2.9478e-05 | 1 | 368 | Planned | Planned interruption | RMU & TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 925 | SRS010 | GRM CB5- TE50 CCT18-RMU E14-Links LB Q44 | Nile Street | 2024-10-30 09:00 | 2024-10-30 09:24 | 0.1047 | 0.0043627 | 148 | 3552 | Planned | Planned interruption | DB Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 926 | SRS010 | TE50 CCT18-DB Q89-DB V12 | Nile Street | 2024-10-30 09:00 | 2024-10-30 16:15 | 0.064114 | 0.00014739 | 5 | 2175 | Planned | Planned interruption | DB Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 927 | SRS010 | DB Q89 | Nile Street | 2024-10-30 09:00 | 2024-10-30 16:23 | 0.065293 | 0.00014739 | 5 | 2215 | Planned | Planned interruption | DB Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 928 | SRS010 | DB V12 | Nile Street | 2024-10-30 09:00 | 2024-10-30 16:50 | 0.096981 | 0.00020634 | 7 | 3290 | Planned | Planned interruption | DB Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 929 | SRS010 | GRM CB5- TE50 CCT18-RMU E14-Links LB Q44 | Nile Street | 2024-10-30 16:00 | 2024-10-30 16:15 | 0.06544 | 0.0043627 | 148 | 2220 | Planned | Planned interruption | DB Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 930 | SRS012 | CB T127 to ABS TX57 minus TX62 minus TX D911 | Rangitata | 2024-10-31 08:00 | 2024-10-31 15:26 | 0.60476 | 0.001356 | 46 | 20516 | Planned | Planned interruption | Yellow tagged pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 931 | SRS012 | TX D911 | Rangitata | 2024-10-31 08:00 | 2024-10-31 15:35 | 0.013412 | 2.9478e-05 | 1 | 455 | Planned | Planned interruption | Yellow tagged pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 932 | DVE377 | ABS T422 to Temp Links at pole #04506 minus TX D309 | Woodbury | 2024-10-31 09:12 | 2024-10-31 16:24 | 0.11461 | 0.0002653 | 9 | 3888 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 933 | DVE377 | TX D309 to end | Woodbury | 2024-10-31 09:12 | 2024-10-31 16:32 | 0.01297 | 2.9478e-05 | 1 | 440 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 934 | JRM035 | TX D1711 | Speechley | 2024-10-31 10:48 | 2024-10-31 12:52 | 0.0036552 | 2.9478e-05 | 1 | 124 | Planned | Planned interruption | Remove ferro capacitor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 935 | JRM035 | Fuses G272-TX D1711 | Speechley | 2024-10-31 10:48 | 2024-10-31 12:38 | 0.0097276 | 8.8433e-05 | 3 | 330 | Planned | Planned interruption | Remove ferro capacitor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 936 | DVE377 | Temp links at pole #04506 to Abs T426 minus TX D675 | Woodbury | 2024-10-31 17:30 | 2024-10-31 17:43 | 0.0049817 | 0.00038321 | 13 | 169 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 937 | DVE377 | TX D675 to end | Woodbury | 2024-10-31 17:30 | 2024-10-31 17:46 | 0.00047164 | 2.9478e-05 | 1 | 16 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 938 | DVE377 | ABS T426 to end | Woodbury | 2024-10-31 17:30 | 2024-10-31 17:49 | 0.068329 | 0.0035963 | 122 | 2318 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 939 | SRT264A | Fuses W510 to end | Waihao Downs | 2024-11-01 09:00 | 2024-11-01 12:04 | 0.048815 | 0.0002653 | 9 | 1656 | Planned | Planned interruption | Red tagged Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 940 | GWM1185 | Fuses L713 to end | Hadlow | 2024-11-02 09:00 | 2024-11-02 13:45 | 0.11762 | 0.00041269 | 14 | 3990 | Planned | Planned interruption | Tree Cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 941 | 3878 | Fuses T108 to end | Milford | 2024-11-02 18:02 | 2024-11-02 19:26 | 0.027237 | 0.00032425 | 11 | 924 | Unplanned | Adverse weather | Wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 942 | 3879 | RMU W699 MS to end | Waihaorunga | 2024-11-03 17:39 | 2024-11-03 17:55 | 0.0047164 | 0.00029478 | 10 | 160 | Unplanned | Vegetation | Branch removal | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 943 | SKE1757A | Tx E367 | Lakeside Drive | 2024-11-04 08:30 | 2024-11-04 15:44 | 0.12793 | 0.00029478 | 10 | 4340 | Planned | Planned interruption | RMU maintenance & Tx upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 944 | SKE1757A | Tx E250 | Lakeside Drive | 2024-11-04 08:30 | 2024-11-04 15:47 | 0.025763 | 5.8955e-05 | 2 | 874 | Planned | Planned interruption | RMU maintenance & Tx upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 945 | SKE1757A | Tx E311 | Lakeside Drive | 2024-11-04 08:30 | 2024-11-04 15:50 | 0.02594 | 5.8955e-05 | 2 | 880 | Planned | Planned interruption | RMU maintenance & Tx upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 946 | SKE1757A | Tx E262 | Lakeside Drive | 2024-11-04 08:30 | 2024-11-04 16:05 | 0.013412 | 2.9478e-05 | 1 | 455 | Planned | Planned interruption | RMU maintenance & Tx upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 947 | SKE1757A | Tx E148 | Lakeside Drive | 2024-11-04 08:30 | 2024-11-04 16:02 | 0.053296 | 0.00011791 | 4 | 1808 | Planned | Planned interruption | RMU maintenance & Tx upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 948 | SLA658 | from Temp Links pole #01505 | Woodbury | 2024-11-04 08:30 | 2024-11-04 15:52 | 0.11726 | 0.0002653 | 9 | 3978 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 949 | SLA658 | Tx D1816 | Woodbury | 2024-11-04 08:30 | 2024-11-04 16:24 | 0.013972 | 2.9478e-05 | 1 | 474 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 950 | SLA658 | Tx D323 | Woodbury | 2024-11-04 08:30 | 2024-11-04 16:28 | 0.028181 | 5.8955e-05 | 2 | 956 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 951 | SLA658 | Tx D324 | Woodbury | 2024-11-04 08:30 | 2024-11-04 16:22 | 0.013913 | 2.9478e-05 | 1 | 472 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 952 | SLA658 | Tx D1310 | Woodbury | 2024-11-04 08:30 | 2024-11-04 16:19 | 0.013825 | 2.9478e-05 | 1 | 469 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 953 | SLA658 | Tx D326 | Woodbury | 2024-11-04 08:30 | 2024-11-04 16:13 | 0.013648 | 2.9478e-05 | 1 | 463 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 954 | SLA657 | from temp links p#04932 - T423 | Woodbury | 2024-11-04 08:30 | 2024-11-04 15:32 | 0.22391 | 0.0005306 | 18 | 7596 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 955 | SLA657 | Tx D689 | Woodbury | 2024-11-04 08:30 | 2024-11-04 15:40 | 0.012675 | 2.9478e-05 | 1 | 430 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 956 | WMR116 | ABS W415 to end | Otaio | 2024-11-04 10:30 | 2024-11-04 10:59 | 0.0017097 | 5.8955e-05 | 2 | 58 | Planned | Planned interruption | Tap changes on Tx A1285 & A1299 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 957 | SLA657 | T423 | Woodbury | 2024-11-04 17:30 | 2024-11-04 17:43 | 0.055949 | 0.0043037 | 146 | 1898 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 958 | 4417 | G275 - G327 | Geraldine Township | 2024-11-04 19:28 | 2024-11-04 21:18 | 1.5175 | 0.013796 | 468 | 51480 | Unplanned | Unknown | Unknown - Possibly vegettion or bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 959 | 4417 | G327 | Geraldine Township | 2024-11-04 19:28 | 2024-11-04 21:26 | 0.43132 | 0.0036552 | 124 | 14632 | Unplanned | Unknown | Unknown - Possibly vegettion or bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 960 | 4608 | ABS L820 to end | Sutherland | 2024-11-06 14:01 | 2024-11-06 17:13 | 0.056597 | 0.00029478 | 10 | 1920 | Unplanned | Defective equipment | Broken Jumper at ABS L820 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 961 | 4608 | ABS L1239 minus ABS L820 | Sutherland | 2024-11-06 16:02 | 2024-11-06 17:13 | 0.03558 | 0.00050112 | 17 | 1207 | Unplanned | Defective equipment | Broken Jumper at ABS L820 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 962 | DVE380 | from Temp Links pole #01505 | Woodbury | 2024-11-07 08:30 | 2024-11-07 15:38 | 0.1514 | 0.00035373 | 12 | 5136 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 963 | DVE380 | D1310 & individual ICPs | Woodbury | 2024-11-07 08:30 | 2024-11-07 15:45 | 0.038468 | 8.8433e-05 | 3 | 1305 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 964 | JRM040 | G242 minus D996-03 | Geraldine Township | 2024-11-08 10:39 | 2024-11-08 14:07 | 0.22073 | 0.0010612 | 36 | 7488 | Planned | Planned interruption | Tx Repairs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 965 | WMR115 | TO Tx E230 | Pukaki | 2024-11-08 12:48 | 2024-11-08 12:53 | 0.00014739 | 2.9478e-05 | 1 | 5 | Planned | Planned interruption | Tap changes on Tx E230 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 966 | 4609 | TO D139 | Waitohi | 2024-11-09 11:08 | 2024-11-09 12:17 | 0.0081358 | 0.00011791 | 4 | 276 | Unplanned | Vegetation | Disconnect LV service line due to trees on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 967 | 4610 | G194 - G305 - G251 | Speechley | 2024-11-09 16:11 | 2024-11-09 17:44 | 0.55103 | 0.005925 | 201 | 18693 | Unplanned | Vegetation | Trees on line P#08334 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 968 | 4610 | G251 | Speechley | 2024-11-09 16:11 | 2024-11-09 17:46 | 0.40045 | 0.0042153 | 143 | 13585 | Unplanned | Vegetation | Trees on line P#08334 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 969 | 4610 | G253 | Speechley | 2024-11-09 16:11 | 2024-11-09 21:40 | 0.10668 | 0.00032425 | 11 | 3619 | Unplanned | Defective equipment | Disc insulator broken P#08142 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 970 | 4610 | G178 | Speechley | 2024-11-09 16:11 | 2024-11-09 19:25 | 0.022875 | 0.00011791 | 4 | 776 | Unplanned | Vegetation | Trees on line P#08334 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 971 | 4610 | G136 - G137 | Speechley | 2024-11-09 16:11 | 2024-11-09 19:25 | 0.14869 | 0.00076642 | 26 | 5044 | Unplanned | Vegetation | Trees on line P#08334 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 972 | 4610 | G137 | Speechley | 2024-11-09 16:11 | 2024-11-09 19:25 | 0.074343 | 0.00038321 | 13 | 2522 | Unplanned | Vegetation | Trees on line P#08334 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 973 | 4610 | G305 - G136 - D178 - G253 | Speechley | 2024-11-09 16:11 | 2024-11-09 19:25 | 0.22303 | 0.0011496 | 39 | 7566 | Unplanned | Vegetation | Trees on line P#08334 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 974 | 4610 | G178 | Speechley | 2024-11-09 19:27 | 2024-11-09 19:43 | 0.0018866 | 0.00011791 | 4 | 64 | Unplanned | Vegetation | Trees on line P#08334 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 975 | 4610 | G136 - G137 | Speechley | 2024-11-09 19:27 | 2024-11-09 19:34 | 0.0053649 | 0.00076642 | 26 | 182 | Unplanned | Vegetation | Trees on line P#08334 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 976 | 4610 | G137 | Speechley | 2024-11-09 19:27 | 2024-11-09 19:34 | 0.0026825 | 0.00038321 | 13 | 91 | Unplanned | Vegetation | Trees on line P#08334 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 977 | 4610 | G305 - G136 - D178 - G253 | Speechley | 2024-11-09 19:27 | 2024-11-09 19:34 | 0.0080474 | 0.0011496 | 39 | 273 | Unplanned | Vegetation | Trees on line P#08334 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 978 | 4610 | G136 - G137 | Speechley | 2024-11-09 19:35 | 2024-11-09 19:56 | 0.016095 | 0.00076642 | 26 | 546 | Unplanned | Vegetation | Trees on line P#08334 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 979 | 4610 | G137 | Speechley | 2024-11-09 19:35 | 2024-11-09 22:21 | 0.063613 | 0.00038321 | 13 | 2158 | Unplanned | Vegetation | Trees on line P#08334 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 980 | 4610 | G305 - G136 - D178 - G253 | Speechley | 2024-11-09 19:35 | 2024-11-09 19:43 | 0.009197 | 0.0011496 | 39 | 312 | Unplanned | Vegetation | Trees on line P#08334 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 981 | JDJ127 | W308 TO END | Otaio | 2024-11-11 09:00 | 2024-11-11 14:24 | 0.11461 | 0.00035373 | 12 | 3888 | Planned | Planned interruption | Red tagged Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 982 | 999 | Fuses L209 | Levels Plain | 2024-11-11 10:41 | 2024-11-11 12:38 | 0.3104 | 0.002653 | 90 | 10530 | Unplanned | Wildlife | Duck V pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 983 | 4743 | STU CB9 - Links W742 | Morven | 2024-11-11 14:17 | 2024-11-11 14:48 | 0.31252 | 0.010081 | 342 | 10602 | Unplanned | Defective equipment | Broke Conductor between Pole #32053 and Pole #32054 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 984 | 4743 | Links W742 - ABS W461 | Morven | 2024-11-11 14:17 | 2024-11-11 18:38 | 0.092324 | 0.00035373 | 12 | 3132 | Unplanned | Defective equipment | Broke Conductor between Pole #32053 and Pole #32054 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 985 | 4743 | ABS W461 | Morven | 2024-11-11 14:17 | 2024-11-11 18:42 | 0.0078116 | 2.9478e-05 | 1 | 265 | Unplanned | Defective equipment | Broke Conductor between Pole #32053 and Pole #32054 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 986 | DVE381 | TX D675 to end | Woodbury | 2024-11-12 08:30 | 2024-11-12 17:50 | 0.016507 | 2.9478e-05 | 1 | 560 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 987 | DVE381 | Tx D310 to end | Woodbury | 2024-11-12 08:30 | 2024-11-12 16:25 | 0.028004 | 5.8955e-05 | 2 | 950 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 988 | DVE381 | Tx D1305 to end | Woodbury | 2024-11-12 08:30 | 2024-11-12 16:20 | 0.027709 | 5.8955e-05 | 2 | 940 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 989 | DVE381 | ABS T422 - Links at Pole #04506 - Tx D310 - Tx D675 - Tx D1305 | Woodbury | 2024-11-12 08:30 | 2024-11-12 16:03 | 0.08012 | 0.00017687 | 6 | 2718 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 990 | SKE1313 | Tx B1397 + Tx B899 + Tx B1078 | Highfield | 2024-11-12 09:49 | 2024-11-12 17:34 | 3.1115 | 0.0066914 | 227 | 105555 | Planned | Planned interruption | Transformer maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 991 | 4612 | FUSES TO B1193 | Pleasant Point Township | 2024-11-12 16:08 | 2024-11-12 19:40 | 0.12499 | 0.00058955 | 20 | 4240 | Unplanned | Unknown | Fuses TOB1193 blown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 992 | 4612 | FUSES TO B1193 | Pleasant Point Township | 2024-11-12 16:08 | 2024-11-12 19:53 | 0.14591 | 0.00064851 | 22 | 4950 | Unplanned | Unknown | Fuses TOB1193 blown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 993 | 4612 | Fuses TO B1193 | Pleasant Point Township | 2024-11-12 16:08 | 2024-11-13 11:41 | 0.034577 | 2.9478e-05 | 1 | 1173 | Unplanned | Unknown | Fuses TOB1193 blown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 994 | 4612 | Fuses TO B1193 | Pleasant Point Township | 2024-11-12 16:08 | 2024-11-13 08:00 | 0.028063 | 2.9478e-05 | 1 | 952 | Unplanned | Unknown | Fuses TOB1193 blown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 995 | DVE381 | ABS T426 to end | Woodbury | 2024-11-12 17:41 | 2024-11-12 17:53 | 0.043155 | 0.0035963 | 122 | 1464 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 996 | DVE381 | Links at Pole #04506 - ABS T426 | Woodbury | 2024-11-12 17:41 | 2024-11-12 17:45 | 0.0016507 | 0.00041269 | 14 | 56 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 997 | SKE1889 | Tx E129-05 | M159 | 2024-11-13 08:30 | 2024-11-13 15:24 | 0.09763 | 0.00023582 | 8 | 3312 | Planned | Planned interruption | RMU replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 998 | SKE1889 | LB74 | M159 | 2024-11-13 08:30 | 2024-11-13 15:27 | 0.049169 | 0.00011791 | 4 | 1668 | Planned | Planned interruption | RMU replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 999 | DVE382 | ABS T422- ABS T426 - Tx D626 - Tx D675 | Woodbury | 2024-11-13 08:30 | 2024-11-13 16:10 | 0.29831 | 0.00064851 | 22 | 10120 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1000 | DVE382 | Tx D626 | Woodbury | 2024-11-13 08:30 | 2024-11-13 16:25 | 0.014002 | 2.9478e-05 | 1 | 475 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1001 | DVE382 | TX D675 to end | Woodbury | 2024-11-13 08:30 | 2024-11-13 16:15 | 0.013707 | 2.9478e-05 | 1 | 465 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1002 | GWM1195 | Fuses L226 to end | Sutherland | 2024-11-13 09:00 | 2024-11-13 14:13 | 0.083039 | 0.0002653 | 9 | 2817 | Planned | Planned interruption | Tree Trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1003 | DVE382 | ABS T426 to end | Woodbury | 2024-11-13 17:38 | 2024-11-13 17:41 | 0.010789 | 0.0035963 | 122 | 366 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1004 | 5024 | F284 to end | Fairlie Rural | 2024-11-14 04:50 | 2024-11-14 07:32 | 0.019102 | 0.00011791 | 4 | 648 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1005 | DVE383 | ABS T426 to end | Woodbury | 2024-11-14 07:45 | 2024-11-14 08:13 | 0.1007 | 0.0035963 | 122 | 3416 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1006 | DVE383 | ABS T422 - ABS T426 | Woodbury | 2024-11-14 07:45 | 2024-11-14 08:20 | 0.024761 | 0.00070746 | 24 | 840 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1007 | DVE383 | Links at Pole #04932 | Woodbury | 2024-11-14 07:45 | 2024-11-14 08:26 | 0.022963 | 0.00056008 | 19 | 779 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1008 | SKE1890 | TX E154 | M159 | 2024-11-14 08:30 | 2024-11-14 10:17 | 0.012616 | 0.00011791 | 4 | 428 | Planned | Planned interruption | RMU replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1009 | SKE1890 | Tx E155 | M159 | 2024-11-14 08:30 | 2024-11-14 14:58 | 0.011437 | 2.9478e-05 | 1 | 388 | Planned | Planned interruption | RMU replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1010 | DVE383 | ABS TX48 - Links at Pole #04392 - Tx D1434 - Tx D1788 - Fuses T420 | Woodbury | 2024-11-14 08:31 | 2024-11-14 16:18 | 0.041298 | 8.8433e-05 | 3 | 1401 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1011 | DVE383 | Tx D1434 to end | Woodbury | 2024-11-14 08:31 | 2024-11-14 16:37 | 0.014326 | 2.9478e-05 | 1 | 486 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1012 | DVE383 | Tx D1788 to end | Woodbury | 2024-11-14 08:31 | 2024-11-14 16:34 | 0.014238 | 2.9478e-05 | 1 | 483 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1013 | DVE383 | Fuses T420 to end | Woodbury | 2024-11-14 08:31 | 2024-11-14 16:25 | 0.39123 | 0.00082537 | 28 | 13272 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1014 | SKE1890 | TX E170 | M159 | 2024-11-14 08:37 | 2024-11-14 10:12 | 0.0028004 | 2.9478e-05 | 1 | 95 | Planned | Planned interruption | RMU replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1015 | 4744 | Fuses W460 | St Andrews | 2024-11-14 12:32 | 2024-11-14 15:15 | 0.024024 | 0.00014739 | 5 | 815 | Unplanned | Third party interference | Digger Vs OH lines pole #483854 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1016 | DVE383 | Links at Pole #04932 | Woodbury | 2024-11-14 17:30 | 2024-11-14 17:46 | 0.077821 | 0.0048638 | 165 | 2640 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1017 | SKE1899 | ABS T426 to end | Woodbury | 2024-11-15 09:20 | 2024-11-15 10:15 | 0.1978 | 0.0035963 | 122 | 6710 | Planned | Planned interruption | Disconnecting NWL Genset | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1018 | LXL084 | Fuses TOD83 | Old Main South Road | 2024-11-15 15:14 | 2024-11-15 15:44 | 0.002653 | 8.8433e-05 | 3 | 90 | Unplanned | Lighting | Lightning at Tx D83 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1019 | 5025 | Fuses TO D756 | Woodbury | 2024-11-15 18:20 | 2024-11-15 19:20 | 0.0088433 | 0.00014739 | 5 | 300 | Unplanned | Defective equipment | Jumper against X Arm at Pole #46013 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1020 | SRS024 | Fuses TO B381 | Grants Road | 2024-11-18 09:00 | 2024-11-18 10:41 | 0.17863 | 0.0017687 | 60 | 6060 | Planned | Planned interruption | Hotspot repair @ Tx B381 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1021 | ACD168 | ABS W555 - TO A313 | Tawai | 2024-11-18 09:00 | 2024-11-18 15:34 | 0.19744 | 0.00050112 | 17 | 6698 | Planned | Planned interruption | Replace P#33252 & upgrade Tx A313 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1022 | ACD168 | TO A313 | Tawai | 2024-11-18 09:00 | 2024-11-18 15:48 | 0.024054 | 5.8955e-05 | 2 | 816 | Planned | Planned interruption | Replace P#33252 & upgrade Tx A313 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1023 | ACD169A | ABS L344 | Waitawa | 2024-11-18 09:06 | 2024-11-18 13:41 | 0.17834 | 0.00064851 | 22 | 6050 | Planned | Planned interruption | Upgrade Tx B2215 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1024 | 4614 | M154 to M126 + E384 | M159 | 2024-11-18 15:49 | 2024-11-18 17:09 | 0.075463 | 0.00094328 | 32 | 2560 | Unplanned | Defective equipment | Damaged Bushing on RMU | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1025 | 4614 | M159 to M162 less E384 | M159 | 2024-11-18 15:49 | 2024-11-18 17:35 | 0.015623 | 0.00014739 | 5 | 530 | Unplanned | Defective equipment | Damaged Bushing on RMU | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1026 | 4614 | M125 | M159 | 2024-11-18 15:49 | 2024-11-18 18:14 | 0.14105 | 0.00097276 | 33 | 4785 | Unplanned | Defective equipment | Damaged Bushing on RMU | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1027 | 1201 | Fuses TOA313 | Tawai | 2024-11-19 07:37 | 2024-11-19 07:44 | 0.00020634 | 2.9478e-05 | 1 | 7 | Planned | Planned interruption | Tap change Tx A313 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1028 | SRS025 | RMU M369 - ICP DB4715 | Lakeside Drive | 2024-11-19 09:00 | 2024-11-19 10:10 | 0.13206 | 0.0018866 | 64 | 4480 | Planned | Planned interruption | Tx E183 Hotspot repairs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1029 | SRS025 | ICP DB4715 | Lakeside Drive | 2024-11-19 09:00 | 2024-11-19 10:17 | 0.0022698 | 2.9478e-05 | 1 | 77 | Planned | Planned interruption | Tx E183 Hotspot repairs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1030 | DVE384 | ABS T419 - Tx D300 - Tx D751 - Tx D1278 - Tx D616 | Woodbury | 2024-11-19 09:00 | 2024-11-19 17:30 | 3.0819 | 0.0060429 | 205 | 104550 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1031 | DVE384 | Tx D300 | Woodbury | 2024-11-19 09:00 | 2024-11-19 17:40 | 0.045985 | 8.8433e-05 | 3 | 1560 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1032 | DVE384 | Tx D1278 | Woodbury | 2024-11-19 09:00 | 2024-11-19 17:50 | 0.031246 | 5.8955e-05 | 2 | 1060 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1033 | DVE384 | Tx D616 | Woodbury | 2024-11-19 09:00 | 2024-11-19 17:41 | 0.015358 | 2.9478e-05 | 1 | 521 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1034 | DVE384 | Tx D751 3pH ICP | Woodbury | 2024-11-19 09:00 | 2024-11-19 17:46 | 0.015505 | 2.9478e-05 | 1 | 526 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1035 | DVE384 | Tx D751 - Tx D751 3pH ICP | Woodbury | 2024-11-19 09:00 | 2024-11-19 17:55 | 0.063082 | 0.00011791 | 4 | 2140 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1036 | DVE384 | ABS T441 | Woodbury | 2024-11-19 09:03 | 2024-11-19 17:30 | 0.13451 | 0.0002653 | 9 | 4563 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1037 | DVE384 | P#08381 - ABS T419 - ABS T441 | Woodbury | 2024-11-19 09:09 | 2024-11-19 17:28 | 0.058837 | 0.00011791 | 4 | 1996 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1038 | SKE1892A | Tx E170 | M159 | 2024-11-20 08:00 | 2024-11-20 16:49 | 0.015594 | 2.9478e-05 | 1 | 529 | Planned | Planned interruption | Install & liven new RMU & Tx | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1039 | DVE385 | Fuses T445 - Tx D1278 - Tx D1279 - Tx D300 | Woodbury | 2024-11-20 08:32 | 2024-11-20 15:47 | 0.038468 | 8.8433e-05 | 3 | 1305 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1040 | DVE385 | Tx D1278 | Woodbury | 2024-11-20 08:32 | 2024-11-20 15:52 | 0.02594 | 5.8955e-05 | 2 | 880 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1041 | DVE385 | Tx D1279 | Woodbury | 2024-11-20 08:32 | 2024-11-20 16:00 | 0.013206 | 2.9478e-05 | 1 | 448 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1042 | DVE385 | Tx D300 | Woodbury | 2024-11-20 08:32 | 2024-11-20 16:08 | 0.040325 | 8.8433e-05 | 3 | 1368 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1043 | SKE1893A | Tx E154-02 | M159 | 2024-11-21 08:00 | 2024-11-21 14:40 | 0.011791 | 2.9478e-05 | 1 | 400 | Planned | Planned interruption | Install new Tx E383 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1044 | SKE1893A | Tx E154-03 | M159 | 2024-11-21 08:00 | 2024-11-21 14:50 | 0.012086 | 2.9478e-05 | 1 | 410 | Planned | Planned interruption | Install new Tx E383 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1045 | SKE1893A | Tx E154-Metal workshop | M159 | 2024-11-21 08:00 | 2024-11-21 14:56 | 0.012263 | 2.9478e-05 | 1 | 416 | Planned | Planned interruption | Install new Tx E383 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1046 | SKE1893A | Tx E154-Wood workshop | M159 | 2024-11-21 08:00 | 2024-11-21 15:16 | 0.012852 | 2.9478e-05 | 1 | 436 | Planned | Planned interruption | Install new Tx E383 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1047 | DVE386 | Fuses T445 | Woodbury | 2024-11-21 08:30 | 2024-11-21 13:33 | 0.080386 | 0.0002653 | 9 | 2727 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1048 | HTR072 | Fuses TO D608 | Woodbury | 2024-11-22 08:30 | 2024-11-22 10:43 | 0.015682 | 0.00011791 | 4 | 532 | Planned | Planned interruption | Tree cutting P#08373 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1049 | DVE387 | ABS T441 - Tx D615 | Woodbury | 2024-11-22 08:30 | 2024-11-22 14:20 | 0.082537 | 0.00023582 | 8 | 2800 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1050 | DVE387 | Tx D615 | Woodbury | 2024-11-22 08:30 | 2024-11-22 14:49 | 0.011172 | 2.9478e-05 | 1 | 379 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1051 | ACD171 | Fuses W155 - Tx A1255 3pH ICP - Tx A1255 1pH ICP | Waikakahi | 2024-11-22 09:00 | 2024-11-22 14:40 | 0.050112 | 0.00014739 | 5 | 1700 | Planned | Planned interruption | Pole replacement P#43887 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1052 | ACD171 | Tx A1255 1pH ICP | Waikakahi | 2024-11-22 09:00 | 2024-11-22 15:00 | 0.010612 | 2.9478e-05 | 1 | 360 | Planned | Planned interruption | Pole replacement P#43887 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1053 | ACD171 | Tx A1255 3pH ICP | Waikakahi | 2024-11-22 09:00 | 2024-11-22 15:03 | 0.0107 | 2.9478e-05 | 1 | 363 | Planned | Planned interruption | Pole replacement P#43887 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1054 | HTR074 | Fuses TO D255 | Speechley | 2024-11-22 13:00 | 2024-11-22 14:18 | 0.009197 | 0.00011791 | 4 | 312 | Planned | Planned interruption | Tree cutting P#03294 & P#03295 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1055 | MCV633 | TX A817 to end | Morven | 2024-11-25 07:52 | 2024-11-25 08:07 | 0.00088433 | 5.8955e-05 | 2 | 30 | Planned | Planned interruption | Install Covers | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1056 | HTR073 | Fuses F209 to end | Cricklewood | 2024-11-25 08:38 | 2024-11-25 10:43 | 0.051586 | 0.00041269 | 14 | 1750 | Planned | Planned interruption | Tree Cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1057 | ACD172 | Links F430 to end | Raincliff | 2024-11-25 09:01 | 2024-11-25 12:30 | 0.012322 | 5.8955e-05 | 2 | 418 | Planned | Planned interruption | Pole Repacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1058 | DVE388 | ABS T426 to end minus #10 Horsfall Rd | Woodbury | 2024-11-26 08:30 | 2024-11-26 17:25 | 1.924 | 0.0035963 | 122 | 65270 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1059 | DVE388 | TX D627 to end | Woodbury | 2024-11-26 08:30 | 2024-11-26 17:33 | 0.016006 | 2.9478e-05 | 1 | 543 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1060 | DVE388 | Temp Links to ABS T426 minus TX D627 minus TX D675 | Woodbury | 2024-11-26 08:32 | 2024-11-26 17:10 | 0.16796 | 0.00032425 | 11 | 5698 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1061 | DVE388 | #10 Horsefall Rd | Woodbury | 2024-11-26 08:32 | 2024-11-26 17:38 | 0.016095 | 2.9478e-05 | 1 | 546 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1062 | DVE388 | TX D675 to end | Woodbury | 2024-11-26 08:32 | 2024-11-26 17:20 | 0.015564 | 2.9478e-05 | 1 | 528 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1063 | SKE1896 | TX E153 /2 to end minus #1 De Faur Place | M159 | 2024-11-27 08:30 | 2024-11-27 14:17 | 0.051144 | 0.00014739 | 5 | 1735 | Planned | Planned interruption | Mt Cook RMU & TX's Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1064 | SKE1896 | #1 De Faur Place | M159 | 2024-11-27 08:30 | 2024-11-27 14:53 | 0.01129 | 2.9478e-05 | 1 | 383 | Planned | Planned interruption | Mt Cook RMU & TX's Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1065 | SKE1896 | TX E153 /3 to end | M159 | 2024-11-27 08:30 | 2024-11-27 14:36 | 0.17262 | 0.00047164 | 16 | 5856 | Planned | Planned interruption | Mt Cook RMU & TX's Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1066 | SKE1896 | TX E153 /4 to end minus 3/7 Wakefield Drive | M159 | 2024-11-27 08:30 | 2024-11-27 14:28 | 0.094977 | 0.0002653 | 9 | 3222 | Planned | Planned interruption | Mt Cook RMU & TX's Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1067 | SKE1896 | 3/7 Wakefiled Drive | M159 | 2024-11-27 08:30 | 2024-11-27 14:52 | 0.01126 | 2.9478e-05 | 1 | 382 | Planned | Planned interruption | Mt Cook RMU & TX's Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1068 | SKE1896 | TX E153/5 to end (DB1210 / #4 Kitchener Dr) | M159 | 2024-11-27 08:30 | 2024-11-27 14:50 | 0.011202 | 2.9478e-05 | 1 | 380 | Planned | Planned interruption | Mt Cook RMU & TX's Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1069 | DVE389 | Temp links at pole #04383 to End minus TX D675, D1767 and TX D320 ICP #1 & ICP #2 | Woodbury | 2024-11-27 08:30 | 2024-11-27 16:20 | 0.083127 | 0.00017687 | 6 | 2820 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1070 | DVE389 | TX D675 to end | Woodbury | 2024-11-27 08:30 | 2024-11-27 16:29 | 0.01412 | 2.9478e-05 | 1 | 479 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1071 | DVE389 | TX D1767 to end | Woodbury | 2024-11-27 08:30 | 2024-11-27 16:44 | 0.014562 | 2.9478e-05 | 1 | 494 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1072 | DVE389 | TX D320 ICP #1 | Woodbury | 2024-11-27 08:30 | 2024-11-27 16:49 | 0.014709 | 2.9478e-05 | 1 | 499 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1073 | DVE389 | TX D320 ICP #2 | Woodbury | 2024-11-27 08:30 | 2024-11-27 17:02 | 0.015093 | 2.9478e-05 | 1 | 512 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1074 | DVE394 | Fuses T424 to end minus TX D320, D311 , D321 | Woodbury | 2024-11-28 08:30 | 2024-11-28 15:19 | 0.072338 | 0.00017687 | 6 | 2454 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1075 | DVE394 | TX D320 | Woodbury | 2024-11-28 08:30 | 2024-11-28 15:36 | 0.025115 | 5.8955e-05 | 2 | 852 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1076 | DVE394 | TX D311 | Woodbury | 2024-11-28 08:30 | 2024-11-28 15:44 | 0.012793 | 2.9478e-05 | 1 | 434 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1077 | DVE394 | TX D321 | Woodbury | 2024-11-28 08:30 | 2024-11-28 15:58 | 0.013206 | 2.9478e-05 | 1 | 448 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1078 | JRM046 | TX E248 Sewer Pump | Lakeside Drive | 2024-11-28 10:18 | 2024-11-28 13:53 | 0.0063377 | 2.9478e-05 | 1 | 215 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1079 | JRM046 | TX E248 Toilet Block | Lakeside Drive | 2024-11-28 10:18 | 2024-11-28 13:43 | 0.0060429 | 2.9478e-05 | 1 | 205 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1080 | 4619 | Recloser F418 | Raincliff | 2024-11-28 21:18 | 2024-11-29 01:16 | 0.30167 | 0.0012675 | 43 | 10234 | Unplanned | Vegetation | Tree Branch on line at pole #48318 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1081 | 4615 | TVS CB Z3 to end | Pukaki | 2024-11-29 13:51 | 2024-11-29 14:45 | 0.070039 | 0.001297 | 44 | 2376 | Unplanned | Wildlife | Possum on lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1082 | 4620 | Fuses F129 | Totara Valley | 2024-11-30 06:10 | 2024-11-30 06:55 | 0.007959 | 0.00017687 | 6 | 270 | Unplanned | Third party interference | Possible water from irrigator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1083 | SRT278 | From Pole #09232 - 2 ICP fed from Pole 09238 | Winchester | 2024-12-02 08:37 | 2024-12-02 16:39 | 0.085249 | 0.00017687 | 6 | 2892 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1084 | SRT278 | 2 ICP fed from Pole 09238 | Winchester | 2024-12-02 08:37 | 2024-12-02 16:51 | 0.029124 | 5.8955e-05 | 2 | 988 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1085 | HTR082 | Links W740 | Waihuna | 2024-12-02 08:54 | 2024-12-02 14:36 | 0.07057 | 0.00020634 | 7 | 2394 | Planned | Planned interruption | Tree Cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1086 | 4616 | Fuses W526 to end | Waikakahi | 2024-12-02 10:37 | 2024-12-02 14:16 | 0.15493 | 0.00070746 | 24 | 5256 | Unplanned | Third party interference | Tree fell on lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1087 | 4617 | ABS T579 to end | Milford | 2024-12-02 16:49 | 2024-12-02 17:01 | 0.00070746 | 5.8955e-05 | 2 | 24 | Unplanned | Defective equipment | TMK CB2 Overload | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1088 | 4617 | Links T121 minus ABS T579 | Milford | 2024-12-02 16:53 | 2024-12-02 16:58 | 0.0022108 | 0.00044216 | 15 | 75 | Unplanned | Defective equipment | TMK CB2 Overload | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1089 | 4618 | Fuses G236 to end | Speechley | 2024-12-03 05:58 | 2024-12-03 09:02 | 0.016272 | 8.8433e-05 | 3 | 552 | Unplanned | Defective equipment | Line on ground - Corroded / Rotten termination at Dead end | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1090 | DVE391 | From Temp Links at Pole #01505 - D323 - D1816 - D324 - D1310 - D326 | Woodbury | 2024-12-03 08:43 | 2024-12-03 15:56 | 0.11487 | 0.0002653 | 9 | 3897 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1091 | DVE391 | From D323 | Woodbury | 2024-12-03 08:43 | 2024-12-03 16:00 | 0.025763 | 5.8955e-05 | 2 | 874 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1092 | DVE391 | From D1816 | Woodbury | 2024-12-03 08:43 | 2024-12-03 16:02 | 0.012941 | 2.9478e-05 | 1 | 439 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1093 | DVE391 | From D324 | Woodbury | 2024-12-03 08:43 | 2024-12-03 16:08 | 0.013118 | 2.9478e-05 | 1 | 445 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1094 | DVE391 | From D1310 | Woodbury | 2024-12-03 08:43 | 2024-12-03 16:14 | 0.013294 | 2.9478e-05 | 1 | 451 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1095 | DVE391 | From D326 | Woodbury | 2024-12-03 08:43 | 2024-12-03 16:19 | 0.013442 | 2.9478e-05 | 1 | 456 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1096 | HTR083 | From ABS W158 | Waikakahi | 2024-12-04 07:37 | 2024-12-04 07:38 | 0.00070746 | 0.00070746 | 24 | 24 | Planned | Planned interruption | Tree Cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1097 | HTR083 | From ABS WX46 - W158 - WX45 | Waikakahi | 2024-12-04 08:00 | 2024-12-04 16:06 | 0.12894 | 0.0002653 | 9 | 4374 | Planned | Planned interruption | Tree Cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1098 | DVE392 | From Temp Links at Pole #01505 - D323 - D1816 - D324 - D1310 - D326 | Woodbury | 2024-12-04 08:30 | 2024-12-04 15:40 | 0.11408 | 0.0002653 | 9 | 3870 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1099 | DVE392 | From D323 | Woodbury | 2024-12-04 08:30 | 2024-12-04 15:46 | 0.025705 | 5.8955e-05 | 2 | 872 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1100 | DVE392 | From D1816 | Woodbury | 2024-12-04 08:30 | 2024-12-04 15:45 | 0.012823 | 2.9478e-05 | 1 | 435 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1101 | DVE392 | From D324 | Woodbury | 2024-12-04 08:30 | 2024-12-04 15:49 | 0.012941 | 2.9478e-05 | 1 | 439 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1102 | DVE392 | From D1310 | Woodbury | 2024-12-04 08:30 | 2024-12-04 15:56 | 0.013147 | 2.9478e-05 | 1 | 446 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1103 | DVE392 | From D326 | Woodbury | 2024-12-04 08:30 | 2024-12-04 15:47 | 0.012882 | 2.9478e-05 | 1 | 437 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1104 | HTR083 | From ABS W158 | Waikakahi | 2024-12-04 17:25 | 2024-12-04 17:26 | 0.00070746 | 0.00070746 | 24 | 24 | Planned | Planned interruption | Tree Cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1105 | DVE393 | From T429 - D1301 | Woodbury | 2024-12-05 08:30 | 2024-12-05 14:56 | 0.1593 | 0.00041269 | 14 | 5404 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1106 | DVE393 | From D1301 | Woodbury | 2024-12-05 08:30 | 2024-12-05 15:03 | 0.011585 | 2.9478e-05 | 1 | 393 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1107 | 4621 | From RMU Z105 | Glen Lyon | 2024-12-05 09:00 | 2024-12-05 10:30 | 0.034489 | 0.00038321 | 13 | 1170 | Unplanned | Defective equipment | Line Repair | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1108 | HTR085 | TOA317 Fuses | Tawai | 2024-12-06 08:00 | 2024-12-06 13:05 | 0.0089907 | 2.9478e-05 | 1 | 305 | Planned | Planned interruption | Tree trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1109 | JRM049 | RMU L381 to RMU L973 | Arowhenua | 2024-12-08 08:33 | 2024-12-08 14:46 | 0.010995 | 2.9478e-05 | 1 | 373 | Planned | Planned interruption | RMU replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1110 | 5144 | CB T565 | Woodbury | 2024-12-08 12:37 | 2024-12-08 13:07 | 0.17068 | 0.0056892 | 193 | 5790 | Unplanned | Unknown | Lines down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1111 | 1301 | CB G249-LB ABS G353 | Woodbury | 2024-12-08 14:59 | 2024-12-08 16:51 | 0.93102 | 0.0083127 | 282 | 31584 | Unplanned | Adverse weather | Branches on lines due to wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1112 | 1301 | LB ABS G353 | Woodbury | 2024-12-08 14:59 | 2024-12-08 17:32 | 0.30669 | 0.0020045 | 68 | 10404 | Unplanned | Adverse weather | Branches on lines due to wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1113 | 5143 | CB F359- ABS F225 | Fairlie Rural | 2024-12-08 15:31 | 2024-12-08 16:27 | 0.3252 | 0.0058071 | 197 | 11032 | Unplanned | Adverse weather | Tree on lines and pole replacement due to wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1114 | 5143 | ABS F225-Fuses F226 | Fairlie Rural | 2024-12-08 15:31 | 2024-12-08 18:52 | 0.22515 | 0.0011202 | 38 | 7638 | Unplanned | Adverse weather | Tree on lines and pole replacement due to wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1115 | 5143 | Fuses F226 | Fairlie Rural | 2024-12-08 15:31 | 2024-12-08 22:28 | 0.13521 | 0.00032425 | 11 | 4587 | Unplanned | Adverse weather | Tree on lines and pole replacement due to wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1116 | SRT272 | Fuses T112 | Milford | 2024-12-09 09:00 | 2024-12-09 12:54 | 0.11036 | 0.00047164 | 16 | 3744 | Planned | Planned interruption | Replace red tagged pole #01927 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1117 | SRT272 | Fuses TOD412 | Milford | 2024-12-09 09:00 | 2024-12-09 13:20 | 0.022993 | 8.8433e-05 | 3 | 780 | Planned | Planned interruption | Replace red tagged pole #01927 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1118 | GWM1216 | Fuses L757 | Arowhenua | 2024-12-09 09:03 | 2024-12-09 12:50 | 0.013383 | 5.8955e-05 | 2 | 454 | Planned | Planned interruption | Tree cutting pole #36019 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1119 | 4622 | Fuses W305 to end | Otaio | 2024-12-09 10:00 | 2024-12-09 11:31 | 0.029507 | 0.00032425 | 11 | 1001 | Unplanned | Adverse weather | Wind - Branch on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1120 | 4418 | Fuses TO B890 | Cave | 2024-12-09 14:03 | 2024-12-09 15:23 | 0.0023582 | 2.9478e-05 | 1 | 80 | Unplanned | Defective equipment | Broken 11kV jumper to Tx D890 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1121 | 4419 | CB L792 - LB L1339 | Elginshire | 2024-12-09 14:39 | 2024-12-09 15:30 | 0.091705 | 0.0017981 | 61 | 3111 | Unplanned | Defective equipment | Loose Jumper @ Links L309 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1122 | SRT276 | CB T626 | Rolleston Road | 2024-12-10 09:00 | 2024-12-10 09:07 | 0.0061903 | 0.00088433 | 30 | 210 | Planned | Planned interruption | ABS T490 replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1123 | SRT276 | CB T626 | Rolleston Road | 2024-12-10 09:00 | 2024-12-10 16:34 | 2.1011 | 0.004628 | 157 | 71278 | Planned | Planned interruption | ABS T490 replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1124 | SKE1850A | CB13 to RMU E46 | Clifton Terrace | 2024-12-10 09:00 | 2024-12-10 14:55 | 1.4755 | 0.0041563 | 141 | 50055 | Planned | Planned interruption | TE26 maintenance & DB P39 replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1125 | SKE1850A | CB13 to RMU E46 | Clifton Terrace | 2024-12-10 09:00 | 2024-12-10 15:01 | 0.053207 | 0.00014739 | 5 | 1805 | Planned | Planned interruption | TE26 maintenance & DB P39 replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1126 | SKE1850A | CB13 to RMU E46 | Clifton Terrace | 2024-12-10 09:00 | 2024-12-10 15:15 | 0.011054 | 2.9478e-05 | 1 | 375 | Planned | Planned interruption | TE26 maintenance & DB P39 replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1127 | JRM047 | RMU Z449 TOE362 Fuses | Pukaki | 2024-12-10 09:05 | 2024-12-10 13:27 | 0.0077231 | 2.9478e-05 | 1 | 262 | Planned | Planned interruption | Tx E362 oil weep repair | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1128 | JRM047 | RMU Z449 TOE363 Fuses | Pukaki | 2024-12-10 09:05 | 2024-12-10 13:29 | 0.0077821 | 2.9478e-05 | 1 | 264 | Planned | Planned interruption | Tx E362 oil weep repair | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1129 | SRT274 | Links W537 | Waihuna | 2024-12-10 10:02 | 2024-12-10 11:00 | 0.0085485 | 0.00014739 | 5 | 290 | Planned | Planned interruption | Repairs pole #31018 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1130 | 4623 | TX Fuses TO B867 to end | Holme Station | 2024-12-10 11:46 | 2024-12-10 12:47 | 0.0035963 | 5.8955e-05 | 2 | 122 | Unplanned | Defective equipment | Customer pole broken | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1131 | 4624 | RMU TER38 to end | Le Cren Street | 2024-12-10 13:03 | 2024-12-10 13:13 | 0.056597 | 0.0056597 | 192 | 1920 | Unplanned | Defective equipment | Cable fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1132 | 4624 | RMU TEK4 minus RMU TER38 | Le Cren Street | 2024-12-10 13:03 | 2024-12-10 13:20 | 0.097718 | 0.0057481 | 195 | 3315 | Unplanned | Defective equipment | Cable fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1133 | 4624 | HNT CB5 (Le Cren St) minus RMU TEK4 | Le Cren Street | 2024-12-10 13:03 | 2024-12-10 13:23 | 0.11614 | 0.0058071 | 197 | 3940 | Unplanned | Defective equipment | Cable fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1134 | SRT275 | Fuses W312 Tx A163 | Mt Studholme | 2024-12-10 13:30 | 2024-12-10 15:15 | 0.0061903 | 5.8955e-05 | 2 | 210 | Planned | Planned interruption | Tx A163 Crouch Rd conductor replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1135 | SRT275 | Fuses W312 | Mt Studholme | 2024-12-10 13:30 | 2024-12-10 15:01 | 0.0080474 | 8.8433e-05 | 3 | 273 | Planned | Planned interruption | Tx A163 Crouch Rd conductor replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1136 | SRT276 | CB T626 | Rolleston Road | 2024-12-10 16:30 | 2024-12-10 16:34 | 0.0035373 | 0.00088433 | 30 | 120 | Planned | Planned interruption | ABS T490 replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1137 | DVE395 | Fuses T425 TX D775 | Woodbury | 2024-12-11 08:30 | 2024-12-11 14:00 | 0.0097276 | 2.9478e-05 | 1 | 330 | Planned | Planned interruption | Arundel maintenance Task 12 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1138 | DVE395 | Fuses T425 TX D319 | Woodbury | 2024-12-11 08:30 | 2024-12-11 14:12 | 0.020163 | 5.8955e-05 | 2 | 684 | Planned | Planned interruption | Arundel maintenance Task 12 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1139 | DVE395 | Fuses T425 TX D649 | Woodbury | 2024-12-11 08:30 | 2024-12-11 15:35 | 0.012528 | 2.9478e-05 | 1 | 425 | Planned | Planned interruption | Arundel maintenance Task 12 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1140 | JDJ148 | Fuses TOB756 | Pleasant Point Township | 2024-12-11 09:03 | 2024-12-11 15:29 | 0.011378 | 2.9478e-05 | 1 | 386 | Planned | Planned interruption | Pole #39794 replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1141 | WMR156 | Fuses TOC404 | Fairlie Rural | 2024-12-11 11:49 | 2024-12-11 12:03 | 0.00041269 | 2.9478e-05 | 1 | 14 | Planned | Planned interruption | Tap change TX C404 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1142 | 5130 | Pole #31784 to end | Morven | 2024-12-11 11:54 | 2024-12-11 21:15 | 0.066148 | 0.00011791 | 4 | 2244 | Unplanned | Third party interference | Tree fellers dropped tree on lines - broken poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1143 | 5130 | ABS W264 to pole #31784 | Morven | 2024-12-11 12:07 | 2024-12-11 21:15 | 0.38769 | 0.00070746 | 24 | 13152 | Unplanned | Third party interference | Tree fellers dropped tree on lines - broken poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1144 | 5130 | STU CB9 to end minus ABS W264 | Morven | 2024-12-11 12:07 | 2024-12-11 13:00 | 0.50619 | 0.0095508 | 324 | 17172 | Unplanned | Third party interference | Tree fellers dropped tree on lines - broken poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1145 | DVE396 | Links pole #04694 Tx D624 | Woodbury | 2024-12-12 08:30 | 2024-12-12 14:32 | 0.010671 | 2.9478e-05 | 1 | 362 | Planned | Planned interruption | Arundel maintenance Task 13 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1146 | DVE396 | Links pole #04694 Tx D308 | Woodbury | 2024-12-12 08:30 | 2024-12-12 15:15 | 0.035815 | 8.8433e-05 | 3 | 1215 | Planned | Planned interruption | Arundel maintenance Task 13 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1147 | DVE397 | Links pole #04534 | Woodbury | 2024-12-12 08:30 | 2024-12-12 15:51 | 0.025999 | 5.8955e-05 | 2 | 882 | Planned | Planned interruption | Arundel maintenance Task 15 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1148 | JDJ144 | TOB1750 Fuses | Elginshire | 2024-12-13 08:30 | 2024-12-13 14:18 | 0.010258 | 2.9478e-05 | 1 | 348 | Planned | Planned interruption | replace pole #46998 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1149 | 3880 | Fues TO A16 to end | St Andrews | 2024-12-14 23:59 | 2024-12-15 09:33 | 0.03384 | 5.8955e-05 | 2 | 1148 | Unplanned | Wildlife | Possum on TX A16 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1150 | DVE398 / GWM1210 | DB4677 to end | Woodbury | 2024-12-16 08:30 | 2024-12-16 16:15 | 0.013707 | 2.9478e-05 | 1 | 465 | Planned | Planned interruption | Arundel Maintenance Task 14 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1151 | DVE398 / GWM1210 | Fuses TOD312 to end | Woodbury | 2024-12-16 08:30 | 2024-12-16 16:39 | 0.057658 | 0.00011791 | 4 | 1956 | Planned | Planned interruption | Arundel Maintenance Task 14 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1152 | DVE398 / GWM1210 | Fuses TOD629 to end | Woodbury | 2024-12-16 08:30 | 2024-12-16 16:59 | 0.030008 | 5.8955e-05 | 2 | 1018 | Planned | Planned interruption | Arundel Maintenance Task 14 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1153 | DVE398 / GWM1210 | ABS T426 - DB4677 - Fuses TOD312 - Fuses TOD629 | Woodbury | 2024-12-16 08:30 | 2024-12-16 16:00 | 1.5255 | 0.0033899 | 115 | 51750 | Planned | Planned interruption | Arundel Maintenance Task 14 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1154 | SRS026 | ABS F332 to end | Fairlie Rural | 2024-12-16 10:04 | 2024-12-16 13:38 | 0.0063082 | 2.9478e-05 | 1 | 214 | Planned | Planned interruption | Tx C487 replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1155 | 01202 | TO D269 | Speechley | 2024-12-16 15:06 | 2024-12-16 15:45 | 0.0022993 | 5.8955e-05 | 2 | 78 | Unplanned | Wildlife | Remove Possum from Tx D269 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1156 | DVE399 | FusesTOD324 to end | Woodbury | 2024-12-17 08:30 | 2024-12-17 15:05 | 0.011644 | 2.9478e-05 | 1 | 395 | Planned | Planned interruption | Arundel Maintenance Task 14 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1157 | DVE399 | Fuses TOD1816 to end | Woodbury | 2024-12-17 08:30 | 2024-12-17 15:06 | 0.011673 | 2.9478e-05 | 1 | 396 | Planned | Planned interruption | Arundel Maintenance Task 14 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1158 | DVE399 | Fues TOD323 to end | Woodbury | 2024-12-17 08:30 | 2024-12-17 15:10 | 0.023582 | 5.8955e-05 | 2 | 800 | Planned | Planned interruption | Arundel Maintenance Task 14 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1159 | DVE399 | ABS T429 - Fuses TOD323 - Fuses TOD1816 - Fuses TOD324 | Woodbury | 2024-12-17 08:30 | 2024-12-17 14:58 | 0.12581 | 0.00032425 | 11 | 4268 | Planned | Planned interruption | Arundel Maintenance Task 14 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1160 | SRS028 | DB2787 to end | Highfield | 2024-12-17 08:44 | 2024-12-17 15:05 | 0.022462 | 5.8955e-05 | 2 | 762 | Planned | Planned interruption | DB Removal | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1161 | SRS028 | Fuses TOB1186 - DB2787 | Highfield | 2024-12-17 08:44 | 2024-12-17 16:55 | 0.028947 | 5.8955e-05 | 2 | 982 | Planned | Planned interruption | DB Removal | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1162 | GWM1227 | ABS T450 to end | Rangitata | 2024-12-17 09:00 | 2024-12-17 11:58 | 0.19939 | 0.0011202 | 38 | 6764 | Planned | Planned interruption | Tree trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1163 | SKE1759 | Tx E212'01' to end | Lakeside Drive | 2024-12-17 09:17 | 2024-12-17 15:23 | 0.36682 | 0.0010022 | 34 | 12444 | Planned | Planned interruption | RMU maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1164 | SKE1759 | Tx E254-02 | Lakeside Drive | 2024-12-17 09:17 | 2024-12-17 15:29 | 0.010966 | 2.9478e-05 | 1 | 372 | Planned | Planned interruption | RMU maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1165 | 4625 | Fuses TO B1159 to end | Arowhenua | 2024-12-17 11:26 | 2024-12-17 12:29 | 0.0018571 | 2.9478e-05 | 1 | 63 | Unplanned | Unknown | Unknown - 2x blown DO's | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1166 | 5145 | TX B1110 CCT7 | Washdyke | 2024-12-18 07:08 | 2024-12-18 09:58 | 0.045101 | 0.0002653 | 9 | 1530 | Unplanned | Defective equipment | Blown pothead pole #24243 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1167 | 5145 | TX B1110 CCT6 | Washdyke | 2024-12-18 07:08 | 2024-12-18 10:03 | 0.051586 | 0.00029478 | 10 | 1750 | Unplanned | Defective equipment | Blown pothead pole #24243 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1168 | 5145 | TX B1110 CCT4 | Washdyke | 2024-12-18 07:08 | 2024-12-18 11:41 | 0.072427 | 0.0002653 | 9 | 2457 | Unplanned | Defective equipment | Blown pothead pole #24243 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1169 | 5145 | TX B1110 CCT2 | Washdyke | 2024-12-18 07:08 | 2024-12-18 11:44 | 0.089494 | 0.00032425 | 11 | 3036 | Unplanned | Defective equipment | Blown pothead pole #24243 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1170 | 5145 | TX B1110 CCT3 | Washdyke | 2024-12-18 07:08 | 2024-12-18 11:44 | 0.09763 | 0.00035373 | 12 | 3312 | Unplanned | Defective equipment | Blown pothead pole #24243 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1171 | 5145 | TX B1110 CCT5 | Washdyke | 2024-12-18 07:08 | 2024-12-18 11:45 | 0.073488 | 0.0002653 | 9 | 2493 | Unplanned | Defective equipment | Blown pothead pole #24243 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1172 | 5145 | TX B1110 01 | Washdyke | 2024-12-18 07:08 | 2024-12-18 11:41 | 0.0080474 | 2.9478e-05 | 1 | 273 | Unplanned | Defective equipment | Blown pothead pole #24243 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1173 | DVE400 | TX D322'01' | Woodbury | 2024-12-18 08:41 | 2024-12-18 15:12 | 0.046103 | 0.00011791 | 4 | 1564 | Planned | Planned interruption | Arundel Maintenance Task 15 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1174 | 3792 | CB W366 - W560 | Otaio | 2024-12-18 19:01 | 2024-12-18 19:23 | 0.21012 | 0.0095508 | 324 | 7128 | Unplanned | Wildlife | Lines down due to bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1175 | 3792 | W560 | Otaio | 2024-12-18 19:01 | 2024-12-18 21:23 | 0.054416 | 0.00038321 | 13 | 1846 | Unplanned | Wildlife | Lines down due to bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1176 | SRT281 | Tx B544'01' | Holme Station | 2024-12-19 09:24 | 2024-12-19 10:57 | 0.0054828 | 5.8955e-05 | 2 | 186 | Planned | Planned interruption | Transformer replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1177 | SRT281 | ABS L134 to end | Holme Station | 2024-12-19 09:24 | 2024-12-19 10:44 | 0.042448 | 0.0005306 | 18 | 1440 | Planned | Planned interruption | Transformer replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1178 | SRT281 | Links L132 - ABS L134 - Tx B544'01' | Holme Station | 2024-12-19 09:24 | 2024-12-19 10:41 | 0.043126 | 0.00056008 | 19 | 1463 | Planned | Planned interruption | Transformer replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1179 | SRT282 | TX B338 01 | Cave | 2024-12-19 10:00 | 2024-12-19 11:36 | 0.0028299 | 2.9478e-05 | 1 | 96 | Planned | Planned interruption | Transformer replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1180 | 5145 | Gen OFF Tx B1110 (CCT 2, 3, 5 & ICP off bus) - Restore | Washdyke | 2024-12-20 10:40 | 2024-12-20 10:44 | 0.0038911 | 0.00097276 | 33 | 132 | Unplanned | Defective equipment | Blown pothead pole #24243 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1181 | 5145 | Gen OFF Tx B1110 CCT 4 - Restore | Washdyke | 2024-12-20 10:40 | 2024-12-20 11:12 | 0.0084896 | 0.0002653 | 9 | 288 | Unplanned | Defective equipment | Blown pothead pole #24243 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1182 | 3793 | L808 - L1342 | Hadlow | 2024-12-20 17:04 | 2024-12-20 17:12 | 0.035845 | 0.0044806 | 152 | 1216 | Unplanned | Third party interference | Car v Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1183 | 3793 | L1342 - LX99 | Hadlow | 2024-12-20 17:10 | 2024-12-20 17:20 | 0.015918 | 0.0015918 | 54 | 540 | Unplanned | Third party interference | Car v Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1184 | 3793 | LX99 - L710 | Hadlow | 2024-12-20 17:10 | 2024-12-20 20:35 | 0.51969 | 0.0025351 | 86 | 17630 | Unplanned | Third party interference | Car v Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1185 | 3795 | F380 | Fairlie Rural | 2024-12-21 16:29 | 2024-12-21 18:01 | 2.0963 | 0.022786 | 773 | 71116 | Unplanned | Lighting | Lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1186 | 4626 | Fuses TOD1960 | Woodbury | 2024-12-21 16:44 | 2024-12-21 18:13 | 0.0026235 | 2.9478e-05 | 1 | 89 | Unplanned | Lighting | Lightning storm Tripp Settlement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1187 | 4626 | Fuses TOD383 | Woodbury | 2024-12-21 16:44 | 2024-12-21 18:26 | 0.0030067 | 2.9478e-05 | 1 | 102 | Unplanned | Lighting | Lightning storm Tripp Settlement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1188 | 4626 | Fuses G159 | Woodbury | 2024-12-21 16:44 | 2024-12-21 18:51 | 0.022462 | 0.00017687 | 6 | 762 | Unplanned | Lighting | Lightning storm Tripp Settlement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1189 | 4626 | Fuses TOD298 | Woodbury | 2024-12-21 16:44 | 2024-12-21 19:22 | 0.0046575 | 2.9478e-05 | 1 | 158 | Unplanned | Lighting | Lightning storm Tripp Settlement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1190 | 4626 | Fuses TOD978 | Woodbury | 2024-12-21 16:44 | 2024-12-21 19:45 | 0.0053355 | 2.9478e-05 | 1 | 181 | Unplanned | Lighting | Lightning storm Tripp Settlement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1191 | 4626 | Fuses TOD865 | Woodbury | 2024-12-21 16:44 | 2024-12-21 20:05 | 0.005925 | 2.9478e-05 | 1 | 201 | Unplanned | Lighting | Lightning storm Tripp Settlement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1192 | 4626 | Fuses TOD380 | Woodbury | 2024-12-21 16:44 | 2024-12-21 20:17 | 0.0062787 | 2.9478e-05 | 1 | 213 | Unplanned | Lighting | Lightning storm Tripp Settlement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1193 | 4626 | Fuses TOD294 | Woodbury | 2024-12-21 16:44 | 2024-12-22 08:14 | 0.21931 | 0.00023582 | 8 | 7440 | Unplanned | Lighting | Lightning storm Tripp Settlement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1194 | 4626 | Fuses TOD379 | Woodbury | 2024-12-21 16:44 | 2024-12-22 10:36 | 0.0316 | 2.9478e-05 | 1 | 1072 | Unplanned | Lighting | Lightning storm Tripp Settlement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1195 | 4626 | Fuses TOD947 | Woodbury | 2024-12-21 16:44 | 2024-12-22 10:36 | 0.0316 | 2.9478e-05 | 1 | 1072 | Unplanned | Lighting | Lightning storm Tripp Settlement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1196 | 4626 | Fuses TOD1150 | Woodbury | 2024-12-21 16:44 | 2024-12-22 12:11 | 0.068801 | 5.8955e-05 | 2 | 2334 | Unplanned | Lighting | Lightning storm Tripp Settlement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1197 | 4626 | Fuses TOD297 | Woodbury | 2024-12-21 16:44 | 2024-12-22 12:38 | 0.035196 | 2.9478e-05 | 1 | 1194 | Unplanned | Lighting | Lightning storm Tripp Settlement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1198 | 4626 | LBS G353 | Woodbury | 2024-12-22 08:38 | 2024-12-22 10:27 | 0.20564 | 0.0018866 | 64 | 6976 | Unplanned | Lighting | Lightning storm Tripp Settlement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1199 | 3882 | CB T626 minus LBS T775 | Rolleston Road | 2024-12-24 22:30 | 2024-12-24 22:39 | 0.010347 | 0.0011496 | 39 | 351 | Unplanned | Wildlife | Bird Strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1200 | 3882 | LBS T775 minus ABS T675 | Rolleston Road | 2024-12-24 22:30 | 2024-12-24 23:49 | 0.33301 | 0.0042153 | 143 | 11297 | Unplanned | Wildlife | Bird Strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1201 | 3882 | ABS T675 to end | Rolleston Road | 2024-12-24 22:30 | 2024-12-25 03:51 | 0.047312 | 0.00014739 | 5 | 1605 | Unplanned | Wildlife | Bird Strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1202 | 3881 | ABS M385 to end | Haldon-Lilybank 22kV | 2024-12-28 08:31 | 2024-12-28 09:58 | 0.041033 | 0.00047164 | 16 | 1392 | Unplanned | Defective equipment | Reported defect - Missing Arm brace bolts | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1203 | 3796 | CB6 - L166 | Normanby | 2024-12-31 18:44 | 2024-12-31 19:51 | 0.7031 | 0.010494 | 356 | 23852 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1204 | 3796 | L166 - L1220 | Normanby | 2024-12-31 18:44 | 2024-12-31 20:12 | 0.23606 | 0.0026825 | 91 | 8008 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1205 | 3796 | L1220 | Normanby | 2024-12-31 18:44 | 2024-12-31 20:13 | 0.33056 | 0.0037142 | 126 | 11214 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1206 | 3797 | T626 - T665 | Rolleston Road | 2025-01-01 13:42 | 2025-01-01 14:30 | 0.24337 | 0.0050702 | 172 | 8256 | Unplanned | Wildlife | Bird strike - Lines down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1207 | 3797 | T665 | Rolleston Road | 2025-01-01 13:42 | 2025-01-01 16:03 | 0.062345 | 0.00044216 | 15 | 2115 | Unplanned | Wildlife | Bird strike - Lines down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1208 | 3797 | Temp Fuses P#08511 | Winchester | 2025-01-05 04:56 | 2025-01-05 06:35 | 0.014591 | 0.00014739 | 5 | 495 | Unplanned | Vegetation | Tree on line @ P#08525 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1209 | SLA687 | Fuses TO C355 | Fairlie Rural | 2025-01-06 08:02 | 2025-01-06 08:06 | 0.0011791 | 0.00029478 | 10 | 40 | Planned | Planned interruption | Retap Tx C355 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1210 | 5146 | TOD63 | Mahan Road | 2025-01-06 11:03 | 2025-01-06 15:06 | 0.028652 | 0.00011791 | 4 | 972 | Unplanned | Vegetation | Tree on line at p #06518 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1211 | 5147 | L187 | Holme Station | 2025-01-07 11:28 | 2025-01-07 16:05 | 0.016331 | 5.8955e-05 | 2 | 554 | Unplanned | Vegetation | Trees on line @ P#43786 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1212 | 5149 | PLP CB4 to end | Totara Valley | 2025-01-07 19:47 | 2025-01-07 20:27 | 0.68152 | 0.017038 | 578 | 23120 | Unplanned | Adverse weather | Tree branch on line at pole #40317 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1213 | 5148 | GLD G191 to G237 | Geraldine Township | 2025-01-07 20:09 | 2025-01-07 21:02 | 2.0623 | 0.038911 | 1320 | 69960 | Unplanned | Adverse weather | Unkown - Possible trees near lines touching due to winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1214 | 5148 | G237 to end | Geraldine Township | 2025-01-07 20:09 | 2025-01-07 21:21 | 0.43721 | 0.0060724 | 206 | 14832 | Unplanned | Adverse weather | Unkown - Possible trees near lines touching due to winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1215 | 4628 | Fuses W503 | Waikakahi | 2025-01-10 00:10 | 2025-01-10 00:49 | 0.0068978 | 0.00017687 | 6 | 234 | Unplanned | Wildlife | Bird Strke | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1216 | 4629 | CB3 - T642 | Mahan Road | 2025-01-11 17:32 | 2025-01-11 19:29 | 0.082773 | 0.00070746 | 24 | 2808 | Unplanned | Defective equipment | Lines down near pole #05365 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1217 | 4629 | ABS T642 - T464 | Mahan Road | 2025-01-11 17:32 | 2025-01-11 17:53 | 0.042094 | 0.0020045 | 68 | 1428 | Unplanned | Defective equipment | Lines down near pole #05365 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1218 | 4651 | Fuses TO B5 | St Andrews | 2025-01-15 19:53 | 2025-01-16 00:15 | 0.0077231 | 2.9478e-05 | 1 | 262 | Unplanned | Defective equipment | Broken Insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1219 | HTR075 | Fuses L804 TO END | Hadlow | 2025-01-20 08:30 | 2025-01-20 12:57 | 0.38566 | 0.0014444 | 49 | 13083 | Planned | Planned interruption | Tree Trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1220 | HTR076 | ABS L347 - Fuses L341 - ABS L346 | Waitawa | 2025-01-20 08:54 | 2025-01-20 12:53 | 0.1409 | 0.00058955 | 20 | 4780 | Planned | Planned interruption | Tree Trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1221 | HTR078 | Fuses TO B1086 | Waipopo | 2025-01-21 08:30 | 2025-01-21 12:15 | 0.013265 | 5.8955e-05 | 2 | 450 | Planned | Planned interruption | Tree Trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1222 | HTR077 | ABS L878 TO END | Normanby | 2025-01-21 08:30 | 2025-01-21 11:55 | 0.12086 | 0.00058955 | 20 | 4100 | Planned | Planned interruption | Tree Trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1223 | SKE1910 | Fuses T0 B600 + Fuses TO B638 | Highfield | 2025-01-21 08:30 | 2025-01-21 17:04 | 1.3939 | 0.0027119 | 92 | 47288 | Planned | Planned interruption | New RMU Installation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1224 | ACD184 | Fuses T573 - Fuses TO D910 | Winchester | 2025-01-21 09:00 | 2025-01-21 15:11 | 0.032809 | 8.8433e-05 | 3 | 1113 | Planned | Planned interruption | Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1225 | ACD184 | Fuses TO D910 | Winchester | 2025-01-21 09:00 | 2025-01-21 15:36 | 0.023346 | 5.8955e-05 | 2 | 792 | Planned | Planned interruption | Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1226 | JRM050 | Fuses TO B1964 | Totara Valley | 2025-01-21 09:00 | 2025-01-21 12:05 | 0.0054534 | 2.9478e-05 | 1 | 185 | Planned | Planned interruption | Transformer maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1227 | SLA694 | ABS W557 | Tawai | 2025-01-21 09:27 | 2025-01-21 13:28 | 0.042625 | 0.00017687 | 6 | 1446 | Unplanned | Third party interference | Safety Disconnect | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1228 | SKE1911 | Fuses To B686 | Highfield | 2025-01-22 08:33 | 2025-01-22 15:16 | 0.89096 | 0.0022108 | 75 | 30225 | Planned | Planned interruption | New RMU Installation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1229 | JDJ151 | Fuses TO D306 | Woodbury | 2025-01-22 09:31 | 2025-01-22 14:30 | 0.0088138 | 2.9478e-05 | 1 | 299 | Planned | Planned interruption | Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1230 | SKE1912 | Fuses TO B685 + Fuses To B1349 | Highfield | 2025-01-23 08:00 | 2025-01-23 16:08 | 0.79118 | 0.0016213 | 55 | 26840 | Planned | Planned interruption | New RMU Installation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1231 | SKE1912 | Pole #27844 to end | Highfield | 2025-01-23 08:00 | 2025-01-23 16:14 | 0.058248 | 0.00011791 | 4 | 1976 | Planned | Planned interruption | New RMU Installation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1232 | SKE1912 | Fuses To B1425 | Highfield | 2025-01-23 08:00 | 2025-01-23 16:16 | 0.014621 | 2.9478e-05 | 1 | 496 | Planned | Planned interruption | New RMU Installation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1233 | SKE1912 | Tx B686-02 | Highfield | 2025-01-23 08:06 | 2025-01-23 15:36 | 0.4908 | 0.0010907 | 37 | 16650 | Planned | Planned interruption | New RMU Installation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1234 | SKE1904 | TO B1332 - 251 Wai-Iti (P#27656) - 4 Broadway (P#27656) | Highfield | 2025-01-25 07:30 | 2025-01-25 18:30 | 1.3035 | 0.001975 | 67 | 44220 | Planned | Planned interruption | Pages to Centennial OH to UG | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1235 | SKE1904 | 251 Wai-Iti (P#27656) + 4 Broadway (P#27656) | Highfield | 2025-01-25 07:30 | 2025-01-25 19:06 | 0.041033 | 5.8955e-05 | 2 | 1392 | Planned | Planned interruption | Pages to Centennial OH to UG | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1236 | SKE1904 | LB45 | Highfield | 2025-01-25 07:34 | 2025-01-25 18:33 | 0.25254 | 0.00038321 | 13 | 8567 | Planned | Planned interruption | Pages to Centennial OH to UG | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1237 | SKE1904 | P#27642 + P#54685 + 293 Wai-Iti (P#27646) - 2-13 Morgans Rd (P#27643) - 11A Morgans Rd (P#27643) - 11C Morgans Rd (P#27643) - 305 Wai-Iti (P#27643) - 307 Wai-Iti (P#27643) - 289 Wai-Iti (P#27646) - 291 Wai-Iti (P#27646) - 293 Wai-Iti (P#27646) - 295 Wai-Iti (P#27646) | Highfield | 2025-01-25 07:35 | 2025-01-25 18:41 | 0.45154 | 0.00067799 | 23 | 15318 | Planned | Planned interruption | Pages to Centennial OH to UG | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1238 | SKE1904 | 307 Wai-Iti (P#27643) | Highfield | 2025-01-25 07:35 | 2025-01-25 18:47 | 0.019809 | 2.9478e-05 | 1 | 672 | Planned | Planned interruption | Pages to Centennial OH to UG | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1239 | SKE1904 | 305 Wai-Iti (P#27643) + 2-13 Morgans Rd (P#27643) + 11A Morgans Rd (P#27643) + 11C Morgans Rd (P#27643) | Highfield | 2025-01-25 07:35 | 2025-01-25 18:49 | 0.079472 | 0.00011791 | 4 | 2696 | Planned | Planned interruption | Pages to Centennial OH to UG | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1240 | SKE1904 | 289 Wai-Iti (P#27646) + 291 Wai-Iti (P#27646) + 293 Wai-Iti (P#27646) + 295 Wai-Iti (P#27646) | Highfield | 2025-01-25 07:35 | 2025-01-25 18:57 | 0.080415 | 0.00011791 | 4 | 2728 | Planned | Planned interruption | Pages to Centennial OH to UG | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1241 | 4752 | RGA CB3 | Mahan Road | 2025-01-26 07:00 | 2025-01-26 11:16 | 0.69426 | 0.0027119 | 92 | 23552 | Unplanned | Defective equipment | Broken insulator and LAs pole #05386 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1242 | 4751 | CB T127 | Rangitata | 2025-01-26 07:01 | 2025-01-26 09:47 | 0.3621 | 0.0021813 | 74 | 12284 | Unplanned | Third party interference | Irrigator spraying lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1243 | 4752 | RGA CB3-ABS T642 | Mahan Road | 2025-01-26 19:10 | 2025-01-27 01:57 | 0.28794 | 0.00070746 | 24 | 9768 | Unplanned | Defective equipment | Broken insulator and LAs pole #05386 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1244 | 4752 | ABS T642 | Mahan Road | 2025-01-26 19:10 | 2025-01-26 20:54 | 0.20847 | 0.0020045 | 68 | 7072 | Unplanned | Defective equipment | Broken insulator and LAs pole #05386 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1245 | 1203 | TIM CB2832 | Grants Road | 2025-01-27 05:54 | 2025-01-27 06:05 | 0.37451 | 0.034047 | 1155 | 12705 | Unplanned | Third party interference | Isolation for Car V Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1246 | SKE1760A | L425 | Old North Road | 2025-01-27 08:03 | 2025-01-29 17:10 | 0.10102 | 2.9478e-05 | 1 | 3427 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1247 | SKE1760A | L426 | Old North Road | 2025-01-27 08:03 | 2025-01-29 17:20 | 0.20263 | 5.8955e-05 | 2 | 6874 | Planned | Planned interruption | RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1248 | 5132 | RMU M146 to end | Lakeside Drive | 2025-01-27 16:19 | 2025-01-27 18:54 | 0.018276 | 0.00011791 | 4 | 620 | Unplanned | Defective equipment | Damaged insulation on RMU Bushing | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1249 | 5132 | RMU M101 to end minus M146 | Lakeside Drive | 2025-01-27 18:40 | 2025-01-27 18:54 | 0.00041269 | 2.9478e-05 | 1 | 14 | Unplanned | Defective equipment | Damaged insulation on RMU Bushing | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1250 | ACD175 | G177 (LBS G353) - D2158 (Ex. Tx D865) - D947 - D1126 - D297 | Woodbury | 2025-01-28 08:31 | 2025-01-28 16:43 | 0.91369 | 0.0018571 | 63 | 30996 | Planned | Planned interruption | Tripp Settlement Line maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1251 | ACD175 | D2158 (Ex. Tx D865) | Woodbury | 2025-01-28 08:31 | 2025-01-28 17:06 | 0.015181 | 2.9478e-05 | 1 | 515 | Planned | Planned interruption | Tripp Settlement Line maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1252 | ACD175 | D947 | Woodbury | 2025-01-28 08:31 | 2025-01-28 17:19 | 0.015564 | 2.9478e-05 | 1 | 528 | Planned | Planned interruption | Tripp Settlement Line maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1253 | ACD175 | D1126 | Woodbury | 2025-01-28 08:31 | 2025-01-28 17:28 | 0.031659 | 5.8955e-05 | 2 | 1074 | Planned | Planned interruption | Tripp Settlement Line maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1254 | ACD175 | D297 | Woodbury | 2025-01-28 08:31 | 2025-01-28 17:43 | 0.016272 | 2.9478e-05 | 1 | 552 | Planned | Planned interruption | Tripp Settlement Line maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1255 | 5150 | RMU L352 | Elginshire | 2025-01-28 13:12 | 2025-01-28 15:11 | 0.0035078 | 2.9478e-05 | 1 | 119 | Unplanned | Unknown | Tap Tx B1346 down to Tap #1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1256 | 5133 | CB W590 to end minus ABS W494 | Tawai | 2025-01-28 21:15 | 2025-01-28 21:52 | 0.18651 | 0.0050407 | 171 | 6327 | Unplanned | Unknown | Broken Conductor - Possible corrosion from PG Clamp | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1257 | 5133 | ABS W494 to end | Tawai | 2025-01-28 21:15 | 2025-01-29 00:04 | 0.45832 | 0.0027119 | 92 | 15548 | Unplanned | Unknown | Broken Conductor - Possible corrosion from PG Alamp | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1258 | ACD176 | G177 (LBS G353) | Woodbury | 2025-01-29 08:30 | 2025-01-29 15:48 | 0.87796 | 0.0020045 | 68 | 29784 | Planned | Planned interruption | Tripp Settlement Line maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1259 | GWM1236 | LX82 | Hadlow | 2025-01-29 09:00 | 2025-01-29 11:42 | 0.19579 | 0.0012086 | 41 | 6642 | Planned | Planned interruption | Tree Cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1260 | 5131 | GLD CB G191 to end minus TX D373 | Geraldine Township | 2025-01-29 17:16 | 2025-01-29 18:06 | 2.2403 | 0.044806 | 1520 | 76000 | Unplanned | Third party interference | Emergency Trip - Lines down - Woodbury Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1261 | 5131 | TX D373 | Geraldine Township | 2025-01-29 17:16 | 2025-01-29 19:19 | 0.021755 | 0.00017687 | 6 | 738 | Unplanned | Third party interference | Emergency Trip - Lines down - Woodbury Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1262 | ACD177 | G162 - D298 - D378 | Woodbury | 2025-01-30 08:30 | 2025-01-30 14:30 | 0.042448 | 0.00011791 | 4 | 1440 | Planned | Planned interruption | Tripp Settlement Line maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1263 | ACD177 | D298 | Woodbury | 2025-01-30 08:30 | 2025-01-30 14:42 | 0.010966 | 2.9478e-05 | 1 | 372 | Planned | Planned interruption | Tripp Settlement Line maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1264 | ACD177 | D378 | Woodbury | 2025-01-30 08:30 | 2025-01-30 15:02 | 0.02311 | 5.8955e-05 | 2 | 784 | Planned | Planned interruption | Tripp Settlement Line maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1265 | 3884 | Fuses W266 to end | Morven | 2025-02-01 21:53 | 2025-02-01 23:48 | 0.030509 | 0.0002653 | 9 | 1035 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1266 | 3883 | Fuses L208 to end | Levels Plain | 2025-02-02 06:05 | 2025-02-02 07:23 | 0.041387 | 0.0005306 | 18 | 1404 | Unplanned | Wildlife | Bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1267 | SEM099 | Fuses TO A1053 to end | Glenavy | 2025-02-03 09:04 | 2025-02-03 16:19 | 0.025646 | 5.8955e-05 | 2 | 870 | Planned | Planned interruption | Tree Cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1268 | SRS031 | TE140 CCT14 to end | Le Cren Street | 2025-02-03 18:11 | 2025-02-03 18:36 | 0.0022108 | 8.8433e-05 | 3 | 75 | Planned | Planned interruption | Lucy Box Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1269 | SRS031 | TE140 CCT15 to end minus conduit box H253 to end | Le Cren Street | 2025-02-03 18:11 | 2025-02-03 18:29 | 0.0015918 | 8.8433e-05 | 3 | 54 | Planned | Planned interruption | Lucy Box Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1270 | SRS031 | Conduit box H253 to end | Le Cren Street | 2025-02-03 18:11 | 2025-02-03 18:35 | 0.0028299 | 0.00011791 | 4 | 96 | Planned | Planned interruption | Lucy Box Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1271 | SRS031 | TE140 CCT16 to end | Le Cren Street | 2025-02-03 18:11 | 2025-02-03 18:36 | 0.0051586 | 0.00020634 | 7 | 175 | Planned | Planned interruption | Lucy Box Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1272 | SRS031 | TE140 CCT17 to end | Le Cren Street | 2025-02-03 18:11 | 2025-02-03 18:41 | 0.0035373 | 0.00011791 | 4 | 120 | Planned | Planned interruption | Lucy Box Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1273 | SRS031 | TE140 CCT13 - New LB H359 - 1 (H251) | Le Cren Street | 2025-02-03 18:11 | 2025-02-04 04:05 | 0.052529 | 8.8433e-05 | 3 | 1782 | Planned | Planned interruption | Lucy Box Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1274 | SRS031 | TE140 CCT13 - New LB H359 - 1 (H250) | Le Cren Street | 2025-02-03 18:11 | 2025-02-04 04:32 | 0.036611 | 5.8955e-05 | 2 | 1242 | Planned | Planned interruption | Lucy Box Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1275 | SRS031 | TE140 CCT13 - New LB H359 - 2 | Le Cren Street | 2025-02-03 18:11 | 2025-02-04 04:38 | 0.018482 | 2.9478e-05 | 1 | 627 | Planned | Planned interruption | Lucy Box Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1276 | SRS031 | TE140 CCT13 - New LB H359 - 7 | Le Cren Street | 2025-02-03 18:11 | 2025-02-04 03:52 | 0.034253 | 5.8955e-05 | 2 | 1162 | Planned | Planned interruption | Lucy Box Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1277 | SRS031 | TE140 CCT15 to end minus conduit box H253 to end | Le Cren Street | 2025-02-04 03:21 | 2025-02-04 03:43 | 0.0019455 | 8.8433e-05 | 3 | 66 | Planned | Planned interruption | Lucy Box Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1278 | SRS031 | TE140 CCT17 to end | Le Cren Street | 2025-02-04 03:21 | 2025-02-04 03:43 | 0.002594 | 0.00011791 | 4 | 88 | Planned | Planned interruption | Lucy Box Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1279 | SRS031 | Conduit box H253 to end | Le Cren Street | 2025-02-04 03:23 | 2025-02-04 03:43 | 0.0023582 | 0.00011791 | 4 | 80 | Planned | Planned interruption | Lucy Box Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1280 | SRS031 | TE140 CCT14 to end | Le Cren Street | 2025-02-04 03:25 | 2025-02-04 03:43 | 0.0015918 | 8.8433e-05 | 3 | 54 | Planned | Planned interruption | Lucy Box Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1281 | SRS031 | TE140 CCT16 to end | Le Cren Street | 2025-02-04 03:25 | 2025-02-04 03:43 | 0.0037142 | 0.00020634 | 7 | 126 | Planned | Planned interruption | Lucy Box Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1282 | 5075 | T644 | Arundel | 2025-02-04 06:09 | 2025-02-04 07:07 | 0.0051291 | 8.8433e-05 | 3 | 174 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1283 | ACD178 | Fuses G163 to end minus TX D380, D381, D1163, D978, D1150 | Woodbury | 2025-02-04 08:30 | 2025-02-04 15:43 | 0.038291 | 8.8433e-05 | 3 | 1299 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1284 | ACD178 | TX D380 to end | Woodbury | 2025-02-04 08:30 | 2025-02-04 16:02 | 0.013324 | 2.9478e-05 | 1 | 452 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1285 | ACD178 | TX D381 to end | Woodbury | 2025-02-04 08:30 | 2025-02-04 16:23 | 0.013943 | 2.9478e-05 | 1 | 473 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1286 | ACD178 | TX D1163 to end | Woodbury | 2025-02-04 08:30 | 2025-02-04 16:15 | 0.013707 | 2.9478e-05 | 1 | 465 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1287 | ACD178 | TX D978 to end | Woodbury | 2025-02-04 08:30 | 2025-02-04 16:29 | 0.01412 | 2.9478e-05 | 1 | 479 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1288 | ACD178 | TX D1150 to end | Woodbury | 2025-02-04 08:30 | 2025-02-04 16:57 | 0.02989 | 5.8955e-05 | 2 | 1014 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1289 | LXL128A | TE19 - TE19-11 | Park Lane | 2025-02-04 20:22 | 2025-02-04 21:44 | 0.21271 | 0.002594 | 88 | 7216 | Unplanned | Defective equipment | Cable fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1290 | LXL128A | TE19-11 - DB Z57 | Park Lane | 2025-02-04 20:22 | 2025-02-04 22:17 | 0.027119 | 0.00023582 | 8 | 920 | Unplanned | Defective equipment | Cable fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1291 | LXL128A | DB Z57 | Park Lane | 2025-02-04 20:22 | 2025-02-04 21:50 | 0.0051881 | 5.8955e-05 | 2 | 176 | Unplanned | Defective equipment | Cable fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1292 | GWM1241 | ABS T665 to end | Rolleston Road | 2025-02-05 09:00 | 2025-02-05 11:12 | 0.058366 | 0.00044216 | 15 | 1980 | Planned | Planned interruption | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1293 | WMR163 | BPD13 - ABS WX46 | Waikakahi | 2025-02-06 03:53 | 2025-02-06 05:53 | 0.21578 | 0.0017981 | 61 | 7320 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1294 | WMR163 | BPD13 - ABS W117 | Waikakahi | 2025-02-06 03:53 | 2025-02-06 06:38 | 0.1216 | 0.00073694 | 25 | 4125 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1295 | WMR163 | ABS W117 | Waikakahi | 2025-02-06 03:53 | 2025-02-06 06:58 | 1.0143 | 0.0054828 | 186 | 34410 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1296 | WMR164/165 | Links T785 @ Pole #03968 | Waitohi | 2025-02-06 23:53 | 2025-02-07 03:00 | 0.038586 | 0.00020634 | 7 | 1309 | Unplanned | Third party interference | Car v Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1297 | WMR164/165 | TMK CB9 -(ABS T315 - Links T785 @ Pole #03968) | Waitohi | 2025-02-06 23:53 | 2025-02-07 05:31 | 2.1621 | 0.0063967 | 217 | 73346 | Unplanned | Third party interference | Car v Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1298 | WMR164/165 | ABS T315 - Links T785 @ Pole #03968 | Waitohi | 2025-02-06 23:53 | 2025-02-07 08:26 | 1.1039 | 0.0021519 | 73 | 37449 | Unplanned | Third party interference | Car v Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1299 | WMR164/165 | Links T785 @ Pole #03968 | Waitohi | 2025-02-07 08:16 | 2025-02-07 08:26 | 0.0020634 | 0.00020634 | 7 | 70 | Unplanned | Third party interference | Car v Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1300 | 4653 | Fuses TOB1463 | Normanby | 2025-02-07 12:04 | 2025-02-07 13:39 | 0.0084011 | 8.8433e-05 | 3 | 285 | Unplanned | Third party interference | Damaged Stay wire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1301 | 1210 | Fuses TOB1463 | Normanby | 2025-02-07 12:04 | 2025-02-07 13:39 | 0.0084011 | 8.8433e-05 | 3 | 285 | Unplanned | Third party interference | Blown Fuses due to stay wire in contact with lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1302 | WMR166 | STU CB9 - Links W742 | Morven | 2025-02-09 02:39 | 2025-02-09 04:56 | 1.3811 | 0.010081 | 342 | 46854 | Unplanned | Wildlife | Bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1303 | WMR166 | Links W742 | Morven | 2025-02-09 02:39 | 2025-02-09 08:02 | 0.12378 | 0.00038321 | 13 | 4199 | Unplanned | Wildlife | Bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1304 | WMR167 | W590 - W494 | Tawai | 2025-02-09 06:14 | 2025-02-09 06:54 | 0.20163 | 0.0050407 | 171 | 6840 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1305 | WMR167 | W494 | Tawai | 2025-02-09 06:14 | 2025-02-09 07:36 | 0.22238 | 0.0027119 | 92 | 7544 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1306 | 1205 | Fuses L124-TX B100 | Holme Station | 2025-02-10 08:05 | 2025-02-10 08:38 | 0.0038911 | 0.00011791 | 4 | 132 | Unplanned | Vegetation | Bark on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1307 | 1205 | TX B100 | Holme Station | 2025-02-10 08:05 | 2025-02-10 08:53 | 0.0014149 | 2.9478e-05 | 1 | 48 | Unplanned | Vegetation | Bark on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1308 | GWM1245 | Links F453 to end | Totara Valley | 2025-02-10 09:00 | 2025-02-10 13:49 | 0.15334 | 0.0005306 | 18 | 5202 | Planned | Planned interruption | Tree Cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1309 | SRT293 | W203 minus W710 minus W267 minus TX A544 | Waimate | 2025-02-11 08:01 | 2025-02-11 16:48 | 0.031069 | 5.8955e-05 | 2 | 1054 | Planned | Planned interruption | TX Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1310 | SRT293 | TX A544 CCT2 minus #18 & #26 Leanord St | Waimate | 2025-02-11 08:01 | 2025-02-11 17:00 | 0.22244 | 0.00041269 | 14 | 7546 | Planned | Planned interruption | TX Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1311 | SRT293 | 18 Leonard St | Waimate | 2025-02-11 08:01 | 2025-02-11 17:05 | 0.016036 | 2.9478e-05 | 1 | 544 | Planned | Planned interruption | TX Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1312 | SRT293 | 26 Leonard St | Waimate | 2025-02-11 08:01 | 2025-02-11 17:06 | 0.016065 | 2.9478e-05 | 1 | 545 | Planned | Planned interruption | TX Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1313 | SRT293 | TX A544 CCT3 minus 156 High St and poles #22273/22274 | Waimate | 2025-02-11 08:01 | 2025-02-11 17:07 | 0.69208 | 0.0012675 | 43 | 23478 | Planned | Planned interruption | TX Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1314 | SRT293 | #156 High St | Waimate | 2025-02-11 08:01 | 2025-02-11 17:15 | 0.016331 | 2.9478e-05 | 1 | 554 | Planned | Planned interruption | TX Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1315 | SRT293 | ICP's fed from poles #22273/22274 | Waimate | 2025-02-11 08:01 | 2025-02-11 17:16 | 0.06544 | 0.00011791 | 4 | 2220 | Planned | Planned interruption | TX Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1316 | JRM053 | TX E253 to end | Haldon-Lilybank | 2025-02-11 09:00 | 2025-02-11 14:41 | 0.23119 | 0.00067799 | 23 | 7843 | Planned | Planned interruption | LB Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1317 | JRM053 | TX E245 to end | Haldon-Lilybank | 2025-02-11 09:00 | 2025-02-11 14:46 | 0.33658 | 0.00097276 | 33 | 11418 | Planned | Planned interruption | LB Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1318 | JRM053 | TX E314 to end | Haldon-Lilybank | 2025-02-11 09:00 | 2025-02-11 14:52 | 0.29053 | 0.00082537 | 28 | 9856 | Planned | Planned interruption | LB Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1319 | JMR760 | RMU M146 FS to end | Lakeside Drive | 2025-02-11 11:51 | 2025-02-11 12:44 | 0.0062493 | 0.00011791 | 4 | 212 | Unplanned | Defective equipment | Repairs to LV bushing after flashover | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1320 | ACD182 | W461 to end | Morven | 2025-02-12 08:30 | 2025-02-12 15:31 | 0.01241 | 2.9478e-05 | 1 | 421 | Planned | Planned interruption | Line Alteration (Delta Arms) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1321 | ACD182 | Links W742 minus W461, TX A233, A1154, A1157 & A1158 | Morven | 2025-02-12 08:31 | 2025-02-12 15:27 | 0.073576 | 0.00017687 | 6 | 2496 | Planned | Planned interruption | Line Alteration (Delta Arms) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1322 | ACD182 | TX A233 | Morven | 2025-02-12 08:31 | 2025-02-12 15:37 | 0.037672 | 8.8433e-05 | 3 | 1278 | Planned | Planned interruption | Line Alteration (Delta Arms) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1323 | ACD182 | TX A1154 | Morven | 2025-02-12 08:31 | 2025-02-12 15:43 | 0.012734 | 2.9478e-05 | 1 | 432 | Planned | Planned interruption | Line Alteration (Delta Arms) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1324 | ACD182 | TX A1157 | Morven | 2025-02-12 08:31 | 2025-02-12 15:48 | 0.012882 | 2.9478e-05 | 1 | 437 | Planned | Planned interruption | Line Alteration (Delta Arms) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1325 | ACD182 | TX A1158 | Morven | 2025-02-12 08:31 | 2025-02-12 15:55 | 0.013088 | 2.9478e-05 | 1 | 444 | Planned | Planned interruption | Line Alteration (Delta Arms) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1326 | ACD183 | W461 to end | Morven | 2025-02-13 08:30 | 2025-02-13 15:09 | 0.011762 | 2.9478e-05 | 1 | 399 | Planned | Planned interruption | Line Alteration (Delta Arms) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1327 | ACD183 | Links W742 minus W461, TX A856 | Morven | 2025-02-13 08:32 | 2025-02-13 15:05 | 0.12743 | 0.00032425 | 11 | 4323 | Planned | Planned interruption | Line Alteration (Delta Arms) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1328 | ACD183 | A856 to end | Morven | 2025-02-13 08:32 | 2025-02-13 15:18 | 0.011968 | 2.9478e-05 | 1 | 406 | Planned | Planned interruption | Line Alteration (Delta Arms) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1329 | 4753 | Fuses T317 to end | Waitohi | 2025-02-13 14:42 | 2025-02-13 18:30 | 0.12098 | 0.0005306 | 18 | 4104 | Unplanned | Third party interference | Mower vs pole #01317 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1330 | 5026 | TVS CB3 Pukaki | Pukaki | 2025-02-14 09:00 | 2025-02-14 11:03 | 0.15953 | 0.001297 | 44 | 5412 | Unplanned | Defective equipment | Broken insulator replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1331 | WMR168 | TX A1106 to end | Tawai | 2025-02-14 12:26 | 2025-02-14 12:31 | 0.00014739 | 2.9478e-05 | 1 | 5 | Planned | Planned interruption | TX Tap Change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1332 | SRS037 | TX B2116 to end | Washdyke | 2025-02-15 07:30 | 2025-02-15 13:16 | 0.010199 | 2.9478e-05 | 1 | 346 | Planned | Planned interruption | RMU Upgrade. DB Switched off for automation supply connection | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1333 | GWM1244 | ABS W221 to end | Mt Studholme | 2025-02-15 09:00 | 2025-02-15 12:00 | 0.15918 | 0.00088433 | 30 | 5400 | Planned | Planned interruption | Tree Cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1334 | GWM1247 | Fuses W741 to end | Waihuna | 2025-02-17 09:20 | 2025-02-17 15:51 | 0.08068 | 0.00020634 | 7 | 2737 | Planned | Planned interruption | Tree Cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1335 | SRS032 | ICP fed from LB H360/5 | Stafford Street | 2025-02-17 18:47 | 2025-02-18 01:09 | 0.01126 | 2.9478e-05 | 1 | 382 | Planned | Planned interruption | Lucy Box Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1336 | SRS032 | ICP fed from LB H360/6 | Stafford Street | 2025-02-17 18:47 | 2025-02-18 09:48 | 0.053119 | 5.8955e-05 | 2 | 1802 | Planned | Planned interruption | Lucy Box Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1337 | SRS032 | ICP fed from LB H360/7 | Stafford Street | 2025-02-17 18:47 | 2025-02-18 08:33 | 0.073046 | 8.8433e-05 | 3 | 2478 | Planned | Planned interruption | Lucy Box Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1338 | SRS032 | ICP fed from LB H360/8 | Stafford Street | 2025-02-17 18:47 | 2025-02-18 07:38 | 0.022727 | 2.9478e-05 | 1 | 771 | Planned | Planned interruption | Lucy Box Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1339 | SRS032 | ICP fed from LB H360/4 | Stafford Street | 2025-02-17 18:47 | 2025-02-18 07:20 | 0.022197 | 2.9478e-05 | 1 | 753 | Planned | Planned interruption | Lucy Box Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1340 | SRS032 | TE5 CCT19 | Stafford Street | 2025-02-17 19:00 | 2025-02-17 19:05 | 0.00058955 | 0.00011791 | 4 | 20 | Planned | Planned interruption | Lucy Box Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1341 | SRS032 | TE5 CCT14 & TE5 CCT13 minus LB H289 CCT7 | Stafford Street | 2025-02-17 19:00 | 2025-02-17 19:06 | 0.0005306 | 8.8433e-05 | 3 | 18 | Planned | Planned interruption | Lucy Box Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1342 | SRS032 | TE5 CCT14 & TE5 CCT13 minus LB H289 CCT7 | Stafford Street | 2025-02-18 00:50 | 2025-02-18 00:58 | 0.00070746 | 8.8433e-05 | 3 | 24 | Planned | Planned interruption | Lucy Box Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1343 | SRS032 | TE5 CCT19 | Stafford Street | 2025-02-18 00:52 | 2025-02-18 00:58 | 0.00070746 | 0.00011791 | 4 | 24 | Planned | Planned interruption | Lucy Box Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1344 | 1206 | Fuses F331 to end | Fairlie Rural | 2025-02-18 15:40 | 2025-02-18 16:05 | 0.0044216 | 0.00017687 | 6 | 150 | Unplanned | Unknown | Blown Fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1345 | SRS033 | TE36 minus CCT13, CCT16 & Lucy box H6/3 | Stafford Street | 2025-02-18 18:27 | 2025-02-18 22:59 | 0.024054 | 8.8433e-05 | 3 | 816 | Planned | Planned interruption | Lucy Box Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1346 | SKE1927 / SKE1931 | CB L107 to end minus Links L225 | Totara Valley | 2025-02-19 09:00 | 2025-02-19 16:22 | 1.2378 | 0.0028004 | 95 | 41990 | Planned | Planned interruption | ABS Upgrade to LBS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1347 | SKE1927 / SKE1931 | Links L225 to end | Totara Valley | 2025-02-19 09:00 | 2025-02-19 09:06 | 0.010966 | 0.0018276 | 62 | 372 | Planned | Planned interruption | ABS Upgrade to LBS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1348 | JRM057 | TX B1244 to end | Normanby | 2025-02-19 09:13 | 2025-02-19 14:06 | 0.017274 | 5.8955e-05 | 2 | 586 | Planned | Planned interruption | TX Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1349 | 5134 | GLD CB G191 to Links G237 minus TX D1094 | Geraldine Township | 2025-02-19 12:13 | 2025-02-19 14:05 | 4.216 | 0.037643 | 1277 | 143024 | Unplanned | Defective equipment | Cable Fault at RMU G240 Cable Box | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1350 | 5134 | RMU G232 to end | Geraldine Township | 2025-02-19 12:13 | 2025-02-19 14:14 | 0.56712 | 0.0046869 | 159 | 19239 | Unplanned | Defective equipment | Cable Fault at RMU G240 Cable Box | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1351 | 5134 | TX D854 Minus CCT2, CCT3, CCt4 | Geraldine Township | 2025-02-19 12:13 | 2025-02-19 14:40 | 0.0043332 | 2.9478e-05 | 1 | 147 | Unplanned | Defective equipment | Cable Fault at RMU G240 Cable Box | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1352 | 5134 | TX D854 CCT2 | Geraldine Township | 2025-02-19 12:13 | 2025-02-19 14:41 | 0.043627 | 0.00029478 | 10 | 1480 | Unplanned | Defective equipment | Cable Fault at RMU G240 Cable Box | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1353 | 5134 | TX D854 CCT3 | Geraldine Township | 2025-02-19 12:13 | 2025-02-19 14:32 | 0.049169 | 0.00035373 | 12 | 1668 | Unplanned | Defective equipment | Cable Fault at RMU G240 Cable Box | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1354 | 5134 | TX D854 CCT4 | Geraldine Township | 2025-02-19 12:13 | 2025-02-19 14:30 | 0.096923 | 0.00070746 | 24 | 3288 | Unplanned | Defective equipment | Cable Fault at RMU G240 Cable Box | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1355 | 5134 | TX D1094 Minus CCT2, CCT3 | Geraldine Township | 2025-02-19 12:13 | 2025-02-19 14:34 | 0.12469 | 0.00088433 | 30 | 4230 | Unplanned | Defective equipment | Cable Fault at RMU G240 Cable Box | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1356 | 5134 | TX D1094 CCT2 | Geraldine Township | 2025-02-19 12:13 | 2025-02-19 14:26 | 0.019603 | 0.00014739 | 5 | 665 | Unplanned | Defective equipment | Cable Fault at RMU G240 Cable Box | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1357 | 5134 | TX D1094 CCT3 | Geraldine Township | 2025-02-19 12:13 | 2025-02-19 14:30 | 0.032308 | 0.00023582 | 8 | 1096 | Unplanned | Defective equipment | Cable Fault at RMU G240 Cable Box | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1358 | 4756 | Fuses L122 | Holme Station | 2025-02-19 18:48 | 2025-02-19 20:33 | 0.046427 | 0.00044216 | 15 | 1575 | Unplanned | Lighting | Blown fuses due to lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1359 | 4756 | Fuses TOB538 | Holme Station | 2025-02-19 18:48 | 2025-02-19 20:30 | 0.0030067 | 2.9478e-05 | 1 | 102 | Unplanned | Lighting | Blown fuses due to lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1360 | 4755 | Fuses TOA869 | Mt Studholme | 2025-02-19 18:55 | 2025-02-19 20:07 | 0.0021224 | 2.9478e-05 | 1 | 72 | Unplanned | Lighting | Lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1361 | 4759 | Fuses TOA386 | Waikakahi | 2025-02-19 19:02 | 2025-02-20 10:09 | 0.026736 | 2.9478e-05 | 1 | 907 | Unplanned | Lighting | Blown fuses due to lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1362 | 4759 | Fuses TOA385 | Waikakahi | 2025-02-19 19:02 | 2025-02-20 10:05 | 0.026618 | 2.9478e-05 | 1 | 903 | Unplanned | Lighting | Blown fuses due to lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1363 | 4759 | Fuses TO809 | Waikakahi | 2025-02-19 19:02 | 2025-02-20 10:09 | 0.026736 | 2.9478e-05 | 1 | 907 | Unplanned | Lighting | Blown fuses due to lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1364 | 4759 | Fuses W538 | Waikakahi | 2025-02-19 19:02 | 2025-02-20 09:46 | 0.026058 | 2.9478e-05 | 1 | 884 | Unplanned | Lighting | Blown fuses due to lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1365 | 4761 | Fuses TOA384 | Waikakahi | 2025-02-19 19:02 | 2025-02-20 10:22 | 0.027119 | 2.9478e-05 | 1 | 920 | Unplanned | Lighting | Blown fuses due to lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1366 | 4754 | CB W196 to end | Morven | 2025-02-19 19:17 | 2025-02-19 20:35 | 0.10577 | 0.001356 | 46 | 3588 | Unplanned | Lighting | Lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1367 | 3916 | CB F426 - Links F107 - Fuses TOC32 | Cave | 2025-02-19 20:18 | 2025-02-20 10:17 | 0.51937 | 0.00061903 | 21 | 17619 | Unplanned | Lighting | Lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1368 | 3916 | Links F107 - Fuses F110 - Fuses F109 | Cave | 2025-02-19 20:18 | 2025-02-20 11:30 | 0.18819 | 0.00020634 | 7 | 6384 | Unplanned | Lighting | Lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1369 | 3916 | Fuses F109 to end | Cave | 2025-02-19 20:18 | 2025-02-20 11:35 | 0.081093 | 8.8433e-05 | 3 | 2751 | Unplanned | Lighting | Lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1370 | 3916 | Fuses F110 - Fuses F111 | Cave | 2025-02-19 20:18 | 2025-02-20 12:02 | 0.3061 | 0.00032425 | 11 | 10384 | Unplanned | Lighting | Lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1371 | 3916 | Fuses F111 - Fuses F105 | Cave | 2025-02-19 20:18 | 2025-02-20 12:48 | 0.029183 | 2.9478e-05 | 1 | 990 | Unplanned | Lighting | Lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1372 | 3916 | Fuses F105 to end | Cave | 2025-02-19 20:18 | 2025-02-20 13:17 | 0.15019 | 0.00014739 | 5 | 5095 | Unplanned | Lighting | Lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1373 | 3918 | Fuses TOC32 | Cave | 2025-02-19 20:18 | 2025-02-20 15:10 | 0.033369 | 2.9478e-05 | 1 | 1132 | Unplanned | Lighting | Lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1374 | 4761 | Fuses TOC353 | Cave | 2025-02-19 20:18 | 2025-02-20 08:46 | 0.022049 | 2.9478e-05 | 1 | 748 | Unplanned | Lighting | Blown fuses due to lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1375 | 4759 | Fuses TOA855 | St Andrews | 2025-02-19 20:28 | 2025-02-20 09:10 | 0.044924 | 5.8955e-05 | 2 | 1524 | Unplanned | Lighting | Blown fuses due to lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1376 | 4759 | Fuses TOA1422 | St Andrews | 2025-02-19 20:28 | 2025-02-20 09:10 | 0.022462 | 2.9478e-05 | 1 | 762 | Unplanned | Lighting | Blown fuses due to lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1377 | 4759 | Fuses TOA8 | St Andrews | 2025-02-19 20:28 | 2025-02-20 08:30 | 0.021283 | 2.9478e-05 | 1 | 722 | Unplanned | Lighting | Blown fuses due to lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1378 | 4759 | Fuses TOA7 | St Andrews | 2025-02-19 20:28 | 2025-02-20 09:26 | 0.068801 | 8.8433e-05 | 3 | 2334 | Unplanned | Lighting | Blown fuses due to lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1379 | 4759 | Fuses TOA6 | St Andrews | 2025-02-19 20:28 | 2025-02-20 09:00 | 0.044334 | 5.8955e-05 | 2 | 1504 | Unplanned | Lighting | Blown fuses due to lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1380 | 4759 | Fuses TOA1548 | St Andrews | 2025-02-19 20:28 | 2025-02-20 08:45 | 0.021725 | 2.9478e-05 | 1 | 737 | Unplanned | Lighting | Blown fuses due to lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1381 | 4760 | Fuses TOA1291 | St Andrews | 2025-02-19 20:28 | 2025-02-20 13:50 | 0.030716 | 2.9478e-05 | 1 | 1042 | Unplanned | Lighting | Blown Tx due to lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1382 | 4761 | Fuses TOA10 | St Andrews | 2025-02-19 20:28 | 2025-02-20 12:48 | 0.057776 | 5.8955e-05 | 2 | 1960 | Unplanned | Lighting | Blown fuses due to lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1383 | 4761 | Fuses TOB1322 | St Andrews | 2025-02-19 20:31 | 2025-02-20 09:45 | 0.023405 | 2.9478e-05 | 1 | 794 | Unplanned | Lighting | Blown fuses due to lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1384 | 4757 | CB W664 - ABS W258 | Waihaorunga | 2025-02-19 23:05 | 2025-02-19 23:39 | 0.449 | 0.013206 | 448 | 15232 | Unplanned | Defective equipment | Broken insulator pole #20685 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1385 | 4757 | ABS W258 - ABS W254 | Waihaorunga | 2025-02-19 23:05 | 2025-02-19 23:52 | 0.48906 | 0.010406 | 353 | 16591 | Unplanned | Defective equipment | Broken insulator pole #20685 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1386 | 4757 | CB W664 - ABS W263 | Waihaorunga | 2025-02-19 23:40 | 2025-02-19 23:45 | 0.022698 | 0.0045396 | 154 | 770 | Unplanned | Defective equipment | Broken insulator pole #20685 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1387 | 4757 | ABS W263 - ABS W258 | Waihaorunga | 2025-02-19 23:40 | 2025-02-20 02:49 | 1.638 | 0.0086664 | 294 | 55566 | Unplanned | Defective equipment | Broken insulator pole #20685 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1388 | SKE1932 | ABS L109 (new LBS L1496) to end minus links L225 | Totara Valley | 2025-02-20 09:00 | 2025-02-20 10:54 | 0.11089 | 0.00097276 | 33 | 3762 | Planned | Planned interruption | LBS commissioning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1389 | 3916 | CB F426 - Links F107 - Fuses TOC32 | Cave | 2025-02-20 11:26 | 2025-02-20 11:30 | 0.0024761 | 0.00061903 | 21 | 84 | Unplanned | Lighting | Lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1390 | 4760 | CB W598 - ABS W417 | St Andrews | 2025-02-20 12:00 | 2025-02-20 13:32 | 0.13017 | 0.0014149 | 48 | 4416 | Unplanned | Lighting | Blown Tx due to lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1391 | 3918 | Fuses F103 - Fuses TOC32 | Cave | 2025-02-20 12:45 | 2025-02-20 14:45 | 0.024761 | 0.00020634 | 7 | 840 | Unplanned | Lighting | Lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1392 | 5028 | G328 to end | Geraldine Township | 2025-02-21 07:30 | 2025-02-21 12:19 | 0.11927 | 0.00041269 | 14 | 4046 | Unplanned | Vegetation | Trees on line @ P#50789 - P#35022 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1393 | 4758 | Fuses TOA48 | St Andrews | 2025-02-21 08:46 | 2025-02-24 12:37 | 0.26831 | 5.8955e-05 | 2 | 9102 | Unplanned | Defective equipment | Blown Tx A48 due to Lightning storm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1394 | JDJ158 | CB W470 to Links at pole #28974 & ABS W337 minus TX A1 | St Andrews | 2025-02-21 08:47 | 2025-02-21 12:32 | 0.099487 | 0.00044216 | 15 | 3375 | Planned | Planned interruption | Lines maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1395 | JDJ158 | TX A1 to end | St Andrews | 2025-02-21 08:47 | 2025-02-21 13:18 | 0.015977 | 5.8955e-05 | 2 | 542 | Planned | Planned interruption | Lines maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1396 | JDJ158 | ABS W337 to CB W598 | St Andrews | 2025-02-21 08:47 | 2025-02-21 12:43 | 0.59828 | 0.0025351 | 86 | 20296 | Planned | Planned interruption | Lines maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1397 | JDJ158 | ABS W648 to end | St Andrews | 2025-02-21 08:47 | 2025-02-21 12:49 | 0.16407 | 0.00067799 | 23 | 5566 | Planned | Planned interruption | Lines maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1398 | JDJ158 | Temp Links at pole #28974 to end + CB W598 to end minus ABS W598 | St Andrews | 2025-02-21 08:47 | 2025-02-21 08:58 | 0.018158 | 0.0016507 | 56 | 616 | Planned | Planned interruption | Lines maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1399 | JDJ158 | Regs A1228 to CB W470 | St Andrews | 2025-02-21 09:10 | 2025-02-21 12:15 | 0.0054534 | 2.9478e-05 | 1 | 185 | Planned | Planned interruption | Lines maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1400 | JDJ158 | Temp Links at pole #28974 to end + CB W598 to end minus ABS W598 | St Andrews | 2025-02-21 12:23 | 2025-02-21 12:32 | 0.014857 | 0.0016507 | 56 | 504 | Planned | Planned interruption | Lines maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1401 | 5135 | G165 to end minus TX D292 | Woodbury | 2025-02-21 14:29 | 2025-02-21 16:40 | 0.0077231 | 5.8955e-05 | 2 | 262 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1402 | 5135 | TX D292 to end | Woodbury | 2025-02-21 14:29 | 2025-02-21 16:50 | 0.0041563 | 2.9478e-05 | 1 | 141 | Unplanned | Unknown | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1403 | SRS035A & B | RMU L1264 minus CB L876 Minus RMU L1140 minus TX B1959, TX B1245 minus Fuses L192 | Levels Plain | 2025-02-22 06:35 | 2025-02-22 15:36 | 0.079737 | 0.00014739 | 5 | 2705 | Planned | Planned interruption | RMU & Field Recloser replacements / Upgrades | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1404 | SRS035A & B | Fuses L192 minus TX B264 | Levels Plain | 2025-02-22 06:35 | 2025-02-22 17:04 | 0.018541 | 2.9478e-05 | 1 | 629 | Planned | Planned interruption | RMU & Field Recloser replacements / Upgrades | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1405 | SRS035A & B | TX B264 | Levels Plain | 2025-02-22 06:35 | 2025-02-22 13:12 | 0.023405 | 5.8955e-05 | 2 | 794 | Planned | Planned interruption | RMU & Field Recloser replacements / Upgrades | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1406 | SRS035A & B | RMU L780 to CB L355 (Links L356) | Arowhenua | 2025-02-22 06:35 | 2025-02-22 15:26 | 0.26609 | 0.00050112 | 17 | 9027 | Planned | Planned interruption | RMU & Field Recloser replacements / Upgrades | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1407 | SRS035A & B | CB L876 minus Links L1253 | Levels Plain | 2025-02-22 06:36 | 2025-02-22 15:48 | 0.30916 | 0.00056008 | 19 | 10488 | Planned | Planned interruption | RMU & Field Recloser replacements / Upgrades | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1408 | SRS035A & B | TX B264 | Levels Plain | 2025-02-22 16:39 | 2025-02-22 17:04 | 0.0014739 | 5.8955e-05 | 2 | 50 | Planned | Planned interruption | RMU & Field Recloser replacements / Upgrades | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1409 | SRT295 | Links L225 - ABS FX16 | Totara Valley | 2025-02-24 09:00 | 2025-02-24 09:06 | 0.0035373 | 0.00058955 | 20 | 120 | Planned | Planned interruption | Replace LB ABS LX92 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1410 | 4758 | ABS W324 - ABS W457 | St Andrews | 2025-02-24 11:14 | 2025-02-24 12:16 | 0.023759 | 0.00038321 | 13 | 806 | Unplanned | Defective equipment | Blown Tx A48 due to Lightning storm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1411 | SRT295 | ABS FX16 - LB ABS F122 | Totara Valley | 2025-02-24 16:00 | 2025-02-24 16:02 | 0.0024761 | 0.0012381 | 42 | 84 | Planned | Planned interruption | Replace LB ABS LX92 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1412 | JDJ159 | ABS W337 - CB W598 | St Andrews | 2025-02-25 08:45 | 2025-02-25 16:53 | 1.2371 | 0.0025351 | 86 | 41968 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1413 | JDJ159 | W470 - p#28974 - ABS W337 | St Andrews | 2025-02-25 08:45 | 2025-02-25 16:38 | 0.13943 | 0.00029478 | 10 | 4730 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1414 | JDJ159 | W598 + p#28974 | St Andrews | 2025-02-25 08:45 | 2025-02-25 09:01 | 0.026412 | 0.0016507 | 56 | 896 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1415 | JDJ159 | W648 to end | St Andrews | 2025-02-25 08:45 | 2025-02-25 17:27 | 0.35391 | 0.00067799 | 23 | 12006 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1416 | JDJ159 | Tx A45 | St Andrews | 2025-02-25 08:45 | 2025-02-25 18:16 | 0.016832 | 2.9478e-05 | 1 | 571 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1417 | JDJ159 | Tx A1 | St Andrews | 2025-02-25 08:45 | 2025-02-25 17:43 | 0.031718 | 5.8955e-05 | 2 | 1076 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1418 | JDJ159 | Tx A1343 | St Andrews | 2025-02-25 08:45 | 2025-02-25 17:58 | 0.016301 | 2.9478e-05 | 1 | 553 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1419 | JDJ159 | Tx A757 | St Andrews | 2025-02-25 08:45 | 2025-02-25 18:10 | 0.016655 | 2.9478e-05 | 1 | 565 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1420 | JDJ159 | Tx A733 | St Andrews | 2025-02-25 08:45 | 2025-02-25 18:28 | 0.017185 | 2.9478e-05 | 1 | 583 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1421 | JDJ159 | Tx A732 | St Andrews | 2025-02-25 08:45 | 2025-02-25 18:17 | 0.016861 | 2.9478e-05 | 1 | 572 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1422 | SKE1928 | Old ABS L221 (N LBS L1510) | Totara Valley | 2025-02-25 09:00 | 2025-02-25 11:00 | 0.18748 | 0.0015623 | 53 | 6360 | Planned | Planned interruption | LBS commissioning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1423 | JDJ159 | L294 - W470 | St Andrews | 2025-02-25 09:11 | 2025-02-25 16:28 | 0.012882 | 2.9478e-05 | 1 | 437 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1424 | JDJ159 | W598 + p#28974 | St Andrews | 2025-02-25 16:30 | 2025-02-25 16:38 | 0.013206 | 0.0016507 | 56 | 448 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1425 | JDJ159/4762 | CB W470 minus ABS W648 | St Andrews | 2025-02-25 16:53 | 2025-02-25 17:19 | 0.12186 | 0.0046869 | 159 | 4134 | Unplanned | Defective equipment | Faulty Link p#28974 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1426 | JDJ161 | Fuses W331 | St Andrews | 2025-02-26 08:44 | 2025-02-26 17:02 | 0.01468 | 2.9478e-05 | 1 | 498 | Planned | Planned interruption | Lines maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1427 | JDJ161 | Tx A549 | St Andrews | 2025-02-26 08:44 | 2025-02-26 17:16 | 0.015093 | 2.9478e-05 | 1 | 512 | Planned | Planned interruption | Lines maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1428 | JDJ161 | Tx A732 | St Andrews | 2025-02-26 08:44 | 2025-02-26 17:30 | 0.015505 | 2.9478e-05 | 1 | 526 | Planned | Planned interruption | Lines maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1429 | JDJ161 | LV to 113 Otaio River Rd | St Andrews | 2025-02-26 08:44 | 2025-02-26 17:34 | 0.015623 | 2.9478e-05 | 1 | 530 | Planned | Planned interruption | Lines maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1430 | JDJ161 | LV to 129 Otaio River Rd | St Andrews | 2025-02-26 08:44 | 2025-02-26 17:37 | 0.015712 | 2.9478e-05 | 1 | 533 | Planned | Planned interruption | Lines maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1431 | JDJ161 | Tx A757 | St Andrews | 2025-02-26 08:44 | 2025-02-26 17:55 | 0.016242 | 2.9478e-05 | 1 | 551 | Planned | Planned interruption | Lines maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1432 | JDJ161 | Tx A733 | St Andrews | 2025-02-26 08:44 | 2025-02-26 18:09 | 0.016655 | 2.9478e-05 | 1 | 565 | Planned | Planned interruption | Lines maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1433 | JDJ161 | Tx A3 | St Andrews | 2025-02-26 08:44 | 2025-02-26 18:23 | 0.017068 | 2.9478e-05 | 1 | 579 | Planned | Planned interruption | Lines maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1434 | JDJ160 | P#28974 - ABS W324 | St Andrews | 2025-02-26 08:45 | 2025-02-26 14:19 | 0.0098455 | 2.9478e-05 | 1 | 334 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1435 | JDJ152 | T780 - LB ABS WX48 | Woodbury | 2025-02-26 08:57 | 2025-02-26 09:00 | 0.0002653 | 8.8433e-05 | 3 | 9 | Planned | Planned interruption | Lines maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1436 | SRS039 | D1404-CCT2 + pool minus LG005 | Geraldine Township | 2025-02-26 09:12 | 2025-02-26 10:09 | 0.0084011 | 0.00014739 | 5 | 285 | Planned | Planned interruption | New equipment install TX D2148, Outage started and was then cancelled due to sensitive customer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1437 | JDJ152 | T780 - LB ABS WX48 | Woodbury | 2025-02-26 15:00 | 2025-02-26 15:03 | 0.0002653 | 8.8433e-05 | 3 | 9 | Planned | Planned interruption | Lines maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1438 | ACD185 | Fuses W460 | St Andrews | 2025-02-28 09:00 | 2025-02-28 11:19 | 0.020487 | 0.00014739 | 5 | 695 | Planned | Planned interruption | Lines maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1439 | GWM1254 | Fuses G272 | Speechley | 2025-02-28 09:00 | 2025-02-28 13:30 | 0.031836 | 0.00011791 | 4 | 1080 | Planned | Planned interruption | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1440 | ACD186 | Tx B249 | Arowhenua | 2025-02-28 09:00 | 2025-02-28 12:12 | 0.11319 | 0.00058955 | 20 | 3840 | Planned | Planned interruption | Tx B249 & B720 replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1441 | ACD186 | ABS L318 - ABS L319 | Arowhenua | 2025-02-28 09:00 | 2025-02-28 12:29 | 0.56064 | 0.0026825 | 91 | 19019 | Planned | Planned interruption | Tx B249 & B720 replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1442 | 5454 | TX A1556 to end | Glenavy | 2025-02-28 13:13 | 2025-02-28 13:28 | 0.00044216 | 2.9478e-05 | 1 | 15 | Unplanned | Defective equipment | Tap Change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1443 | PJD1736 | TX D1006 | Speechley | 2025-03-01 10:15 | 2025-03-01 13:20 | 0.0054534 | 2.9478e-05 | 1 | 185 | Planned | Planned interruption | Replace LAs & Dos | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1444 | SEM131 | STU CB2 (Glenavy) - Links W144 | Glenavy | 2025-03-01 10:38 | 2025-03-01 11:27 | 0.27155 | 0.0055418 | 188 | 9212 | Unplanned | Third party interference | Truck on fire near pole #817083 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1445 | SEM131 | Links W144 to end | Glenavy | 2025-03-01 10:38 | 2025-03-01 13:11 | 0.02255 | 0.00014739 | 5 | 765 | Unplanned | Third party interference | Truck on fire near pole #817083 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1446 | SEM132 | STU CB2 (Glenavy) - Links W144 | Glenavy | 2025-03-01 15:11 | 2025-03-01 15:47 | 0.1995 | 0.0055418 | 188 | 6768 | Unplanned | Third party interference | Hay fire near pole #817083 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1447 | SEM132 | Links W144 to end | Glenavy | 2025-03-01 15:11 | 2025-03-01 16:47 | 0.014149 | 0.00014739 | 5 | 480 | Unplanned | Third party interference | Hay fire near pole #817083 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1448 | SEM133 | Fuses TO C420 | Cricklewood | 2025-03-01 23:50 | 2025-03-02 00:45 | 0.0016213 | 2.9478e-05 | 1 | 55 | Unplanned | Defective equipment | Burnt LV Fuse carrier | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1449 | 5455 | Links F209 to end | Cricklewood | 2025-03-03 09:06 | 2025-03-03 13:14 | 0.10235 | 0.00041269 | 14 | 3472 | Unplanned | Third party interference | Truck Vs Lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1450 | JDJ168 | TX D664 | Woodbury | 2025-03-03 09:50 | 2025-03-03 11:49 | 0.0070157 | 5.8955e-05 | 2 | 238 | Planned | Planned interruption | Red tag pole replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1451 | JDJ163 | TX A733 | St Andrews | 2025-03-04 08:45 | 2025-03-04 17:08 | 0.014827 | 2.9478e-05 | 1 | 503 | Planned | Planned interruption | Otaio Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1452 | JDJ163 | Fuses W321-TX A733 | St Andrews | 2025-03-04 08:45 | 2025-03-04 16:54 | 0.014415 | 2.9478e-05 | 1 | 489 | Planned | Planned interruption | Otaio Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1453 | 5077 | Fuses TOA1422 | St Andrews | 2025-03-04 13:29 | 2025-03-04 17:31 | 0.0071336 | 2.9478e-05 | 1 | 242 | Unplanned | Defective equipment | TX A1422 Failed | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1454 | 5077 | Fuses W326 | St Andrews | 2025-03-04 15:46 | 2025-03-04 17:16 | 0.034489 | 0.00038321 | 13 | 1170 | Unplanned | Defective equipment | TX A1422 Failed | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1455 | ACD187 | CB G295-ABS G184 | Woodbury | 2025-03-05 09:04 | 2025-03-05 12:20 | 0.10977 | 0.00056008 | 19 | 3724 | Planned | Planned interruption | Red tag pole replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1456 | 5456 | BPD CB2 - ABS W554 | Tawai | 2025-03-06 05:40 | 2025-03-06 15:51 | 0.43226 | 0.00070746 | 24 | 14664 | Unplanned | Third party interference | Car v Pole #31151 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1457 | 5456 | ABS W554 | Tawai | 2025-03-06 05:40 | 2025-03-06 07:13 | 0.87451 | 0.0094034 | 319 | 29667 | Unplanned | Third party interference | Car v Pole #31151 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1458 | SRT285 | TX A72 | Otaio | 2025-03-06 08:30 | 2025-03-06 14:54 | 0.033958 | 8.8433e-05 | 3 | 1152 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1459 | SRT285 | Temp links Pole #29337-TX A72 | Otaio | 2025-03-06 08:30 | 2025-03-06 14:37 | 0.010818 | 2.9478e-05 | 1 | 367 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1460 | 5456 | ABS W554 | Tawai | 2025-03-06 16:12 | 2025-03-06 16:13 | 0.0094034 | 0.0094034 | 319 | 319 | Unplanned | Third party interference | Car v Pole #31151 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1461 | 5456 | W176 | Tawai | 2025-03-06 16:12 | 2025-03-06 16:13 | 0.00014739 | 0.00014739 | 5 | 5 | Unplanned | Third party interference | Car v Pole #31151 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1462 | SRT290 & SKE1797 | CB W465 | Otaio | 2025-03-07 08:30 | 2025-03-07 15:59 | 1.125 | 0.0025056 | 85 | 38165 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1463 | SRT290 & SKE1797 | CB W685-Temp Links Pole #43015 | Otaio | 2025-03-07 08:30 | 2025-03-07 16:44 | 0.043686 | 8.8433e-05 | 3 | 1482 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1464 | SRT290 & SKE1797 | Temp Links Pole #43015 | Otaio | 2025-03-07 08:30 | 2025-03-07 08:38 | 0.014149 | 0.0017687 | 60 | 480 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1465 | SRT290 & SKE1797 | ABS W302-ABS W303 | Otaio | 2025-03-07 08:30 | 2025-03-07 15:56 | 0.19721 | 0.00044216 | 15 | 6690 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1466 | SRT290 & SKE1797 | Pole #43083 | Otaio | 2025-03-07 08:31 | 2025-03-07 16:12 | 0.027178 | 5.8955e-05 | 2 | 922 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1467 | SRT290 & SKE1797 | Pole #43082 | Otaio | 2025-03-07 08:31 | 2025-03-07 16:06 | 0.013412 | 2.9478e-05 | 1 | 455 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1468 | SRT290 & SKE1797 | Pole #43033 | Otaio | 2025-03-07 08:31 | 2025-03-07 16:07 | 0.040325 | 8.8433e-05 | 3 | 1368 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1469 | SRT290 & SKE1797 | TX A683 | Otaio | 2025-03-07 08:31 | 2025-03-07 16:26 | 0.014002 | 2.9478e-05 | 1 | 475 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1470 | SRT290 & SKE1797 | TX A895 | Otaio | 2025-03-07 08:31 | 2025-03-07 16:27 | 0.028063 | 5.8955e-05 | 2 | 952 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1471 | SRT290 & SKE1797 | TX A88 | Otaio | 2025-03-07 08:31 | 2025-03-07 16:24 | 0.041829 | 8.8433e-05 | 3 | 1419 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1472 | SRT290 & SKE1797 | TX A786 | Otaio | 2025-03-07 08:31 | 2025-03-07 16:22 | 0.013884 | 2.9478e-05 | 1 | 471 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1473 | SRT290 & SKE1797 | TX A1421 | Otaio | 2025-03-07 08:31 | 2025-03-07 16:20 | 0.013825 | 2.9478e-05 | 1 | 469 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1474 | SRT290 & SKE1797 | TX A87 | Otaio | 2025-03-07 08:31 | 2025-03-07 16:13 | 0.068093 | 0.00014739 | 5 | 2310 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1475 | SRT290 & SKE1797 | Links W348-pole #43083-Pole #43082-Pole #43033-TX A683-TX A895-TX A88-TX A786-TX A1421-TX A87-CB W465-CB W685-TX A628 | Otaio | 2025-03-07 08:31 | 2025-03-07 15:52 | 0.63698 | 0.0014444 | 49 | 21609 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1476 | SRT290 & SKE1797 | TX A628 | Otaio | 2025-03-07 08:31 | 2025-03-07 16:09 | 0.013501 | 2.9478e-05 | 1 | 458 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1477 | SRT290 & SKE1797 | Temp Links Pole #43015 | Otaio | 2025-03-07 16:40 | 2025-03-07 16:44 | 0.0070746 | 0.0017687 | 60 | 240 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1478 | GWM1257 | ABS T404 | Rangitata | 2025-03-10 09:00 | 2025-03-10 15:42 | 0.15405 | 0.00038321 | 13 | 5226 | Planned | Planned interruption | Tree Cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1479 | SRT286 | Temp Links at pole #29337 to end | Otaio | 2025-03-11 08:33 | 2025-03-11 08:37 | 0.00047164 | 0.00011791 | 4 | 16 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1480 | SRT286 | Temp Links at pole #43015 to pole #29337 minus TX A31 & TX A558 | Otaio | 2025-03-11 08:33 | 2025-03-11 15:35 | 0.6593 | 0.0015623 | 53 | 22366 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1481 | SRT286 | TX A31 to end | Otaio | 2025-03-11 08:33 | 2025-03-11 15:55 | 0.013029 | 2.9478e-05 | 1 | 442 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1482 | SRT286 | TX A558 to end | Otaio | 2025-03-11 08:33 | 2025-03-11 15:56 | 0.026117 | 5.8955e-05 | 2 | 886 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1483 | 5136 | TX D24 to end | Milford | 2025-03-11 18:38 | 2025-03-12 11:45 | 0.030274 | 2.9478e-05 | 1 | 1027 | Unplanned | Adverse weather | Broken Pole - Wind - Tree branch | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1484 | SRT287 | Temp links at pole #43015 to pole #29337 minus TX's A1424, A1119, A1205, A75, A1248, A1258, LV Fuses at pole #29482, Links W362 and Fuses W344 | Otaio | 2025-03-12 08:37 | 2025-03-12 15:05 | 0.35456 | 0.00091381 | 31 | 12028 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1485 | SRT287 | A1424 to end | Otaio | 2025-03-12 08:37 | 2025-03-12 15:23 | 0.011968 | 2.9478e-05 | 1 | 406 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1486 | SRT287 | A1119 to end | Otaio | 2025-03-12 08:37 | 2025-03-12 15:29 | 0.012145 | 2.9478e-05 | 1 | 412 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1487 | SRT287 | A1205 to end | Otaio | 2025-03-12 08:37 | 2025-03-12 15:32 | 0.012233 | 2.9478e-05 | 1 | 415 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1488 | SRT287 | A75 to end | Otaio | 2025-03-12 08:37 | 2025-03-12 15:24 | 0.059987 | 0.00014739 | 5 | 2035 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1489 | SRT287 | A1248 to end | Otaio | 2025-03-12 08:37 | 2025-03-12 15:22 | 0.011938 | 2.9478e-05 | 1 | 405 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1490 | SRT287 | A1258 to end | Otaio | 2025-03-12 08:37 | 2025-03-12 15:16 | 0.011762 | 2.9478e-05 | 1 | 399 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1491 | SRT287 | Fuses W362 to end | Otaio | 2025-03-12 08:37 | 2025-03-12 15:28 | 0.048461 | 0.00011791 | 4 | 1644 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1492 | SRT287 | Links W344 to end | Otaio | 2025-03-12 08:37 | 2025-03-12 15:26 | 0.10851 | 0.0002653 | 9 | 3681 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1493 | SRT287 | LV Fuses at pole #29482 | Otaio | 2025-03-12 08:37 | 2025-03-12 15:28 | 0.024231 | 5.8955e-05 | 2 | 822 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1494 | SRT287 | Temp Links at pole #29337 to end | Otaio | 2025-03-12 16:30 | 2025-03-12 16:33 | 0.00035373 | 0.00011791 | 4 | 12 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1495 | SRT289 | Fuses W340 to end | Otaio | 2025-03-13 08:30 | 2025-03-13 12:25 | 0.020782 | 8.8433e-05 | 3 | 705 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1496 | JDJ153 | TX D99 to end | Pleasant Point Township | 2025-03-14 09:06 | 2025-03-14 14:22 | 0.0093149 | 2.9478e-05 | 1 | 316 | Planned | Planned interruption | Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1497 | SKE1919 | TE1 Minus LB J146/2, LB J146/4, LB J20, Council M/S (= DB J22) | Arthur Street | 2025-03-16 07:00 | 2025-03-16 18:22 | 0.060311 | 8.8433e-05 | 3 | 2046 | Planned | Planned interruption | Sub Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1498 | SKE1919 | Council M/S | Arthur Street | 2025-03-16 07:00 | 2025-03-16 18:01 | 0.019485 | 2.9478e-05 | 1 | 661 | Planned | Planned interruption | Sub Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1499 | SKE1919 | New LB H362/25 (= DB J98 - Old TE2 CCT22) | Arthur Street | 2025-03-16 07:00 | 2025-03-16 18:50 | 0.18836 | 0.0002653 | 9 | 6390 | Planned | Planned interruption | Sub Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1500 | SKE1919 | New LB H362/22 (= Telecom Exchange - Old TE2 CCT23) | Arthur Street | 2025-03-16 07:00 | 2025-03-16 18:59 | 0.042389 | 5.8955e-05 | 2 | 1438 | Planned | Planned interruption | Sub Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1501 | SKE1919 | New LB H363/33 (St Mary's Church - Old TE2 CCT12) | Arthur Street | 2025-03-16 07:00 | 2025-03-16 19:03 | 0.021312 | 2.9478e-05 | 1 | 723 | Planned | Planned interruption | Sub Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1502 | SKE1919 | TE202 CCT15 (DB J147 - Old TE2 CCT11 - Museum) | Arthur Street | 2025-03-16 07:00 | 2025-03-16 19:14 | 0.021637 | 2.9478e-05 | 1 | 734 | Planned | Planned interruption | Sub Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1503 | JDJ157 | CB W470 - ABS W337 | St Andrews | 2025-03-17 08:30 | 2025-03-17 08:33 | 0.0041563 | 0.0013854 | 47 | 141 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1504 | JDJ157 | ABS W337 | St Andrews | 2025-03-17 08:30 | 2025-03-17 16:42 | 1.9579 | 0.0039795 | 135 | 66420 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1505 | JDJ157 | Links L294 - CB W470 | St Andrews | 2025-03-17 08:40 | 2025-03-17 08:41 | 2.9478e-05 | 2.9478e-05 | 1 | 1 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1506 | JDJ157 | Links @ P#40903 - Links L294 | St Andrews | 2025-03-17 08:45 | 2025-03-17 16:23 | 0.10801 | 0.00023582 | 8 | 3664 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1507 | JDJ157 | Links @ P#40903 - Links L294 | St Andrews | 2025-03-17 08:45 | 2025-03-17 16:56 | 0.014474 | 2.9478e-05 | 1 | 491 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1508 | 5029 | Tx B1981 | Normanby | 2025-03-17 10:57 | 2025-03-17 10:59 | 5.8955e-05 | 2.9478e-05 | 1 | 2 | Planned | Planned interruption | Tap Change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1509 | 5032 | TE172 CCT18-LB S47-DB S48-DB S49-DB S50 | Hobbs Street | 2025-03-17 15:28 | 2025-03-18 14:53 | 0.16566 | 0.00011791 | 4 | 5620 | Unplanned | Defective equipment | DB S47 replacement due to fire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1510 | 5032 | LB S47 | Hobbs Street | 2025-03-17 15:28 | 2025-03-18 15:10 | 0.083834 | 5.8955e-05 | 2 | 2844 | Unplanned | Defective equipment | DB S47 replacement due to fire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1511 | 5032 | DB S48 | Hobbs Street | 2025-03-17 15:28 | 2025-03-18 15:25 | 0.084719 | 5.8955e-05 | 2 | 2874 | Unplanned | Defective equipment | DB S47 replacement due to fire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1512 | 5032 | DB S49 | Hobbs Street | 2025-03-17 15:28 | 2025-03-18 15:28 | 0.084896 | 5.8955e-05 | 2 | 2880 | Unplanned | Defective equipment | DB S47 replacement due to fire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1513 | 5032 | DB S50 | Hobbs Street | 2025-03-17 15:28 | 2025-03-18 15:41 | 0.47114 | 0.00032425 | 11 | 15983 | Unplanned | Defective equipment | DB S47 replacement due to fire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1514 | JDJ157 | Links L294 - CB W470 | St Andrews | 2025-03-17 16:34 | 2025-03-17 16:40 | 0.00017687 | 2.9478e-05 | 1 | 6 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1515 | JDJ157 | CB W470 - ABS W337 | St Andrews | 2025-03-17 16:35 | 2025-03-17 16:42 | 0.0096981 | 0.0013854 | 47 | 329 | Planned | Planned interruption | OH Refurbishment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1516 | 5078 | PLPTCB2 to L234 | Sutherland | 2025-03-18 03:34 | 2025-03-18 04:17 | 0.0012675 | 2.9478e-05 | 1 | 43 | Unplanned | Vegetation | Gum Tree Branch on Line at Pole #26364 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1517 | 5078 | From L234 | Sutherland | 2025-03-18 03:34 | 2025-03-18 04:42 | 0.19443 | 0.0028593 | 97 | 6596 | Unplanned | Vegetation | Gum Tree Branch on Line at Pole #26364 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1518 | 5078 | From L1239 | Sutherland | 2025-03-18 03:34 | 2025-03-18 05:19 | 0.083569 | 0.0007959 | 27 | 2835 | Unplanned | Vegetation | Gum Tree Branch on Line at Pole #26364 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1519 | 5078 | PLPTCB2 to L234 | Sutherland | 2025-03-18 04:39 | 2025-03-18 04:42 | 8.8433e-05 | 2.9478e-05 | 1 | 3 | Unplanned | Vegetation | Gum Tree Branch on Line at Pole #26364 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1520 | SKE1929 | ABS L722 to end | Highfield | 2025-03-18 09:00 | 2025-03-19 14:41 | 0.6825 | 0.00038321 | 13 | 23153 | Planned | Planned interruption | Replace ABS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1521 | SRT288 | Pole #29337 to end | Otaio | 2025-03-19 08:30 | 2025-03-19 08:36 | 0.00070746 | 0.00011791 | 4 | 24 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1522 | SRT288 | Pole #43015 - Pole #29337 - Fuses TOA84 | Otaio | 2025-03-19 08:30 | 2025-03-19 15:52 | 0.7166 | 0.0016213 | 55 | 24310 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1523 | SRT288 | Fuses TOA84 | Otaio | 2025-03-19 08:30 | 2025-03-19 16:08 | 0.013501 | 2.9478e-05 | 1 | 458 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1524 | HTR108/5031 | From G112 | Winchester | 2025-03-19 09:00 | 2025-03-19 09:34 | 0.024054 | 0.00070746 | 24 | 816 | Unplanned | Human error | Switching error - Paperwork had been redated but faultman had incorrect dated switching. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1525 | SRT288 | Pole #29337 to end | Otaio | 2025-03-19 16:30 | 2025-03-19 16:32 | 0.00023582 | 0.00011791 | 4 | 8 | Planned | Planned interruption | Makikihi Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1526 | 5079 | Fuses TO D1043 | Waitohi | 2025-03-19 17:26 | 2025-03-19 21:19 | 0.013737 | 5.8955e-05 | 2 | 466 | Unplanned | Defective equipment | Faulty Transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1527 | ACD189 | ABS W324 - ABS W457 | St Andrews | 2025-03-21 09:00 | 2025-03-21 11:27 | 0.064998 | 0.00044216 | 15 | 2205 | Planned | Planned interruption | Replace Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1528 | ACD188 | CB W664 - ABS W263 - ABS W577 + Tx A191 | Waihaorunga | 2025-03-21 09:01 | 2025-03-21 13:49 | 0.38203 | 0.0013265 | 45 | 12960 | Planned | Planned interruption | New Line to Tx A1631 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1529 | ACD188 | TO A192 | Waihaorunga | 2025-03-21 09:01 | 2025-03-21 13:59 | 0.043922 | 0.00014739 | 5 | 1490 | Planned | Planned interruption | New Line to Tx A1631 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1530 | 5080 | G251 - G204 | Speechley | 2025-03-23 00:23 | 2025-03-23 02:37 | 0.21725 | 0.0016213 | 55 | 7370 | Unplanned | Third party interference | Car v Pole #09898 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1531 | 5080 | G204 | Speechley | 2025-03-23 00:23 | 2025-03-23 07:11 | 1.0463 | 0.0025646 | 87 | 35496 | Unplanned | Third party interference | Car v Pole #09898 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1532 | SRS059 | From TO D1404 - LG006 - D1404-04 | Geraldine Township | 2025-03-25 08:30 | 2025-03-25 17:18 | 0.077821 | 0.00014739 | 5 | 2640 | Planned | Planned interruption | Install new RMU G362 G363 G364 & TX D2148 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1533 | GWM1267 | From TO D1260 | Milford | 2025-03-26 09:00 | 2025-03-26 09:51 | 0.0030067 | 5.8955e-05 | 2 | 102 | Planned | Planned interruption | Tree Trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1534 | SRT301 | From Temp Links @ Pole #35566 | Waipopo | 2025-03-26 09:01 | 2025-03-26 15:59 | 0.036965 | 8.8433e-05 | 3 | 1254 | Planned | Planned interruption | Install new LBS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1535 | SRT299 | Tx B2296 CCT 03 - Highlighted ICPs | Grants Road | 2025-03-27 08:00 | 2025-03-27 17:30 | 0.38645 | 0.00067799 | 23 | 13110 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1536 | SRT299 | Tx B2296 CCT 02 - Highlighted ICPs | Grants Road | 2025-03-27 08:00 | 2025-03-27 17:36 | 0.35656 | 0.00061903 | 21 | 12096 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1537 | SRT299 | 6 Andrew St | Grants Road | 2025-03-27 08:00 | 2025-03-27 17:53 | 0.01748 | 2.9478e-05 | 1 | 593 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1538 | SRT299 | 21 Bouverie St | Grants Road | 2025-03-27 08:00 | 2025-03-27 17:44 | 0.017215 | 2.9478e-05 | 1 | 584 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1539 | SRT299 | 31 Bouverie St | Grants Road | 2025-03-27 08:00 | 2025-03-27 17:46 | 0.017274 | 2.9478e-05 | 1 | 586 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1540 | SRT299 | 20 & 22 Bouverie St | Grants Road | 2025-03-27 08:00 | 2025-03-27 17:45 | 0.034489 | 5.8955e-05 | 2 | 1170 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1541 | SRT299 | 3 Andrew St + 23, 24 & 33 Bouverie St | Grants Road | 2025-03-27 08:00 | 2025-03-27 17:48 | 0.069331 | 0.00011791 | 4 | 2352 | Planned | Planned interruption | Line Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1542 | SRS042 | TO A841 - DB3255 ICP1 - DB3255 ICP2 | Waihaorunga | 2025-03-27 09:00 | 2025-03-27 13:44 | 0.42695 | 0.0015034 | 51 | 14484 | Planned | Planned interruption | Replace DB3255 & maintain DB3256, DB3257 & DB3254 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1543 | SRS042 | DB3255 ICP1 + DB3255 ICP2 | Waihaorunga | 2025-03-27 09:00 | 2025-03-27 14:05 | 0.017981 | 5.8955e-05 | 2 | 610 | Planned | Planned interruption | Replace DB3255 & maintain DB3256, DB3257 & DB3254 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1544 | 5033 | TX A86 | Otaio | 2025-03-28 13:15 | 2025-03-28 13:18 | 8.8433e-05 | 2.9478e-05 | 1 | 3 | Unplanned | Defective equipment | TX Tap change for voltage | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1545 | 3799 | T626 - T775(T490) | Rolleston Road | 2025-03-29 20:47 | 2025-03-29 20:55 | 0.009197 | 0.0011496 | 39 | 312 | Unplanned | Unknown | Possible line clash past ABS T675 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1546 | 3799 | T775(T490) | Rolleston Road | 2025-03-29 20:47 | 2025-03-29 22:01 | 0.32284 | 0.0043627 | 148 | 10952 | Unplanned | Unknown | Possible line clash past ABS T675 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1547 | 3800 | T675 | Rolleston Road | 2025-03-30 10:47 | 2025-03-30 12:20 | 0.013707 | 0.00014739 | 5 | 465 | Unplanned | Defective equipment | Conductor repair @ P#488723 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1548 | JJV153 | E148-03 (Motor Camp) | Lakeside Drive | 2025-03-31 07:26 | 2025-03-31 07:45 | 0.00056008 | 2.9478e-05 | 1 | 19 | Planned | Planned interruption | Replace RMU (M146, M147) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1549 | JJV153 | E148-04 (Caravan Points) | Lakeside Drive | 2025-03-31 07:26 | 2025-03-31 07:45 | 0.00056008 | 2.9478e-05 | 1 | 19 | Planned | Planned interruption | Replace RMU (M146, M147) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1550 | JJV153 | E148-02 (Boat Club) | Lakeside Drive | 2025-03-31 07:58 | 2025-03-31 16:16 | 0.01468 | 2.9478e-05 | 1 | 498 | Planned | Planned interruption | Replace RMU (M146, M147) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1551 | JJV153 | E148-05 (Toilets) | Lakeside Drive | 2025-03-31 07:58 | 2025-03-31 16:16 | 0.01468 | 2.9478e-05 | 1 | 498 | Planned | Planned interruption | Replace RMU (M146, M147) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1552 | JJV153 | E262 '01' (Ice Rink) | Lakeside Drive | 2025-03-31 07:58 | 2025-03-31 16:15 | 0.01465 | 2.9478e-05 | 1 | 497 | Planned | Planned interruption | Replace RMU (M146, M147) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1553 | HTR104 | ABS L803 - ABS L806 | Hadlow | 2025-03-31 08:56 | 2025-03-31 13:40 | 1.2725 | 0.0044806 | 152 | 43168 | Planned | Planned interruption | Tree Cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1554 | HTR105 | ABS L175 | Normanby | 2025-03-31 13:00 | 2025-03-31 15:29 | 0.043922 | 0.00029478 | 10 | 1490 | Planned | Planned interruption | Tree Cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1555 | JJV153 | E148-03 (Motor Camp) | Lakeside Drive | 2025-03-31 16:18 | 2025-03-31 16:38 | 0.00058955 | 2.9478e-05 | 1 | 20 | Planned | Planned interruption | Replace RMU (M146, M147) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1556 | JJV153 | E148-04 (Caravan Points) | Lakeside Drive | 2025-03-31 16:18 | 2025-03-31 16:38 | 0.00058955 | 2.9478e-05 | 1 | 20 | Planned | Planned interruption | Replace RMU (M146, M147) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1557 | 5129 | CB W196 to W171 | Morven | 2024-10-09 16:32 | 2024-10-09 17:38 | 0.07393 | 0.0011202 | 38 | 2508 | Unplanned | Vegetation | Trees on line past W171 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1558 | 5129 | W171 to end | Morven | 2024-10-09 16:32 | 2024-10-09 20:24 | 0.054711 | 0.00023582 | 8 | 1856 | Unplanned | Vegetation | Trees on line past W171 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1559 | 3827 | G297 to end | Winchester | 2024-12-09 05:02 | 2024-12-09 05:56 | 0.54439 | 0.010081 | 342 | 18468 | Unplanned | Vegetation | Branch on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1560 | 4401 | M272 closed | M159 | 2024-04-15 18:35 | 2024-04-15 22:06 | 0.42917 | 0.002034 | 69 | 14559 | Unplanned | Unknown | Unknown - possible bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1561 | 4401 | M272 closed | M158 | 2024-04-15 18:35 | 2024-04-15 22:06 | 0.10574 | 0.00050112 | 17 | 3587 | Unplanned | Unknown | Unknown - possible bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1562 | 5040 | M272 + M158 + M159 | M159 | 2024-05-09 11:08 | 2024-05-09 12:00 | 0.10577 | 0.002034 | 69 | 3588 | Unplanned | Defective equipment | Repair conductor @ P#21659 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1563 | 5040 | M272 + M158 + M159 | M158 | 2024-05-09 11:08 | 2024-05-09 12:00 | 0.026058 | 0.00050112 | 17 | 884 | Unplanned | Defective equipment | Repair conductor @ P#21659 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1564 | ACD153 | RMU M364 MS | M158 | 2024-06-26 09:07 | 2024-06-26 16:11 | 0.19998 | 0.00047164 | 16 | 6784 | Planned | Planned interruption | Red Tag Pole replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Alpine Energy | 2025 |  | 1565 | ACD153 | RMU M363 MS | M159 | 2024-06-26 09:07 | 2024-06-26 16:11 | 0.8749 | 0.0020634 | 70 | 29680 | Planned | Planned interruption | Red Tag Pole replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 9 | 16094 | East Taieri | ET5 | 2024-04-02 09:06 | 2024-04-02 13:24 | 0.064367 | 0.00024949 | 24 | 6192 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 10 | 16089 | Port Chalmers | PC7 | 2024-04-02 09:57 | 2024-04-02 15:55 | 0.044658 | 0.00012474 | 12 | 4296 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 11 | 16088 | Port Chalmers | PC7 | 2024-04-02 09:57 | 2024-04-02 15:52 | 0.33951 | 0.00095636 | 92 | 32660 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 12 | 16098 | Omakau | CB656 | 2024-04-03 00:05 | 2024-04-03 02:41 | 0.15146 | 0.00097715 | 94 | 14570 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 13 | 16105 | Wanaka | CB2754 | 2024-04-03 08:04 | 2024-04-03 17:01 | 0.0055822 | 1.0395e-05 | 1 | 537 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 14 | 16106 | Wanaka | CB2754 | 2024-04-03 08:04 | 2024-04-03 17:01 | 0.0055822 | 1.0395e-05 | 1 | 537 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 15 | 16107 | Wanaka | CB2754 | 2024-04-03 08:04 | 2024-04-03 17:01 | 0.0055822 | 1.0395e-05 | 1 | 537 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 16 | 16103 | Wanaka | CB2754 | 2024-04-03 08:04 | 2024-04-03 16:33 | 0.418 | 0.00082122 | 79 | 40211 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 17 | 16090 | East Taieri | ET9 | 2024-04-03 08:38 | 2024-04-03 08:39 | 0.00056134 | 0.00056134 | 54 | 54 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 18 | 16101 | Camp Hill | CB2008 | 2024-04-03 09:59 | 2024-04-03 10:48 | 0.1742 | 0.0035552 | 342 | 16758 | Unplanned | Defective Equipment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 19 | 16092 | East Taieri | ET9 | 2024-04-03 16:03 | 2024-04-03 16:06 | 0.001684 | 0.00056134 | 54 | 162 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 20 | 16129 | Cromwell | CB822 | 2024-04-03 21:35 | 2024-04-03 23:38 | 0.0012786 | 1.0395e-05 | 1 | 123 | Unplanned | Wildlife | animal in equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 21 | 16128 | Queenstown | CB5242 | 2024-04-03 23:35 | 2024-04-04 05:25 | 0.0072767 | 2.079e-05 | 2 | 700 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 22 | 16243 | Cromwell | CB832 | 2024-04-04 08:14 | 2024-04-04 09:08 | 0.0011227 | 2.079e-05 | 2 | 108 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 23 | 16242 | Cromwell | CB832 | 2024-04-04 08:30 | 2024-04-04 16:37 | 3.8019 | 0.0078068 | 751 | 365737 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 24 | 16244 | Cromwell | CB832 | 2024-04-04 08:30 | 2024-04-04 16:37 | 0.0050625 | 1.0395e-05 | 1 | 487 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 25 | 16241 | Cromwell | CB832 | 2024-04-04 08:35 | 2024-04-04 16:24 | 2.1842 | 0.0046571 | 448 | 210112 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 26 | 16121 | Corstorphine | CO2 | 2024-04-04 09:11 | 2024-04-04 13:18 | 0.64447 | 0.0026092 | 251 | 61997 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 27 | 16120 | Cromwell | CB832 | 2024-04-04 09:24 | 2024-04-04 16:28 | 0.0044076 | 1.0395e-05 | 1 | 424 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 28 | 16124 | Frankton | CB7782 | 2024-04-04 10:02 | 2024-04-04 12:14 | 0.0068608 | 5.1976e-05 | 5 | 660 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 29 | 16122 | Frankton | CB7782 | 2024-04-04 10:02 | 2024-04-04 10:07 | 0.0019751 | 0.00039502 | 38 | 190 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 30 | 16123 | Frankton | CB7782 | 2024-04-04 10:02 | 2024-04-04 12:07 | 0.051976 | 0.00041581 | 40 | 5000 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 31 | 16126 | Frankton | CB7782 | 2024-04-04 12:02 | 2024-04-04 12:07 | 0.0019751 | 0.00039502 | 38 | 190 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 32 | 16245 | Cromwell | CB832 | 2024-04-04 17:45 | 2024-04-04 17:57 | 0.00024949 | 2.079e-05 | 2 | 24 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 33 | 16138 | Frankton | CB7782 | 2024-04-05 09:04 | 2024-04-05 13:51 | 0.25657 | 0.00089399 | 86 | 24682 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 34 | 16139 | Frankton | CB7782 | 2024-04-05 09:04 | 2024-04-05 13:51 | 0.0029834 | 1.0395e-05 | 1 | 287 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 35 | 16137 | Frankton | CB7782 | 2024-04-05 09:08 | 2024-04-05 13:22 | 0.0052808 | 2.079e-05 | 2 | 508 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 36 | 16136 | Frankton | CB7782 | 2024-04-05 09:08 | 2024-04-05 13:22 | 0.055448 | 0.0002183 | 21 | 5334 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 37 | 16176 | Cromwell | CB831 | 2024-04-08 09:07 | 2024-04-08 16:17 | 0.2235 | 0.00051976 | 50 | 21500 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 38 | 16185 | East Taieri | ET5 | 2024-04-08 09:45 | 2024-04-08 11:13 | 0.0027443 | 3.1186e-05 | 3 | 264 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 39 | 16187 | Queenstown | CB5252 | 2024-04-08 22:06 | 2024-04-09 04:47 | 0.11255 | 0.00028067 | 27 | 10827 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 40 | 16186 | Queenstown | CB5252 | 2024-04-08 22:06 | 2024-04-09 04:47 | 0.21259 | 0.00053016 | 51 | 20451 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 41 | 16257 | St. Kilda | SK4 | 2024-04-09 07:37 | 2024-04-09 08:08 | 0.00032225 | 1.0395e-05 | 1 | 31 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 42 | 16189 | Alexandra | CB168 | 2024-04-09 08:06 | 2024-04-09 15:37 | 0.10783 | 0.00023909 | 23 | 10373 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 43 | 16188 | Alexandra | CB168 | 2024-04-09 08:06 | 2024-04-09 15:37 | 0.26723 | 0.00059253 | 57 | 25707 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 44 | 16177 | Cromwell | CB831 | 2024-04-09 09:03 | 2024-04-09 13:52 | 0.99139 | 0.0034304 | 330 | 95370 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 45 | 16180 | South City | SC9 | 2024-04-09 09:08 | 2024-04-09 16:01 | 0.53665 | 0.0012994 | 125 | 51625 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 46 | 16179 | Frankton | CB7782 | 2024-04-09 09:35 | 2024-04-09 13:23 | 0.068733 | 0.00030146 | 29 | 6612 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 47 | 16230 | Alexandra | CB167 | 2024-04-09 23:02 | 2024-04-10 00:34 | 0.39115 | 0.0042516 | 409 | 37628 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 48 | 16228 | Cromwell | CB832 | 2024-04-10 08:36 | 2024-04-10 16:42 | 0.55068 | 0.0011331 | 109 | 52974 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 49 | 16227 | Cromwell | CB832 | 2024-04-10 08:36 | 2024-04-10 16:35 | 0.86142 | 0.0017984 | 173 | 82867 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 50 | 16675 | Cromwell | CB832 | 2024-04-10 08:36 | 2024-04-10 16:42 | 0.0050521 | 1.0395e-05 | 1 | 486 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 51 | 16247 | Frankton | CB7790 | 2024-04-10 08:59 | 2024-04-10 16:17 | 0.05919 | 0.00013514 | 13 | 5694 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 52 | 16246 | Frankton | CB7790 | 2024-04-10 08:59 | 2024-04-10 16:17 | 1.4024 | 0.0032017 | 308 | 134904 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 53 | 16249 | East Taieri | ET3 | 2024-04-10 09:25 | 2024-04-10 16:28 | 0.0087944 | 2.079e-05 | 2 | 846 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 54 | 16234 | Queenstown | CB5292 | 2024-04-10 09:27 | 2024-04-10 11:01 | 0.00096676 | 1.0395e-05 | 1 | 93 | Unplanned | Third-party Interference | machinery contact | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 55 | 16235 | Queenstown | CB5292 | 2024-04-10 09:27 | 2024-04-10 11:26 | 0.099358 | 0.00084201 | 81 | 9558 | Unplanned | Third-party Interference | machinery contact | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 56 | 16236 | Queenstown | CB5242 | 2024-04-10 09:35 | 2024-04-10 10:01 | 0.086218 | 0.0033161 | 319 | 8294 | Unplanned | Third-party Interference | machinery contact | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 57 | 16231 | Arrowtown | CB7652 | 2024-04-10 10:06 | 2024-04-10 12:51 | 0.030874 | 0.00018711 | 18 | 2970 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 58 | 16253 | Fernhill | CB5310 | 2024-04-10 11:10 | 2024-04-10 11:30 | 0.27547 | 0.013774 | 1325 | 26500 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 59 | 16254 | Fernhill | CB5309 | 2024-04-10 11:10 | 2024-04-10 11:30 | 0.08732 | 0.004366 | 420 | 8400 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 60 | 16232 | Omakau | CB656 | 2024-04-10 11:54 | 2024-04-10 16:17 | 0.035541 | 0.00013514 | 13 | 3419 | Unplanned | Defective Equipment | pole replacement - unplanned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 61 | 16248 | St. Kilda | SK10 | 2024-04-11 08:33 | 2024-04-11 14:12 | 0.66603 | 0.0019647 | 189 | 64071 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 62 | 16250 | Mosgiel | MG6 | 2024-04-11 11:33 | 2024-04-11 12:56 | 0.0017256 | 2.079e-05 | 2 | 166 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 63 | 16277 | Fernhill | CB5310 | 2024-04-11 18:41 | 2024-04-11 22:14 | 0.0022038 | 1.0395e-05 | 1 | 212 | Unplanned | Human Error | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 64 | 16274 | Fernhill | CB5310 | 2024-04-11 18:41 | 2024-04-11 19:57 | 0.061623 | 0.00081083 | 78 | 5928 | Unplanned | Human Error | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 65 | 16278 | Fernhill | CB5310 | 2024-04-11 18:41 | 2024-04-11 23:39 | 0.43059 | 0.0014449 | 139 | 41422 | Unplanned | Human Error | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 66 | 16276 | Fernhill | CB5310 | 2024-04-11 18:41 | 2024-04-11 22:08 | 0.63048 | 0.0030458 | 293 | 60651 | Unplanned | Human Error | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 67 | 16275 | Fernhill | CB5310 | 2024-04-11 18:41 | 2024-04-11 20:48 | 1.0746 | 0.0084617 | 814 | 103378 | Unplanned | Human Error | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 68 | 16256 | Camp Hill | CB2006 | 2024-04-11 19:22 | 2024-04-11 21:33 | 0.16757 | 0.001289 | 124 | 16120 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 69 | 16279 | Queensberry | CB2423 | 2024-04-11 20:10 | 2024-04-11 23:37 | 0.83921 | 0.0040541 | 390 | 80730 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 70 | 16270 | Fernhill | CB5309 | 2024-04-11 20:57 | 2024-04-11 21:22 | 0.041415 | 0.0017256 | 166 | 3984 | Unplanned | Human Error | operator error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 71 | 16271 | Fernhill | CB5309 | 2024-04-11 20:57 | 2024-04-11 21:22 | 0.21492 | 0.0085969 | 827 | 20675 | Unplanned | Human Error | operator error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 72 | 16273 | Fernhill | CB5310 | 2024-04-11 21:24 | 2024-04-11 21:50 | 0.021082 | 0.00081083 | 78 | 2028 | Unplanned | Human Error | operator error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 73 | 16272 | Fernhill | CB5309 | 2024-04-11 21:24 | 2024-04-11 21:43 | 0.16334 | 0.0085969 | 827 | 15713 | Unplanned | Human Error | operator error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 74 | 16280 | Camp Hill | CB2006 | 2024-04-12 00:46 | 2024-04-12 01:01 | 0.019335 | 0.001289 | 124 | 1860 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 75 | 16281 | Camp Hill | CB2006 | 2024-04-12 01:03 | 2024-04-12 02:40 | 0.016133 | 0.00016632 | 16 | 1552 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 76 | 16282 | Camp Hill | CB2006 | 2024-04-12 01:03 | 2024-04-12 10:42 | 0.64891 | 0.0011227 | 108 | 62424 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 77 | 16284 | Camp Hill | CB2006 | 2024-04-12 02:40 | 2024-04-12 10:42 | 0.02 | 4.1581e-05 | 4 | 1924 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 78 | 16283 | Camp Hill | CB2006 | 2024-04-12 02:40 | 2024-04-12 03:13 | 0.0041165 | 0.00012474 | 12 | 396 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 79 | 16285 | Camp Hill | CB2006 | 2024-04-12 03:13 | 2024-04-12 10:42 | 0.055885 | 0.00012474 | 12 | 5376 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 80 | 16513 | East Taieri | ET5 | 2024-04-12 07:35 | 2024-04-12 13:40 | 0.011383 | 3.1186e-05 | 3 | 1095 | Unplanned | Defective Equipment | overload | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 81 | 16288 | Ettrick | CB480 | 2024-04-12 08:11 | 2024-04-12 17:45 | 0.0059669 | 1.0395e-05 | 1 | 574 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 82 | 16289 | Ettrick | CB480 | 2024-04-12 08:13 | 2024-04-12 17:45 | 0.02973 | 5.1976e-05 | 5 | 2860 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 83 | 16514 | Alexandra | CB168 | 2024-04-12 08:25 | 2024-04-12 13:07 | 0.023452 | 8.3162e-05 | 8 | 2256 | Unplanned | Defective Equipment | faulty lightning arrestor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 84 | 16296 | Clyde-Earnscleugh | CB192 | 2024-04-15 09:02 | 2024-04-15 10:57 | 0.068141 | 0.00059253 | 57 | 6555 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 85 | 16294 | Cromwell | CB832 | 2024-04-15 09:03 | 2024-04-15 11:24 | 0.080615 | 0.00057174 | 55 | 7755 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 86 | 16307 | St. Kilda | SK7 | 2024-04-15 09:07 | 2024-04-15 16:08 | 0.15755 | 0.00037423 | 36 | 15156 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 87 | 16303 | Frankton | CB7782 | 2024-04-15 09:08 | 2024-04-15 11:43 | 0.030614 | 0.00019751 | 19 | 2945 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 88 | 16304 | St. Kilda | SK6 | 2024-04-15 09:27 | 2024-04-15 09:30 | 0.0029626 | 0.00098755 | 95 | 285 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 89 | 16625 | Mosgiel | MG5 | 2024-04-15 11:04 | 2024-04-15 11:18 | 0.00014553 | 1.0395e-05 | 1 | 14 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 90 | 16305 | St. Kilda | SK6 | 2024-04-15 15:52 | 2024-04-15 16:00 | 0.0079004 | 0.00098755 | 95 | 760 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 91 | 16325 | Frankton | CB7782 | 2024-04-16 08:33 | 2024-04-16 15:47 | 0.0045115 | 1.0395e-05 | 1 | 434 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 92 | 16324 | Frankton | CB7782 | 2024-04-16 08:33 | 2024-04-16 15:38 | 0.013254 | 3.1186e-05 | 3 | 1275 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 93 | 16328 | Frankton | CB7782 | 2024-04-16 08:33 | 2024-04-16 15:47 | 0.076696 | 0.00017672 | 17 | 7378 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 94 | 16327 | Frankton | CB7782 | 2024-04-16 08:33 | 2024-04-16 15:47 | 0.085719 | 0.00019751 | 19 | 8246 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 95 | 16323 | Frankton | CB7782 | 2024-04-16 08:33 | 2024-04-16 08:44 | 0.0043452 | 0.00039502 | 38 | 418 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 96 | 16329 | Frankton | CB7782 | 2024-04-16 08:33 | 2024-04-16 15:47 | 0.0045115 | 1.0395e-05 | 1 | 434 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 97 | 16301 | Wanaka | CB2754 | 2024-04-16 08:59 | 2024-04-16 15:57 | 0.0043452 | 1.0395e-05 | 1 | 418 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 98 | 16306 | Alexandra | CB168 | 2024-04-16 09:01 | 2024-04-16 12:28 | 0.02367 | 0.00011435 | 11 | 2277 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 99 | 16295 | St. Kilda | SK3 | 2024-04-16 09:04 | 2024-04-16 14:42 | 0.3092 | 0.00091478 | 88 | 29744 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 100 | 16298 | Halfway Bush | HB10 | 2024-04-16 09:04 | 2024-04-16 15:24 | 0.25676 | 0.00067569 | 65 | 24700 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 101 | 16299 | Wanaka | CB2754 | 2024-04-16 09:12 | 2024-04-16 15:56 | 0.054596 | 0.00013514 | 13 | 5252 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 102 | 16332 | Frankton | CB7782 | 2024-04-16 09:17 | 2024-04-16 16:33 | 0.0045323 | 1.0395e-05 | 1 | 436 | Planned | Planned interruption | line upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 103 | 16331 | Frankton | CB7782 | 2024-04-16 09:29 | 2024-04-16 16:50 | 0.013753 | 3.1186e-05 | 3 | 1323 | Planned | Planned interruption | line upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 104 | 16330 | Frankton | CB7782 | 2024-04-16 09:29 | 2024-04-16 16:46 | 0.15445 | 0.00035344 | 34 | 14858 | Planned | Planned interruption | line upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 105 | 16326 | Frankton | CB7782 | 2024-04-16 15:33 | 2024-04-16 15:38 | 0.0019751 | 0.00039502 | 38 | 190 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 106 | 16355 | Frankton | CB7783 | 2024-04-17 08:40 | 2024-04-17 08:48 | 0.0031601 | 0.00039502 | 38 | 304 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 107 | 16356 | Frankton | CB7783 | 2024-04-17 08:40 | 2024-04-17 08:49 | 0.0095428 | 0.0010603 | 102 | 918 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 108 | 16357 | Frankton | CB7783 | 2024-04-17 08:40 | 2024-04-17 16:59 | 0.63803 | 0.0012786 | 123 | 61377 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 109 | 16506 | Dalefield | CB7828 | 2024-04-17 09:01 | 2024-04-17 15:18 | 0.003919 | 1.0395e-05 | 1 | 377 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 110 | 16505 | Dalefield | CB7828 | 2024-04-17 09:01 | 2024-04-17 15:18 | 0.14108 | 0.00037423 | 36 | 13572 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 111 | 16341 | East Taieri | ET9 | 2024-04-17 13:53 | 2024-04-17 13:55 | 0.00047818 | 0.00023909 | 23 | 46 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 112 | 16342 | East Taieri | ET9 | 2024-04-17 13:56 | 2024-04-17 13:57 | 0.00023909 | 0.00023909 | 23 | 23 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 113 | 16343 | East Taieri | ET9 | 2024-04-17 14:31 | 2024-04-17 14:33 | 0.00047818 | 0.00023909 | 23 | 46 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 114 | 16358 | Frankton | CB7783 | 2024-04-17 16:51 | 2024-04-17 16:59 | 0.0084825 | 0.0010603 | 102 | 816 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 115 | 16359 | Frankton | CB7783 | 2024-04-17 16:54 | 2024-04-17 16:59 | 0.0019751 | 0.00039502 | 38 | 190 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 116 | 16361 | Frankton | CB7782 | 2024-04-18 08:03 | 2024-04-18 15:04 | 0.16193 | 0.00038462 | 37 | 15577 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 117 | 16362 | Frankton | CB7782 | 2024-04-18 08:03 | 2024-04-18 15:04 | 0.21007 | 0.00049897 | 48 | 20208 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 118 | 16363 | Frankton | CB7782 | 2024-04-18 08:03 | 2024-04-18 15:04 | 0.47703 | 0.0011331 | 109 | 45889 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 119 | 16366 | Frankton | CB7782 | 2024-04-18 08:03 | 2024-04-18 15:04 | 0.0043764 | 1.0395e-05 | 1 | 421 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 120 | 16365 | Frankton | CB7782 | 2024-04-18 08:07 | 2024-04-18 15:10 | 0.0087944 | 2.079e-05 | 2 | 846 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 121 | 16364 | Frankton | CB7782 | 2024-04-18 08:07 | 2024-04-18 15:10 | 0.013192 | 3.1186e-05 | 3 | 1269 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 122 | 16360 | Frankton | CB7782 | 2024-04-18 08:07 | 2024-04-18 14:54 | 0.029616 | 7.2767e-05 | 7 | 2849 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 123 | 16348 | St. Kilda | SK4 | 2024-04-18 09:02 | 2024-04-18 16:03 | 0.58644 | 0.001393 | 134 | 56414 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 124 | 16347 | St. Kilda | SK4 | 2024-04-18 09:02 | 2024-04-18 09:18 | 0.02262 | 0.0014138 | 136 | 2176 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 125 | 16349 | St. Kilda | SK4 | 2024-04-18 15:46 | 2024-04-18 16:03 | 0.024034 | 0.0014138 | 136 | 2312 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 126 | 16397 | Remarkables | CB710 | 2024-04-19 08:38 | 2024-04-19 08:47 | 9.3557e-05 | 1.0395e-05 | 1 | 9 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 127 | 16387 | Green Island | GI12 | 2024-04-19 08:53 | 2024-04-19 15:58 | 0.088359 | 0.0002079 | 20 | 8500 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 128 | 16388 | Green Island | GI12 | 2024-04-19 08:53 | 2024-04-19 15:58 | 0.19439 | 0.00045739 | 44 | 18700 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 129 | 16389 | Green Island | GI12 | 2024-04-19 09:05 | 2024-04-19 15:58 | 0.20607 | 0.00049897 | 48 | 19824 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 130 | 16390 | Green Island | GI12 | 2024-04-19 09:07 | 2024-04-19 15:58 | 0.072631 | 0.00017672 | 17 | 6987 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 131 | 16391 | Green Island | GI12 | 2024-04-19 09:21 | 2024-04-19 15:58 | 0.13206 | 0.00033265 | 32 | 12704 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 132 | 16393 | Green Island | GI12 | 2024-04-19 09:26 | 2024-04-19 16:03 | 0.0041269 | 1.0395e-05 | 1 | 397 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 133 | 16392 | Green Island | GI12 | 2024-04-19 09:26 | 2024-04-19 15:58 | 0.80276 | 0.0020479 | 197 | 77224 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 134 | 16377 | East Taieri | ET3 | 2024-04-19 16:03 | 2024-04-19 17:43 | 0.16466 | 0.0016632 | 160 | 15840 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 135 | 16378 | East Taieri | ET3 | 2024-04-19 17:43 | 2024-04-19 19:06 | 0.060396 | 0.00072767 | 70 | 5810 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 136 | 16379 | Commonage | CB5732 | 2024-04-19 18:25 | 2024-04-19 20:07 | 0.0010603 | 1.0395e-05 | 1 | 102 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 137 | 16374 | Alexandra | CB169 | 2024-04-20 08:01 | 2024-04-20 08:06 | 0.00010395 | 2.079e-05 | 2 | 10 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 138 | 16375 | Alexandra | CB169 | 2024-04-20 08:01 | 2024-04-20 13:50 | 1.1392 | 0.0032641 | 314 | 109586 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 139 | 16396 | Green Island | GI10 | 2024-04-20 09:06 | 2024-04-20 14:07 | 0.003129 | 1.0395e-05 | 1 | 301 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 140 | 16395 | Green Island | GI10 | 2024-04-20 09:06 | 2024-04-20 14:07 | 0.13142 | 0.0004366 | 42 | 12642 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 141 | 16376 | Alexandra | CB169 | 2024-04-20 13:48 | 2024-04-20 13:50 | 4.1581e-05 | 2.079e-05 | 2 | 4 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 142 | 16515 | East Taieri | ET5 | 2024-04-21 14:00 | 2024-04-21 18:42 | 0.070355 | 0.00024949 | 24 | 6768 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 143 | 16419 | Andersons Bay | AB8 | 2024-04-22 08:38 | 2024-04-22 09:20 | 0.0004366 | 1.0395e-05 | 1 | 42 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 144 | 16422 | Andersons Bay | AB8 | 2024-04-22 08:38 | 2024-04-22 09:20 | 0.010042 | 0.00023909 | 23 | 966 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 145 | 16420 | Andersons Bay | AB8 | 2024-04-22 08:38 | 2024-04-22 09:20 | 0.013098 | 0.00031186 | 30 | 1260 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 146 | 16423 | Andersons Bay | AB8 | 2024-04-22 09:07 | 2024-04-22 09:20 | 0.0093245 | 0.00071727 | 69 | 897 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 147 | 16406 | Arrowtown | CB7652 | 2024-04-22 09:26 | 2024-04-22 09:45 | 0.18684 | 0.0098339 | 946 | 17974 | Unplanned | Human Error | switching error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 148 | 16407 | Arrowtown | CB7652 | 2024-04-22 09:47 | 2024-04-22 09:48 | 0.0027755 | 0.0027755 | 267 | 267 | Unplanned | Human Error | switching error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 149 | 16398 | Wanaka | CB2754 | 2024-04-22 09:48 | 2024-04-22 12:41 | 0.012589 | 7.2767e-05 | 7 | 1211 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 150 | 16424 | Andersons Bay | AB8 | 2024-04-22 17:38 | 2024-04-22 18:35 | 0.00059253 | 1.0395e-05 | 1 | 57 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 151 | 16426 | Andersons Bay | AB8 | 2024-04-22 17:38 | 2024-04-22 18:35 | 0.013628 | 0.00023909 | 23 | 1311 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 152 | 16425 | Andersons Bay | AB8 | 2024-04-22 17:38 | 2024-04-22 18:35 | 0.017776 | 0.00031186 | 30 | 1710 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 153 | 16427 | Andersons Bay | AB8 | 2024-04-22 18:08 | 2024-04-22 18:43 | 0.025104 | 0.00071727 | 69 | 2415 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 154 | 16400 | South City | SC4 | 2024-04-22 23:01 | 2024-04-23 02:48 | 0.16046 | 0.00070688 | 68 | 15436 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 155 | 16437 | Frankton | CB7782 | 2024-04-23 07:32 | 2024-04-23 16:48 | 0.011559 | 2.079e-05 | 2 | 1112 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 156 | 16438 | Frankton | CB7782 | 2024-04-23 07:32 | 2024-04-23 16:48 | 0.017339 | 3.1186e-05 | 3 | 1668 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 157 | 16431 | Andersons Bay | AB9 | 2024-04-23 08:32 | 2024-04-23 16:49 | 0.067028 | 0.00013514 | 13 | 6448 | Planned | Planned interruption | network extension | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 158 | 16430 | Andersons Bay | AB9 | 2024-04-23 08:32 | 2024-04-23 16:48 | 0.32483 | 0.0006549 | 63 | 31248 | Planned | Planned interruption | network extension | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 159 | 16439 | Frankton | CB7782 | 2024-04-23 08:32 | 2024-04-23 16:48 | 0.005156 | 1.0395e-05 | 1 | 496 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 160 | 16435 | Frankton | CB7782 | 2024-04-23 08:32 | 2024-04-23 16:35 | 0.015063 | 3.1186e-05 | 3 | 1449 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 161 | 16441 | Frankton | CB7782 | 2024-04-23 08:32 | 2024-04-23 16:48 | 0.087653 | 0.00017672 | 17 | 8432 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 162 | 16440 | Frankton | CB7782 | 2024-04-23 08:32 | 2024-04-23 16:48 | 0.097965 | 0.00019751 | 19 | 9424 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 163 | 16434 | Frankton | CB7782 | 2024-04-23 08:32 | 2024-04-23 08:36 | 0.0015801 | 0.00039502 | 38 | 152 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 164 | 16442 | Frankton | CB7782 | 2024-04-23 08:32 | 2024-04-23 16:48 | 0.005156 | 1.0395e-05 | 1 | 496 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 165 | 16674 | Andersons Bay | AB9 | 2024-04-23 08:32 | 2024-04-23 16:48 | 0.005156 | 1.0395e-05 | 1 | 496 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 166 | 16415 | St. Kilda | SK9 | 2024-04-23 09:01 | 2024-04-23 11:17 | 0.0014138 | 1.0395e-05 | 1 | 136 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 167 | 16416 | St. Kilda | SK9 | 2024-04-23 09:01 | 2024-04-23 11:17 | 0.13289 | 0.00097715 | 94 | 12784 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 168 | 16402 | Dalefield | CB7828 | 2024-04-23 09:05 | 2024-04-23 14:11 | 0.50577 | 0.0016528 | 159 | 48654 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 169 | 16418 | St. Kilda | SK9 | 2024-04-23 11:18 | 2024-04-23 14:01 | 0.0016944 | 1.0395e-05 | 1 | 163 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 170 | 16417 | St. Kilda | SK9 | 2024-04-23 11:18 | 2024-04-23 14:01 | 0.15928 | 0.00097715 | 94 | 15322 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 171 | 16413 | Dalefield | CB7830 | 2024-04-23 12:06 | 2024-04-23 14:20 | 0.001393 | 1.0395e-05 | 1 | 134 | Unplanned | Defective Equipment | faulty lightning arrestor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 172 | 16414 | Dalefield | CB7830 | 2024-04-23 12:06 | 2024-04-23 14:35 | 0.0015489 | 1.0395e-05 | 1 | 149 | Unplanned | Defective Equipment | faulty lightning arrestor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 173 | 16412 | Dalefield | CB7830 | 2024-04-23 12:06 | 2024-04-23 12:29 | 0.019127 | 0.00083162 | 80 | 1840 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 174 | 16429 | Andersons Bay | AB7 | 2024-04-24 08:34 | 2024-04-24 14:30 | 0.0074014 | 2.079e-05 | 2 | 712 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 175 | 16428 | Andersons Bay | AB7 | 2024-04-24 08:34 | 2024-04-24 14:28 | 0.073598 | 0.0002079 | 20 | 7080 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 176 | 16447 | Wanaka | CB2754 | 2024-04-24 08:40 | 2024-04-24 15:30 | 0.004262 | 1.0395e-05 | 1 | 410 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 177 | 16448 | Lindis Crossing | CB2086 | 2024-04-24 09:07 | 2024-04-24 15:33 | 0.21668 | 0.00056134 | 54 | 20844 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 178 | 16450 | Lindis Crossing | CB2086 | 2024-04-24 09:08 | 2024-04-24 16:31 | 0.0046051 | 1.0395e-05 | 1 | 443 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 179 | 16449 | Lindis Crossing | CB2086 | 2024-04-24 09:08 | 2024-04-24 16:08 | 0.30562 | 0.00072767 | 70 | 29400 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 180 | 16453 | Lindis Crossing | CB2086 | 2024-04-24 09:11 | 2024-04-24 16:30 | 0.34226 | 0.00077964 | 75 | 32925 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 181 | 16516 | East Taieri | ET5 | 2024-04-24 14:38 | 2024-04-24 14:57 | 0.0047402 | 0.00024949 | 24 | 456 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 182 | 16454 | Cromwell GXP | CB2424 | 2024-04-25 02:31 | 2024-04-25 02:52 | 0.0056758 | 0.00027028 | 26 | 546 | Unplanned | Third-party Interference | 33/66kv to 11/6.6kv line clash | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 183 | 16455 | Cromwell GXP | CB2423 | 2024-04-25 02:31 | 2024-04-25 05:42 | 0.77434 | 0.0040541 | 390 | 74490 | Unplanned | Third-party Interference | 33/66kv to 11/6.6kv line clash | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 184 | 16481 | Alexandra | CB168 | 2024-04-25 08:06 | 2024-04-25 09:33 | 0.092081 | 0.0010707 | 103 | 8858 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 185 | 16485 | Alexandra | CB168 | 2024-04-25 08:06 | 2024-04-25 10:48 | 0.22566 | 0.001393 | 134 | 21708 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 186 | 16480 | Alexandra | CB168 | 2024-04-25 08:06 | 2024-04-25 09:32 | 0.12248 | 0.0014241 | 137 | 11782 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 187 | 16482 | Alexandra | CB168 | 2024-04-25 08:06 | 2024-04-25 09:34 | 0.17472 | 0.0019855 | 191 | 16808 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 188 | 16483 | Alexandra | CB168 | 2024-04-25 08:06 | 2024-04-25 10:46 | 0.50742 | 0.0031913 | 307 | 48813 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 189 | 16484 | Alexandra | CB168 | 2024-04-25 08:06 | 2024-04-25 10:48 | 0.51548 | 0.0032017 | 308 | 49588 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 190 | 16477 | Omakau | CB656 | 2024-04-25 10:10 | 2024-04-25 10:36 | 0.0010811 | 4.1581e-05 | 4 | 104 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 191 | 16479 | Omakau | CB656 | 2024-04-25 10:56 | 2024-04-25 11:42 | 0.0019127 | 4.1581e-05 | 4 | 184 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 192 | 16478 | Omakau | CB656 | 2024-04-25 10:56 | 2024-04-25 11:42 | 0.00526 | 0.00011435 | 11 | 506 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 193 | 16498 | Port Chalmers | PC7 | 2024-04-26 09:05 | 2024-04-26 11:10 | 0.015593 | 0.00012474 | 12 | 1500 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 194 | 16499 | Port Chalmers | PC7 | 2024-04-26 09:05 | 2024-04-26 11:12 | 0.079212 | 0.00062371 | 60 | 7620 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 195 | 16497 | Port Chalmers | PC7 | 2024-04-26 09:05 | 2024-04-26 11:10 | 0.15203 | 0.0012162 | 117 | 14625 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 196 | 16446 | Wanaka | CB2756 | 2024-04-26 09:28 | 2024-04-26 14:07 | 0.043504 | 0.00015593 | 15 | 4185 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 197 | 16521 | Clyde-Earnscleugh | CB192 | 2024-04-30 08:03 | 2024-04-30 14:21 | 0.22398 | 0.00059253 | 57 | 21546 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 198 | 16523 | Frankton | CB7782 | 2024-04-30 08:37 | 2024-04-30 14:20 | 0.0035656 | 1.0395e-05 | 1 | 343 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 199 | 16520 | Andersons Bay | AB9 | 2024-04-30 08:47 | 2024-04-30 17:27 | 0.016217 | 3.1186e-05 | 3 | 1560 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 200 | 16519 | Andersons Bay | AB9 | 2024-04-30 08:47 | 2024-04-30 17:25 | 0.053847 | 0.00010395 | 10 | 5180 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 201 | 16522 | Smith Street | SS11 | 2024-04-30 09:01 | 2024-04-30 11:05 | 0.13535 | 0.0010915 | 105 | 13020 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 202 | 16525 | Dalefield | CB7828 | 2024-04-30 09:04 | 2024-04-30 14:40 | 0.020957 | 6.2371e-05 | 6 | 2016 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 203 | 16524 | Dalefield | CB7828 | 2024-04-30 09:04 | 2024-04-30 14:30 | 0.044055 | 0.00013514 | 13 | 4238 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 204 | 16527 | East Taieri | ET2 | 2024-04-30 12:23 | 2024-04-30 13:08 | 0.0028067 | 6.2371e-05 | 6 | 270 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 205 | 16528 | East Taieri | ET2 | 2024-04-30 12:47 | 2024-04-30 12:58 | 0.011549 | 0.0010499 | 101 | 1111 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 206 | 16532 | Frankton | CB7790 | 2024-04-30 14:50 | 2024-04-30 19:34 | 0.0029418 | 1.0395e-05 | 1 | 283 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 207 | 16531 | Frankton | CB7790 | 2024-04-30 14:50 | 2024-04-30 19:07 | 0.19959 | 0.00077964 | 75 | 19200 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 208 | 16530 | Frankton | CB7790 | 2024-04-30 14:50 | 2024-04-30 15:45 | 0.13753 | 0.0025468 | 245 | 13230 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 209 | 16534 | Queenstown | CB5731 | 2024-04-30 14:50 | 2024-04-30 14:59 | 0.075594 | 0.0094493 | 909 | 7272 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 210 | 16533 | Queenstown | CB5730 | 2024-04-30 14:50 | 2024-04-30 14:57 | 0.067423 | 0.011237 | 1081 | 6486 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 211 | 16581 | Frankton | CB7784 | 2024-05-01 08:39 | 2024-05-01 15:08 | 0.0040437 | 1.0395e-05 | 1 | 389 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 212 | 16583 | Frankton | CB7784 | 2024-05-01 08:39 | 2024-05-01 15:08 | 0.0040437 | 1.0395e-05 | 1 | 389 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 213 | 16582 | Frankton | CB7784 | 2024-05-01 08:39 | 2024-05-01 15:08 | 0.012131 | 3.1186e-05 | 3 | 1167 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 214 | 16584 | Frankton | CB7784 | 2024-05-01 08:39 | 2024-05-01 15:08 | 0.028306 | 7.2767e-05 | 7 | 2723 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 215 | 16579 | Frankton | CB7784 | 2024-05-01 08:39 | 2024-05-01 15:08 | 0.040437 | 0.00010395 | 10 | 3890 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 216 | 16580 | Frankton | CB7784 | 2024-05-01 08:39 | 2024-05-01 15:08 | 0.12131 | 0.00031186 | 30 | 11670 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 217 | 16578 | Frankton | CB7784 | 2024-05-01 08:39 | 2024-05-01 15:08 | 0.17388 | 0.00044699 | 43 | 16727 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 218 | 16577 | Frankton | CB7784 | 2024-05-01 08:39 | 2024-05-01 14:29 | 0.29107 | 0.00083162 | 80 | 28000 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 219 | 16585 | Frankton | CB7784 | 2024-05-01 08:39 | 2024-05-01 16:30 | 2.4432 | 0.0051872 | 499 | 235029 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 220 | 16544 | Andersons Bay | AB9 | 2024-05-01 08:42 | 2024-05-01 16:01 | 0.009127 | 2.079e-05 | 2 | 878 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 221 | 16543 | Andersons Bay | AB9 | 2024-05-01 08:42 | 2024-05-01 15:52 | 0.03576 | 8.3162e-05 | 8 | 3440 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 222 | 16565 | Clyde-Earnscleugh | CB192 | 2024-05-01 09:03 | 2024-05-01 14:36 | 0.16962 | 0.00050937 | 49 | 16317 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 223 | 16566 | Clyde-Earnscleugh | CB192 | 2024-05-01 17:34 | 2024-05-01 19:36 | 0.076093 | 0.00062371 | 60 | 7320 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 224 | 16567 | Clyde-Earnscleugh | CB192 | 2024-05-01 17:39 | 2024-05-01 19:36 | 0.0012162 | 1.0395e-05 | 1 | 117 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 225 | 16568 | Clyde-Earnscleugh | CB192 | 2024-05-01 17:46 | 2024-05-01 19:36 | 0.0091478 | 8.3162e-05 | 8 | 880 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 226 | 16563 | Clyde-Earnscleugh | CB199 | 2024-05-02 08:43 | 2024-05-02 15:45 | 0.14476 | 0.00034304 | 33 | 13926 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 227 | 16587 | Frankton | CB7782 | 2024-05-02 08:44 | 2024-05-02 13:10 | 0.011061 | 4.1581e-05 | 4 | 1064 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 228 | 16586 | Frankton | CB7782 | 2024-05-02 08:44 | 2024-05-02 13:10 | 0.022121 | 8.3162e-05 | 8 | 2128 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 229 | 16561 | Clyde-Earnscleugh | CB199 | 2024-05-02 09:03 | 2024-05-02 15:45 | 0.025073 | 6.2371e-05 | 6 | 2412 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 230 | 16547 | Dalefield | CB7830 | 2024-05-02 09:06 | 2024-05-02 15:30 | 0.0039918 | 1.0395e-05 | 1 | 384 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 231 | 16549 | Dalefield | CB7830 | 2024-05-02 09:06 | 2024-05-02 15:37 | 0.0040645 | 1.0395e-05 | 1 | 391 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 232 | 16550 | Dalefield | CB7830 | 2024-05-02 09:06 | 2024-05-02 15:22 | 0.0078172 | 2.079e-05 | 2 | 752 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 233 | 16552 | Dalefield | CB7830 | 2024-05-02 09:06 | 2024-05-02 15:31 | 0.020011 | 5.1976e-05 | 5 | 1925 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 234 | 16545 | Dalefield | CB7830 | 2024-05-02 09:06 | 2024-05-02 15:10 | 0.090813 | 0.00024949 | 24 | 8736 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 235 | 16817 | Dalefield | CB7830 | 2024-05-02 09:06 | 2024-05-02 15:10 | 0.0037839 | 1.0395e-05 | 1 | 364 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 236 | 16555 | Wanaka | CB2751 | 2024-05-02 09:09 | 2024-05-02 15:35 | 0.21267 | 0.00055095 | 53 | 20458 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 237 | 16557 | Commonage | CB5730 | 2024-05-02 09:11 | 2024-05-02 15:45 | 0.81505 | 0.0020687 | 199 | 78406 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 238 | 16560 | Clyde-Earnscleugh | CB199 | 2024-05-02 09:32 | 2024-05-02 15:40 | 0.019127 | 5.1976e-05 | 5 | 1840 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 239 | 16556 | Commonage | CB5730 | 2024-05-02 09:47 | 2024-05-02 15:38 | 0.22622 | 0.0006445 | 62 | 21762 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 240 | 16589 | Wanaka | CB2754 | 2024-05-02 10:17 | 2024-05-02 15:18 | 0.003129 | 1.0395e-05 | 1 | 301 | Planned | Planned interruption | network extension | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 241 | 16592 | Wanaka | CB2754 | 2024-05-02 10:17 | 2024-05-02 15:48 | 0.0034408 | 1.0395e-05 | 1 | 331 | Planned | Planned interruption | network extension | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 242 | 16588 | Wanaka | CB2754 | 2024-05-02 10:17 | 2024-05-02 10:22 | 0.0012474 | 0.00024949 | 24 | 120 | Planned | Planned interruption | network extension | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 243 | 16590 | Wanaka | CB2754 | 2024-05-02 10:17 | 2024-05-02 15:18 | 0.17835 | 0.00059253 | 57 | 17157 | Planned | Planned interruption | network extension | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 244 | 16591 | Wanaka | CB2754 | 2024-05-02 15:17 | 2024-05-02 15:18 | 0.00024949 | 0.00024949 | 24 | 24 | Planned | Planned interruption | network extension | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 245 | 16598 | Roxburgh | HSB33 | 2024-05-02 22:26 | 2024-05-03 00:14 | 0.0044492 | 4.1581e-05 | 4 | 428 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 246 | 16612 | Roxburgh | CB4639 | 2024-05-05 08:31 | 2024-05-05 10:58 | 0.0015281 | 1.0395e-05 | 1 | 147 | Unplanned | Wildlife | animal in equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 247 | 16615 | Andersons Bay | AB9 | 2024-05-06 08:37 | 2024-05-06 16:35 | 0.0049689 | 1.0395e-05 | 1 | 478 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 248 | 16614 | Andersons Bay | AB9 | 2024-05-06 08:37 | 2024-05-06 16:35 | 0.0099378 | 2.079e-05 | 2 | 956 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 249 | 16613 | Andersons Bay | AB9 | 2024-05-06 08:37 | 2024-05-06 16:28 | 0.019585 | 4.1581e-05 | 4 | 1884 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 250 | 16610 | South City | SC1 | 2024-05-06 14:26 | 2024-05-06 17:35 | 0.11002 | 0.00058213 | 56 | 10584 | Unplanned | Defective Equipment | faulty fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 251 | 16618 | Kaikorai Valley | KV4 | 2024-05-06 18:09 | 2024-05-06 23:44 | 0.1184 | 0.00035344 | 34 | 11390 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 252 | 16616 | Dalefield | CB7830 | 2024-05-07 09:03 | 2024-05-07 15:06 | 0.0075469 | 2.079e-05 | 2 | 726 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 253 | 16617 | Dalefield | CB7830 | 2024-05-07 09:03 | 2024-05-07 15:25 | 0.007942 | 2.079e-05 | 2 | 764 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 254 | 16619 | Lindis Crossing | CB2084 | 2024-05-07 17:02 | 2024-05-07 17:52 | 0.032745 | 0.0006549 | 63 | 3150 | Unplanned | Defective Equipment | broken crossarm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 255 | 16627 | Commonage | CB5732 | 2024-05-08 08:03 | 2024-05-08 13:48 | 0.10042 | 0.00029107 | 28 | 9660 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 256 | 16634 | East Taieri | ET5 | 2024-05-08 08:12 | 2024-05-08 08:28 | 0.0069856 | 0.0004366 | 42 | 672 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 257 | 16637 | East Taieri | ET5 | 2024-05-08 08:12 | 2024-05-08 08:28 | 0.031768 | 0.0019855 | 191 | 3056 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 258 | 16626 | Wanaka | CB2752 | 2024-05-08 08:31 | 2024-05-08 16:18 | 0.72333 | 0.0015489 | 149 | 69583 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 259 | 16636 | East Taieri | ET5 | 2024-05-08 08:38 | 2024-05-08 17:06 | 0.06865 | 0.00013514 | 13 | 6604 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 260 | 16635 | East Taieri | ET5 | 2024-05-08 08:38 | 2024-05-08 16:41 | 0.89372 | 0.0018504 | 178 | 85974 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 261 | 16639 | Arrowtown | CB7692 | 2024-05-08 09:02 | 2024-05-08 09:04 | 2.079e-05 | 1.0395e-05 | 1 | 2 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 262 | 16640 | Arrowtown | CB7692 | 2024-05-08 09:02 | 2024-05-08 15:44 | 0.17551 | 0.0004366 | 42 | 16884 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 263 | 16641 | Arrowtown | CB7692 | 2024-05-08 15:47 | 2024-05-08 15:53 | 6.2371e-05 | 1.0395e-05 | 1 | 6 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 264 | 16657 | Outram | OT3 | 2024-05-09 04:15 | 2024-05-09 07:23 | 0.14462 | 0.00076925 | 74 | 13912 | Unplanned | Third-party Interference | vandalism | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 265 | 16650 | Arrowtown | CB7692 | 2024-05-09 09:04 | 2024-05-09 14:02 | 0.052662 | 0.00017672 | 17 | 5066 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 266 | 16644 | Camp Hill | CB2006 | 2024-05-09 23:04 | 2024-05-09 23:21 | 0.00053016 | 3.1186e-05 | 3 | 51 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 267 | 16645 | Camp Hill | CB2006 | 2024-05-09 23:28 | 2024-05-10 00:03 | 0.022921 | 0.0006549 | 63 | 2205 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 268 | 16649 | Camp Hill | CB2006 | 2024-05-10 00:04 | 2024-05-10 01:49 | 0.21066 | 0.0020063 | 193 | 20265 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 269 | 16647 | Camp Hill | CB2006 | 2024-05-10 00:37 | 2024-05-10 01:33 | 0.0052392 | 9.3557e-05 | 9 | 504 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 270 | 16651 | Cromwell | CB821 | 2024-05-10 09:09 | 2024-05-10 12:25 | 0.0020375 | 1.0395e-05 | 1 | 196 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 271 | 16714 | Willowbank | WB3 | 2024-05-13 09:02 | 2024-05-13 18:42 | 0.0060292 | 1.0395e-05 | 1 | 580 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 272 | 16712 | Willowbank | WB3 | 2024-05-13 09:02 | 2024-05-13 17:38 | 0.02682 | 5.1976e-05 | 5 | 2580 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 273 | 16718 | Willowbank | WB3 | 2024-05-13 09:02 | 2024-05-13 18:42 | 0.048234 | 8.3162e-05 | 8 | 4640 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 274 | 16716 | Willowbank | WB3 | 2024-05-13 09:02 | 2024-05-13 18:42 | 0.072351 | 0.00012474 | 12 | 6960 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 275 | 16719 | Willowbank | WB3 | 2024-05-13 09:02 | 2024-05-13 18:42 | 0.07838 | 0.00013514 | 13 | 7540 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 276 | 16720 | Willowbank | WB3 | 2024-05-13 09:02 | 2024-05-13 18:42 | 0.10853 | 0.00018711 | 18 | 10440 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 277 | 16715 | Willowbank | WB3 | 2024-05-13 09:02 | 2024-05-13 18:42 | 0.13264 | 0.00022869 | 22 | 12760 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 278 | 16713 | Willowbank | WB3 | 2024-05-13 09:02 | 2024-05-13 18:42 | 0.18088 | 0.00031186 | 30 | 17400 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 279 | 16717 | Willowbank | WB3 | 2024-05-13 09:02 | 2024-05-13 18:42 | 0.22308 | 0.00038462 | 37 | 21460 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 280 | 16676 | Queenstown | CB5242 | 2024-05-13 09:03 | 2024-05-13 18:14 | 0.0057278 | 1.0395e-05 | 1 | 551 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 281 | 16698 | Queenstown | CB5202 | 2024-05-13 09:07 | 2024-05-13 09:34 | 0.00056134 | 2.079e-05 | 2 | 54 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 282 | 16677 | Fernhill | CB5309 | 2024-05-13 09:11 | 2024-05-13 10:51 | 0.0031186 | 3.1186e-05 | 3 | 300 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 283 | 16687 | Wanaka | CB2753 | 2024-05-13 09:11 | 2024-05-13 15:19 | 0.2785 | 0.00075885 | 73 | 26791 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 284 | 16689 | Wanaka | CB2753 | 2024-05-13 09:12 | 2024-05-13 15:35 | 0.011944 | 3.1186e-05 | 3 | 1149 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 285 | 16685 | Wanaka | CB2753 | 2024-05-13 09:12 | 2024-05-13 15:09 | 0.089066 | 0.00024949 | 24 | 8568 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 286 | 16700 | Queenstown | CB5202 | 2024-05-13 10:02 | 2024-05-13 10:09 | 0.0016009 | 0.00022869 | 22 | 154 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 287 | 16701 | Queenstown | CB5202 | 2024-05-13 10:32 | 2024-05-13 10:39 | 0.00036383 | 5.1976e-05 | 5 | 35 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 288 | 16690 | Camp Hill | CB2006 | 2024-05-13 10:33 | 2024-05-13 11:46 | 0.00075885 | 1.0395e-05 | 1 | 73 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 289 | 16702 | Queenstown | CB5202 | 2024-05-13 11:01 | 2024-05-13 11:05 | 4.1581e-05 | 1.0395e-05 | 1 | 4 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 290 | 16703 | Queenstown | CB5202 | 2024-05-13 11:31 | 2024-05-13 11:36 | 5.1976e-05 | 1.0395e-05 | 1 | 5 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 291 | 16704 | Queenstown | CB5202 | 2024-05-13 12:01 | 2024-05-13 12:08 | 0.00014553 | 2.079e-05 | 2 | 14 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 292 | 16678 | Fernhill | CB5309 | 2024-05-13 12:16 | 2024-05-13 12:34 | 0.00037423 | 2.079e-05 | 2 | 36 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 293 | 16707 | Queenstown | CB5202 | 2024-05-13 12:39 | 2024-05-13 13:31 | 0.00054055 | 1.0395e-05 | 1 | 52 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 294 | 16705 | Queenstown | CB5202 | 2024-05-13 12:39 | 2024-05-13 13:15 | 0.0014969 | 4.1581e-05 | 4 | 144 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 295 | 16706 | Queenstown | CB5202 | 2024-05-13 12:39 | 2024-05-13 13:21 | 0.0017464 | 4.1581e-05 | 4 | 168 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 296 | 16679 | Fernhill | CB5309 | 2024-05-13 12:50 | 2024-05-13 12:54 | 8.3162e-05 | 2.079e-05 | 2 | 8 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 297 | 16680 | Fernhill | CB5309 | 2024-05-13 13:05 | 2024-05-13 13:17 | 0.00012474 | 1.0395e-05 | 1 | 12 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 298 | 16708 | Queenstown | CB5202 | 2024-05-13 13:33 | 2024-05-13 13:38 | 0.00036383 | 7.2767e-05 | 7 | 35 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 299 | 16681 | Fernhill | CB5309 | 2024-05-13 13:34 | 2024-05-13 13:40 | 0.00018711 | 3.1186e-05 | 3 | 18 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 300 | 16709 | Queenstown | CB5202 | 2024-05-13 14:03 | 2024-05-13 14:07 | 4.1581e-05 | 1.0395e-05 | 1 | 4 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 301 | 16682 | Fernhill | CB5309 | 2024-05-13 14:34 | 2024-05-13 14:37 | 3.1186e-05 | 1.0395e-05 | 1 | 3 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 302 | 16710 | Queenstown | CB5202 | 2024-05-13 14:36 | 2024-05-13 14:54 | 0.00018711 | 1.0395e-05 | 1 | 18 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 303 | 16711 | Queenstown | CB5202 | 2024-05-13 14:36 | 2024-05-13 15:06 | 0.00093557 | 3.1186e-05 | 3 | 90 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 304 | 16683 | Fernhill | CB5309 | 2024-05-13 15:31 | 2024-05-13 15:33 | 2.079e-05 | 1.0395e-05 | 1 | 2 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 305 | 16684 | Fernhill | CB5309 | 2024-05-13 16:03 | 2024-05-13 16:10 | 0.0064762 | 0.00092518 | 89 | 623 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 306 | 16775 | Frankton | CB7789 | 2024-05-13 17:16 | 2024-05-13 23:21 | 0.0075885 | 2.079e-05 | 2 | 730 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 307 | 16723 | Willowbank | WB3 | 2024-05-13 18:14 | 2024-05-13 18:42 | 0.0014553 | 5.1976e-05 | 5 | 140 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 308 | 16729 | Halfway Bush | HB13 | 2024-05-14 08:01 | 2024-05-14 08:23 | 0.04734 | 0.0021518 | 207 | 4554 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 309 | 16728 | Halfway Bush | HB13 | 2024-05-14 08:01 | 2024-05-14 08:18 | 0.044003 | 0.0025884 | 249 | 4233 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 310 | 16727 | Dalefield | CB7830 | 2024-05-14 09:03 | 2024-05-14 16:39 | 0.014221 | 3.1186e-05 | 3 | 1368 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 311 | 16726 | Dalefield | CB7830 | 2024-05-14 09:03 | 2024-05-14 16:31 | 0.16765 | 0.00037423 | 36 | 16128 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 312 | 16724 | Queenstown | CB5212 | 2024-05-14 09:08 | 2024-05-14 16:28 | 0.61748 | 0.0014034 | 135 | 59400 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 313 | 16738 | East Taieri | ET4 | 2024-05-14 09:38 | 2024-05-14 10:33 | 0.0017152 | 3.1186e-05 | 3 | 165 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 314 | 16730 | Halfway Bush | HB13 | 2024-05-14 16:00 | 2024-05-14 16:13 | 0.027974 | 0.0021518 | 207 | 2691 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 315 | 16731 | Halfway Bush | HB13 | 2024-05-14 16:01 | 2024-05-14 16:13 | 0.031061 | 0.0025884 | 249 | 2988 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 316 | 16750 | Andersons Bay | AB4 | 2024-05-15 08:33 | 2024-05-15 16:40 | 0.025312 | 5.1976e-05 | 5 | 2435 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 317 | 16749 | Andersons Bay | AB4 | 2024-05-15 08:33 | 2024-05-15 16:38 | 0.050417 | 0.00010395 | 10 | 4850 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 318 | 16748 | Andersons Bay | AB4 | 2024-05-15 08:33 | 2024-05-15 16:33 | 0.22454 | 0.00046779 | 45 | 21600 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 319 | 16746 | Ettrick | CB480 | 2024-05-15 08:36 | 2024-05-15 15:24 | 0.046654 | 0.00011435 | 11 | 4488 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 320 | 16816 | Frankton | CB7789 | 2024-05-15 22:38 | 2024-05-15 22:39 | 2.079e-05 | 2.079e-05 | 2 | 2 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 321 | 16763 | Camp Hill | CB2004 | 2024-05-16 08:03 | 2024-05-16 17:54 | 0.0061436 | 1.0395e-05 | 1 | 591 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 322 | 16764 | Camp Hill | CB2004 | 2024-05-16 08:03 | 2024-05-16 17:55 | 0.018462 | 3.1186e-05 | 3 | 1776 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 323 | 16765 | Camp Hill | CB2004 | 2024-05-16 08:03 | 2024-05-16 17:56 | 0.018493 | 3.1186e-05 | 3 | 1779 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 324 | 16766 | Camp Hill | CB2004 | 2024-05-16 08:03 | 2024-05-16 17:58 | 0.018555 | 3.1186e-05 | 3 | 1785 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 325 | 16762 | Camp Hill | CB2004 | 2024-05-16 08:20 | 2024-05-16 17:45 | 0.0058733 | 1.0395e-05 | 1 | 565 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 326 | 16759 | Camp Hill | CB2004 | 2024-05-16 08:20 | 2024-05-16 17:38 | 0.017402 | 3.1186e-05 | 3 | 1674 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 327 | 16761 | Camp Hill | CB2004 | 2024-05-16 08:20 | 2024-05-16 17:42 | 0.017526 | 3.1186e-05 | 3 | 1686 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 328 | 16760 | Camp Hill | CB2004 | 2024-05-16 08:20 | 2024-05-16 17:40 | 0.052392 | 9.3557e-05 | 9 | 5040 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 329 | 16757 | East Taieri | ET2 | 2024-05-16 08:45 | 2024-05-16 10:32 | 0.0011123 | 1.0395e-05 | 1 | 107 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 330 | 16770 | Dalefield | CB7830 | 2024-05-16 09:02 | 2024-05-16 15:29 | 0.020115 | 5.1976e-05 | 5 | 1935 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 331 | 16803 | Dalefield | CB7830 | 2024-05-16 09:06 | 2024-05-16 15:19 | 0.0077548 | 2.079e-05 | 2 | 746 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 332 | 16781 | Omakau | CB656 | 2024-05-16 09:55 | 2024-05-16 09:56 | 0.00097715 | 0.00097715 | 94 | 94 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 333 | 16802 | Omakau | CB656 | 2024-05-16 10:00 | 2024-05-16 12:08 | 0.0013306 | 1.0395e-05 | 1 | 128 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 334 | 16801 | Omakau | CB656 | 2024-05-16 10:00 | 2024-05-16 12:08 | 0.031934 | 0.00024949 | 24 | 3072 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 335 | 16771 | Andersons Bay | AB9 | 2024-05-17 08:43 | 2024-05-17 13:10 | 0.0027755 | 1.0395e-05 | 1 | 267 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 336 | 16772 | Andersons Bay | AB9 | 2024-05-17 08:43 | 2024-05-17 13:13 | 0.033681 | 0.00012474 | 12 | 3240 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 337 | 16767 | Wanaka | CB2754 | 2024-05-17 09:03 | 2024-05-17 16:50 | 0.1068 | 0.00022869 | 22 | 10274 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 338 | 16758 | Arrowtown | CB7632 | 2024-05-17 10:25 | 2024-05-17 10:41 | 0.00016632 | 1.0395e-05 | 1 | 16 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 339 | 16756 | Kaikorai Valley | KV8 | 2024-05-17 13:09 | 2024-05-17 13:55 | 0.011476 | 0.00024949 | 24 | 1104 | Unplanned | Defective Equipment | broken crossarm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 340 | 17102 | St. Kilda | SK7 | 2024-05-17 16:36 | 2024-05-17 17:28 | 0.15298 | 0.0029418 | 283 | 14716 | Unplanned | Defective Equipment | broken tie wire (floater) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 341 | 16813 | Wanaka | CB2755 | 2024-05-20 00:32 | 2024-05-20 03:02 | 0.030978 | 0.0002079 | 20 | 2980 | Unplanned | Wildlife | possum on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 342 | 16811 | Wanaka | CB2755 | 2024-05-20 00:32 | 2024-05-20 01:29 | 0.2119 | 0.0037839 | 364 | 20384 | Unplanned | Wildlife | possum on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 343 | 16812 | Wanaka | CB2755 | 2024-05-20 00:32 | 2024-05-20 01:55 | 0.41939 | 0.0051145 | 492 | 40344 | Unplanned | Wildlife | possum on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 344 | 16805 | East Taieri | ET4 | 2024-05-20 09:21 | 2024-05-20 09:41 | 0.0022869 | 0.00011435 | 11 | 220 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 345 | 16806 | East Taieri | ET4 | 2024-05-20 10:29 | 2024-05-20 10:44 | 0.0012474 | 8.3162e-05 | 8 | 120 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 346 | 16807 | East Taieri | ET4 | 2024-05-20 11:19 | 2024-05-20 11:24 | 5.1976e-05 | 1.0395e-05 | 1 | 5 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 347 | 16808 | East Taieri | ET4 | 2024-05-20 12:49 | 2024-05-20 13:28 | 0.0020271 | 5.1976e-05 | 5 | 195 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 348 | 16809 | East Taieri | ET4 | 2024-05-20 14:36 | 2024-05-20 15:20 | 0.00045739 | 1.0395e-05 | 1 | 44 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 349 | 16837 | St. Kilda | SK12 | 2024-05-21 08:35 | 2024-05-21 15:57 | 0.027568 | 6.2371e-05 | 6 | 2652 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 350 | 16838 | East Taieri | ET9 | 2024-05-21 09:01 | 2024-05-21 09:19 | 0.008233 | 0.00045739 | 44 | 792 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 351 | 16818 | Dalefield | CB7828 | 2024-05-21 09:06 | 2024-05-21 09:11 | 0.00051976 | 0.00010395 | 10 | 50 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 352 | 16839 | East Taieri | ET9 | 2024-05-21 09:10 | 2024-05-21 09:21 | 0.0020583 | 0.00018711 | 18 | 198 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 353 | 16819 | Dalefield | CB7828 | 2024-05-21 09:24 | 2024-05-21 09:29 | 5.1976e-05 | 1.0395e-05 | 1 | 5 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 354 | 16820 | Dalefield | CB7828 | 2024-05-21 09:44 | 2024-05-21 09:53 | 0.00074846 | 8.3162e-05 | 8 | 72 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 355 | 16840 | East Taieri | ET9 | 2024-05-21 10:03 | 2024-05-21 10:14 | 0.0038878 | 0.00035344 | 34 | 374 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 356 | 16841 | East Taieri | ET9 | 2024-05-21 10:04 | 2024-05-21 10:30 | 0.0081083 | 0.00031186 | 30 | 780 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 357 | 16821 | Dalefield | CB7828 | 2024-05-21 10:21 | 2024-05-21 10:31 | 0.0076925 | 0.00076925 | 74 | 740 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 358 | 16842 | East Taieri | ET9 | 2024-05-21 11:00 | 2024-05-21 11:14 | 0.0034928 | 0.00024949 | 24 | 336 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 359 | 16843 | East Taieri | ET9 | 2024-05-21 11:05 | 2024-05-21 11:25 | 0.021414 | 0.0010707 | 103 | 2060 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 360 | 16822 | Dalefield | CB7828 | 2024-05-21 11:08 | 2024-05-21 11:11 | 3.1186e-05 | 1.0395e-05 | 1 | 3 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 361 | 16823 | Dalefield | CB7828 | 2024-05-21 11:33 | 2024-05-21 11:38 | 5.1976e-05 | 1.0395e-05 | 1 | 5 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 362 | 16824 | Dalefield | CB7828 | 2024-05-21 11:58 | 2024-05-21 12:42 | 0.0013722 | 3.1186e-05 | 3 | 132 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 363 | 16825 | Dalefield | CB7828 | 2024-05-21 13:11 | 2024-05-21 13:13 | 2.079e-05 | 1.0395e-05 | 1 | 2 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 364 | 16844 | East Taieri | ET9 | 2024-05-21 13:14 | 2024-05-21 13:31 | 0.0049481 | 0.00029107 | 28 | 476 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 365 | 16845 | East Taieri | ET9 | 2024-05-21 13:18 | 2024-05-21 16:01 | 0.069471 | 0.0004262 | 41 | 6683 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 366 | 16829 | East Taieri | ET3 | 2024-05-21 13:20 | 2024-05-21 14:00 | 0.0012474 | 3.1186e-05 | 3 | 120 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 367 | 16826 | Dalefield | CB7828 | 2024-05-21 13:30 | 2024-05-21 13:35 | 0.00015593 | 3.1186e-05 | 3 | 15 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 368 | 16834 | East Taieri | ET9 | 2024-05-21 13:40 | 2024-05-21 13:43 | 0.0033888 | 0.0016944 | 163 | 326 | Unplanned | Defective Equipment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 369 | 16835 | East Taieri | ET9 | 2024-05-21 13:40 | 2024-05-21 13:50 | 0.13711 | 0.013711 | 1319 | 13190 | Unplanned | Defective Equipment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 370 | 16827 | Dalefield | CB7828 | 2024-05-21 13:54 | 2024-05-21 13:58 | 0.0002079 | 5.1976e-05 | 5 | 20 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 371 | 16846 | East Taieri | ET9 | 2024-05-21 14:15 | 2024-05-21 14:22 | 0.0071311 | 0.0010187 | 98 | 686 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 372 | 16828 | Dalefield | CB7828 | 2024-05-21 14:33 | 2024-05-21 14:36 | 6.2371e-05 | 2.079e-05 | 2 | 6 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 373 | 16884 | East Taieri | ET7 | 2024-05-22 08:54 | 2024-05-22 15:04 | 0.1 | 0.00027028 | 26 | 9620 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 374 | 16886 | East Taieri | ET7 | 2024-05-22 08:54 | 2024-05-22 15:04 | 0.38462 | 0.0010395 | 100 | 37000 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 375 | 16857 | East Taieri | ET3 | 2024-05-22 09:01 | 2024-05-22 09:50 | 0.00050937 | 1.0395e-05 | 1 | 49 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 376 | 16862 | Arrowtown | CB7692 | 2024-05-22 09:11 | 2024-05-22 14:26 | 0.0032745 | 1.0395e-05 | 1 | 315 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 377 | 16863 | Arrowtown | CB7692 | 2024-05-22 09:11 | 2024-05-22 14:41 | 0.0068608 | 2.079e-05 | 2 | 660 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 378 | 16861 | Arrowtown | CB7692 | 2024-05-22 09:11 | 2024-05-22 14:26 | 0.049117 | 0.00015593 | 15 | 4725 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 379 | 16968 | Outram | OT3 | 2024-05-22 10:25 | 2024-05-22 12:17 | 0.0011643 | 1.0395e-05 | 1 | 112 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 380 | 16858 | East Taieri | ET3 | 2024-05-22 14:17 | 2024-05-22 14:40 | 0.00047818 | 2.079e-05 | 2 | 46 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 381 | 16864 | East Taieri | ET4 | 2024-05-23 07:02 | 2024-05-23 07:09 | 0.0004366 | 6.2371e-05 | 6 | 42 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 382 | 16872 | St. Kilda | SK2 | 2024-05-23 07:39 | 2024-05-23 07:45 | 0.0036175 | 0.00060292 | 58 | 348 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 383 | 16876 | Lindis Crossing | CB2086 | 2024-05-23 07:40 | 2024-05-23 11:35 | 0.0024429 | 1.0395e-05 | 1 | 235 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 384 | 16874 | East Taieri | ET5 | 2024-05-23 08:11 | 2024-05-23 14:59 | 0.076343 | 0.00018711 | 18 | 7344 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 385 | 16865 | East Taieri | ET4 | 2024-05-23 08:36 | 2024-05-23 09:47 | 0.0088567 | 0.00012474 | 12 | 852 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 386 | 16871 | Wanaka | CB2754 | 2024-05-23 09:15 | 2024-05-23 15:38 | 0.0039814 | 1.0395e-05 | 1 | 383 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 387 | 16870 | Wanaka | CB2754 | 2024-05-23 09:15 | 2024-05-23 15:20 | 0.030354 | 8.3162e-05 | 8 | 2920 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 388 | 16866 | East Taieri | ET4 | 2024-05-23 10:30 | 2024-05-23 10:49 | 0.010863 | 0.00057174 | 55 | 1045 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 389 | 16868 | East Taieri | ET4 | 2024-05-23 13:09 | 2024-05-23 13:33 | 0.00024949 | 1.0395e-05 | 1 | 24 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 390 | 16869 | East Taieri | ET4 | 2024-05-23 14:45 | 2024-05-23 15:51 | 0.0020583 | 3.1186e-05 | 3 | 198 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 391 | 16873 | St. Kilda | SK2 | 2024-05-23 15:19 | 2024-05-23 15:22 | 0.0018088 | 0.00060292 | 58 | 174 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 392 | 16887 | Andersons Bay | AB7 | 2024-05-24 08:38 | 2024-05-24 11:41 | 0.070386 | 0.00038462 | 37 | 6771 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 393 | 16893 | Andersons Bay | AB9 | 2024-05-24 08:40 | 2024-05-24 16:42 | 0.020042 | 4.1581e-05 | 4 | 1928 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 394 | 16892 | Andersons Bay | AB9 | 2024-05-24 08:40 | 2024-05-24 16:27 | 0.19904 | 0.0004262 | 41 | 19147 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 395 | 16888 | East Taieri | ET5 | 2024-05-24 08:57 | 2024-05-24 10:17 | 0.054055 | 0.00067569 | 65 | 5200 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 396 | 16891 | Queenstown | CB5202 | 2024-05-24 10:25 | 2024-05-24 12:45 | 0.010187 | 7.2767e-05 | 7 | 980 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 397 | 16889 | East Taieri | ET5 | 2024-05-24 13:12 | 2024-05-24 13:44 | 0.00033265 | 1.0395e-05 | 1 | 32 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 398 | 16890 | East Taieri | ET5 | 2024-05-24 14:34 | 2024-05-24 14:39 | 5.1976e-05 | 1.0395e-05 | 1 | 5 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 399 | 16902 | Omakau | CB656 | 2024-05-25 08:29 | 2024-05-25 09:40 | 0.040593 | 0.00057174 | 55 | 3905 | Unplanned | Cause Unknown | auto reclose operation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 400 | 16912 | Ettrick | CB480 | 2024-05-25 20:16 | 2024-05-26 11:27 | 0.12298 | 0.00013514 | 13 | 11830 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 401 | 16911 | Ettrick | CB480 | 2024-05-25 20:16 | 2024-05-25 21:54 | 0.064534 | 0.00066529 | 64 | 6208 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 402 | 16913 | Port Chalmers | PC5 | 2024-05-25 22:29 | 2024-05-26 00:04 | 0.14122 | 0.0014865 | 143 | 13585 | Unplanned | Defective Equipment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 403 | 16918 | Roxburgh | CB4639 | 2024-05-26 01:22 | 2024-05-26 02:49 | 0.11757 | 0.0013514 | 130 | 11310 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 404 | 16930 | Roxburgh | CB4639 | 2024-05-26 12:28 | 2024-05-26 13:59 | 0.0085137 | 9.3557e-05 | 9 | 819 | Unplanned | Defective Equipment | broken tie wire (floater) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 405 | 16932 | Roxburgh | HSB33 | 2024-05-27 09:14 | 2024-05-27 16:21 | 0.0088775 | 2.079e-05 | 2 | 854 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 406 | 16937 | Lauder Flat | CB6576 | 2024-05-27 17:26 | 2024-05-27 17:28 | 2.079e-05 | 1.0395e-05 | 1 | 2 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 407 | 16947 | St. Kilda | SK4 | 2024-05-28 08:05 | 2024-05-28 15:33 | 0.07917 | 0.00017672 | 17 | 7616 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 408 | 16954 | Frankton | CB7782 | 2024-05-28 08:32 | 2024-05-28 14:54 | 0.091332 | 0.00023909 | 23 | 8786 | Planned | Planned interruption | line upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 409 | 16957 | Queensberry | CB2423 | 2024-05-28 08:35 | 2024-05-28 15:10 | 0.0041061 | 1.0395e-05 | 1 | 395 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 410 | 16959 | Queensberry | CB2423 | 2024-05-28 08:35 | 2024-05-28 15:10 | 0.0041061 | 1.0395e-05 | 1 | 395 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 411 | 16958 | Queensberry | CB2423 | 2024-05-28 08:35 | 2024-05-28 15:10 | 0.016424 | 4.1581e-05 | 4 | 1580 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 412 | 16960 | Queensberry | CB2423 | 2024-05-28 08:35 | 2024-05-28 15:23 | 0.029689 | 7.2767e-05 | 7 | 2856 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 413 | 16956 | Queensberry | CB2423 | 2024-05-28 08:35 | 2024-05-28 15:10 | 0.045167 | 0.00011435 | 11 | 4345 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 414 | 16953 | Frankton | CB7782 | 2024-05-28 08:37 | 2024-05-28 14:52 | 0.0038982 | 1.0395e-05 | 1 | 375 | Planned | Planned interruption | line upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 415 | 16955 | Frankton | CB7782 | 2024-05-28 08:37 | 2024-05-28 15:09 | 0.020375 | 5.1976e-05 | 5 | 1960 | Planned | Planned interruption | line upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 416 | 16946 | Halfway Bush | HB13 | 2024-05-28 09:01 | 2024-05-28 15:24 | 0.011944 | 3.1186e-05 | 3 | 1149 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 417 | 16945 | Halfway Bush | HB13 | 2024-05-28 09:01 | 2024-05-28 15:11 | 0.042309 | 0.00011435 | 11 | 4070 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 418 | 16949 | Wanaka | CB2757 | 2024-05-28 09:21 | 2024-05-28 16:40 | 0.3377 | 0.00076925 | 74 | 32486 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 419 | 16971 | Cromwell | CB831 | 2024-05-29 05:05 | 2024-05-29 05:07 | 6.2371e-05 | 3.1186e-05 | 3 | 6 | Unplanned | Defective Equipment | burning link | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 420 | 16974 | Cromwell | CB831 | 2024-05-29 05:05 | 2024-05-29 05:07 | 0.0002079 | 0.00010395 | 10 | 20 | Unplanned | Defective Equipment | burning link | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 421 | 16976 | Cromwell | CB831 | 2024-05-29 05:05 | 2024-05-29 11:49 | 0.041997 | 0.00010395 | 10 | 4040 | Unplanned | Defective Equipment | burning link | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 422 | 16975 | Cromwell | CB831 | 2024-05-29 05:05 | 2024-05-29 05:07 | 0.00045739 | 0.00022869 | 22 | 44 | Unplanned | Defective Equipment | burning link | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 423 | 16972 | Cromwell | CB831 | 2024-05-29 05:05 | 2024-05-29 05:07 | 0.00066529 | 0.00033265 | 32 | 64 | Unplanned | Defective Equipment | burning link | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 424 | 16973 | Cromwell | CB831 | 2024-05-29 05:05 | 2024-05-29 05:07 | 0.0010395 | 0.00051976 | 50 | 100 | Unplanned | Defective Equipment | burning link | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 425 | 16967 | South City | SC12 | 2024-05-29 09:02 | 2024-05-29 14:56 | 0.23919 | 0.00067569 | 65 | 23010 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 426 | 16966 | South City | SC12 | 2024-05-29 09:02 | 2024-05-29 14:45 | 0.35299 | 0.0010291 | 99 | 33957 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 427 | 16988 | Fernhill | CB5309 | 2024-05-29 09:02 | 2024-05-29 17:27 | 0.073494 | 0.00014553 | 14 | 7070 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 428 | 16987 | Fernhill | CB5309 | 2024-05-29 09:02 | 2024-05-29 17:26 | 0.094305 | 0.00018711 | 18 | 9072 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 429 | 16989 | Fernhill | CB5309 | 2024-05-29 09:02 | 2024-05-29 17:27 | 0.10499 | 0.0002079 | 20 | 10100 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 430 | 16961 | Wanaka | CB2758 | 2024-05-29 09:03 | 2024-05-29 16:22 | 0.022818 | 5.1976e-05 | 5 | 2195 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 431 | 16962 | Wanaka | CB2758 | 2024-05-29 09:11 | 2024-05-29 16:22 | 0.022402 | 5.1976e-05 | 5 | 2155 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 432 | 16964 | Carisbrook | CK2 | 2024-05-29 10:24 | 2024-05-29 14:53 | 0.25167 | 0.00093557 | 90 | 24210 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 433 | 16998 | Alexandra | CB169 | 2024-05-29 11:08 | 2024-05-29 15:32 | 0.13996 | 0.00053016 | 51 | 13464 | Unplanned | Defective Equipment | communications equip - error/failure | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 434 | 17057 | Ettrick | CB480 | 2024-05-29 12:30 | 2024-05-29 15:30 | 0.013098 | 7.2767e-05 | 7 | 1260 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 435 | 16999 | Alexandra | CB169 | 2024-05-29 15:32 | 2024-05-29 17:16 | 0.014054 | 0.00013514 | 13 | 1352 | Unplanned | Defective Equipment | communications equip - error/failure | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 436 | 17001 | Alexandra | CB169 | 2024-05-29 15:32 | 2024-05-29 22:11 | 0.062215 | 0.00015593 | 15 | 5985 | Unplanned | Defective Equipment | communications equip - error/failure | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 437 | 17000 | Alexandra | CB169 | 2024-05-29 15:32 | 2024-05-29 22:02 | 0.093245 | 0.00023909 | 23 | 8970 | Unplanned | Defective Equipment | communications equip - error/failure | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 438 | 17002 | Alexandra | CB169 | 2024-05-29 17:16 | 2024-05-29 19:01 | 0.014054 | 0.00013514 | 13 | 1352 | Unplanned | Defective Equipment | communications equip - error/failure | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 439 | 16979 | Omakau | CB656 | 2024-05-29 17:35 | 2024-05-29 18:58 | 0.0008628 | 1.0395e-05 | 1 | 83 | Unplanned | Defective Equipment | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 440 | 17006 | Omakau | CB656 | 2024-05-29 18:55 | 2024-05-29 18:58 | 0.0026196 | 0.0008732 | 84 | 252 | Unplanned | Defective Equipment | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 441 | 17003 | Alexandra | CB169 | 2024-05-29 19:01 | 2024-05-29 19:43 | 0.0055407 | 0.00013514 | 13 | 533 | Unplanned | Defective Equipment | communications equip - error/failure | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 442 | 17004 | Alexandra | CB169 | 2024-05-29 19:43 | 2024-05-29 21:55 | 0.017838 | 0.00013514 | 13 | 1716 | Unplanned | Defective Equipment | communications equip - error/failure | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 443 | 16996 | Ettrick | CB480 | 2024-05-30 08:32 | 2024-05-30 13:41 | 0.077091 | 0.00024949 | 24 | 7416 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 444 | 17034 | Clyde-Earnscleugh | CB192 | 2024-05-30 09:02 | 2024-05-31 15:57 | 0.019283 | 1.0395e-05 | 1 | 1855 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 445 | 17036 | Clyde-Earnscleugh | CB192 | 2024-05-30 09:02 | 2024-05-31 16:15 | 0.01947 | 1.0395e-05 | 1 | 1873 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 446 | 17033 | Clyde-Earnscleugh | CB192 | 2024-05-30 09:02 | 2024-05-30 09:12 | 0.00031186 | 3.1186e-05 | 3 | 30 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 447 | 16994 | Wanaka | CB2756 | 2024-05-30 09:14 | 2024-05-30 16:50 | 0.27967 | 0.00061332 | 59 | 26904 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 448 | 16992 | Wanaka | CB2756 | 2024-05-30 09:14 | 2024-05-30 16:40 | 0.5239 | 0.0011747 | 113 | 50398 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 449 | 16995 | Clyde-Earnscleugh | CB192 | 2024-05-30 09:14 | 2024-05-30 13:34 | 0.010811 | 4.1581e-05 | 4 | 1040 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 450 | 17013 | Corstorphine | CO5 | 2024-05-30 11:50 | 2024-05-30 12:14 | 0.10735 | 0.0046675 | 449 | 10327 | Unplanned | Defective Equipment | communications equip - error/failure | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 451 | 17016 | Alexandra | CB169 | 2024-05-30 13:21 | 2024-05-30 15:46 | 0.0060292 | 4.1581e-05 | 4 | 580 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 452 | 17017 | Alexandra | CB169 | 2024-05-30 13:21 | 2024-05-30 16:02 | 0.084825 | 0.00053016 | 51 | 8160 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 453 | 17030 | St. Kilda | SK7 | 2024-05-31 08:10 | 2024-05-31 14:57 | 0.0042309 | 1.0395e-05 | 1 | 407 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 454 | 17024 | Roxburgh | CB4639 | 2024-05-31 08:33 | 2024-05-31 12:24 | 0.021612 | 9.3557e-05 | 9 | 2079 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 455 | 17025 | Andersons Bay | AB4 | 2024-05-31 08:37 | 2024-05-31 14:08 | 0.017204 | 5.1976e-05 | 5 | 1655 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 456 | 17027 | Andersons Bay | AB4 | 2024-05-31 08:56 | 2024-05-31 14:49 | 0.007339 | 2.079e-05 | 2 | 706 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 457 | 17026 | Andersons Bay | AB4 | 2024-05-31 08:56 | 2024-05-31 14:29 | 0.034616 | 0.00010395 | 10 | 3330 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 458 | 17028 | Arrowtown | CB7662 | 2024-05-31 09:05 | 2024-05-31 11:53 | 0.1205 | 0.00071727 | 69 | 11592 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 459 | 17032 | Alexandra | CB169 | 2024-05-31 09:06 | 2024-05-31 15:31 | 0.012006 | 3.1186e-05 | 3 | 1155 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 460 | 17031 | Alexandra | CB169 | 2024-05-31 09:06 | 2024-05-31 15:28 | 0.071478 | 0.00018711 | 18 | 6876 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 461 | 17035 | Clyde-Earnscleugh | CB192 | 2024-05-31 15:52 | 2024-05-31 15:57 | 0.00015593 | 3.1186e-05 | 3 | 15 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 462 | 17053 | Fernhill | CB5300 | 2024-05-31 16:39 | 2024-05-31 16:58 | 0.00019751 | 1.0395e-05 | 1 | 19 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 463 | 17039 | Lauder Flat | CB6576 | 2024-06-01 06:24 | 2024-06-01 08:33 | 0.10512 | 0.00082122 | 79 | 10112 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 464 | 17040 | Queensberry | CB2423 | 2024-06-01 06:52 | 2024-06-01 07:53 | 0.24667 | 0.0040437 | 389 | 23729 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 465 | 17042 | Queensberry | CB2423 | 2024-06-01 07:53 | 2024-06-01 08:19 | 0.038462 | 0.0015385 | 148 | 3700 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 466 | 17041 | Queensberry | CB2423 | 2024-06-01 07:53 | 2024-06-01 08:06 | 0.032568 | 0.0025052 | 241 | 3133 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 467 | 17044 | Queensberry | CB2423 | 2024-06-01 08:06 | 2024-06-01 13:31 | 0.11788 | 0.00036383 | 35 | 11340 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 468 | 17043 | Queensberry | CB2423 | 2024-06-01 08:06 | 2024-06-01 08:57 | 0.10707 | 0.0021414 | 206 | 10300 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 469 | 17045 | Queensberry | CB2423 | 2024-06-01 08:42 | 2024-06-01 08:57 | 0.023077 | 0.0015385 | 148 | 2220 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 470 | 17046 | Outram | OT1 | 2024-06-01 12:42 | 2024-06-01 14:02 | 0.0024949 | 3.1186e-05 | 3 | 240 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 471 | 17048 | Alexandra | CB168 | 2024-06-01 13:56 | 2024-06-01 14:44 | 0.58879 | 0.012266 | 1180 | 56640 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 472 | 17051 | Lauder Flat | CB6576 | 2024-06-01 16:05 | 2024-06-01 17:08 | 0.0019647 | 3.1186e-05 | 3 | 189 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 473 | 17056 | Alexandra | CB169 | 2024-06-04 09:06 | 2024-06-04 15:48 | 0.087757 | 0.0002183 | 21 | 8442 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 474 | 17073 | Wanaka | CB2758 | 2024-06-04 09:07 | 2024-06-04 17:45 | 0.026924 | 5.1976e-05 | 5 | 2590 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 475 | 17085 | East Taieri | ET2 | 2024-06-05 08:06 | 2024-06-05 15:37 | 0.0797 | 0.00017672 | 17 | 7667 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 476 | 17086 | Wanaka | CB2756 | 2024-06-05 08:40 | 2024-06-05 16:56 | 0.24233 | 0.00048858 | 47 | 23312 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 477 | 17087 | Wanaka | CB2756 | 2024-06-05 08:49 | 2024-06-05 16:56 | 0.091125 | 0.00018711 | 18 | 8766 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 478 | 17089 | Wanaka | CB2756 | 2024-06-05 08:53 | 2024-06-05 16:56 | 0.1205 | 0.00024949 | 24 | 11592 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 479 | 17075 | Port Chalmers | PC3 | 2024-06-05 09:01 | 2024-06-05 16:57 | 0.0049481 | 1.0395e-05 | 1 | 476 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 480 | 17076 | Port Chalmers | PC3 | 2024-06-05 09:01 | 2024-06-05 16:58 | 0.0049585 | 1.0395e-05 | 1 | 477 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 481 | 17077 | Port Chalmers | PC3 | 2024-06-05 09:01 | 2024-06-05 17:00 | 0.0099586 | 2.079e-05 | 2 | 958 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 482 | 17079 | Port Chalmers | PC3 | 2024-06-05 09:01 | 2024-06-05 17:02 | 0.015 | 3.1186e-05 | 3 | 1443 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 483 | 17081 | Port Chalmers | PC3 | 2024-06-05 09:01 | 2024-06-05 17:06 | 0.015125 | 3.1186e-05 | 3 | 1455 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 484 | 17082 | Port Chalmers | PC3 | 2024-06-05 09:01 | 2024-06-05 17:10 | 0.13216 | 0.00027028 | 26 | 12714 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 485 | 17074 | Port Chalmers | PC3 | 2024-06-05 09:01 | 2024-06-05 16:54 | 0.95389 | 0.0020167 | 194 | 91762 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 486 | 17129 | Wanaka | CB2752 | 2024-06-05 09:01 | 2024-06-05 17:44 | 0.01631 | 3.1186e-05 | 3 | 1569 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 487 | 17128 | Wanaka | CB2752 | 2024-06-05 09:01 | 2024-06-05 16:53 | 0.098131 | 0.0002079 | 20 | 9440 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 488 | 17107 | Halfway Bush | HB13 | 2024-06-05 09:04 | 2024-06-05 15:20 | 0.12508 | 0.00033265 | 32 | 12032 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 489 | 17106 | Halfway Bush | HB13 | 2024-06-05 09:04 | 2024-06-05 15:09 | 0.31492 | 0.0008628 | 83 | 30295 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 490 | 17105 | Halfway Bush | HB13 | 2024-06-05 09:04 | 2024-06-05 09:24 | 0.022038 | 0.0011019 | 106 | 2120 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 491 | 17072 | Frankton | CB7783 | 2024-06-05 09:09 | 2024-06-05 12:37 | 0.19676 | 0.00094597 | 91 | 18928 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 492 | 17109 | Wanaka | CB2752 | 2024-06-05 09:18 | 2024-06-05 16:51 | 0.004709 | 1.0395e-05 | 1 | 453 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 493 | 17110 | Wanaka | CB2752 | 2024-06-05 09:18 | 2024-06-05 16:51 | 0.0094181 | 2.079e-05 | 2 | 906 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 494 | 17111 | Wanaka | CB2752 | 2024-06-05 09:18 | 2024-06-05 16:52 | 0.023597 | 5.1976e-05 | 5 | 2270 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 495 | 17108 | Wanaka | CB2752 | 2024-06-05 09:18 | 2024-06-05 16:51 | 0.075345 | 0.00016632 | 16 | 7248 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 496 | 17112 | Wanaka | CB2752 | 2024-06-05 09:18 | 2024-06-05 16:51 | 0.004709 | 1.0395e-05 | 1 | 453 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 497 | 17114 | Alexandra | CB162 | 2024-06-06 08:01 | 2024-06-06 10:40 | 0.0016528 | 1.0395e-05 | 1 | 159 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 498 | 17115 | Kaikorai Valley | KV9 | 2024-06-06 08:11 | 2024-06-06 15:19 | 0.54725 | 0.0012786 | 123 | 52644 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 499 | 17120 | Andersons Bay | AB8 | 2024-06-06 08:35 | 2024-06-06 16:22 | 0.27186 | 0.00058213 | 56 | 26152 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 500 | 17119 | Port Chalmers | PC7 | 2024-06-06 09:03 | 2024-06-06 16:38 | 0.056758 | 0.00012474 | 12 | 5460 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 501 | 17118 | Port Chalmers | PC7 | 2024-06-06 09:03 | 2024-06-06 16:25 | 0.27568 | 0.00062371 | 60 | 26520 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 502 | 17117 | Port Chalmers | PC7 | 2024-06-06 09:03 | 2024-06-06 16:19 | 0.53028 | 0.0012162 | 117 | 51012 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 503 | 17122 | Cromwell | CB821 | 2024-06-06 09:12 | 2024-06-06 11:36 | 0.0014969 | 1.0395e-05 | 1 | 144 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 504 | 17121 | Ettrick | CB480 | 2024-06-06 10:00 | 2024-06-06 12:49 | 0.0035136 | 2.079e-05 | 2 | 338 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 505 | 17125 | Outram | OT3 | 2024-06-06 10:09 | 2024-06-06 13:03 | 0.0017984 | 1.0395e-05 | 1 | 173 | Unplanned | Third-party Interference | tree trimming error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 506 | 17124 | Outram | OT3 | 2024-06-06 10:09 | 2024-06-06 10:54 | 0.10932 | 0.0024845 | 239 | 10516 | Unplanned | Third-party Interference | tree trimming error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 507 | 17127 | Cromwell | CB832 | 2024-06-06 11:57 | 2024-06-06 14:45 | 0.12749 | 0.00075885 | 73 | 12264 | Unplanned | Defective Equipment | burning link | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 508 | 17116 | Alexandra | CB169 | 2024-06-06 12:07 | 2024-06-06 13:49 | 0.0010603 | 1.0395e-05 | 1 | 102 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 509 | 17143 | Willowbank | WB11 | 2024-06-06 22:11 | 2024-06-06 23:22 | 0.15721 | 0.0022142 | 213 | 15123 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 510 | 17145 | Willowbank | WB11 | 2024-06-06 23:23 | 2024-06-06 23:24 | 0.0022142 | 0.0022142 | 213 | 213 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 511 | 17147 | Willowbank | WB11 | 2024-06-06 23:24 | 2024-06-07 00:37 | 0.074097 | 0.0010291 | 99 | 7128 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 512 | 17146 | Willowbank | WB11 | 2024-06-06 23:24 | 2024-06-06 23:51 | 0.031997 | 0.0011851 | 114 | 3078 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 513 | 17148 | Willowbank | WB11 | 2024-06-06 23:51 | 2024-06-07 00:13 | 0.00045739 | 2.079e-05 | 2 | 44 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 514 | 17149 | Willowbank | WB11 | 2024-06-06 23:51 | 2024-06-07 00:31 | 0.045406 | 0.0011643 | 112 | 4368 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 515 | 17150 | Willowbank | WB11 | 2024-06-07 00:13 | 2024-06-07 00:24 | 0.0002079 | 2.079e-05 | 2 | 20 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 516 | 17139 | Port Chalmers | PC7 | 2024-06-07 08:12 | 2024-06-07 15:54 | 0.028816 | 6.2371e-05 | 6 | 2772 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 517 | 17140 | Port Chalmers | PC7 | 2024-06-07 08:12 | 2024-06-07 16:03 | 0.1322 | 0.00028067 | 27 | 12717 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 518 | 17136 | Mosgiel | MG6 | 2024-06-07 08:42 | 2024-06-07 14:36 | 0.19136 | 0.00054055 | 52 | 18408 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 519 | 17138 | Alexandra | CB169 | 2024-06-07 09:21 | 2024-06-07 14:58 | 0.073567 | 0.0002183 | 21 | 7077 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 520 | 17137 | Cromwell | CB838 | 2024-06-08 09:05 | 2024-06-08 15:20 | 0.15983 | 0.0004262 | 41 | 15375 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 521 | 17163 | Cromwell | CB838 | 2024-06-09 11:09 | 2024-06-09 12:09 | 0.034304 | 0.00057174 | 55 | 3300 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 522 | 17208 | Queenstown | CB5212 | 2024-06-10 08:19 | 2024-06-10 08:45 | 0.00054055 | 2.079e-05 | 2 | 52 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 523 | 17209 | Queenstown | CB5212 | 2024-06-10 08:24 | 2024-06-10 09:53 | 0.00092518 | 1.0395e-05 | 1 | 89 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 524 | 17173 | Alexandra | CB169 | 2024-06-10 08:39 | 2024-06-10 18:11 | 0.0059461 | 1.0395e-05 | 1 | 572 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 525 | 17172 | Alexandra | CB169 | 2024-06-10 08:39 | 2024-06-10 18:11 | 0.11892 | 0.0002079 | 20 | 11440 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 526 | 17174 | Alexandra | CB169 | 2024-06-10 08:41 | 2024-06-10 18:11 | 0.017776 | 3.1186e-05 | 3 | 1710 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 527 | 17177 | Port Chalmers | PC3 | 2024-06-10 09:10 | 2024-06-10 15:51 | 0.0041685 | 1.0395e-05 | 1 | 401 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 528 | 17176 | Port Chalmers | PC3 | 2024-06-10 09:10 | 2024-06-10 15:50 | 0.0083162 | 2.079e-05 | 2 | 800 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 529 | 17175 | Port Chalmers | PC3 | 2024-06-10 09:10 | 2024-06-10 15:46 | 0.93445 | 0.0023597 | 227 | 89892 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 530 | 17188 | Kaikorai Valley | KV6 | 2024-06-11 08:07 | 2024-06-11 14:58 | 0.46997 | 0.0011435 | 110 | 45210 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 531 | 17252 | Queenstown | CB5212 | 2024-06-11 08:07 | 2024-06-11 18:05 | 0.018649 | 3.1186e-05 | 3 | 1794 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 532 | 17251 | Queenstown | CB5212 | 2024-06-11 08:07 | 2024-06-11 17:44 | 0.15595 | 0.00027028 | 26 | 15002 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 533 | 17250 | Queenstown | CB5212 | 2024-06-11 08:07 | 2024-06-11 17:35 | 0.46055 | 0.00081083 | 78 | 44304 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 534 | 17181 | Green Island | GI6 | 2024-06-11 08:20 | 2024-06-11 16:15 | 0.14319 | 0.00030146 | 29 | 13775 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 535 | 17183 | Ettrick | CB480 | 2024-06-11 08:31 | 2024-06-11 14:24 | 0.088068 | 0.00024949 | 24 | 8472 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 536 | 17184 | Frankton | CB7789 | 2024-06-11 08:41 | 2024-06-11 09:33 | 0.023784 | 0.00045739 | 44 | 2288 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 537 | 17180 | Green Island | GI6 | 2024-06-11 08:46 | 2024-06-11 08:51 | 0.0028587 | 0.00057174 | 55 | 275 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 538 | 17185 | Lindis Crossing | CB2084 | 2024-06-11 09:00 | 2024-06-11 13:55 | 0.039866 | 0.00013514 | 13 | 3835 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 539 | 17186 | Wanaka | CB2753 | 2024-06-11 09:01 | 2024-06-11 16:44 | 0.086634 | 0.00018711 | 18 | 8334 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 540 | 17187 | Wanaka | CB2753 | 2024-06-11 09:01 | 2024-06-11 16:50 | 0.17064 | 0.00036383 | 35 | 16415 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 541 | 17192 | Outram | OT2 | 2024-06-11 09:04 | 2024-06-11 15:35 | 0.024387 | 6.2371e-05 | 6 | 2346 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 542 | 17190 | Outram | OT2 | 2024-06-11 09:04 | 2024-06-11 15:22 | 0.051082 | 0.00013514 | 13 | 4914 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 543 | 17191 | Outram | OT2 | 2024-06-11 09:04 | 2024-06-11 15:34 | 0.052704 | 0.00013514 | 13 | 5070 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 544 | 17201 | East Taieri | ET5 | 2024-06-11 09:13 | 2024-06-11 10:35 | 0.0025572 | 3.1186e-05 | 3 | 246 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 545 | 17189 | East Taieri | ET3 | 2024-06-11 12:21 | 2024-06-11 13:05 | 0.00045739 | 1.0395e-05 | 1 | 44 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 546 | 17182 | Green Island | GI6 | 2024-06-11 16:10 | 2024-06-11 16:22 | 0.0068608 | 0.00057174 | 55 | 660 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 547 | 17239 | Port Chalmers | PC7 | 2024-06-12 08:02 | 2024-06-12 17:46 | 0.036425 | 6.2371e-05 | 6 | 3504 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 548 | 17240 | Port Chalmers | PC7 | 2024-06-12 08:02 | 2024-06-12 17:52 | 0.1656 | 0.00028067 | 27 | 15930 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 549 | 17260 | Halfway Bush | HB13 | 2024-06-12 10:12 | 2024-06-12 11:15 | 0.054357 | 0.0008628 | 83 | 5229 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 550 | 17216 | Lindis Crossing | CB2084 | 2024-06-12 12:45 | 2024-06-12 14:19 | 0.032246 | 0.00034304 | 33 | 3102 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 551 | 17218 | East Taieri | ET8 | 2024-06-12 12:50 | 2024-06-12 13:41 | 0.00053016 | 1.0395e-05 | 1 | 51 | Unplanned | Defective Equipment | faulty transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 552 | 17220 | East Taieri | ET8 | 2024-06-12 14:15 | 2024-06-12 16:34 | 0.0014449 | 1.0395e-05 | 1 | 139 | Unplanned | Defective Equipment | faulty transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 553 | 17221 | East Taieri | ET8 | 2024-06-12 15:35 | 2024-06-12 16:33 | 0.0018088 | 3.1186e-05 | 3 | 174 | Unplanned | Defective Equipment | faulty transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 554 | 17255 | Queenstown | CB5212 | 2024-06-12 16:50 | 2024-06-12 17:00 | 0.00010395 | 1.0395e-05 | 1 | 10 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 555 | 17256 | Queenstown | CB5212 | 2024-06-12 16:50 | 2024-06-12 17:08 | 0.00018711 | 1.0395e-05 | 1 | 18 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 556 | 17223 | Arrowtown | CB7662 | 2024-06-12 17:34 | 2024-06-12 22:26 | 0.20944 | 0.00071727 | 69 | 20148 | Unplanned | Defective Equipment | hv isolation for lv fuse replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 557 | 17225 | Ward Street | WS4 | 2024-06-13 00:12 | 2024-06-13 01:17 | 0.0073182 | 0.00011435 | 11 | 704 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 558 | 17227 | Ward Street | WS4 | 2024-06-13 00:12 | 2024-06-13 06:39 | 0.22872 | 0.00059253 | 57 | 22002 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 559 | 17226 | Ward Street | WS4 | 2024-06-13 00:12 | 2024-06-13 03:11 | 0.44964 | 0.002526 | 243 | 43254 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 560 | 17245 | Wanaka | CB2752 | 2024-06-13 09:03 | 2024-06-13 16:32 | 0.0046675 | 1.0395e-05 | 1 | 449 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 561 | 17246 | Wanaka | CB2752 | 2024-06-13 09:03 | 2024-06-13 16:32 | 0.0046675 | 1.0395e-05 | 1 | 449 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 562 | 17244 | Wanaka | CB2752 | 2024-06-13 09:03 | 2024-06-13 16:19 | 0.0090646 | 2.079e-05 | 2 | 872 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 563 | 17242 | Wanaka | CB2752 | 2024-06-13 09:03 | 2024-06-13 16:08 | 0.15905 | 0.00037423 | 36 | 15300 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 564 | 17241 | Wanaka | CB2752 | 2024-06-13 09:03 | 2024-06-13 09:10 | 0.0045843 | 0.0006549 | 63 | 441 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 565 | 17206 | Omakau | CB656 | 2024-06-13 09:04 | 2024-06-13 15:11 | 0.003815 | 1.0395e-05 | 1 | 367 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 566 | 17249 | Outram | OT2 | 2024-06-13 09:11 | 2024-06-13 15:38 | 0.024138 | 6.2371e-05 | 6 | 2322 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 567 | 17247 | Outram | OT2 | 2024-06-13 09:11 | 2024-06-13 15:22 | 0.050136 | 0.00013514 | 13 | 4823 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 568 | 17248 | Outram | OT2 | 2024-06-13 09:11 | 2024-06-13 15:38 | 0.052298 | 0.00013514 | 13 | 5031 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 569 | 17211 | Frankton | CB7790 | 2024-06-13 09:20 | 2024-06-13 18:26 | 0.0056654 | 1.0395e-05 | 1 | 545 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 570 | 17210 | Frankton | CB7790 | 2024-06-13 09:20 | 2024-06-13 16:41 | 0.34304 | 0.00077964 | 75 | 33000 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 571 | 17243 | Wanaka | CB2752 | 2024-06-13 16:02 | 2024-06-13 16:08 | 0.0039294 | 0.0006549 | 63 | 378 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 572 | 17262 | Green Island | GI11 | 2024-06-14 08:39 | 2024-06-14 14:31 | 0.0036591 | 1.0395e-05 | 1 | 352 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 573 | 17257 | Omakau | CB656 | 2024-06-14 09:03 | 2024-06-14 13:53 | 0.0030146 | 1.0395e-05 | 1 | 290 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 574 | 17259 | East Taieri | ET9 | 2024-06-14 10:05 | 2024-06-14 14:22 | 0.090833 | 0.00035344 | 34 | 8738 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 575 | 17258 | Ward Street | WS12 | 2024-06-15 08:02 | 2024-06-15 15:03 | 0.21007 | 0.00049897 | 48 | 20208 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 576 | 17359 | Andersons Bay | AB4 | 2024-06-15 09:22 | 2024-06-15 10:21 | 0.0072351 | 0.00012474 | 12 | 696 | Unplanned | Defective Equipment | burnt connector | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 577 | 17285 | South City | SC14 | 2024-06-17 17:42 | 2024-06-17 21:39 | 0.1084 | 0.00045739 | 44 | 10428 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 578 | 17318 | Berwick | BK2 | 2024-06-17 17:48 | 2024-06-18 11:32 | 0.011061 | 1.0395e-05 | 1 | 1064 | Unplanned | Defective Equipment | faulty transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 579 | 17293 | South City | SC12 | 2024-06-18 06:03 | 2024-06-18 06:17 | 0.011352 | 0.00081083 | 78 | 1092 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 580 | 17294 | South City | SC12 | 2024-06-18 06:33 | 2024-06-18 06:43 | 0.0071727 | 0.00071727 | 69 | 690 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 581 | 17299 | Green Island | GI6 | 2024-06-18 06:56 | 2024-06-18 07:55 | 0.0030666 | 5.1976e-05 | 5 | 295 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 582 | 17287 | Wanaka | CB2752 | 2024-06-18 09:01 | 2024-06-18 16:18 | 0.018171 | 4.1581e-05 | 4 | 1748 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 583 | 17289 | Outram | OT2 | 2024-06-18 09:09 | 2024-06-18 16:53 | 0.062704 | 0.00013514 | 13 | 6032 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 584 | 17288 | Outram | OT2 | 2024-06-18 09:20 | 2024-06-18 16:45 | 0.0046259 | 1.0395e-05 | 1 | 445 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 585 | 17290 | Outram | OT2 | 2024-06-18 09:20 | 2024-06-18 16:59 | 0.0047714 | 1.0395e-05 | 1 | 459 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 586 | 17291 | Outram | OT2 | 2024-06-18 09:20 | 2024-06-18 17:07 | 0.0097091 | 2.079e-05 | 2 | 934 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 587 | 17292 | Wanaka | CB2757 | 2024-06-18 10:00 | 2024-06-18 10:38 | 0.023306 | 0.00061332 | 59 | 2242 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 588 | 17301 | Camp Hill | CB2006 | 2024-06-18 11:00 | 2024-06-18 15:37 | 0.0028795 | 1.0395e-05 | 1 | 277 | Unplanned | Wildlife | animal in equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 589 | 17307 | Camp Hill | CB2006 | 2024-06-18 12:14 | 2024-06-18 15:37 | 0.0021102 | 1.0395e-05 | 1 | 203 | Unplanned | Wildlife | animal in equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 590 | 17295 | South City | SC12 | 2024-06-18 15:30 | 2024-06-18 15:46 | 0.012973 | 0.00081083 | 78 | 1248 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 591 | 17296 | South City | SC12 | 2024-06-18 15:46 | 2024-06-18 15:51 | 0.0035864 | 0.00071727 | 69 | 345 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 592 | 17321 | Clyde-Earnscleugh | CB192 | 2024-06-18 21:47 | 2024-06-18 23:58 | 0.15 | 0.0011539 | 111 | 14430 | Unplanned | Defective Equipment | communications equip - error/failure | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 593 | 17322 | Clyde-Earnscleugh | CB192 | 2024-06-18 23:58 | 2024-06-18 23:59 | 0.0011539 | 0.0011539 | 111 | 111 | Unplanned | Defective Equipment | communications equip - error/failure | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 594 | 17523 | Commonage | CB5732 | 2024-06-19 09:00 | 2024-06-19 09:03 | 0.015905 | 0.0053016 | 510 | 1530 | Unplanned | Human Error | incorrect records | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 595 | 17316 | Cromwell | CB831 | 2024-06-19 09:04 | 2024-06-19 15:03 | 0.14554 | 0.00040541 | 39 | 14001 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 596 | 17326 | Commonage | CB5733 | 2024-06-19 10:16 | 2024-06-19 10:18 | 0.0062475 | 0.0062475 | 601 | 601 | Unplanned | Third-party Interference | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 597 | 17338 | Outram | OT3 | 2024-06-19 13:29 | 2024-06-19 14:22 | 0.021487 | 0.00040541 | 39 | 2067 | Unplanned | Defective Equipment | failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 598 | 17319 | Berwick | BK2 | 2024-06-19 14:09 | 2024-06-19 14:33 | 0.00024949 | 1.0395e-05 | 1 | 24 | Unplanned | Defective Equipment | faulty transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 599 | 17314 | Lauder Flat | CB6576 | 2024-06-20 08:37 | 2024-06-20 08:58 | 0.0041477 | 0.00019751 | 19 | 399 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 600 | 17313 | Halfway Bush | HB9 | 2024-06-20 08:43 | 2024-06-20 17:15 | 0.36192 | 0.00070688 | 68 | 34816 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 601 | 17317 | Wanaka | CB2757 | 2024-06-20 09:00 | 2024-06-20 15:10 | 0.22693 | 0.00061332 | 59 | 21830 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 602 | 17310 | Kaikorai Valley | KV5 | 2024-06-20 09:10 | 2024-06-20 09:14 | 0.0037423 | 0.00093557 | 90 | 360 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 603 | 17342 | Lauder Flat | CB6576 | 2024-06-20 09:12 | 2024-06-20 14:42 | 0.12693 | 0.00038462 | 37 | 12210 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 604 | 17311 | Kaikorai Valley | KV5 | 2024-06-20 09:17 | 2024-06-20 16:21 | 0.28208 | 0.00066529 | 64 | 27136 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 605 | 17346 | Fernhill | CB5309 | 2024-06-20 09:43 | 2024-06-20 09:49 | 0.0014969 | 0.00024949 | 24 | 144 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 606 | 17347 | Fernhill | CB5309 | 2024-06-20 10:00 | 2024-06-20 10:04 | 0.00054055 | 0.00013514 | 13 | 52 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 607 | 17348 | Fernhill | CB5309 | 2024-06-20 10:43 | 2024-06-20 11:11 | 0.0011643 | 4.1581e-05 | 4 | 112 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 608 | 17349 | Fernhill | CB5309 | 2024-06-20 11:16 | 2024-06-20 11:18 | 0.00012474 | 6.2371e-05 | 6 | 12 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 609 | 17350 | Fernhill | CB5309 | 2024-06-20 11:45 | 2024-06-20 11:53 | 8.3162e-05 | 1.0395e-05 | 1 | 8 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 610 | 17352 | Fernhill | CB5309 | 2024-06-20 12:49 | 2024-06-20 13:03 | 0.0032017 | 0.00022869 | 22 | 308 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 611 | 17351 | Fernhill | CB5309 | 2024-06-20 12:52 | 2024-06-20 12:57 | 0.00036383 | 7.2767e-05 | 7 | 35 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 612 | 17353 | Fernhill | CB5309 | 2024-06-20 13:02 | 2024-06-20 13:06 | 4.1581e-05 | 1.0395e-05 | 1 | 4 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 613 | 17354 | Fernhill | CB5309 | 2024-06-20 13:32 | 2024-06-20 13:42 | 0.00010395 | 1.0395e-05 | 1 | 10 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 614 | 17355 | Fernhill | CB5309 | 2024-06-20 14:22 | 2024-06-20 14:38 | 0.0016632 | 0.00010395 | 10 | 160 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 615 | 17356 | Fernhill | CB5309 | 2024-06-20 14:38 | 2024-06-20 14:42 | 0.00029107 | 7.2767e-05 | 7 | 28 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 616 | 17357 | Fernhill | CB5309 | 2024-06-20 15:00 | 2024-06-20 15:04 | 8.3162e-05 | 2.079e-05 | 2 | 8 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 617 | 17315 | Lauder Flat | CB6576 | 2024-06-20 15:04 | 2024-06-20 15:22 | 0.0035552 | 0.00019751 | 19 | 342 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 618 | 17358 | Fernhill | CB5309 | 2024-06-20 15:09 | 2024-06-20 15:18 | 0.00037423 | 4.1581e-05 | 4 | 36 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 619 | 17312 | Kaikorai Valley | KV5 | 2024-06-20 17:02 | 2024-06-20 17:08 | 0.0056134 | 0.00093557 | 90 | 540 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 620 | 17416 | Ward Street | WS10 | 2024-06-21 08:43 | 2024-06-21 17:15 | 0.0053224 | 1.0395e-05 | 1 | 512 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 621 | 17370 | Commonage | CB5730 | 2024-06-21 10:03 | 2024-06-21 13:38 | 0.28831 | 0.001341 | 129 | 27735 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 622 | 17369 | Commonage | CB5730 | 2024-06-21 10:05 | 2024-06-21 13:28 | 0.13083 | 0.0006445 | 62 | 12586 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 623 | 17360 | Outram | OT1 | 2024-06-21 11:06 | 2024-06-21 11:31 | 0.00025988 | 1.0395e-05 | 1 | 25 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 624 | 17365 | Fernhill | CB5308 | 2024-06-21 20:22 | 2024-06-21 20:59 | 0.41427 | 0.011508 | 1107 | 39852 | Unplanned | Defective Equipment | hv isolation for lv fuse replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 625 | 19361 | Clyde-Earnscleugh | CB199 | 2024-06-22 10:37 | 2024-06-22 14:44 | 0.0051352 | 2.079e-05 | 2 | 494 | Unplanned | Defective Equipment | broken lead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 626 | 17390 | Green Island | GI3 | 2024-06-24 07:41 | 2024-06-24 08:11 | 0.00031186 | 1.0395e-05 | 1 | 30 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 627 | 17393 | Green Island | GI3 | 2024-06-24 08:03 | 2024-06-24 15:43 | 0.0047818 | 1.0395e-05 | 1 | 460 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 628 | 17392 | Green Island | GI3 | 2024-06-24 08:03 | 2024-06-24 15:30 | 0.40891 | 0.00091478 | 88 | 39336 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 629 | 17391 | Green Island | GI3 | 2024-06-24 08:12 | 2024-06-24 15:24 | 0.46704 | 0.0010811 | 104 | 44928 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 630 | 17372 | East Taieri | ET3 | 2024-06-24 09:58 | 2024-06-24 12:11 | 0.0027651 | 2.079e-05 | 2 | 266 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 631 | 17371 | Cromwell | CB838 | 2024-06-24 10:07 | 2024-06-24 12:30 | 0.081758 | 0.00057174 | 55 | 7865 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 632 | 17394 | Green Island | GI3 | 2024-06-24 16:17 | 2024-06-24 16:25 | 8.3162e-05 | 1.0395e-05 | 1 | 8 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 633 | 17401 | East Taieri | ET9 | 2024-06-25 08:02 | 2024-06-25 14:19 | 0.14892 | 0.00039502 | 38 | 14326 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 634 | 17395 | North City | NC6 | 2024-06-25 08:05 | 2024-06-25 16:10 | 0.23696 | 0.00048858 | 47 | 22795 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 635 | 17396 | Lauder Flat | CB6576 | 2024-06-25 08:35 | 2024-06-25 12:39 | 0.010146 | 4.1581e-05 | 4 | 976 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 636 | 17398 | Outram | OT2 | 2024-06-25 09:03 | 2024-06-25 15:07 | 0.04919 | 0.00013514 | 13 | 4732 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 637 | 17400 | Camp Hill | CB2004 | 2024-06-25 09:04 | 2024-06-25 14:07 | 0.0031498 | 1.0395e-05 | 1 | 303 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 638 | 17399 | Outram | OT2 | 2024-06-25 09:08 | 2024-06-25 15:12 | 0.0037839 | 1.0395e-05 | 1 | 364 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 639 | 17397 | Outram | OT2 | 2024-06-25 09:08 | 2024-06-25 15:02 | 0.01104 | 3.1186e-05 | 3 | 1062 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 640 | 17457 | Mosgiel | MG6 | 2024-06-26 07:40 | 2024-06-26 07:42 | 6.2371e-05 | 3.1186e-05 | 3 | 6 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 641 | 17458 | Mosgiel | MG6 | 2024-06-26 07:43 | 2024-06-26 07:45 | 0.00010395 | 5.1976e-05 | 5 | 10 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 642 | 17459 | Mosgiel | MG6 | 2024-06-26 07:54 | 2024-06-26 07:58 | 4.1581e-05 | 1.0395e-05 | 1 | 4 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 643 | 17451 | Arrowtown | CB7632 | 2024-06-26 08:30 | 2024-06-26 08:35 | 5.1976e-05 | 1.0395e-05 | 1 | 5 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 644 | 17407 | Lauder Flat | CB6576 | 2024-06-26 08:36 | 2024-06-26 13:50 | 0.013056 | 4.1581e-05 | 4 | 1256 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 645 | 17452 | Arrowtown | CB7632 | 2024-06-26 08:38 | 2024-06-26 08:47 | 0.00018711 | 2.079e-05 | 2 | 18 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 646 | 17409 | Outram | OT4 | 2024-06-26 08:47 | 2024-06-26 15:08 | 0.12278 | 0.00032225 | 31 | 11811 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 647 | 17460 | Mosgiel | MG6 | 2024-06-26 08:57 | 2024-06-26 09:04 | 0.0050209 | 0.00071727 | 69 | 483 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 648 | 17408 | Outram | OT3 | 2024-06-26 09:02 | 2024-06-26 13:36 | 0.014241 | 5.1976e-05 | 5 | 1370 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 649 | 17410 | Camp Hill | CB2006 | 2024-06-26 09:02 | 2024-06-26 14:47 | 0.22594 | 0.0006549 | 63 | 21735 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 650 | 17411 | Kaikorai Valley | KV5 | 2024-06-26 09:05 | 2024-06-26 16:28 | 0.41446 | 0.00093557 | 90 | 39870 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 651 | 17450 | Arrowtown | CB7632 | 2024-06-26 09:06 | 2024-06-26 15:16 | 0.011539 | 3.1186e-05 | 3 | 1110 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 652 | 17462 | Mosgiel | MG6 | 2024-06-26 14:54 | 2024-06-26 14:59 | 0.0027028 | 0.00054055 | 52 | 260 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 653 | 17461 | Mosgiel | MG6 | 2024-06-26 14:55 | 2024-06-26 14:58 | 0.00053016 | 0.00017672 | 17 | 51 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 654 | 17454 | Arrowtown | CB7632 | 2024-06-26 17:00 | 2024-06-26 17:03 | 3.1186e-05 | 1.0395e-05 | 1 | 3 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 655 | 17456 | Arrowtown | CB7632 | 2024-06-26 17:00 | 2024-06-26 17:15 | 0.00031186 | 2.079e-05 | 2 | 30 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 656 | 17455 | Arrowtown | CB7632 | 2024-06-26 17:01 | 2024-06-26 17:13 | 0.00024949 | 2.079e-05 | 2 | 24 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 657 | 17463 | Mosgiel | MG6 | 2024-06-26 17:01 | 2024-06-26 17:03 | 6.2371e-05 | 3.1186e-05 | 3 | 6 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 658 | 17464 | Mosgiel | MG6 | 2024-06-26 17:12 | 2024-06-26 17:14 | 2.079e-05 | 1.0395e-05 | 1 | 2 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 659 | 17465 | Mosgiel | MG6 | 2024-06-26 17:15 | 2024-06-26 17:18 | 0.00015593 | 5.1976e-05 | 5 | 15 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 660 | 17422 | Green Island | GI6 | 2024-06-27 08:34 | 2024-06-27 15:48 | 0.099254 | 0.00022869 | 22 | 9548 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 661 | 17423 | Green Island | GI6 | 2024-06-27 08:34 | 2024-06-27 16:00 | 0.25036 | 0.00056134 | 54 | 24084 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 662 | 17421 | Kaikorai Valley | KV5 | 2024-06-27 09:08 | 2024-06-27 13:35 | 0.12767 | 0.00047818 | 46 | 12282 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 663 | 17440 | Queensberry | CB2423 | 2024-06-29 15:31 | 2024-06-29 16:16 | 0.041633 | 0.00092518 | 89 | 4005 | Unplanned | Defective Equipment | broken tie wire (floater) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 664 | 17446 | East Taieri | ET3 | 2024-07-01 09:14 | 2024-07-01 09:40 | 0.00027028 | 1.0395e-05 | 1 | 26 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 665 | 17471 | Smith Street | SS10 | 2024-07-02 01:04 | 2024-07-02 01:10 | 0.0033784 | 0.00067569 | 65 | 325 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 666 | 17474 | Corstorphine | CO7 | 2024-07-02 02:09 | 2024-07-02 11:00 | 0.28703 | 0.00054055 | 52 | 27612 | Unplanned | Defective Equipment | broken lead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 667 | 17475 | Corstorphine | CO7 | 2024-07-02 02:35 | 2024-07-02 08:09 | 0.027693 | 8.3162e-05 | 8 | 2664 | Unplanned | Defective Equipment | broken lead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 668 | 17472 | Smith Street | SS10 | 2024-07-02 03:36 | 2024-07-02 03:38 | 0.00070688 | 0.00035344 | 34 | 68 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 669 | 17473 | Smith Street | SS10 | 2024-07-02 05:18 | 2024-07-02 05:20 | 0.00070688 | 0.00035344 | 34 | 68 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 670 | 17477 | Corstorphine | CO7 | 2024-07-02 07:25 | 2024-07-02 11:00 | 0.25032 | 0.0011643 | 112 | 24080 | Unplanned | Defective Equipment | broken lead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 671 | 17476 | Corstorphine | CO7 | 2024-07-02 07:25 | 2024-07-02 07:30 | 0.016476 | 0.0032953 | 317 | 1585 | Unplanned | Defective Equipment | broken lead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 672 | 17468 | Port Chalmers | PC7 | 2024-07-02 08:34 | 2024-07-02 18:53 | 0.0064346 | 1.0395e-05 | 1 | 619 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 673 | 17493 | Mosgiel | MG6 | 2024-07-02 08:56 | 2024-07-02 17:32 | 0.0053639 | 1.0395e-05 | 1 | 516 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 674 | 17494 | Mosgiel | MG6 | 2024-07-02 08:56 | 2024-07-02 17:36 | 0.010811 | 2.079e-05 | 2 | 1040 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 675 | 17495 | Mosgiel | MG6 | 2024-07-02 08:56 | 2024-07-02 17:38 | 0.027132 | 5.1976e-05 | 5 | 2610 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 676 | 17466 | Lindis Crossing | CB2082 | 2024-07-02 09:05 | 2024-07-02 12:53 | 0.011851 | 5.1976e-05 | 5 | 1140 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 677 | 17490 | Mosgiel | MG6 | 2024-07-02 09:10 | 2024-07-02 09:19 | 0.00046779 | 5.1976e-05 | 5 | 45 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 678 | 17496 | Mosgiel | MG6 | 2024-07-02 09:10 | 2024-07-02 17:41 | 0.031872 | 6.2371e-05 | 6 | 3066 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 679 | 17491 | Mosgiel | MG6 | 2024-07-02 09:10 | 2024-07-02 17:21 | 0.40322 | 0.00082122 | 79 | 38789 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 680 | 17901 | Corstorphine | CO7 | 2024-07-02 10:43 | 2024-07-02 11:00 | 0.0014138 | 8.3162e-05 | 8 | 136 | Unplanned | Defective Equipment | broken lead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 681 | 17974 | Roxburgh | HSB33 | 2024-07-02 13:09 | 2024-07-02 13:22 | 0.00027028 | 2.079e-05 | 2 | 26 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 682 | 17469 | East Taieri | ET9 | 2024-07-03 08:01 | 2024-07-03 11:51 | 0.35146 | 0.0015281 | 147 | 33810 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 683 | 17470 | Alexandra | CB168 | 2024-07-03 09:07 | 2024-07-03 15:02 | 0.0073806 | 2.079e-05 | 2 | 710 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 684 | 17467 | Outram | OT3 | 2024-07-03 09:10 | 2024-07-03 14:28 | 0.0033057 | 1.0395e-05 | 1 | 318 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 685 | 17508 | Alexandra | CB168 | 2024-07-04 08:33 | 2024-07-04 13:25 | 0.0060708 | 2.079e-05 | 2 | 584 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 686 | 17529 | Mosgiel | MG6 | 2024-07-04 08:57 | 2024-07-04 16:54 | 0.009917 | 2.079e-05 | 2 | 954 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 687 | 17525 | Mosgiel | MG6 | 2024-07-04 08:57 | 2024-07-04 09:06 | 0.00046779 | 5.1976e-05 | 5 | 45 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 688 | 17531 | Mosgiel | MG6 | 2024-07-04 08:57 | 2024-07-04 16:55 | 0.039751 | 8.3162e-05 | 8 | 3824 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 689 | 17532 | Mosgiel | MG6 | 2024-07-04 08:57 | 2024-07-04 17:00 | 0.040167 | 8.3162e-05 | 8 | 3864 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 690 | 17526 | Mosgiel | MG6 | 2024-07-04 08:57 | 2024-07-04 16:47 | 0.36643 | 0.00077964 | 75 | 35250 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 691 | 17497 | East Taieri | ET9 | 2024-07-04 09:02 | 2024-07-04 09:14 | 0.0051145 | 0.0004262 | 41 | 492 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 692 | 17498 | East Taieri | ET9 | 2024-07-04 10:03 | 2024-07-04 10:15 | 0.0058629 | 0.00048858 | 47 | 564 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 693 | 17499 | East Taieri | ET9 | 2024-07-04 11:02 | 2024-07-04 11:08 | 0.0014345 | 0.00023909 | 23 | 138 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 694 | 17500 | East Taieri | ET9 | 2024-07-04 13:00 | 2024-07-04 13:09 | 0.0022454 | 0.00024949 | 24 | 216 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 695 | 17501 | East Taieri | ET9 | 2024-07-04 14:02 | 2024-07-04 14:10 | 0.0031601 | 0.00039502 | 38 | 304 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 696 | 17527 | Mosgiel | MG6 | 2024-07-04 16:40 | 2024-07-04 16:47 | 0.00036383 | 5.1976e-05 | 5 | 35 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 697 | 17536 | Port Chalmers | PC7 | 2024-07-05 08:55 | 2024-07-05 15:16 | 0.031685 | 8.3162e-05 | 8 | 3048 | Planned | Planned interruption | tree trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 698 | 17557 | Outram | OT3 | 2024-07-05 09:07 | 2024-07-05 14:58 | 0.0072974 | 2.079e-05 | 2 | 702 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 699 | 17556 | Outram | OT3 | 2024-07-05 09:07 | 2024-07-05 14:50 | 0.021393 | 6.2371e-05 | 6 | 2058 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 700 | 17549 | Frankton | CB7782 | 2024-07-07 11:35 | 2024-07-07 13:15 | 0.0010395 | 1.0395e-05 | 1 | 100 | Unplanned | Wildlife | animal in equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 701 | 17554 | East Taieri | ET4 | 2024-07-07 11:46 | 2024-07-07 13:36 | 0.0022869 | 2.079e-05 | 2 | 220 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 702 | 17550 | Frankton | CB7782 | 2024-07-07 12:59 | 2024-07-07 13:18 | 0.00019751 | 1.0395e-05 | 1 | 19 | Unplanned | Wildlife | animal in equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 703 | 17559 | East Taieri | ET7 | 2024-07-08 08:23 | 2024-07-08 16:43 | 0.71207 | 0.0014241 | 137 | 68500 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 704 | 17558 | Corstorphine | CO7 | 2024-07-08 08:44 | 2024-07-08 12:41 | 0.27593 | 0.0011643 | 112 | 26544 | Planned | Planned interruption | tree trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 705 | 17560 | Outram | OT2 | 2024-07-08 18:06 | 2024-07-08 20:19 | 0.0069128 | 5.1976e-05 | 5 | 665 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 706 | 17574 | Frankton | CB7783 | 2024-07-08 22:05 | 2024-07-09 04:45 | 0.0041581 | 1.0395e-05 | 1 | 400 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 707 | 17575 | Frankton | CB7783 | 2024-07-08 22:05 | 2024-07-09 04:52 | 0.0084617 | 2.079e-05 | 2 | 814 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 708 | 17602 | East Taieri | ET4 | 2024-07-09 08:34 | 2024-07-09 16:51 | 0.0051664 | 1.0395e-05 | 1 | 497 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 709 | 17605 | East Taieri | ET4 | 2024-07-09 08:34 | 2024-07-09 16:58 | 0.0052392 | 1.0395e-05 | 1 | 504 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 710 | 17598 | East Taieri | ET4 | 2024-07-09 08:34 | 2024-07-09 08:39 | 0.00025988 | 5.1976e-05 | 5 | 25 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 711 | 17599 | East Taieri | ET4 | 2024-07-09 08:34 | 2024-07-09 16:42 | 0.3551 | 0.00072767 | 70 | 34160 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 712 | 17608 | Roxburgh | CB4633 | 2024-07-09 09:02 | 2024-07-09 16:30 | 0.0046571 | 1.0395e-05 | 1 | 448 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 713 | 17607 | Roxburgh | CB4633 | 2024-07-09 09:02 | 2024-07-09 16:09 | 0.17311 | 0.00040541 | 39 | 16653 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 714 | 17601 | East Taieri | ET4 | 2024-07-09 16:27 | 2024-07-09 16:42 | 0.00077964 | 5.1976e-05 | 5 | 75 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 715 | 17588 | Omakau | CB656 | 2024-07-09 17:05 | 2024-07-09 18:45 | 0.0010395 | 1.0395e-05 | 1 | 100 | Unplanned | Wildlife | animal in equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 716 | 17610 | Arrowtown | CB7632 | 2024-07-10 07:40 | 2024-07-10 07:48 | 0.00016632 | 2.079e-05 | 2 | 16 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 717 | 17583 | Green Island | GI11 | 2024-07-10 08:02 | 2024-07-10 14:12 | 0.17308 | 0.00046779 | 45 | 16650 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 718 | 17612 | Arrowtown | CB7632 | 2024-07-10 08:03 | 2024-07-10 15:56 | 0.014751 | 3.1186e-05 | 3 | 1419 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 719 | 17582 | Mosgiel | MG6 | 2024-07-10 09:04 | 2024-07-10 11:40 | 0.0081083 | 5.1976e-05 | 5 | 780 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 720 | 17580 | Cromwell | CB821 | 2024-07-10 09:36 | 2024-07-10 11:44 | 0.0079835 | 6.2371e-05 | 6 | 768 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 721 | 17750 | Cromwell | CB821 | 2024-07-10 09:36 | 2024-07-10 11:44 | 0.0013306 | 1.0395e-05 | 1 | 128 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 722 | 17596 | Wanaka | CB2751 | 2024-07-10 14:34 | 2024-07-10 15:16 | 0.032308 | 0.00076925 | 74 | 3108 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 723 | 17614 | Arrowtown | CB7632 | 2024-07-10 17:10 | 2024-07-10 17:11 | 2.079e-05 | 2.079e-05 | 2 | 2 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 724 | 17628 | Arrowtown | CB7632 | 2024-07-11 07:30 | 2024-07-11 07:46 | 0.00033265 | 2.079e-05 | 2 | 32 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 725 | 17641 | St. Kilda | SK10 | 2024-07-11 07:53 | 2024-07-11 08:00 | 7.2767e-05 | 1.0395e-05 | 1 | 7 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 726 | 17645 | St. Kilda | SK10 | 2024-07-11 08:00 | 2024-07-11 08:20 | 0.0002079 | 1.0395e-05 | 1 | 20 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 727 | 17629 | Arrowtown | CB7632 | 2024-07-11 08:01 | 2024-07-11 17:01 | 0.01684 | 3.1186e-05 | 3 | 1620 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 728 | 17617 | Mosgiel | MG6 | 2024-07-11 08:20 | 2024-07-11 08:37 | 0.0091894 | 0.00054055 | 52 | 884 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 729 | 17646 | St. Kilda | SK10 | 2024-07-11 08:37 | 2024-07-11 15:41 | 0.77133 | 0.0018192 | 175 | 74200 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 730 | 17618 | Mosgiel | MG6 | 2024-07-11 08:41 | 2024-07-11 13:50 | 0.054606 | 0.00017672 | 17 | 5253 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 731 | 17616 | Roxburgh | CB4633 | 2024-07-11 09:06 | 2024-07-11 14:43 | 0.014013 | 4.1581e-05 | 4 | 1348 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 732 | 17663 | Wanaka | CB2758 | 2024-07-11 12:16 | 2024-07-11 15:42 | 0.021414 | 0.00010395 | 10 | 2060 | Unplanned | Adverse Environment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 733 | 17619 | Mosgiel | MG6 | 2024-07-11 17:02 | 2024-07-11 17:09 | 0.0037839 | 0.00054055 | 52 | 364 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 734 | 17631 | Arrowtown | CB7632 | 2024-07-11 18:00 | 2024-07-11 18:10 | 0.0002079 | 2.079e-05 | 2 | 20 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 735 | 17632 | Arrowtown | CB7632 | 2024-07-11 18:00 | 2024-07-11 18:18 | 0.00037423 | 2.079e-05 | 2 | 36 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 736 | 17648 | St. Kilda | SK10 | 2024-07-11 18:00 | 2024-07-11 18:18 | 0.00018711 | 1.0395e-05 | 1 | 18 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 737 | 17630 | Arrowtown | CB7632 | 2024-07-11 18:01 | 2024-07-11 18:02 | 1.0395e-05 | 1.0395e-05 | 1 | 1 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 738 | 17643 | St. Kilda | SK10 | 2024-07-11 19:11 | 2024-07-11 19:12 | 1.0395e-05 | 1.0395e-05 | 1 | 1 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 739 | 17653 | Mosgiel | MG6 | 2024-07-12 06:06 | 2024-07-12 11:39 | 0.0034616 | 1.0395e-05 | 1 | 333 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 740 | 17636 | East Taieri | ET6 | 2024-07-12 09:04 | 2024-07-12 13:24 | 0.24055 | 0.00092518 | 89 | 23140 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 741 | 17639 | Mosgiel | MG6 | 2024-07-12 09:04 | 2024-07-12 11:56 | 0.028608 | 0.00016632 | 16 | 2752 | Planned | Planned interruption | network extension | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 742 | 17640 | Mosgiel | MG6 | 2024-07-12 09:22 | 2024-07-12 12:05 | 0.013555 | 8.3162e-05 | 8 | 1304 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 743 | 17649 | Carisbrook | CK3 | 2024-07-13 00:30 | 2024-07-13 05:14 | 0.0029522 | 1.0395e-05 | 1 | 284 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 744 | 17668 | Mosgiel | MG6 | 2024-07-15 09:08 | 2024-07-15 10:27 | 0.0016424 | 2.079e-05 | 2 | 158 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 745 | 17704 | Wanaka | CB2755 | 2024-07-15 09:29 | 2024-07-15 17:29 | 0.0049897 | 1.0395e-05 | 1 | 480 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 746 | 17705 | Wanaka | CB2755 | 2024-07-15 09:29 | 2024-07-15 17:29 | 0.019959 | 4.1581e-05 | 4 | 1920 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 747 | 17707 | Wanaka | CB2755 | 2024-07-15 09:29 | 2024-07-15 17:51 | 0.041747 | 8.3162e-05 | 8 | 4016 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 748 | 17702 | Wanaka | CB2755 | 2024-07-15 09:29 | 2024-07-15 17:13 | 0.072351 | 0.00015593 | 15 | 6960 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 749 | 17703 | Wanaka | CB2755 | 2024-07-15 09:29 | 2024-07-15 17:17 | 0.10703 | 0.00022869 | 22 | 10296 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 750 | 17709 | Queenstown | CB5272 | 2024-07-15 09:35 | 2024-07-15 10:26 | 0.43296 | 0.0086592 | 833 | 41650 | Unplanned | Human Error | switching error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 751 | 17728 | Queenstown | CB5212 | 2024-07-15 10:12 | 2024-07-15 10:26 | 0.011643 | 0.00083162 | 80 | 1120 | Unplanned | Human Error | switching error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 752 | 17818 | Nth East Valley | NV7 | 2024-07-15 17:05 | 2024-07-15 20:59 | 0.0024325 | 1.0395e-05 | 1 | 234 | Unplanned | Defective Equipment | broken lead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 753 | 17819 | Nth East Valley | NV7 | 2024-07-15 20:27 | 2024-07-15 20:55 | 0.017464 | 0.00062371 | 60 | 1680 | Unplanned | Defective Equipment | broken lead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 754 | 17715 | Fernhill | CB5309 | 2024-07-15 23:48 | 2024-07-16 01:04 | 0.32199 | 0.0042932 | 413 | 30975 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 755 | 17688 | Halfway Bush | HB1 | 2024-07-16 08:02 | 2024-07-16 14:28 | 0.064201 | 0.00016632 | 16 | 6176 | Planned | Planned interruption | tree trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 756 | 17698 | Outram | OT3 | 2024-07-16 09:01 | 2024-07-16 15:44 | 0.079596 | 0.00019751 | 19 | 7657 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 757 | 17700 | Fernhill | CB5308 | 2024-07-16 09:02 | 2024-07-16 09:10 | 0.008233 | 0.0010291 | 99 | 792 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 758 | 17691 | Ward Street | WS7 | 2024-07-16 09:05 | 2024-07-16 09:12 | 0.0036383 | 0.00051976 | 50 | 350 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 759 | 17690 | Queenstown | CB5222 | 2024-07-16 09:10 | 2024-07-16 09:14 | 0.00099794 | 0.00024949 | 24 | 96 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 760 | 17696 | Ward Street | WS7 | 2024-07-16 09:19 | 2024-07-16 15:59 | 0.041581 | 0.00010395 | 10 | 4000 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 761 | 17692 | Ward Street | WS7 | 2024-07-16 09:19 | 2024-07-16 15:27 | 0.045905 | 0.00012474 | 12 | 4416 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 762 | 17693 | Ward Street | WS7 | 2024-07-16 09:19 | 2024-07-16 15:58 | 0.1825 | 0.00045739 | 44 | 17556 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 763 | 17721 | Alexandra | CB168 | 2024-07-16 10:00 | 2024-07-16 15:50 | 0.171 | 0.00048858 | 47 | 16450 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 764 | 17720 | Alexandra | CB168 | 2024-07-16 10:00 | 2024-07-16 10:52 | 0.14217 | 0.0027339 | 263 | 13676 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 765 | 17882 | Corstorphine | CO7 | 2024-07-16 11:20 | 2024-07-16 12:04 | 0.0027443 | 6.2371e-05 | 6 | 264 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 766 | 17701 | Fernhill | CB5308 | 2024-07-16 14:52 | 2024-07-16 14:58 | 0.0061748 | 0.0010291 | 99 | 594 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 767 | 17687 | Clyde-Earnscleugh | CB190 | 2024-07-16 15:58 | 2024-07-16 16:17 | 0.013628 | 0.00071727 | 69 | 1311 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 768 | 17722 | Alexandra | CB168 | 2024-07-16 16:06 | 2024-07-16 17:45 | 0.0030874 | 3.1186e-05 | 3 | 297 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 769 | 17738 | Arrowtown | CB7632 | 2024-07-17 07:46 | 2024-07-17 07:52 | 0.00012474 | 2.079e-05 | 2 | 12 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 770 | 17739 | Arrowtown | CB7632 | 2024-07-17 08:02 | 2024-07-17 14:51 | 0.0042516 | 1.0395e-05 | 1 | 409 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 771 | 17735 | Halfway Bush | HB1 | 2024-07-17 08:08 | 2024-07-17 11:44 | 0.024699 | 0.00011435 | 11 | 2376 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 772 | 18073 | Halfway Bush | HB1 | 2024-07-17 08:08 | 2024-07-17 11:44 | 0.0022454 | 1.0395e-05 | 1 | 216 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 773 | 17737 | Roxburgh | CB4633 | 2024-07-17 09:08 | 2024-07-17 15:49 | 0.016674 | 4.1581e-05 | 4 | 1604 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 774 | 17757 | St. Kilda | SK1 | 2024-07-17 18:40 | 2024-07-18 00:51 | 0.0038566 | 1.0395e-05 | 1 | 371 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 775 | 17760 | Arrowtown | CB7632 | 2024-07-18 07:46 | 2024-07-18 07:55 | 0.00018711 | 2.079e-05 | 2 | 18 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 776 | 17761 | Arrowtown | CB7632 | 2024-07-18 08:01 | 2024-07-18 16:05 | 0.0050313 | 1.0395e-05 | 1 | 484 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 777 | 17759 | Berwick | BK2 | 2024-07-18 09:03 | 2024-07-18 15:08 | 0.0037943 | 1.0395e-05 | 1 | 365 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 778 | 17758 | Berwick | BK2 | 2024-07-18 09:03 | 2024-07-18 15:02 | 0.018659 | 5.1976e-05 | 5 | 1795 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 779 | 17754 | Frankton | CB7784 | 2024-07-18 09:28 | 2024-07-18 15:46 | 0.25541 | 0.00067569 | 65 | 24570 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 780 | 18074 | Frankton | CB7784 | 2024-07-18 09:28 | 2024-07-18 15:46 | 0.0039294 | 1.0395e-05 | 1 | 378 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 781 | 17756 | Fernhill | CB5308 | 2024-07-18 09:31 | 2024-07-18 10:26 | 0.02973 | 0.00054055 | 52 | 2860 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 782 | 17770 | Wanaka | CB2758 | 2024-07-18 17:47 | 2024-07-18 19:24 | 0.49298 | 0.0051352 | 494 | 47424 | Unplanned | Defective Equipment | burning link | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 783 | 17769 | Wanaka | CB2758 | 2024-07-18 17:47 | 2024-07-18 18:55 | 0.47639 | 0.0071103 | 684 | 45828 | Unplanned | Defective Equipment | burning link | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 784 | 17773 | Wanaka | CB2758 | 2024-07-18 18:57 | 2024-07-18 19:45 | 0.021456 | 0.00044699 | 43 | 2064 | Unplanned | Defective Equipment | burning link | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 785 | 17774 | Wanaka | CB2758 | 2024-07-18 18:57 | 2024-07-18 20:37 | 0.077964 | 0.00077964 | 75 | 7500 | Unplanned | Defective Equipment | burning link | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 786 | 17771 | Wanaka | CB2758 | 2024-07-18 18:57 | 2024-07-18 19:24 | 0.026944 | 0.00099794 | 96 | 2592 | Unplanned | Defective Equipment | burning link | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 787 | 17772 | Wanaka | CB2758 | 2024-07-18 18:57 | 2024-07-18 19:39 | 0.2052 | 0.0048858 | 470 | 19740 | Unplanned | Defective Equipment | burning link | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 788 | 17775 | Wanaka | CB2758 | 2024-07-18 20:32 | 2024-07-18 20:37 | 0.002235 | 0.00044699 | 43 | 215 | Unplanned | Defective Equipment | burning link | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 789 | 17787 | Mosgiel | MG6 | 2024-07-19 08:35 | 2024-07-19 08:38 | 0.00081083 | 0.00027028 | 26 | 78 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 790 | 17788 | Mosgiel | MG6 | 2024-07-19 08:51 | 2024-07-19 17:17 | 0.07364 | 0.00014553 | 14 | 7084 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 791 | 17783 | Alexandra | CB168 | 2024-07-19 14:10 | 2024-07-19 15:08 | 0.020738 | 0.00036383 | 35 | 1995 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 792 | 17784 | Alexandra | CB168 | 2024-07-19 14:10 | 2024-07-19 15:21 | 0.072767 | 0.0010395 | 100 | 7000 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 793 | 17785 | Alexandra | CB168 | 2024-07-19 15:20 | 2024-07-19 15:21 | 0.00036383 | 0.00036383 | 35 | 35 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 794 | 17789 | Mosgiel | MG6 | 2024-07-19 17:18 | 2024-07-19 17:20 | 0.00054055 | 0.00027028 | 26 | 52 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 795 | 17798 | Alexandra | CB168 | 2024-07-20 14:05 | 2024-07-20 15:38 | 0.00096676 | 1.0395e-05 | 1 | 93 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 796 | 17801 | Port Chalmers | PC3 | 2024-07-20 16:54 | 2024-07-20 20:47 | 0.10899 | 0.00046779 | 45 | 10485 | Unplanned | Defective Equipment | broken lead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 797 | 17800 | Port Chalmers | PC3 | 2024-07-20 16:54 | 2024-07-20 18:22 | 0.322 | 0.0036591 | 352 | 30976 | Unplanned | Defective Equipment | broken lead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 798 | 17806 | Lauder Flat | CB6576 | 2024-07-20 21:52 | 2024-07-21 03:10 | 0.10545 | 0.00033265 | 32 | 10144 | Unplanned | Wildlife | bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 799 | 17805 | Lauder Flat | CB6576 | 2024-07-20 21:52 | 2024-07-20 22:56 | 0.12836 | 0.0020375 | 196 | 12348 | Unplanned | Wildlife | bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 800 | 17808 | Lauder Flat | CB6576 | 2024-07-20 23:41 | 2024-07-20 23:56 | 0.028525 | 0.0020375 | 196 | 2744 | Unplanned | Wildlife | bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 801 | 17815 | South City | SC14 | 2024-07-22 17:40 | 2024-07-23 | 0.027651 | 7.2767e-05 | 7 | 2660 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 802 | 17851 | Queenstown | CB5232 | 2024-07-23 07:33 | 2024-07-24 15:15 | 0.039543 | 2.079e-05 | 2 | 3804 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 803 | 17836 | East Taieri | ET8 | 2024-07-23 08:39 | 2024-07-23 15:06 | 0.020115 | 5.1976e-05 | 5 | 1935 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 804 | 17849 | Outram | OT3 | 2024-07-23 09:02 | 2024-07-23 16:22 | 0.0091478 | 2.079e-05 | 2 | 880 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 805 | 17848 | Outram | OT3 | 2024-07-23 09:02 | 2024-07-23 16:20 | 0.027319 | 6.2371e-05 | 6 | 2628 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 806 | 17847 | Outram | OT3 | 2024-07-23 09:02 | 2024-07-23 16:16 | 0.13986 | 0.00032225 | 31 | 13454 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 807 | 17817 | Alexandra | CB169 | 2024-07-23 09:04 | 2024-07-23 11:59 | 0.0072767 | 4.1581e-05 | 4 | 700 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 808 | 17894 | Frankton | CB7782 | 2024-07-23 09:05 | 2024-07-23 17:01 | 0.0049481 | 1.0395e-05 | 1 | 476 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 809 | 17831 | Frankton | CB7784 | 2024-07-23 13:03 | 2024-07-23 13:20 | 0.0065386 | 0.00038462 | 37 | 629 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 810 | 17858 | Ettrick | CB480 | 2024-07-23 14:33 | 2024-07-23 16:49 | 0.10745 | 0.00079004 | 76 | 10336 | Unplanned | Human Error | tree trimming error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 811 | 17835 | Cromwell | CB821 | 2024-07-24 09:10 | 2024-07-24 12:33 | 0.023213 | 0.00011435 | 11 | 2233 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 812 | 17833 | Cromwell | CB821 | 2024-07-24 09:10 | 2024-07-24 12:30 | 0.058213 | 0.00029107 | 28 | 5600 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 813 | 18075 | Cromwell | CB821 | 2024-07-24 09:10 | 2024-07-24 12:30 | 0.002079 | 1.0395e-05 | 1 | 200 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 814 | 17853 | Mosgiel | MG3 | 2024-07-24 10:05 | 2024-07-24 15:29 | 0.38059 | 0.0011747 | 113 | 36612 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 815 | 17971 | Camp Hill | CB2006 | 2024-07-24 12:34 | 2024-07-24 14:40 | 0.0013098 | 1.0395e-05 | 1 | 126 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 816 | 17865 | Dalefield | CB7830 | 2024-07-24 14:00 | 2024-07-24 14:46 | 0.037891 | 0.00084201 | 81 | 3645 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 817 | 17864 | Dalefield | CB7830 | 2024-07-24 14:00 | 2024-07-24 14:40 | 0.15973 | 0.0040957 | 394 | 15366 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 818 | 17869 | Dalefield | CB7830 | 2024-07-24 14:40 | 2024-07-24 15:57 | 0.049627 | 0.0006445 | 62 | 4774 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 819 | 17868 | Dalefield | CB7830 | 2024-07-24 14:40 | 2024-07-24 15:40 | 0.048026 | 0.00080043 | 77 | 4620 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 820 | 17870 | Dalefield | CB7830 | 2024-07-24 14:40 | 2024-07-24 16:07 | 0.083203 | 0.00095636 | 92 | 8004 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 821 | 17867 | Dalefield | CB7830 | 2024-07-24 14:40 | 2024-07-24 15:17 | 0.062694 | 0.0016944 | 163 | 6031 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 822 | 17871 | Dalefield | CB7830 | 2024-07-24 15:55 | 2024-07-24 15:57 | 0.0024949 | 0.0024949 | 240 | 240 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 823 | 17874 | Dalefield | CB7830 | 2024-07-24 15:57 | 2024-07-24 17:56 | 0.030926 | 0.00025988 | 25 | 2975 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 824 | 17873 | Dalefield | CB7830 | 2024-07-24 15:57 | 2024-07-24 16:07 | 0.0038462 | 0.00038462 | 37 | 370 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 825 | 17872 | Dalefield | CB7830 | 2024-07-24 15:57 | 2024-07-24 16:00 | 0.0074846 | 0.0024949 | 240 | 720 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 826 | 17852 | Queenstown | CB5232 | 2024-07-24 19:14 | 2024-07-24 19:28 | 0.00058213 | 4.1581e-05 | 4 | 56 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 827 | 17896 | Lindis Crossing | CB2084 | 2024-07-25 08:36 | 2024-07-25 09:01 | 0.0036383 | 0.00014553 | 14 | 350 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 828 | 17843 | Outram | OT3 | 2024-07-25 09:03 | 2024-07-25 14:52 | 0.0036279 | 1.0395e-05 | 1 | 349 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 829 | 17845 | Outram | OT3 | 2024-07-25 09:03 | 2024-07-25 14:58 | 0.0073806 | 2.079e-05 | 2 | 710 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 830 | 17839 | Outram | OT3 | 2024-07-25 09:03 | 2024-07-25 14:46 | 0.014262 | 4.1581e-05 | 4 | 1372 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 831 | 17841 | Outram | OT3 | 2024-07-25 09:03 | 2024-07-25 14:47 | 0.01788 | 5.1976e-05 | 5 | 1720 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 832 | 17837 | Outram | OT3 | 2024-07-25 09:03 | 2024-07-25 14:43 | 0.19439 | 0.00057174 | 55 | 18700 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 833 | 17854 | Cromwell | CB821 | 2024-07-25 09:03 | 2024-07-25 14:49 | 0.23379 | 0.00067569 | 65 | 22490 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 834 | 17898 | Lindis Crossing | CB2084 | 2024-07-25 09:08 | 2024-07-25 12:36 | 0.13838 | 0.00066529 | 64 | 13312 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 835 | 17897 | Lindis Crossing | CB2084 | 2024-07-25 09:19 | 2024-07-25 12:35 | 0.0040749 | 2.079e-05 | 2 | 392 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 836 | 17900 | Lindis Crossing | CB2084 | 2024-07-25 09:19 | 2024-07-25 12:35 | 0.0020375 | 1.0395e-05 | 1 | 196 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 837 | 17879 | Berwick | BK2 | 2024-07-25 10:03 | 2024-07-25 12:58 | 0.0054575 | 3.1186e-05 | 3 | 525 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 838 | 17899 | Lindis Crossing | CB2084 | 2024-07-25 15:17 | 2024-07-25 15:18 | 0.00014553 | 0.00014553 | 14 | 14 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 839 | 17887 | Omakau | CB656 | 2024-07-26 17:10 | 2024-07-26 19:37 | 0.0015281 | 1.0395e-05 | 1 | 147 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 840 | 17890 | Omakau | CB656 | 2024-07-26 19:34 | 2024-07-26 19:37 | 0.00012474 | 4.1581e-05 | 4 | 12 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 841 | 17888 | Omakau | CB656 | 2024-07-26 19:36 | 2024-07-26 19:37 | 0.00037423 | 0.00037423 | 36 | 36 | Unplanned | Defective Equipment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 842 | 17903 | Roxburgh | HSB33 | 2024-07-29 00:17 | 2024-07-29 00:38 | 0.00041581 | 2.079e-05 | 2 | 40 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 843 | 17910 | Outram | OT2 | 2024-07-29 10:15 | 2024-07-29 12:55 | 0.026612 | 0.00016632 | 16 | 2560 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 844 | 17907 | Outram | OT2 | 2024-07-29 10:15 | 2024-07-29 11:07 | 0.021082 | 0.00040541 | 39 | 2028 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 845 | 17908 | Outram | OT2 | 2024-07-29 10:15 | 2024-07-29 11:20 | 0.052028 | 0.00080043 | 77 | 5005 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 846 | 17909 | Outram | OT2 | 2024-07-29 10:15 | 2024-07-29 11:54 | 0.18216 | 0.00184 | 177 | 17523 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 847 | 17913 | Cromwell | CB832 | 2024-07-29 16:37 | 2024-07-29 17:23 | 0.08654 | 0.0019231 | 185 | 8325 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 848 | 17914 | Cromwell | CB832 | 2024-07-29 16:37 | 2024-07-29 21:21 | 1.6769 | 0.0059253 | 570 | 161310 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 849 | 17915 | Wanaka | CB2755 | 2024-07-29 17:16 | 2024-07-29 19:17 | 1.122 | 0.0092725 | 892 | 107932 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 850 | 17946 | Mosgiel | MG6 | 2024-07-30 08:23 | 2024-07-30 08:25 | 0.00083162 | 0.00041581 | 40 | 80 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 851 | 17947 | Mosgiel | MG6 | 2024-07-30 08:28 | 2024-07-30 16:00 | 0.028192 | 6.2371e-05 | 6 | 2712 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 852 | 17945 | Ettrick | CB480 | 2024-07-30 10:01 | 2024-07-30 14:31 | 0.033681 | 0.00012474 | 12 | 3240 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 853 | 17941 | Cromwell | CB821 | 2024-07-30 10:05 | 2024-07-30 14:18 | 0.04734 | 0.00018711 | 18 | 4554 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 854 | 17948 | Mosgiel | MG6 | 2024-07-30 17:03 | 2024-07-30 17:11 | 0.0033265 | 0.00041581 | 40 | 320 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 855 | 18042 | Arrowtown | CB7692 | 2024-07-30 20:46 | 2024-07-30 22:41 | 0.023909 | 0.0002079 | 20 | 2300 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 856 | 18043 | Arrowtown | CB7692 | 2024-07-30 22:41 | 2024-07-31 02:03 | 0.041997 | 0.0002079 | 20 | 4040 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 857 | 17967 | Green Island | GI7 | 2024-07-31 08:27 | 2024-07-31 14:22 | 0.0036903 | 1.0395e-05 | 1 | 355 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 858 | 17966 | Green Island | GI7 | 2024-07-31 08:31 | 2024-07-31 09:39 | 0.0021206 | 3.1186e-05 | 3 | 204 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 859 | 17965 | Green Island | GI7 | 2024-07-31 08:38 | 2024-07-31 09:38 | 0.008732 | 0.00014553 | 14 | 840 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 860 | 17970 | Halfway Bush | HB1 | 2024-07-31 08:49 | 2024-07-31 15:14 | 0.012006 | 3.1186e-05 | 3 | 1155 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 861 | 17936 | Mosgiel | MG6 | 2024-07-31 09:00 | 2024-07-31 09:07 | 0.0006549 | 9.3557e-05 | 9 | 63 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 862 | 17938 | Mosgiel | MG6 | 2024-07-31 09:00 | 2024-07-31 14:07 | 0.26807 | 0.0008732 | 84 | 25788 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 863 | 17935 | Wanaka | CB2758 | 2024-07-31 09:07 | 2024-07-31 11:45 | 0.011497 | 7.2767e-05 | 7 | 1106 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 864 | 17933 | Lauder Flat | CB6576 | 2024-07-31 09:40 | 2024-07-31 15:25 | 0.11835 | 0.00034304 | 33 | 11385 | Planned | Planned interruption | network extension | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 865 | 17969 | Green Island | GI7 | 2024-07-31 13:46 | 2024-07-31 14:45 | 0.00184 | 3.1186e-05 | 3 | 177 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 866 | 17968 | Green Island | GI7 | 2024-07-31 13:53 | 2024-07-31 14:44 | 0.0074222 | 0.00014553 | 14 | 714 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 867 | 17939 | Mosgiel | MG6 | 2024-07-31 13:57 | 2024-07-31 14:07 | 0.00093557 | 9.3557e-05 | 9 | 90 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 868 | 17990 | Cromwell | CB838 | 2024-07-31 19:05 | 2024-07-31 19:23 | 0.0076717 | 0.0004262 | 41 | 738 | Unplanned | Defective Equipment | faulty transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 869 | 17977 | Corstorphine | CO9 | 2024-07-31 21:11 | 2024-07-31 21:46 | 0.044388 | 0.0012682 | 122 | 4270 | Unplanned | Defective Equipment | burnt connector | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 870 | 17976 | Corstorphine | CO9 | 2024-07-31 21:11 | 2024-07-31 21:12 | 0.0051041 | 0.0051041 | 491 | 491 | Unplanned | Defective Equipment | burnt connector | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 871 | 17996 | North City | NC6 | 2024-08-01 01:05 | 2024-08-01 01:11 | 0.0036175 | 0.00060292 | 58 | 348 | Unplanned | Defective Equipment | hv isolation for lv fuse replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 872 | 17973 | Arrowtown | CB7632 | 2024-08-01 09:10 | 2024-08-01 14:34 | 0.010104 | 3.1186e-05 | 3 | 972 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 873 | 17992 | Roxburgh | CB4639 | 2024-08-01 11:50 | 2024-08-01 14:20 | 0.0015593 | 1.0395e-05 | 1 | 150 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 874 | 17997 | South City | SC6 | 2024-08-01 22:32 | 2024-08-02 05:40 | 0.040042 | 9.3557e-05 | 9 | 3852 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 875 | 18007 | Frankton | CB7782 | 2024-08-02 12:58 | 2024-08-02 13:54 | 0.044824 | 0.00080043 | 77 | 4312 | Unplanned | Defective Equipment | broken fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 876 | 18012 | Outram | OT2 | 2024-08-03 01:30 | 2024-08-03 03:39 | 0.004023 | 3.1186e-05 | 3 | 387 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 877 | 18002 | Mosgiel | MG6 | 2024-08-03 08:03 | 2024-08-03 17:11 | 0.0056966 | 1.0395e-05 | 1 | 548 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 878 | 18030 | East Taieri | ET9 | 2024-08-04 11:47 | 2024-08-04 12:32 | 0.048182 | 0.0010707 | 103 | 4635 | Unplanned | Defective Equipment | faulty fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 879 | 18060 | Fernhill | CB5309 | 2024-08-05 09:11 | 2024-08-05 17:54 | 0.48387 | 0.00092518 | 89 | 46547 | Unplanned | Defective Equipment | faulty transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 880 | 18033 | Nth East Valley | NV7 | 2024-08-05 09:21 | 2024-08-05 09:25 | 0.0017464 | 0.0004366 | 42 | 168 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 881 | 18034 | Nth East Valley | NV7 | 2024-08-05 09:21 | 2024-08-05 15:31 | 0.16539 | 0.00044699 | 43 | 15910 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 882 | 18035 | Nth East Valley | NV7 | 2024-08-05 15:27 | 2024-08-05 15:31 | 0.0017464 | 0.0004366 | 42 | 168 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 883 | 18046 | Arrowtown | CB7692 | 2024-08-05 17:02 | 2024-08-05 17:18 | 0.00083162 | 5.1976e-05 | 5 | 80 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 884 | 18047 | Arrowtown | CB7692 | 2024-08-05 17:36 | 2024-08-05 17:55 | 0.0039502 | 0.0002079 | 20 | 380 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 885 | 18088 | Arrowtown | CB7632 | 2024-08-06 08:07 | 2024-08-06 15:52 | 0.014501 | 3.1186e-05 | 3 | 1395 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 886 | 18069 | Mosgiel | MG3 | 2024-08-06 08:32 | 2024-08-06 17:28 | 0.28416 | 0.00053016 | 51 | 27336 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 887 | 18066 | Mosgiel | MG3 | 2024-08-06 08:32 | 2024-08-06 17:00 | 0.33269 | 0.0006549 | 63 | 32004 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 888 | 18070 | Mosgiel | MG3 | 2024-08-06 08:32 | 2024-08-06 18:17 | 0.45001 | 0.00076925 | 74 | 43290 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 889 | 18065 | Mosgiel | MG3 | 2024-08-06 08:32 | 2024-08-06 08:48 | 0.028275 | 0.0017672 | 170 | 2720 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 890 | 18064 | Mosgiel | MG3 | 2024-08-06 08:32 | 2024-08-06 08:34 | 0.0075469 | 0.0037735 | 363 | 726 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 891 | 18036 | Halfway Bush | HB3 | 2024-08-06 08:45 | 2024-08-06 16:20 | 0.2696 | 0.00059253 | 57 | 25935 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 892 | 18038 | Arrowtown | CB7662 | 2024-08-06 09:15 | 2024-08-06 16:31 | 0.10424 | 0.00023909 | 23 | 10028 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 893 | 18040 | Lindis Crossing | CB2084 | 2024-08-06 09:18 | 2024-08-06 12:55 | 0.0022558 | 1.0395e-05 | 1 | 217 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 894 | 18037 | Arrowtown | CB7662 | 2024-08-06 09:23 | 2024-08-06 16:17 | 0.1162 | 0.00028067 | 27 | 11178 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 895 | 18048 | Arrowtown | CB7692 | 2024-08-06 11:45 | 2024-08-06 12:25 | 0.0083162 | 0.0002079 | 20 | 800 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 896 | 18067 | Mosgiel | MG3 | 2024-08-06 17:05 | 2024-08-06 17:08 | 0.0072663 | 0.0024221 | 233 | 699 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 897 | 18068 | Mosgiel | MG3 | 2024-08-06 17:06 | 2024-08-06 17:08 | 0.0062371 | 0.0031186 | 300 | 600 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 898 | 18071 | Mosgiel | MG3 | 2024-08-06 17:06 | 2024-08-06 17:08 | 0.0013098 | 0.0006549 | 63 | 126 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 899 | 18091 | Arrowtown | CB7632 | 2024-08-06 17:09 | 2024-08-06 17:17 | 0.00016632 | 2.079e-05 | 2 | 16 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 900 | 18090 | Arrowtown | CB7632 | 2024-08-06 17:12 | 2024-08-06 17:16 | 8.3162e-05 | 2.079e-05 | 2 | 8 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 901 | 18078 | Halfway Bush | HB2 | 2024-08-07 09:02 | 2024-08-07 15:45 | 0.3142 | 0.00077964 | 75 | 30225 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 902 | 18077 | Alexandra | CB169 | 2024-08-07 09:07 | 2024-08-07 13:44 | 0.005759 | 2.079e-05 | 2 | 554 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 903 | 18104 | Roxburgh | CB4635 | 2024-08-07 13:13 | 2024-08-07 19:31 | 0.20379 | 0.00054055 | 52 | 19604 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 904 | 18103 | Roxburgh | CB4635 | 2024-08-07 13:13 | 2024-08-07 13:54 | 0.057111 | 0.001393 | 134 | 5494 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 905 | 18100 | Clyde-Earnscleugh | CB192 | 2024-08-08 09:21 | 2024-08-08 14:41 | 0.0033265 | 1.0395e-05 | 1 | 320 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 906 | 18092 | Port Chalmers | PC4 | 2024-08-09 09:07 | 2024-08-09 15:32 | 0.028015 | 7.2767e-05 | 7 | 2695 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 907 | 18101 | Alexandra | CB169 | 2024-08-09 09:18 | 2024-08-09 13:15 | 0.007391 | 3.1186e-05 | 3 | 711 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 908 | 18128 | Cromwell | CB831 | 2024-08-10 12:47 | 2024-08-10 13:17 | 0.00031186 | 1.0395e-05 | 1 | 30 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 909 | 18096 | Nth East Valley | NV4 | 2024-08-11 08:03 | 2024-08-11 15:58 | 0.0098755 | 2.079e-05 | 2 | 950 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 910 | 18094 | Nth East Valley | NV4 | 2024-08-11 08:10 | 2024-08-11 15:56 | 0.21314 | 0.00045739 | 44 | 20504 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 911 | 18133 | Cromwell | CB838 | 2024-08-11 09:05 | 2024-08-11 16:37 | 0.11277 | 0.00024949 | 24 | 10848 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 912 | 18131 | Cromwell | CB838 | 2024-08-11 10:03 | 2024-08-11 10:05 | 0.00045739 | 0.00022869 | 22 | 44 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 913 | 18132 | Cromwell | CB838 | 2024-08-11 15:49 | 2024-08-11 15:51 | 0.00045739 | 0.00022869 | 22 | 44 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 914 | 18123 | Cromwell | CB822 | 2024-08-11 16:10 | 2024-08-11 16:17 | 0.011715 | 0.0016736 | 161 | 1127 | Unplanned | Human Error | operator error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 915 | 18137 | Outram | OT1 | 2024-08-12 02:10 | 2024-08-12 04:21 | 0.0013618 | 1.0395e-05 | 1 | 131 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 916 | 18138 | Outram | OT1 | 2024-08-12 04:21 | 2024-08-12 04:23 | 0.0011331 | 0.0011331 | 109 | 109 | Unplanned | Defective Equipment | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 917 | 18144 | Arrowtown | CB7632 | 2024-08-12 09:10 | 2024-08-12 12:18 | 0.0019543 | 1.0395e-05 | 1 | 188 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 918 | 18143 | Arrowtown | CB7632 | 2024-08-12 09:10 | 2024-08-12 12:14 | 0.011476 | 6.2371e-05 | 6 | 1104 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 919 | 18147 | East Taieri | ET9 | 2024-08-13 09:08 | 2024-08-13 13:44 | 0.18649 | 0.00067569 | 65 | 17940 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 920 | 18145 | Lindis Crossing | CB2084 | 2024-08-13 09:24 | 2024-08-13 15:59 | 0.012318 | 3.1186e-05 | 3 | 1185 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 921 | 18146 | Cromwell | CB838 | 2024-08-13 10:03 | 2024-08-13 10:34 | 0.027714 | 0.00089399 | 86 | 2666 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 922 | 18148 | Alexandra | CB169 | 2024-08-13 13:11 | 2024-08-13 15:03 | 0.0011643 | 1.0395e-05 | 1 | 112 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 923 | 18181 | Dalefield | CB7828 | 2024-08-14 08:06 | 2024-08-14 08:15 | 0.00018711 | 2.079e-05 | 2 | 18 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 924 | 18169 | Green Island | GI3 | 2024-08-14 08:32 | 2024-08-14 16:32 | 0.0049897 | 1.0395e-05 | 1 | 480 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 925 | 18167 | Green Island | GI3 | 2024-08-14 08:32 | 2024-08-14 16:29 | 0.049585 | 0.00010395 | 10 | 4770 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 926 | 18168 | Green Island | GI3 | 2024-08-14 08:32 | 2024-08-14 16:30 | 0.43726 | 0.00091478 | 88 | 42064 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 927 | 18170 | Green Island | GI3 | 2024-08-14 08:32 | 2024-08-14 16:35 | 0.44686 | 0.00092518 | 89 | 42987 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 928 | 18204 | Green Island | GI3 | 2024-08-14 08:32 | 2024-08-14 16:35 | 0.0050209 | 1.0395e-05 | 1 | 483 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 929 | 18173 | Alexandra | CB169 | 2024-08-14 08:35 | 2024-08-14 16:09 | 0.0094389 | 2.079e-05 | 2 | 908 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 930 | 18182 | Dalefield | CB7828 | 2024-08-14 09:04 | 2024-08-14 17:12 | 0.1877 | 0.00038462 | 37 | 18056 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 931 | 18183 | Dalefield | CB7828 | 2024-08-14 09:04 | 2024-08-14 17:27 | 0.25621 | 0.00050937 | 49 | 24647 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 932 | 18184 | Dalefield | CB7828 | 2024-08-14 15:44 | 2024-08-14 15:58 | 0.00029107 | 2.079e-05 | 2 | 28 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 933 | 18185 | Dalefield | CB7828 | 2024-08-14 15:44 | 2024-08-14 15:58 | 0.012516 | 0.00089399 | 86 | 1204 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 934 | 18156 | Outram | OT2 | 2024-08-14 18:04 | 2024-08-14 18:15 | 0.00057174 | 5.1976e-05 | 5 | 55 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 935 | 18164 | Corstorphine | CO9 | 2024-08-15 08:43 | 2024-08-15 15:12 | 0.31137 | 0.00080043 | 77 | 29953 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 936 | 18158 | Cromwell | CB821 | 2024-08-15 09:02 | 2024-08-15 15:25 | 0.0039814 | 1.0395e-05 | 1 | 383 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 937 | 18162 | Cromwell | CB821 | 2024-08-15 09:02 | 2024-08-15 15:39 | 0.012381 | 3.1186e-05 | 3 | 1191 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 938 | 18160 | Cromwell | CB821 | 2024-08-15 09:02 | 2024-08-15 15:30 | 0.068567 | 0.00017672 | 17 | 6596 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 939 | 18165 | Green Island | GI3 | 2024-08-15 09:06 | 2024-08-15 15:32 | 0.35712 | 0.00092518 | 89 | 34354 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 940 | 18468 | Green Island | GI3 | 2024-08-15 09:06 | 2024-08-15 15:32 | 0.0040126 | 1.0395e-05 | 1 | 386 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 941 | 18174 | Halfway Bush | HB9 | 2024-08-15 09:10 | 2024-08-15 15:40 | 0.028379 | 7.2767e-05 | 7 | 2730 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 942 | 18163 | Corstorphine | CO7 | 2024-08-15 12:39 | 2024-08-15 14:36 | 0.055947 | 0.00047818 | 46 | 5382 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 943 | 18186 | Wanaka | CB2755 | 2024-08-16 09:35 | 2024-08-16 12:56 | 0.0062683 | 3.1186e-05 | 3 | 603 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 944 | 18199 | Omakau | CB656 | 2024-08-18 09:25 | 2024-08-18 11:42 | 0.0014241 | 1.0395e-05 | 1 | 137 | Unplanned | Wildlife | bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 945 | 18200 | Omakau | CB656 | 2024-08-18 10:20 | 2024-08-18 12:04 | 0.0032433 | 3.1186e-05 | 3 | 312 | Unplanned | Wildlife | bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 946 | 18203 | Omakau | CB656 | 2024-08-18 11:36 | 2024-08-18 11:41 | 0.00015593 | 3.1186e-05 | 3 | 15 | Unplanned | Wildlife | bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 947 | 18207 | Halfway Bush | HB6 | 2024-08-19 10:02 | 2024-08-19 15:08 | 0.0095428 | 3.1186e-05 | 3 | 918 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 948 | 18216 | East Taieri | ET2 | 2024-08-19 12:53 | 2024-08-19 16:54 | 0.014969 | 6.2371e-05 | 6 | 1440 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 949 | 18215 | East Taieri | ET2 | 2024-08-19 12:53 | 2024-08-19 14:55 | 0.4742 | 0.003919 | 377 | 45617 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 950 | 18213 | East Taieri | ET2 | 2024-08-19 12:53 | 2024-08-19 14:29 | 0.086904 | 0.00091478 | 88 | 8360 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 951 | 18214 | East Taieri | ET2 | 2024-08-19 12:53 | 2024-08-19 16:49 | 0.24917 | 0.0010603 | 102 | 23970 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 952 | 18217 | Green Island | GI3 | 2024-08-19 13:40 | 2024-08-19 13:44 | 0.032433 | 0.0081083 | 780 | 3120 | Unplanned | Human Error | operator error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 953 | 18236 | Roxburgh | CB4633 | 2024-08-19 22:14 | 2024-08-19 23:20 | 0.037163 | 0.00057174 | 55 | 3575 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 954 | 18240 | Roxburgh | CB4633 | 2024-08-19 23:20 | 2024-08-20 03:54 | 0.0056758 | 2.079e-05 | 2 | 546 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 955 | 18237 | Roxburgh | CB4633 | 2024-08-19 23:20 | 2024-08-19 23:25 | 0.00062371 | 0.00015593 | 15 | 60 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 956 | 18239 | Roxburgh | CB4633 | 2024-08-19 23:20 | 2024-08-20 01:17 | 0.018088 | 0.00015593 | 15 | 1740 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 957 | 18238 | Roxburgh | CB4633 | 2024-08-19 23:20 | 2024-08-20 01:14 | 0.027017 | 0.00023909 | 23 | 2599 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 958 | 18242 | Roxburgh | CB4633 | 2024-08-19 23:45 | 2024-08-19 23:49 | 0.00062371 | 0.00015593 | 15 | 60 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 959 | 18249 | Wanaka | CB2752 | 2024-08-20 00:05 | 2024-08-20 07:41 | 0.0094804 | 2.079e-05 | 2 | 912 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 960 | 18246 | Wanaka | CB2752 | 2024-08-20 00:05 | 2024-08-20 06:39 | 0.024574 | 6.2371e-05 | 6 | 2364 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 961 | 18248 | Wanaka | CB2752 | 2024-08-20 00:05 | 2024-08-20 07:04 | 0.06969 | 0.00016632 | 16 | 6704 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 962 | 18245 | Wanaka | CB2752 | 2024-08-20 00:05 | 2024-08-20 02:43 | 0.064055 | 0.00040541 | 39 | 6162 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 963 | 18247 | Wanaka | CB2752 | 2024-08-20 00:05 | 2024-08-20 06:48 | 0.22203 | 0.00055095 | 53 | 21359 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 964 | 18250 | Wanaka | CB2752 | 2024-08-20 06:43 | 2024-08-20 06:48 | 0.00088359 | 0.00017672 | 17 | 85 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 965 | 18271 | Mosgiel | MG3 | 2024-08-20 08:31 | 2024-08-20 17:05 | 0.2725 | 0.00053016 | 51 | 26214 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 966 | 18270 | Mosgiel | MG3 | 2024-08-20 08:31 | 2024-08-20 17:00 | 0.33334 | 0.0006549 | 63 | 32067 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 967 | 18272 | Mosgiel | MG3 | 2024-08-20 08:31 | 2024-08-20 17:11 | 0.40001 | 0.00076925 | 74 | 38480 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 968 | 18267 | Mosgiel | MG3 | 2024-08-20 08:31 | 2024-08-20 08:42 | 0.019439 | 0.0017672 | 170 | 1870 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 969 | 18266 | Mosgiel | MG3 | 2024-08-20 08:31 | 2024-08-20 08:33 | 0.0075469 | 0.0037735 | 363 | 726 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 970 | 18252 | Wanaka | CB2752 | 2024-08-20 16:29 | 2024-08-20 18:07 | 0.0040749 | 4.1581e-05 | 4 | 392 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 971 | 18251 | Wanaka | CB2752 | 2024-08-20 16:29 | 2024-08-20 17:53 | 0.010478 | 0.00012474 | 12 | 1008 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 972 | 18268 | Mosgiel | MG3 | 2024-08-20 16:46 | 2024-08-20 16:50 | 0.0070688 | 0.0017672 | 170 | 680 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 973 | 18269 | Mosgiel | MG3 | 2024-08-20 16:48 | 2024-08-20 16:50 | 0.0075469 | 0.0037735 | 363 | 726 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 974 | 18254 | Wanaka | CB2752 | 2024-08-20 18:34 | 2024-08-20 18:47 | 0.00081083 | 6.2371e-05 | 6 | 78 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 975 | 18255 | Wanaka | CB2752 | 2024-08-20 19:05 | 2024-08-20 19:06 | 2.079e-05 | 2.079e-05 | 2 | 2 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 976 | 18225 | Alexandra | CB168 | 2024-08-21 08:39 | 2024-08-21 15:28 | 0.034013 | 8.3162e-05 | 8 | 3272 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 977 | 18226 | Fernhill | CB5308 | 2024-08-21 09:03 | 2024-08-21 09:26 | 0.010998 | 0.00047818 | 46 | 1058 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 978 | 18227 | Fernhill | CB5308 | 2024-08-21 09:03 | 2024-08-21 11:18 | 0.20208 | 0.0014969 | 144 | 19440 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 979 | 18273 | Alexandra | CB167 | 2024-08-21 09:13 | 2024-08-21 15:06 | 0.07339 | 0.0002079 | 20 | 7060 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 980 | 18274 | Alexandra | CB167 | 2024-08-21 09:13 | 2024-08-21 15:06 | 0.11375 | 0.00032225 | 31 | 10943 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 981 | 18275 | Alexandra | CB167 | 2024-08-21 09:13 | 2024-08-21 15:06 | 0.36695 | 0.0010395 | 100 | 35300 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 982 | 18230 | Omakau | CB656 | 2024-08-21 10:13 | 2024-08-21 12:34 | 0.0014657 | 1.0395e-05 | 1 | 141 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 983 | 18231 | Alexandra | CB168 | 2024-08-21 10:17 | 2024-08-21 15:28 | 0.0032329 | 1.0395e-05 | 1 | 311 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 984 | 18228 | Fernhill | CB5308 | 2024-08-21 11:12 | 2024-08-21 11:18 | 0.0028691 | 0.00047818 | 46 | 276 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 985 | 18290 | Frankton | CB7783 | 2024-08-21 23:04 | 2024-08-22 00:45 | 0.0010499 | 1.0395e-05 | 1 | 101 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 986 | 18289 | Frankton | CB7783 | 2024-08-21 23:04 | 2024-08-22 00:45 | 0.0020998 | 2.079e-05 | 2 | 202 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 987 | 18277 | St. Kilda | SK7 | 2024-08-22 09:03 | 2024-08-22 15:27 | 0.26346 | 0.00068608 | 66 | 25344 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 988 | 18292 | Clyde-Earnscleugh | CB190 | 2024-08-22 09:04 | 2024-08-22 19:24 | 0.36737 | 0.00059253 | 57 | 35340 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 989 | 18291 | Clyde-Earnscleugh | CB190 | 2024-08-22 09:04 | 2024-08-22 19:01 | 0.7261 | 0.0012162 | 117 | 69849 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 990 | 18293 | Clyde-Earnscleugh | CB190 | 2024-08-22 09:04 | 2024-08-22 09:18 | 0.028088 | 0.0020063 | 193 | 2702 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 991 | 18276 | Dalefield | CB7830 | 2024-08-22 09:22 | 2024-08-22 12:05 | 0.0016944 | 1.0395e-05 | 1 | 163 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 992 | 18326 | Port Chalmers | PC7 | 2024-08-23 07:32 | 2024-08-23 14:38 | 0.0044284 | 1.0395e-05 | 1 | 426 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 993 | 18327 | Port Chalmers | PC7 | 2024-08-23 07:32 | 2024-08-23 14:39 | 0.0044388 | 1.0395e-05 | 1 | 427 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 994 | 18325 | Port Chalmers | PC7 | 2024-08-23 07:32 | 2024-08-23 14:28 | 0.03892 | 9.3557e-05 | 9 | 3744 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 995 | 18300 | Lindis Crossing | CB2084 | 2024-08-23 19:51 | 2024-08-24 01:04 | 0.20757 | 0.00066529 | 64 | 19968 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 996 | 18299 | Lindis Crossing | CB2084 | 2024-08-23 19:51 | 2024-08-23 22:24 | 0.13905 | 0.00091478 | 88 | 13376 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 997 | 18301 | Lindis Crossing | CB2084 | 2024-08-23 22:24 | 2024-08-23 23:51 | 0.0027132 | 3.1186e-05 | 3 | 261 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 998 | 18303 | Lindis Crossing | CB2084 | 2024-08-23 22:24 | 2024-08-24 00:37 | 0.016591 | 0.00012474 | 12 | 1596 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 999 | 18302 | Lindis Crossing | CB2084 | 2024-08-23 22:24 | 2024-08-24 00:15 | 0.023077 | 0.0002079 | 20 | 2220 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1000 | 18304 | Lindis Crossing | CB2084 | 2024-08-23 22:24 | 2024-08-24 01:02 | 0.08705 | 0.00055095 | 53 | 8374 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1001 | 18307 | Lindis Crossing | CB2084 | 2024-08-24 00:38 | 2024-08-24 15:49 | 0.01894 | 2.079e-05 | 2 | 1822 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1002 | 18306 | Lindis Crossing | CB2084 | 2024-08-24 00:38 | 2024-08-24 00:53 | 0.0014553 | 0.00010395 | 10 | 140 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1003 | 18308 | Lindis Crossing | CB2084 | 2024-08-24 00:51 | 2024-08-24 00:53 | 0.00023909 | 0.00023909 | 23 | 23 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1004 | 18310 | Roxburgh | CB480 | 2024-08-24 10:52 | 2024-08-24 11:59 | 0.29227 | 0.0044284 | 426 | 28116 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1005 | 18309 | Lindis Crossing | CB2084 | 2024-08-25 16:45 | 2024-08-25 17:39 | 0.0011227 | 2.079e-05 | 2 | 108 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1006 | 18317 | Corstorphine | CO5 | 2024-08-26 08:02 | 2024-08-26 16:15 | 0.14862 | 0.00030146 | 29 | 14297 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1007 | 18469 | Corstorphine | CO5 | 2024-08-26 08:02 | 2024-08-26 16:15 | 0.0051248 | 1.0395e-05 | 1 | 493 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1008 | 18322 | Clyde-Earnscleugh | CB190 | 2024-08-26 09:05 | 2024-08-26 17:10 | 0.97305 | 0.0020063 | 193 | 93605 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1009 | 18323 | Clyde-Earnscleugh | CB190 | 2024-08-26 09:12 | 2024-08-26 16:57 | 0.14985 | 0.00032225 | 31 | 14415 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1010 | 18423 | Frankton | CB7782 | 2024-08-26 20:44 | 2024-08-26 23:33 | 0.0052704 | 3.1186e-05 | 3 | 507 | Unplanned | Third-party Interference | machinery contact | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1011 | 18424 | Frankton | CB7782 | 2024-08-26 20:45 | 2024-08-26 23:33 | 0.14146 | 0.00084201 | 81 | 13608 | Unplanned | Third-party Interference | machinery contact | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1012 | 18348 | North City | NC6 | 2024-08-26 22:00 | 2024-08-26 23:19 | 0.047631 | 0.00060292 | 58 | 4582 | Unplanned | Defective Equipment | hv isolation for lv fuse replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1013 | 18560 | North City | NC6 | 2024-08-26 23:14 | 2024-08-26 23:16 | 0.0012058 | 0.00060292 | 58 | 116 | Unplanned | Defective Equipment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1014 | 18357 | Andersons Bay | AB7 | 2024-08-27 00:03 | 2024-08-27 02:38 | 0.27875 | 0.0017984 | 173 | 26815 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1015 | 18336 | Lindis Crossing | CB2084 | 2024-08-27 07:29 | 2024-08-27 08:03 | 0.0049481 | 0.00014553 | 14 | 476 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1016 | 18338 | Lindis Crossing | CB2084 | 2024-08-27 08:03 | 2024-08-27 17:09 | 0.36325 | 0.00066529 | 64 | 34944 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1017 | 18341 | Green Island | GI12 | 2024-08-27 08:47 | 2024-08-27 16:57 | 0.33618 | 0.00068608 | 66 | 32340 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1018 | 18331 | Mosgiel | MG3 | 2024-08-27 09:01 | 2024-08-27 15:44 | 0.18852 | 0.00046779 | 45 | 18135 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1019 | 18329 | Mosgiel | MG3 | 2024-08-27 09:03 | 2024-08-27 15:31 | 0.37107 | 0.00095636 | 92 | 35696 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1020 | 18342 | Green Island | GI12 | 2024-08-27 09:04 | 2024-08-27 16:57 | 0.23601 | 0.00049897 | 48 | 22704 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1021 | 18365 | Clyde-Earnscleugh | CB190 | 2024-08-27 09:04 | 2024-08-27 15:14 | 0.66744 | 0.0018088 | 174 | 64206 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1022 | 18330 | Mosgiel | MG3 | 2024-08-27 09:13 | 2024-08-27 15:37 | 0.13173 | 0.00034304 | 33 | 12672 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1023 | 18328 | Cromwell | CB822 | 2024-08-27 09:22 | 2024-08-27 19:30 | 0.13905 | 0.00022869 | 22 | 13376 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1024 | 18345 | Green Island | GI12 | 2024-08-27 10:01 | 2024-08-27 10:12 | 0.010977 | 0.00099794 | 96 | 1056 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1025 | 18344 | Green Island | GI12 | 2024-08-27 10:11 | 2024-08-27 17:58 | 0.23302 | 0.00049897 | 48 | 22416 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1026 | 18343 | Green Island | GI12 | 2024-08-27 10:11 | 2024-08-27 16:57 | 0.21524 | 0.00053016 | 51 | 20706 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1027 | 18346 | Green Island | GI12 | 2024-08-27 10:11 | 2024-08-27 10:12 | 0.00072767 | 0.00072767 | 70 | 70 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1028 | 18366 | Clyde-Earnscleugh | CB190 | 2024-08-27 15:03 | 2024-08-27 15:14 | 0.022069 | 0.0020063 | 193 | 2123 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1029 | 18337 | Lindis Crossing | CB2084 | 2024-08-27 16:49 | 2024-08-27 16:51 | 0.00029107 | 0.00014553 | 14 | 28 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1030 | 18347 | Green Island | GI12 | 2024-08-27 16:54 | 2024-08-27 16:57 | 0.0051768 | 0.0017256 | 166 | 498 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1031 | 18368 | St. Kilda | SK12 | 2024-08-28 06:40 | 2024-08-28 06:41 | 1.0395e-05 | 1.0395e-05 | 1 | 1 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1032 | 18388 | Roxburgh | CB4637 | 2024-08-28 08:05 | 2024-08-28 17:26 | 0.029159 | 5.1976e-05 | 5 | 2805 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1033 | 18387 | Roxburgh | CB4637 | 2024-08-28 08:05 | 2024-08-28 16:53 | 0.30188 | 0.00057174 | 55 | 29040 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1034 | 18559 | Port Chalmers | PC4 | 2024-08-28 11:34 | 2024-08-28 12:53 | 0.0024637 | 3.1186e-05 | 3 | 237 | Unplanned | Defective Equipment | burnt connector | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1035 | 18371 | Arrowtown | CB7652 | 2024-08-29 00:18 | 2024-08-29 01:16 | 0.13213 | 0.0023181 | 223 | 12711 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1036 | 18372 | Arrowtown | CB7652 | 2024-08-29 00:18 | 2024-08-29 01:18 | 0.20301 | 0.0034408 | 331 | 19529 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1037 | 18367 | Cromwell | CB831 | 2024-08-29 08:37 | 2024-08-29 14:07 | 0.41508 | 0.0012578 | 121 | 39930 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1038 | 18417 | Green Island | GI6 | 2024-08-29 08:40 | 2024-08-29 16:54 | 0.01027 | 2.079e-05 | 2 | 988 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1039 | 18416 | Green Island | GI6 | 2024-08-29 08:40 | 2024-08-29 16:54 | 0.69839 | 0.0014138 | 136 | 67184 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1040 | 18359 | Halfway Bush | HB10 | 2024-08-29 09:03 | 2024-08-29 13:45 | 0.31367 | 0.0011123 | 107 | 30174 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1041 | 18361 | Omakau | CB656 | 2024-08-29 09:08 | 2024-08-29 09:39 | 0.0006445 | 2.079e-05 | 2 | 62 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1042 | 18377 | Camp Hill | CB2006 | 2024-08-29 09:40 | 2024-08-29 12:59 | 0.0020687 | 1.0395e-05 | 1 | 199 | Unplanned | Lightning | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1043 | 18360 | Omakau | CB656 | 2024-08-29 10:06 | 2024-08-29 13:50 | 0.030271 | 0.00013514 | 13 | 2912 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1044 | 18362 | Omakau | CB656 | 2024-08-29 10:07 | 2024-08-29 10:48 | 0.00085241 | 2.079e-05 | 2 | 82 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1045 | 18379 | Roxburgh | CB4639 | 2024-08-29 10:11 | 2024-08-29 12:31 | 0.18919 | 0.0013514 | 130 | 18200 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1046 | 18363 | Omakau | CB656 | 2024-08-29 11:35 | 2024-08-29 12:16 | 0.0004262 | 1.0395e-05 | 1 | 41 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1047 | 18364 | Omakau | CB656 | 2024-08-29 13:08 | 2024-08-29 14:00 | 0.0016217 | 3.1186e-05 | 3 | 156 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1048 | 18384 | Omakau | CB656 | 2024-08-29 16:21 | 2024-08-29 16:49 | 0.018337 | 0.0006549 | 63 | 1764 | Unplanned | Defective Equipment | failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1049 | 18402 | Clyde-Earnscleugh | CB199 | 2024-08-30 09:01 | 2024-08-30 15:36 | 0.0082122 | 2.079e-05 | 2 | 790 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1050 | 18419 | Queensberry | CB2424 | 2024-08-30 09:06 | 2024-08-30 13:27 | 0.0081395 | 3.1186e-05 | 3 | 783 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1051 | 18418 | Queensberry | CB2424 | 2024-08-30 09:06 | 2024-08-30 13:27 | 0.021705 | 8.3162e-05 | 8 | 2088 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1052 | 18401 | Wanaka | CB2752 | 2024-08-30 09:48 | 2024-08-30 11:07 | 0.0090335 | 0.00011435 | 11 | 869 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1053 | 18415 | Port Chalmers | PC7 | 2024-08-30 10:49 | 2024-08-30 12:57 | 0.0079835 | 6.2371e-05 | 6 | 768 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1054 | 18407 | Roxburgh | CB480 | 2024-08-30 10:50 | 2024-08-30 12:07 | 0.024013 | 0.00031186 | 30 | 2310 | Unplanned | Defective Equipment | failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1055 | 18408 | Roxburgh | CB480 | 2024-08-30 10:50 | 2024-08-30 12:15 | 0.067153 | 0.00079004 | 76 | 6460 | Unplanned | Defective Equipment | failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1056 | 18405 | Roxburgh | CB480 | 2024-08-30 10:50 | 2024-08-30 12:04 | 0.11914 | 0.0016321 | 157 | 11461 | Unplanned | Defective Equipment | failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1057 | 18406 | Roxburgh | CB480 | 2024-08-30 10:50 | 2024-08-30 12:06 | 0.12708 | 0.0016944 | 163 | 12225 | Unplanned | Defective Equipment | failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1058 | 18409 | Alexandra | CB168 | 2024-08-30 13:10 | 2024-08-30 13:53 | 0.53148 | 0.01236 | 1189 | 51127 | Unplanned | Human Error | incorrect installation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1059 | 18413 | Omakau | CB656 | 2024-08-31 07:23 | 2024-08-31 08:24 | 0.025364 | 0.00041581 | 40 | 2440 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1060 | 18414 | Alexandra | CB168 | 2024-09-01 13:40 | 2024-09-01 14:31 | 0.60544 | 0.011871 | 1142 | 58242 | Unplanned | Human Error | incorrect installation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1061 | 18426 | Halfway Bush | HB13 | 2024-09-02 05:00 | 2024-09-02 08:29 | 0.023899 | 0.00011435 | 11 | 2299 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1062 | 18425 | Halfway Bush | HB13 | 2024-09-02 05:00 | 2024-09-02 06:21 | 0.55825 | 0.006892 | 663 | 53703 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1063 | 18427 | Willowbank | WB3 | 2024-09-02 06:40 | 2024-09-02 08:53 | 0.0013826 | 1.0395e-05 | 1 | 133 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1064 | 18421 | Green Island | GI6 | 2024-09-02 08:33 | 2024-09-02 15:29 | 0.0043244 | 1.0395e-05 | 1 | 416 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1065 | 18420 | Green Island | GI6 | 2024-09-02 08:33 | 2024-09-02 15:19 | 0.32076 | 0.00079004 | 76 | 30856 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1066 | 18443 | Wanaka | CB2752 | 2024-09-02 12:00 | 2024-09-02 12:11 | 0.00011435 | 1.0395e-05 | 1 | 11 | Unplanned | Defective Equipment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1067 | 18435 | Wanaka | CB2752 | 2024-09-02 12:00 | 2024-09-02 12:11 | 0.00068608 | 6.2371e-05 | 6 | 66 | Unplanned | Defective Equipment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1068 | 18437 | Wanaka | CB2752 | 2024-09-02 12:00 | 2024-09-02 12:11 | 0.00068608 | 6.2371e-05 | 6 | 66 | Unplanned | Defective Equipment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1069 | 18438 | Wanaka | CB2752 | 2024-09-02 12:00 | 2024-09-02 12:11 | 0.00068608 | 6.2371e-05 | 6 | 66 | Unplanned | Defective Equipment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1070 | 18442 | Wanaka | CB2752 | 2024-09-02 12:00 | 2024-09-02 12:11 | 0.00068608 | 6.2371e-05 | 6 | 66 | Unplanned | Defective Equipment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1071 | 18436 | Wanaka | CB2752 | 2024-09-02 12:00 | 2024-09-02 12:11 | 0.0011435 | 0.00010395 | 10 | 110 | Unplanned | Defective Equipment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1072 | 18439 | Wanaka | CB2752 | 2024-09-02 12:00 | 2024-09-02 12:11 | 0.0012578 | 0.00011435 | 11 | 121 | Unplanned | Defective Equipment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1073 | 18441 | Wanaka | CB2752 | 2024-09-02 12:00 | 2024-09-02 12:11 | 0.0012578 | 0.00011435 | 11 | 121 | Unplanned | Defective Equipment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1074 | 18440 | Wanaka | CB2752 | 2024-09-02 12:00 | 2024-09-02 12:11 | 0.0014865 | 0.00013514 | 13 | 143 | Unplanned | Defective Equipment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1075 | 18444 | Wanaka | CB2752 | 2024-09-02 12:00 | 2024-09-02 12:47 | 0.011726 | 0.00024949 | 24 | 1128 | Unplanned | Defective Equipment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1076 | 18430 | East Taieri | ET5 | 2024-09-02 12:35 | 2024-09-02 14:21 | 0.0033057 | 3.1186e-05 | 3 | 318 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1077 | 18445 | Wanaka | CB2752 | 2024-09-02 12:42 | 2024-09-02 12:47 | 0.0034304 | 0.00068608 | 66 | 330 | Unplanned | Defective Equipment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1078 | 18503 | Commonage | CB5730 | 2024-09-02 19:56 | 2024-09-02 21:07 | 0.030261 | 0.0004262 | 41 | 2911 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1079 | 18502 | Commonage | CB5730 | 2024-09-02 19:56 | 2024-09-02 20:40 | 0.028358 | 0.0006445 | 62 | 2728 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1080 | 18504 | Commonage | CB5730 | 2024-09-02 19:56 | 2024-09-02 21:37 | 0.092393 | 0.00091478 | 88 | 8888 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1081 | 18460 | Alexandra | CB3142 | 2024-09-03 08:21 | 2024-09-03 08:24 | 0.042038 | 0.014013 | 1348 | 4044 | Unplanned | Human Error | operator error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1082 | 18448 | Port Chalmers | PC4 | 2024-09-03 08:40 | 2024-09-03 16:35 | 0.049377 | 0.00010395 | 10 | 4750 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1083 | 18451 | Port Chalmers | PC4 | 2024-09-03 08:40 | 2024-09-03 16:43 | 0.23096 | 0.00047818 | 46 | 22218 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1084 | 18449 | Port Chalmers | PC4 | 2024-09-03 08:40 | 2024-09-03 16:38 | 0.33292 | 0.00069648 | 67 | 32026 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1085 | 18480 | Camp Hill | CB2006 | 2024-09-03 08:50 | 2024-09-03 11:09 | 0.0014449 | 1.0395e-05 | 1 | 139 | Unplanned | Lightning | lightning strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1086 | 18466 | Outram | OT1 | 2024-09-03 09:00 | 2024-09-03 14:54 | 0.091998 | 0.00025988 | 25 | 8850 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1087 | 18453 | Ettrick | CB480 | 2024-09-03 09:08 | 2024-09-03 16:42 | 0.24069 | 0.00053016 | 51 | 23154 | Planned | Planned interruption | tree trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1088 | 18467 | Outram | OT1 | 2024-09-03 09:08 | 2024-09-03 14:56 | 0.16641 | 0.00047818 | 46 | 16008 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1089 | 18454 | Frankton | CB7784 | 2024-09-03 09:11 | 2024-09-03 13:22 | 0.023483 | 9.3557e-05 | 9 | 2259 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1090 | 18455 | Alexandra | CB168 | 2024-09-03 09:47 | 2024-09-03 14:57 | 0.006445 | 2.079e-05 | 2 | 620 | Planned | Planned interruption | network extension | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1091 | 18465 | Camp Hill | CB2006 | 2024-09-03 10:00 | 2024-09-03 13:34 | 0.24915 | 0.0011643 | 112 | 23968 | Unplanned | Adverse Environment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1092 | 18456 | Alexandra | CB168 | 2024-09-03 10:05 | 2024-09-03 15:08 | 0.10709 | 0.00035344 | 34 | 10302 | Planned | Planned interruption | network extension | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1093 | 18505 | Commonage | CB5730 | 2024-09-03 12:56 | 2024-09-03 14:18 | 0.075012 | 0.00091478 | 88 | 7216 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1094 | 18462 | East Taieri | ET2 | 2024-09-03 14:05 | 2024-09-03 15:59 | 0.22516 | 0.0019751 | 190 | 21660 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1095 | 18464 | Cardrona | CB2881 | 2024-09-03 20:25 | 2024-09-03 21:49 | 0.0017464 | 2.079e-05 | 2 | 168 | Unplanned | Wildlife | bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1096 | 18494 | Nth East Valley | NV4 | 2024-09-04 07:25 | 2024-09-04 07:30 | 5.1976e-05 | 1.0395e-05 | 1 | 5 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1097 | 18496 | Commonage | CB5730 | 2024-09-04 07:50 | 2024-09-04 08:30 | 0.017048 | 0.0004262 | 41 | 1640 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1098 | 18470 | Willowbank | WB6 | 2024-09-04 08:01 | 2024-09-04 14:51 | 0.32818 | 0.00080043 | 77 | 31570 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1099 | 18473 | Cromwell | CB838 | 2024-09-04 09:02 | 2024-09-04 14:15 | 0.39044 | 0.0012474 | 120 | 37560 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1100 | 18472 | Lindis Crossing | CB2084 | 2024-09-04 09:45 | 2024-09-04 15:30 | 0.0035864 | 1.0395e-05 | 1 | 345 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1101 | 18471 | Lindis Crossing | CB2084 | 2024-09-04 10:09 | 2024-09-04 15:10 | 0.037548 | 0.00012474 | 12 | 3612 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1102 | 18495 | Nth East Valley | NV4 | 2024-09-04 14:58 | 2024-09-04 15:03 | 5.1976e-05 | 1.0395e-05 | 1 | 5 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1103 | 18506 | Commonage | CB5730 | 2024-09-04 17:26 | 2024-09-04 17:47 | 0.0089503 | 0.0004262 | 41 | 861 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1104 | 18507 | Commonage | CB5730 | 2024-09-04 17:26 | 2024-09-04 17:50 | 0.015468 | 0.0006445 | 62 | 1488 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1105 | 18508 | Commonage | CB5730 | 2024-09-04 19:38 | 2024-09-04 20:59 | 0.074097 | 0.00091478 | 88 | 7128 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1106 | 18486 | Cromwell | CB821 | 2024-09-05 08:00 | 2024-09-05 14:35 | 0.59128 | 0.0014969 | 144 | 56880 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1107 | 18487 | Cromwell | CB821 | 2024-09-05 08:01 | 2024-09-05 14:37 | 0.61336 | 0.0015489 | 149 | 59004 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1108 | 18488 | Cromwell | CB821 | 2024-09-05 08:19 | 2024-09-05 14:37 | 0.88411 | 0.0023389 | 225 | 85050 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1109 | 18490 | Clyde-Earnscleugh | CB195 | 2024-09-05 08:31 | 2024-09-05 09:26 | 0.0017152 | 3.1186e-05 | 3 | 165 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1110 | 18491 | Clyde-Earnscleugh | CB195 | 2024-09-05 08:35 | 2024-09-05 15:38 | 0.013192 | 3.1186e-05 | 3 | 1269 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1111 | 18483 | Cromwell | CB822 | 2024-09-05 09:15 | 2024-09-05 14:50 | 0.10447 | 0.00031186 | 30 | 10050 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1112 | 18511 | Frankton | CB7782 | 2024-09-05 09:15 | 2024-09-05 15:48 | 0.0081706 | 2.079e-05 | 2 | 786 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1113 | 18509 | Frankton | CB7782 | 2024-09-05 09:15 | 2024-09-05 15:24 | 0.023015 | 6.2371e-05 | 6 | 2214 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1114 | 18510 | Frankton | CB7782 | 2024-09-05 09:15 | 2024-09-05 15:44 | 0.028306 | 7.2767e-05 | 7 | 2723 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1115 | 18512 | Green Island | GI12 | 2024-09-06 08:00 | 2024-09-06 14:47 | 0.012693 | 3.1186e-05 | 3 | 1221 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1116 | 18515 | Wanaka | CB2758 | 2024-09-06 11:05 | 2024-09-06 14:45 | 0.068608 | 0.00031186 | 30 | 6600 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1117 | 18525 | Lauder Flat | CB6576 | 2024-09-07 08:17 | 2024-09-07 11:29 | 0.16167 | 0.00084201 | 81 | 15552 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1118 | 18534 | Dalefield | CB7830 | 2024-09-09 08:53 | 2024-09-09 09:40 | 0.039575 | 0.00084201 | 81 | 3807 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1119 | 18553 | Halfway Bush | HB3 | 2024-09-09 09:02 | 2024-09-09 16:12 | 0.2235 | 0.00051976 | 50 | 21500 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1120 | 18552 | Halfway Bush | HB3 | 2024-09-09 09:02 | 2024-09-09 09:08 | 0.0038047 | 0.00063411 | 61 | 366 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1121 | 18537 | Camp Hill | CB2008 | 2024-09-09 16:21 | 2024-09-09 18:54 | 0.0015905 | 1.0395e-05 | 1 | 153 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1122 | 18554 | Halfway Bush | HB3 | 2024-09-09 16:24 | 2024-09-09 16:33 | 0.005707 | 0.00063411 | 61 | 549 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1123 | 18550 | Roxburgh | CB4635 | 2024-09-10 09:03 | 2024-09-10 10:45 | 0.0010603 | 1.0395e-05 | 1 | 102 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1124 | 18570 | North City | NC2 | 2024-09-10 22:18 | 2024-09-10 22:40 | 0.0043452 | 0.00019751 | 19 | 418 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1125 | 18571 | North City | NC2 | 2024-09-11 05:59 | 2024-09-11 06:01 | 0.00019751 | 0.00019751 | 19 | 19 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1126 | 18569 | Nth East Valley | NV8 | 2024-09-11 08:37 | 2024-09-11 18:11 | 0.32818 | 0.00057174 | 55 | 31570 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1127 | 18564 | Nth East Valley | NV8 | 2024-09-11 08:37 | 2024-09-11 18:11 | 0.37591 | 0.0006549 | 63 | 36162 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1128 | 18568 | Nth East Valley | NV8 | 2024-09-11 08:37 | 2024-09-11 18:11 | 0.53105 | 0.00092518 | 89 | 51086 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1129 | 18563 | Camp Hill | CB2008 | 2024-09-11 09:09 | 2024-09-11 15:51 | 0.0083578 | 2.079e-05 | 2 | 804 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1130 | 18572 | Camp Hill | CB2008 | 2024-09-11 10:01 | 2024-09-11 15:28 | 0.0033992 | 1.0395e-05 | 1 | 327 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1131 | 18580 | Omakau | CB656 | 2024-09-11 13:49 | 2024-09-11 14:00 | 0.00011435 | 1.0395e-05 | 1 | 11 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1132 | 18593 | Frankton | CB7783 | 2024-09-12 06:02 | 2024-09-12 06:34 | 0.00033265 | 1.0395e-05 | 1 | 32 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1133 | 18703 | Wanaka | CB2754 | 2024-09-13 01:52 | 2024-09-13 04:32 | 0.14049 | 0.00088359 | 85 | 13515 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1134 | 18704 | Wanaka | CB2754 | 2024-09-13 04:37 | 2024-09-13 04:56 | 0.015905 | 0.00088359 | 85 | 1530 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1135 | 18602 | Alexandra | CB168 | 2024-09-13 05:10 | 2024-09-13 12:15 | 0.20323 | 0.00047818 | 46 | 19550 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1136 | 18603 | Alexandra | CB168 | 2024-09-13 05:10 | 2024-09-13 15:10 | 0.29315 | 0.00048858 | 47 | 28200 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1137 | 18600 | Alexandra | CB168 | 2024-09-13 05:10 | 2024-09-13 09:05 | 0.14657 | 0.00062371 | 60 | 14100 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1138 | 18601 | Alexandra | CB168 | 2024-09-13 05:10 | 2024-09-13 09:50 | 0.45697 | 0.0016321 | 157 | 43960 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1139 | 18609 | Alexandra | CB168 | 2024-09-13 05:12 | 2024-09-13 08:15 | 0.047558 | 0.00025988 | 25 | 4575 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1140 | 18611 | Alexandra | CB168 | 2024-09-13 05:12 | 2024-09-13 08:34 | 0.16799 | 0.00083162 | 80 | 16160 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1141 | 18610 | Alexandra | CB168 | 2024-09-13 05:12 | 2024-09-13 08:21 | 0.20433 | 0.0010811 | 104 | 19656 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1142 | 18612 | Alexandra | CB168 | 2024-09-13 05:12 | 2024-09-13 08:43 | 0.29611 | 0.0014034 | 135 | 28485 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1143 | 18606 | Alexandra | CB168 | 2024-09-13 05:12 | 2024-09-13 06:50 | 0.1416 | 0.0014449 | 139 | 13622 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1144 | 18608 | Alexandra | CB168 | 2024-09-13 05:12 | 2024-09-13 08:02 | 0.3393 | 0.0019959 | 192 | 32640 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1145 | 18607 | Alexandra | CB168 | 2024-09-13 05:12 | 2024-09-13 07:22 | 0.27568 | 0.0021206 | 204 | 26520 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1146 | 18615 | Alexandra | CB168 | 2024-09-13 05:16 | 2024-09-13 12:21 | 1.0117 | 0.0023805 | 229 | 97325 | Unplanned | Defective Equipment | 33/66kv to 11/6.6kv line clash | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1147 | 18614 | Alexandra | CB168 | 2024-09-13 05:16 | 2024-09-13 12:17 | 2.8597 | 0.0068089 | 655 | 275100 | Unplanned | Defective Equipment | 33/66kv to 11/6.6kv line clash | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1148 | 18705 | Wanaka | CB2754 | 2024-09-13 05:34 | 2024-09-13 05:50 | 0.013254 | 0.00088359 | 85 | 1275 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1149 | 18637 | Cromwell | CB821 | 2024-09-13 05:37 | 2024-09-14 16:27 | 0.065178 | 3.1186e-05 | 3 | 6270 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1150 | 18636 | Cromwell | CB821 | 2024-09-13 05:37 | 2024-09-13 08:39 | 0.092705 | 0.00050937 | 49 | 8918 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1151 | 18635 | Cromwell | CB821 | 2024-09-13 05:37 | 2024-09-13 07:23 | 0.15608 | 0.0014865 | 143 | 15015 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1152 | 18634 | Cromwell | CB821 | 2024-09-13 05:37 | 2024-09-13 07:22 | 0.65299 | 0.0062787 | 604 | 62816 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1153 | 18640 | Clyde-Earnscleugh | CB190 | 2024-09-13 06:10 | 2024-09-13 09:17 | 0.0097195 | 5.1976e-05 | 5 | 935 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1154 | 18639 | Clyde-Earnscleugh | CB190 | 2024-09-13 06:10 | 2024-09-13 07:40 | 0.61561 | 0.0068401 | 658 | 59220 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1155 | 18641 | Queenstown | CB5202 | 2024-09-13 07:08 | 2024-09-13 15:20 | 0.066488 | 0.00013514 | 13 | 6396 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1156 | 18638 | Cromwell | CB821 | 2024-09-13 07:53 | 2024-09-13 07:56 | 0.023296 | 0.0077652 | 747 | 2241 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1157 | 18613 | Alexandra | CB168 | 2024-09-13 07:53 | 2024-09-13 07:57 | 0.010697 | 0.0035656 | 343 | 1029 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1158 | 18646 | Frankton | CB7782 | 2024-09-13 08:01 | 2024-09-13 11:55 | 0.094867 | 0.00040541 | 39 | 9126 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1159 | 18645 | Frankton | CB7782 | 2024-09-13 08:01 | 2024-09-13 10:36 | 0.067673 | 0.0004366 | 42 | 6510 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1160 | 18644 | Frankton | CB7782 | 2024-09-13 08:01 | 2024-09-13 09:42 | 0.32862 | 0.0032537 | 313 | 31613 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1161 | 18648 | Clyde-Earnscleugh | CB192 | 2024-09-13 08:03 | 2024-09-13 08:53 | 0.028587 | 0.00057174 | 55 | 2750 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1162 | 18649 | Clyde-Earnscleugh | CB192 | 2024-09-13 08:03 | 2024-09-13 10:32 | 0.087694 | 0.00059253 | 57 | 8436 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1163 | 18664 | Lindis Crossing | CB2084 | 2024-09-13 10:26 | 2024-09-13 18:57 | 0.058432 | 0.00011435 | 11 | 5621 | Unplanned | Defective Equipment | failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1164 | 18665 | Lindis Crossing | CB2084 | 2024-09-13 10:26 | 2024-09-13 21:22 | 0.08865 | 0.00013514 | 13 | 8528 | Unplanned | Defective Equipment | failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1165 | 18663 | Lindis Crossing | CB2084 | 2024-09-13 10:26 | 2024-09-13 18:19 | 0.19668 | 0.00041581 | 40 | 18920 | Unplanned | Defective Equipment | failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1166 | 18647 | Frankton | CB7782 | 2024-09-13 11:46 | 2024-09-13 11:55 | 0.0039294 | 0.0004366 | 42 | 378 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1167 | 18618 | Alexandra | CB168 | 2024-09-13 12:17 | 2024-09-13 12:49 | 0.027391 | 0.00088359 | 85 | 2635 | Unplanned | Defective Equipment | 33/66kv to 11/6.6kv line clash | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1168 | 18619 | Alexandra | CB168 | 2024-09-13 12:17 | 2024-09-13 12:50 | 0.029845 | 0.00090438 | 87 | 2871 | Unplanned | Defective Equipment | 33/66kv to 11/6.6kv line clash | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1169 | 18617 | Alexandra | CB168 | 2024-09-13 12:17 | 2024-09-13 12:43 | 0.0434 | 0.001736 | 167 | 4175 | Unplanned | Defective Equipment | 33/66kv to 11/6.6kv line clash | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1170 | 18616 | Alexandra | CB168 | 2024-09-13 12:17 | 2024-09-13 12:41 | 0.075553 | 0.0032849 | 316 | 7268 | Unplanned | Defective Equipment | 33/66kv to 11/6.6kv line clash | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1171 | 18652 | Lindis Crossing | CB2086 | 2024-09-13 12:31 | 2024-09-13 17:12 | 0.13437 | 0.00047818 | 46 | 12926 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1172 | 18623 | Alexandra | CB168 | 2024-09-13 12:43 | 2024-09-13 14:46 | 0.024294 | 0.00019751 | 19 | 2337 | Unplanned | Defective Equipment | 33/66kv to 11/6.6kv line clash | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1173 | 18624 | Alexandra | CB168 | 2024-09-13 12:43 | 2024-09-13 14:48 | 0.073473 | 0.00059253 | 57 | 7068 | Unplanned | Defective Equipment | 33/66kv to 11/6.6kv line clash | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1174 | 18622 | Alexandra | CB168 | 2024-09-13 12:43 | 2024-09-13 13:30 | 0.043514 | 0.00094597 | 91 | 4186 | Unplanned | Defective Equipment | 33/66kv to 11/6.6kv line clash | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1175 | 18628 | Alexandra | CB168 | 2024-09-13 13:22 | 2024-09-13 19:48 | 0.0040126 | 1.0395e-05 | 1 | 386 | Unplanned | Defective Equipment | 33/66kv to 11/6.6kv line clash | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1176 | 18627 | Alexandra | CB168 | 2024-09-13 13:22 | 2024-09-13 19:47 | 0.32333 | 0.00084201 | 81 | 31104 | Unplanned | Defective Equipment | 33/66kv to 11/6.6kv line clash | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1177 | 18626 | Alexandra | CB168 | 2024-09-13 13:22 | 2024-09-13 16:22 | 0.27506 | 0.0015281 | 147 | 26460 | Unplanned | Defective Equipment | 33/66kv to 11/6.6kv line clash | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1178 | 18604 | Alexandra | CB168 | 2024-09-13 16:13 | 2024-09-13 17:35 | 0.0017048 | 2.079e-05 | 2 | 164 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1179 | 18605 | Alexandra | CB168 | 2024-09-13 16:13 | 2024-09-13 19:04 | 0.014221 | 8.3162e-05 | 8 | 1368 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1180 | 18629 | Alexandra | CB168 | 2024-09-13 16:23 | 2024-09-13 16:50 | 0.0042101 | 0.00015593 | 15 | 405 | Unplanned | Defective Equipment | 33/66kv to 11/6.6kv line clash | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1181 | 18631 | Alexandra | CB168 | 2024-09-13 16:23 | 2024-09-13 19:37 | 0.068567 | 0.00035344 | 34 | 6596 | Unplanned | Defective Equipment | 33/66kv to 11/6.6kv line clash | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1182 | 18630 | Alexandra | CB168 | 2024-09-13 16:23 | 2024-09-13 17:27 | 0.065199 | 0.0010187 | 98 | 6272 | Unplanned | Defective Equipment | 33/66kv to 11/6.6kv line clash | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1183 | 18632 | Alexandra | CB168 | 2024-09-13 16:50 | 2024-09-13 17:16 | 0.0038982 | 0.00015593 | 15 | 375 | Unplanned | Defective Equipment | 33/66kv to 11/6.6kv line clash | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1184 | 18633 | Alexandra | CB168 | 2024-09-13 17:17 | 2024-09-13 19:37 | 0.02183 | 0.00015593 | 15 | 2100 | Unplanned | Defective Equipment | 33/66kv to 11/6.6kv line clash | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1185 | 18689 | Frankton | CB7789 | 2024-09-13 20:28 | 2024-09-13 21:02 | 0.0010603 | 3.1186e-05 | 3 | 102 | Unplanned | Third-party Interference | cable damaged | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1186 | 18690 | Frankton | CB7789 | 2024-09-13 20:56 | 2024-09-13 21:02 | 0.0088567 | 0.0014761 | 142 | 852 | Unplanned | Third-party Interference | cable damaged | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1187 | 18666 | Lindis Crossing | CB2084 | 2024-09-13 21:12 | 2024-09-13 21:22 | 0.0011435 | 0.00011435 | 11 | 110 | Unplanned | Defective Equipment | failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1188 | 18598 | Nth East Valley | NV6 | 2024-09-15 10:13 | 2024-09-15 14:02 | 0.1952 | 0.00085241 | 82 | 18778 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1189 | 18693 | Andersons Bay | AB8 | 2024-09-16 08:01 | 2024-09-16 16:05 | 0.0050313 | 1.0395e-05 | 1 | 484 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1190 | 18695 | Andersons Bay | AB8 | 2024-09-16 08:01 | 2024-09-16 16:05 | 0.11572 | 0.00023909 | 23 | 11132 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1191 | 18694 | Andersons Bay | AB8 | 2024-09-16 08:01 | 2024-09-16 16:05 | 0.15094 | 0.00031186 | 30 | 14520 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1192 | 18678 | Wanaka | CB2757 | 2024-09-16 09:12 | 2024-09-16 17:50 | 0.11308 | 0.0002183 | 21 | 10878 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1193 | 18833 | Frankton | CB7783 | 2024-09-16 17:47 | 2024-09-16 18:06 | 0.00019751 | 1.0395e-05 | 1 | 19 | Unplanned | Defective Equipment | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1194 | 18691 | Omakau | CB656 | 2024-09-16 19:14 | 2024-09-16 19:20 | 6.2371e-05 | 1.0395e-05 | 1 | 6 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1195 | 18696 | Roxburgh | CB4637 | 2024-09-17 08:13 | 2024-09-17 17:14 | 1.0966 | 0.0020271 | 195 | 105495 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1196 | 18698 | Nth East Valley | NV4 | 2024-09-17 08:27 | 2024-09-17 15:47 | 0.47111 | 0.0010707 | 103 | 45320 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1197 | 18697 | Nth East Valley | NV4 | 2024-09-17 08:35 | 2024-09-17 15:38 | 0.17149 | 0.00040541 | 39 | 16497 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1198 | 18702 | Green Island | GI6 | 2024-09-17 08:38 | 2024-09-17 16:50 | 0.010229 | 2.079e-05 | 2 | 984 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1199 | 18701 | Green Island | GI6 | 2024-09-17 08:38 | 2024-09-17 16:28 | 0.097715 | 0.0002079 | 20 | 9400 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1200 | 18700 | Green Island | GI6 | 2024-09-17 08:38 | 2024-09-17 16:17 | 0.25288 | 0.00055095 | 53 | 24327 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1201 | 18709 | Roxburgh | CB4635 | 2024-09-17 09:03 | 2024-09-17 15:42 | 0.016591 | 4.1581e-05 | 4 | 1596 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1202 | 18708 | Roxburgh | CB4635 | 2024-09-17 09:03 | 2024-09-17 15:42 | 0.078806 | 0.00019751 | 19 | 7581 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1203 | 18699 | Commonage | CB5731 | 2024-09-17 10:03 | 2024-09-17 15:52 | 0.11247 | 0.00032225 | 31 | 10819 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1204 | 18713 | Roxburgh | CB4635 | 2024-09-18 08:49 | 2024-09-18 12:20 | 0.017547 | 8.3162e-05 | 8 | 1688 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1205 | 18710 | Omakau | CB656 | 2024-09-18 09:01 | 2024-09-18 16:06 | 0.16346 | 0.00038462 | 37 | 15725 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1206 | 18714 | Wanaka | CB2758 | 2024-09-18 09:09 | 2024-09-18 14:13 | 0.3571 | 0.0011747 | 113 | 34352 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1207 | 18711 | Queenstown | CB5212 | 2024-09-18 10:20 | 2024-09-18 17:11 | 0.4187 | 0.0010187 | 98 | 40278 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1208 | 18715 | Roxburgh | CB4635 | 2024-09-18 13:14 | 2024-09-18 15:20 | 0.0013098 | 1.0395e-05 | 1 | 126 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1209 | 18725 | Roxburgh | CB4637 | 2024-09-19 08:05 | 2024-09-19 14:47 | 0.15044 | 0.00037423 | 36 | 14472 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1210 | 18724 | Roxburgh | CB4637 | 2024-09-19 08:05 | 2024-09-19 14:33 | 0.31057 | 0.00080043 | 77 | 29876 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1211 | 18726 | Roxburgh | CB4635 | 2024-09-19 08:35 | 2024-09-19 10:16 | 0.0010499 | 1.0395e-05 | 1 | 101 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1212 | 18735 | Omakau | CB656 | 2024-09-19 09:03 | 2024-09-19 09:05 | 4.1581e-05 | 2.079e-05 | 2 | 4 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1213 | 18736 | Omakau | CB656 | 2024-09-19 09:05 | 2024-09-19 09:07 | 2.079e-05 | 1.0395e-05 | 1 | 2 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1214 | 18737 | Omakau | CB656 | 2024-09-19 09:12 | 2024-09-19 09:21 | 0.0031809 | 0.00035344 | 34 | 306 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1215 | 18738 | Omakau | CB656 | 2024-09-19 16:01 | 2024-09-19 16:06 | 0.0017672 | 0.00035344 | 34 | 170 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1216 | 18739 | Omakau | CB656 | 2024-09-19 16:13 | 2024-09-19 16:17 | 4.1581e-05 | 1.0395e-05 | 1 | 4 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1217 | 18740 | Omakau | CB656 | 2024-09-19 16:13 | 2024-09-19 16:22 | 0.00018711 | 2.079e-05 | 2 | 18 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1218 | 18746 | Omakau | CB656 | 2024-09-20 04:54 | 2024-09-20 04:55 | 0.00090438 | 0.00090438 | 87 | 87 | Unplanned | Wildlife | bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1219 | 18744 | Roxburgh | CB4635 | 2024-09-20 08:38 | 2024-09-20 13:30 | 0.0030354 | 1.0395e-05 | 1 | 292 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1220 | 18745 | Corstorphine | CO7 | 2024-09-20 09:09 | 2024-09-20 12:18 | 0.011788 | 6.2371e-05 | 6 | 1134 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1221 | 18758 | Omakau | CB656 | 2024-09-20 09:16 | 2024-09-20 09:20 | 0.00012474 | 3.1186e-05 | 3 | 12 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1222 | 18747 | Omakau | CB656 | 2024-09-20 09:21 | 2024-09-20 09:35 | 0.0016009 | 0.00011435 | 11 | 154 | Unplanned | Wildlife | bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1223 | 18760 | Omakau | CB656 | 2024-09-20 09:24 | 2024-09-20 09:29 | 5.1976e-05 | 1.0395e-05 | 1 | 5 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1224 | 18759 | Omakau | CB656 | 2024-09-20 09:24 | 2024-09-20 09:29 | 0.0002079 | 4.1581e-05 | 4 | 20 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1225 | 18761 | Omakau | CB656 | 2024-09-20 09:31 | 2024-09-20 09:40 | 0.00028067 | 3.1186e-05 | 3 | 27 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1226 | 18762 | Omakau | CB656 | 2024-09-20 09:31 | 2024-09-20 09:42 | 0.002973 | 0.00027028 | 26 | 286 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1227 | 18781 | Port Chalmers | PC4 | 2024-09-20 10:42 | 2024-09-20 11:02 | 0.0035344 | 0.00017672 | 17 | 340 | Unplanned | Adverse Environment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1228 | 18782 | Port Chalmers | PC4 | 2024-09-20 15:56 | 2024-09-20 16:17 | 0.0037111 | 0.00017672 | 17 | 357 | Unplanned | Adverse Environment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1229 | 18763 | Omakau | CB656 | 2024-09-20 16:03 | 2024-09-20 16:18 | 0.00046779 | 3.1186e-05 | 3 | 45 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1230 | 18764 | Omakau | CB656 | 2024-09-20 16:05 | 2024-09-20 16:18 | 0.0027028 | 0.0002079 | 20 | 260 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1231 | 18765 | Omakau | CB656 | 2024-09-20 16:05 | 2024-09-20 16:18 | 0.0035136 | 0.00027028 | 26 | 338 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1232 | 18752 | Omakau | CB656 | 2024-09-21 08:40 | 2024-09-21 10:10 | 0.00093557 | 1.0395e-05 | 1 | 90 | Unplanned | Wildlife | bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1233 | 18742 | Cromwell | CB822 | 2024-09-21 09:12 | 2024-09-21 15:09 | 0.0037111 | 1.0395e-05 | 1 | 357 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1234 | 18786 | Omakau | CB656 | 2024-09-23 09:04 | 2024-09-23 09:21 | 0.00017672 | 1.0395e-05 | 1 | 17 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1235 | 18784 | Omakau | CB656 | 2024-09-23 09:04 | 2024-09-23 09:12 | 0.00024949 | 3.1186e-05 | 3 | 24 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1236 | 18787 | Omakau | CB656 | 2024-09-23 09:04 | 2024-09-23 09:21 | 0.00053016 | 3.1186e-05 | 3 | 51 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1237 | 18785 | Omakau | CB656 | 2024-09-23 09:04 | 2024-09-23 09:21 | 0.00070688 | 4.1581e-05 | 4 | 68 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1238 | 18783 | Omakau | CB656 | 2024-09-23 09:04 | 2024-09-23 09:11 | 0.0018919 | 0.00027028 | 26 | 182 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1239 | 18772 | Alexandra | CB169 | 2024-09-23 09:58 | 2024-09-23 13:50 | 0.040999 | 0.00017672 | 17 | 3944 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1240 | 18788 | Omakau | CB656 | 2024-09-23 16:01 | 2024-09-23 16:05 | 0.00012474 | 3.1186e-05 | 3 | 12 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1241 | 18789 | Omakau | CB656 | 2024-09-23 16:01 | 2024-09-23 16:05 | 0.0010811 | 0.00027028 | 26 | 104 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1242 | 18791 | Omakau | CB656 | 2024-09-23 16:33 | 2024-09-23 16:34 | 1.0395e-05 | 1.0395e-05 | 1 | 1 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1243 | 18790 | Omakau | CB656 | 2024-09-23 16:33 | 2024-09-23 16:34 | 3.1186e-05 | 3.1186e-05 | 3 | 3 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1244 | 18792 | Omakau | CB656 | 2024-09-23 16:33 | 2024-09-23 16:34 | 4.1581e-05 | 4.1581e-05 | 4 | 4 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1245 | 18809 | Roxburgh | CB4635 | 2024-09-24 09:01 | 2024-09-24 15:02 | 0.0037527 | 1.0395e-05 | 1 | 361 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1246 | 18808 | Roxburgh | CB4635 | 2024-09-24 09:01 | 2024-09-24 15:02 | 0.078806 | 0.0002183 | 21 | 7581 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1247 | 18811 | Alexandra | CB169 | 2024-09-24 09:02 | 2024-09-24 15:52 | 0.004262 | 1.0395e-05 | 1 | 410 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1248 | 18810 | Alexandra | CB169 | 2024-09-24 09:02 | 2024-09-24 15:33 | 0.10161 | 0.00025988 | 25 | 9775 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1249 | 18794 | Arrowtown | CB7632 | 2024-09-24 09:05 | 2024-09-24 15:12 | 0.0076301 | 2.079e-05 | 2 | 734 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1250 | 18793 | Arrowtown | CB7632 | 2024-09-24 09:05 | 2024-09-24 14:48 | 0.26308 | 0.00076925 | 74 | 25308 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1251 | 18812 | Omakau | CB656 | 2024-09-24 09:05 | 2024-09-24 09:09 | 0.00033265 | 8.3162e-05 | 8 | 32 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1252 | 18813 | Omakau | CB656 | 2024-09-24 09:05 | 2024-09-24 16:07 | 0.12722 | 0.00030146 | 29 | 12238 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1253 | 18814 | Omakau | CB656 | 2024-09-24 15:50 | 2024-09-24 16:07 | 0.0035344 | 0.0002079 | 20 | 340 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1254 | 18815 | Omakau | CB656 | 2024-09-24 15:54 | 2024-09-24 16:07 | 0.0010811 | 8.3162e-05 | 8 | 104 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1255 | 18806 | Port Chalmers | PC3 | 2024-09-24 16:29 | 2024-09-24 18:19 | 0.053255 | 0.00048858 | 47 | 5123 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1256 | 18818 | Wanaka | CB2757 | 2024-09-25 07:45 | 2024-09-25 08:01 | 0.00049897 | 3.1186e-05 | 3 | 48 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1257 | 18816 | East Taieri | ET2 | 2024-09-25 08:04 | 2024-09-25 11:55 | 0.040645 | 0.00017672 | 17 | 3910 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1258 | 18819 | Wanaka | CB2757 | 2024-09-25 08:31 | 2024-09-25 16:00 | 1.1249 | 0.0025052 | 241 | 108209 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1259 | 18828 | Camp Hill | CB2008 | 2024-09-25 09:05 | 2024-09-25 14:19 | 0.058754 | 0.00018711 | 18 | 5652 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1260 | 18820 | Wanaka | CB2757 | 2024-09-25 15:45 | 2024-09-25 16:00 | 0.00046779 | 3.1186e-05 | 3 | 45 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1261 | 18825 | Corstorphine | CO2 | 2024-09-25 16:05 | 2024-09-25 18:32 | 0.045843 | 0.00031186 | 30 | 4410 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1262 | 18826 | Corstorphine | CO2 | 2024-09-25 17:09 | 2024-09-25 18:32 | 0.051768 | 0.00062371 | 60 | 4980 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1263 | 18847 | Cromwell | CB832 | 2024-09-26 09:01 | 2024-09-26 16:30 | 3.5239 | 0.0078484 | 755 | 338995 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1264 | 18843 | Alexandra | CB169 | 2024-09-26 09:03 | 2024-09-26 15:47 | 0.0083993 | 2.079e-05 | 2 | 808 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1265 | 18842 | Alexandra | CB169 | 2024-09-26 09:03 | 2024-09-26 15:47 | 0.037797 | 9.3557e-05 | 9 | 3636 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1266 | 18841 | Alexandra | CB169 | 2024-09-26 09:03 | 2024-09-26 15:47 | 0.062995 | 0.00015593 | 15 | 6060 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1267 | 18846 | Cromwell | CB832 | 2024-09-26 09:07 | 2024-09-26 15:47 | 0.016632 | 4.1581e-05 | 4 | 1600 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1268 | 18844 | Cromwell | CB832 | 2024-09-26 09:07 | 2024-09-26 09:18 | 0.00057174 | 5.1976e-05 | 5 | 55 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1269 | 18845 | Cromwell | CB832 | 2024-09-26 09:07 | 2024-09-26 15:41 | 0.020479 | 5.1976e-05 | 5 | 1970 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1270 | 18908 | Wanaka | CB2754 | 2024-09-26 09:50 | 2024-09-26 12:00 | 0.0013514 | 1.0395e-05 | 1 | 130 | Unplanned | Wildlife | animal in equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1271 | 18829 | Clyde-Earnscleugh | CB190 | 2024-09-26 13:05 | 2024-09-26 15:07 | 0.13316 | 0.0010915 | 105 | 12810 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1272 | 18854 | Cromwell | CB823 | 2024-09-26 14:13 | 2024-09-26 18:00 | 0.10572 | 0.00046779 | 45 | 10170 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1273 | 18853 | Cromwell | CB823 | 2024-09-26 14:13 | 2024-09-26 17:46 | 0.18732 | 0.00088359 | 85 | 18020 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1274 | 18851 | Cromwell | CB823 | 2024-09-26 14:13 | 2024-09-26 14:47 | 0.03499 | 0.0010603 | 102 | 3366 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1275 | 18852 | Cromwell | CB823 | 2024-09-26 14:13 | 2024-09-26 14:51 | 0.089233 | 0.0024117 | 232 | 8584 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1276 | 18855 | Cromwell | CB823 | 2024-09-26 18:10 | 2024-09-26 19:49 | 0.087476 | 0.00088359 | 85 | 8415 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1277 | 18859 | Camp Hill | CB2006 | 2024-09-26 18:23 | 2024-09-26 20:31 | 0.0052808 | 4.1581e-05 | 4 | 508 | Unplanned | Wildlife | possum on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1278 | 18858 | Camp Hill | CB2006 | 2024-09-26 18:23 | 2024-09-26 19:45 | 0.010104 | 0.00012474 | 12 | 972 | Unplanned | Wildlife | possum on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1279 | 18861 | Camp Hill | CB2006 | 2024-09-26 18:23 | 2024-09-26 21:22 | 0.090667 | 0.00050937 | 49 | 8722 | Unplanned | Wildlife | possum on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1280 | 18860 | Camp Hill | CB2006 | 2024-09-26 18:23 | 2024-09-26 21:10 | 0.10181 | 0.00061332 | 59 | 9794 | Unplanned | Wildlife | possum on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1281 | 18849 | Clyde-Earnscleugh | CB195 | 2024-09-27 08:32 | 2024-09-27 11:44 | 0.051893 | 0.00027028 | 26 | 4992 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1282 | 18856 | Cromwell | CB823 | 2024-09-27 14:20 | 2024-09-27 15:23 | 0.02947 | 0.00046779 | 45 | 2835 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1283 | 18857 | Cromwell | CB823 | 2024-09-27 14:20 | 2024-09-27 15:29 | 0.060968 | 0.00088359 | 85 | 5865 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1284 | 18912 | Roxburgh | CB4633 | 2024-09-27 22:29 | 2024-09-28 01:43 | 0.11035 | 0.00057174 | 55 | 10615 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1285 | 18910 | Roxburgh | CB4639 | 2024-09-27 22:29 | 2024-09-28 00:51 | 0.19054 | 0.0013514 | 130 | 18330 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1286 | 18911 | Roxburgh | CB4635 | 2024-09-27 22:29 | 2024-09-28 01:03 | 0.29583 | 0.0019335 | 186 | 28458 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1287 | 18909 | Roxburgh | CB4637 | 2024-09-27 22:29 | 2024-09-28 00:39 | 0.67028 | 0.005156 | 496 | 64480 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1288 | 18869 | Alexandra | CB168 | 2024-09-29 15:48 | 2024-09-29 16:08 | 0.23743 | 0.011871 | 1142 | 22840 | Unplanned | Defective Equipment | faulty pothead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1289 | 18893 | Alexandra | CB199 | 2024-09-29 15:51 | 2024-09-29 16:21 | 0.011227 | 0.00037423 | 36 | 1080 | Unplanned | Defective Equipment | faulty pothead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1290 | 18895 | Alexandra | CB192 | 2024-09-29 15:51 | 2024-09-29 16:23 | 0.036092 | 0.0011643 | 112 | 3472 | Unplanned | Defective Equipment | faulty pothead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1291 | 18896 | Alexandra | CB195 | 2024-09-29 15:51 | 2024-09-29 16:26 | 0.1898 | 0.0055822 | 537 | 18258 | Unplanned | Defective Equipment | faulty pothead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1292 | 18894 | Alexandra | CB190 | 2024-09-29 15:51 | 2024-09-29 16:22 | 0.21365 | 0.006892 | 663 | 20553 | Unplanned | Defective Equipment | faulty pothead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1293 | 18897 | Alexandra | CB6576 | 2024-09-29 15:51 | 2024-09-29 16:14 | 0.054752 | 0.0023805 | 229 | 5267 | Unplanned | Defective Equipment | faulty pothead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1294 | 18898 | Alexandra | CB656 | 2024-09-29 15:51 | 2024-09-29 16:17 | 0.18244 | 0.0072974 | 702 | 17550 | Unplanned | Defective Equipment | faulty pothead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1295 | 18870 | Alexandra | CB163 | 2024-09-29 15:52 | 2024-09-29 16:09 | 0.2242 | 0.014013 | 1348 | 21568 | Unplanned | Defective Equipment | faulty pothead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1296 | 18891 | Alexandra | CB169 | 2024-09-30 09:10 | 2024-09-30 15:30 | 0.0039502 | 1.0395e-05 | 1 | 380 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1297 | 18892 | Alexandra | CB169 | 2024-09-30 09:10 | 2024-09-30 15:35 | 0.0080043 | 2.079e-05 | 2 | 770 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1298 | 18890 | Alexandra | CB169 | 2024-09-30 09:10 | 2024-09-30 15:15 | 0.041737 | 0.00011435 | 11 | 4015 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1299 | 18889 | Willowbank | WB11 | 2024-09-30 09:35 | 2024-09-30 15:15 | 0.34637 | 0.0010187 | 98 | 33320 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1300 | 18914 | Camp Hill | CB2004 | 2024-09-30 20:25 | 2024-09-30 22:00 | 0.00097715 | 1.0395e-05 | 1 | 94 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1301 | 18918 | Cromwell | CB822 | 2024-09-30 20:53 | 2024-09-30 21:44 | 0.011663 | 0.00022869 | 22 | 1122 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1302 | 18913 | Camp Hill | CB2004 | 2024-09-30 22:00 | 2024-09-30 22:02 | 0.00022869 | 0.00011435 | 11 | 22 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1303 | 18921 | Andersons Bay | AB8 | 2024-10-01 08:02 | 2024-10-01 14:39 | 0.0041269 | 1.0395e-05 | 1 | 397 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1304 | 18920 | Andersons Bay | AB8 | 2024-10-01 08:02 | 2024-10-01 14:39 | 0.094919 | 0.00023909 | 23 | 9131 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1305 | 18922 | Andersons Bay | AB8 | 2024-10-01 08:02 | 2024-10-01 14:39 | 0.12381 | 0.00031186 | 30 | 11910 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1306 | 18919 | Andersons Bay | AB8 | 2024-10-01 08:09 | 2024-10-01 14:35 | 0.27687 | 0.00071727 | 69 | 26634 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1307 | 18927 | Roxburgh | CB4637 | 2024-10-01 08:34 | 2024-10-01 15:48 | 0.0045011 | 1.0395e-05 | 1 | 433 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1308 | 18930 | Roxburgh | CB4637 | 2024-10-01 08:34 | 2024-10-01 16:08 | 0.1699 | 0.00037423 | 36 | 16344 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1309 | 18928 | Roxburgh | CB4637 | 2024-10-01 08:34 | 2024-10-01 16:00 | 0.35699 | 0.00080043 | 77 | 34342 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1310 | 19081 | Roxburgh | CB4637 | 2024-10-01 08:34 | 2024-10-01 16:00 | 0.0046363 | 1.0395e-05 | 1 | 446 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1311 | 18923 | East Taieri | ET7 | 2024-10-01 08:48 | 2024-10-01 16:31 | 0.009626 | 2.079e-05 | 2 | 926 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1312 | 18924 | East Taieri | ET7 | 2024-10-01 08:48 | 2024-10-01 16:57 | 0.52866 | 0.0010811 | 104 | 50856 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1313 | 18907 | Alexandra | CB168 | 2024-10-01 09:35 | 2024-10-01 12:18 | 0.10167 | 0.00062371 | 60 | 9780 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1314 | 18935 | Camp Hill | CB2004 | 2024-10-02 08:33 | 2024-10-02 13:58 | 0.10473 | 0.00032225 | 31 | 10075 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1315 | 18941 | Alexandra | CB168 | 2024-10-02 08:34 | 2024-10-02 15:30 | 0.0043244 | 1.0395e-05 | 1 | 416 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1316 | 18945 | Alexandra | CB168 | 2024-10-02 08:34 | 2024-10-02 15:44 | 0.0044699 | 1.0395e-05 | 1 | 430 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1317 | 18946 | Alexandra | CB168 | 2024-10-02 08:34 | 2024-10-02 15:49 | 0.0045219 | 1.0395e-05 | 1 | 435 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1318 | 18942 | Alexandra | CB168 | 2024-10-02 08:34 | 2024-10-02 15:35 | 0.017506 | 4.1581e-05 | 4 | 1684 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1319 | 18944 | Alexandra | CB168 | 2024-10-02 08:34 | 2024-10-02 15:40 | 0.02657 | 6.2371e-05 | 6 | 2556 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1320 | 18943 | Alexandra | CB168 | 2024-10-02 08:34 | 2024-10-02 15:37 | 0.03078 | 7.2767e-05 | 7 | 2961 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1321 | 18940 | Alexandra | CB168 | 2024-10-02 08:34 | 2024-10-02 15:24 | 0.20458 | 0.00049897 | 48 | 19680 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1322 | 18947 | Alexandra | CB168 | 2024-10-02 08:34 | 2024-10-02 15:49 | 0.013566 | 3.1186e-05 | 3 | 1305 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1323 | 18931 | East Taieri | ET8 | 2024-10-02 09:00 | 2024-10-02 15:01 | 0.045032 | 0.00012474 | 12 | 4332 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1324 | 18932 | Wanaka | CB2751 | 2024-10-02 09:02 | 2024-10-02 17:00 | 0.35279 | 0.00073806 | 71 | 33938 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1325 | 18956 | Queensberry | CB2423 | 2024-10-02 14:45 | 2024-10-02 18:44 | 0.97391 | 0.0040749 | 392 | 93688 | Unplanned | Defective Equipment | broken tie wire (floater) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1326 | 18953 | Commonage | CB5730 | 2024-10-03 08:21 | 2024-10-03 13:23 | 0.33905 | 0.0011227 | 108 | 32616 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1327 | 18950 | East Taieri | ET5 | 2024-10-03 08:32 | 2024-10-03 13:55 | 0.040292 | 0.00012474 | 12 | 3876 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1328 | 18949 | East Taieri | ET5 | 2024-10-03 08:40 | 2024-10-03 13:43 | 0.044097 | 0.00014553 | 14 | 4242 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1329 | 18972 | Camp Hill | CB2004 | 2024-10-03 09:00 | 2024-10-03 17:44 | 0.0054471 | 1.0395e-05 | 1 | 524 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1330 | 18969 | Camp Hill | CB2004 | 2024-10-03 09:01 | 2024-10-03 17:35 | 0.0053431 | 1.0395e-05 | 1 | 514 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1331 | 18970 | Camp Hill | CB2004 | 2024-10-03 09:01 | 2024-10-03 17:39 | 0.0053847 | 1.0395e-05 | 1 | 518 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1332 | 18971 | Camp Hill | CB2004 | 2024-10-03 09:01 | 2024-10-03 17:42 | 0.0054159 | 1.0395e-05 | 1 | 521 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1333 | 18973 | Camp Hill | CB2004 | 2024-10-03 09:01 | 2024-10-03 17:47 | 0.0054679 | 1.0395e-05 | 1 | 526 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1334 | 18968 | Camp Hill | CB2004 | 2024-10-03 09:01 | 2024-10-03 17:35 | 0.080147 | 0.00015593 | 15 | 7710 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1335 | 18952 | Cromwell | CB822 | 2024-10-03 09:02 | 2024-10-03 09:40 | 0.0019751 | 5.1976e-05 | 5 | 190 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1336 | 18962 | East Taieri | ET6 | 2024-10-03 12:00 | 2024-10-03 13:59 | 0.029689 | 0.00024949 | 24 | 2856 | Unplanned | Defective Equipment | hv isolation for lv fuse replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1337 | 18963 | East Taieri | ET6 | 2024-10-03 13:57 | 2024-10-03 13:59 | 0.0011643 | 0.00058213 | 56 | 112 | Unplanned | Defective Equipment | hv isolation for lv fuse replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1338 | 18978 | Port Chalmers | PC3 | 2024-10-03 15:20 | 2024-10-03 17:32 | 0.03156 | 0.00023909 | 23 | 3036 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1339 | 18979 | Port Chalmers | PC3 | 2024-10-03 15:20 | 2024-10-04 15:51 | 0.36674 | 0.00024949 | 24 | 35280 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1340 | 18983 | Andersons Bay | AB9 | 2024-10-04 00:43 | 2024-10-04 16:49 | 0.050209 | 5.1976e-05 | 5 | 4830 | Unplanned | Adverse Environment | broken pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1341 | 18982 | Andersons Bay | AB9 | 2024-10-04 00:43 | 2024-10-04 02:42 | 0.019793 | 0.00016632 | 16 | 1904 | Unplanned | Adverse Environment | broken pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1342 | 18981 | Andersons Bay | AB9 | 2024-10-04 00:43 | 2024-10-04 02:05 | 0.035801 | 0.0004366 | 42 | 3444 | Unplanned | Adverse Environment | broken pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1343 | 18991 | Ward Street | WS8 | 2024-10-04 11:48 | 2024-10-04 16:19 | 0.1155 | 0.0004262 | 41 | 11111 | Unplanned | Adverse Environment | flooding | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1344 | 18988 | Omakau | CB656 | 2024-10-04 17:03 | 2024-10-04 17:29 | 0.19054 | 0.0073286 | 705 | 18330 | Unplanned | Adverse Environment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1345 | 18992 | Andersons Bay | AB6 | 2024-10-05 12:22 | 2024-10-05 12:53 | 0.023202 | 0.00074846 | 72 | 2232 | Unplanned | Defective Equipment | faulty lightning arrestor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1346 | 19005 | Outram | OT3 | 2024-10-06 04:14 | 2024-10-06 07:25 | 0.027797 | 0.00014553 | 14 | 2674 | Unplanned | Wildlife | possum on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1347 | 19004 | Outram | OT3 | 2024-10-06 04:14 | 2024-10-06 06:55 | 0.097071 | 0.00060292 | 58 | 9338 | Unplanned | Wildlife | possum on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1348 | 19006 | Outram | OT3 | 2024-10-06 04:14 | 2024-10-06 07:52 | 0.1677 | 0.00076925 | 74 | 16132 | Unplanned | Wildlife | possum on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1349 | 19003 | Outram | OT3 | 2024-10-06 04:14 | 2024-10-06 06:39 | 0.14169 | 0.00097715 | 94 | 13630 | Unplanned | Wildlife | possum on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1350 | 19020 | Omakau | CB656 | 2024-10-06 20:44 | 2024-10-06 23:02 | 0.025635 | 0.00018711 | 18 | 2466 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1351 | 19019 | Omakau | CB656 | 2024-10-06 20:44 | 2024-10-06 22:42 | 0.023109 | 0.00019751 | 19 | 2223 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1352 | 19021 | Omakau | CB656 | 2024-10-06 20:44 | 2024-10-06 23:04 | 0.028899 | 0.0002079 | 20 | 2780 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1353 | 19018 | Omakau | CB656 | 2024-10-06 20:44 | 2024-10-06 22:06 | 0.023576 | 0.00029107 | 28 | 2268 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1354 | 19011 | Wanaka | CB2754 | 2024-10-06 20:50 | 2024-10-06 22:21 | 0.00094597 | 1.0395e-05 | 1 | 91 | Unplanned | Wildlife | bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1355 | 19012 | North City | NC6 | 2024-10-06 22:31 | 2024-10-06 22:56 | 0.082902 | 0.0033161 | 319 | 7975 | Unplanned | Adverse Environment | fire/smoke | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1356 | 19001 | Arrowtown | CB7632 | 2024-10-07 09:07 | 2024-10-07 14:08 | 0.03129 | 0.00010395 | 10 | 3010 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1357 | 19114 | Ward Street | WS4 | 2024-10-07 14:45 | 2024-10-07 14:49 | 4.1581e-05 | 1.0395e-05 | 1 | 4 | Unplanned | Adverse Environment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1358 | 19033 | Wanaka | CB2757 | 2024-10-08 08:56 | 2024-10-08 09:09 | 0.16284 | 0.012526 | 1205 | 15665 | Unplanned | Human Error | switching error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1359 | 19025 | Lauder Flat | CB6576 | 2024-10-08 09:00 | 2024-10-08 12:13 | 0.0020063 | 1.0395e-05 | 1 | 193 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1360 | 19034 | Clyde-Earnscleugh | CB190 | 2024-10-08 09:03 | 2024-10-08 14:46 | 0.3102 | 0.00090438 | 87 | 29841 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1361 | 19035 | Clyde-Earnscleugh | CB190 | 2024-10-08 09:03 | 2024-10-08 14:46 | 0.37795 | 0.0011019 | 106 | 36358 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1362 | 19160 | Port Chalmers | PC4 | 2024-10-08 10:31 | 2024-10-08 17:13 | 0.0041789 | 1.0395e-05 | 1 | 402 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1363 | 19029 | Frankton | CB7784 | 2024-10-08 13:57 | 2024-10-08 14:00 | 0.049897 | 0.016632 | 1600 | 4800 | Unplanned | Third-party Interference | high load | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1364 | 19057 | Willowbank | WB3 | 2024-10-09 08:01 | 2024-10-09 12:30 | 0.1783 | 0.00066529 | 64 | 17152 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1365 | 19056 | Willowbank | WB3 | 2024-10-09 08:01 | 2024-10-09 12:29 | 1.1824 | 0.0044284 | 426 | 113742 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1366 | 19043 | Halfway Bush | HB6 | 2024-10-09 08:10 | 2024-10-09 16:04 | 0.14289 | 0.00030146 | 29 | 13746 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1367 | 19063 | Ettrick | CB480 | 2024-10-09 13:35 | 2024-10-09 15:23 | 0.1931 | 0.001788 | 172 | 18576 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1368 | 19061 | Berwick | BK1 | 2024-10-09 15:12 | 2024-10-09 17:40 | 0.0046155 | 3.1186e-05 | 3 | 444 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1369 | 19064 | Ettrick | CB480 | 2024-10-09 15:23 | 2024-10-09 15:33 | 0.0010291 | 0.00011435 | 11 | 99 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1370 | 19065 | Ettrick | CB480 | 2024-10-09 15:23 | 2024-10-09 15:39 | 0.0037423 | 0.00024949 | 24 | 360 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1371 | 19067 | Ettrick | CB480 | 2024-10-09 15:23 | 2024-10-09 15:43 | 0.0059253 | 0.00031186 | 30 | 570 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1372 | 19066 | Ettrick | CB480 | 2024-10-09 15:23 | 2024-10-09 15:42 | 0.020021 | 0.0011123 | 107 | 1926 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1373 | 19068 | Ettrick | CB480 | 2024-10-09 15:33 | 2024-10-10 00:36 | 0.061976 | 0.00011435 | 11 | 5962 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1374 | 19072 | Roxburgh | CB4633 | 2024-10-09 17:11 | 2024-10-10 00:59 | 0.038837 | 8.3162e-05 | 8 | 3736 | Unplanned | Defective Equipment | burning pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1375 | 19071 | Roxburgh | CB4633 | 2024-10-09 17:11 | 2024-10-09 18:13 | 0.029803 | 0.00048858 | 47 | 2867 | Unplanned | Defective Equipment | burning pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1376 | 19070 | Roxburgh | CB3432 | 2024-10-09 18:06 | 2024-10-10 01:18 | 0.0089815 | 2.079e-05 | 2 | 864 | Unplanned | Defective Equipment | burning pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1377 | 19054 | Green Island | GI8 | 2024-10-10 08:03 | 2024-10-10 16:23 | 1.1643 | 0.0023285 | 224 | 112000 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1378 | 19053 | Frankton | CB7782 | 2024-10-10 08:19 | 2024-10-10 16:46 | 0.0052704 | 1.0395e-05 | 1 | 507 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1379 | 19048 | Roxburgh | CB4637 | 2024-10-10 08:21 | 2024-10-10 08:45 | 0.00024949 | 1.0395e-05 | 1 | 24 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1380 | 19049 | Roxburgh | CB4637 | 2024-10-10 08:45 | 2024-10-10 08:53 | 0.0093973 | 0.0011747 | 113 | 904 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1381 | 19141 | Roxburgh | CB4637 | 2024-10-10 08:45 | 2024-10-10 08:53 | 8.3162e-05 | 1.0395e-05 | 1 | 8 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1382 | 19041 | Cromwell | CB832 | 2024-10-10 09:11 | 2024-10-10 15:27 | 0.0039086 | 1.0395e-05 | 1 | 376 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1383 | 19042 | Cromwell | CB832 | 2024-10-10 09:11 | 2024-10-10 15:28 | 0.003919 | 1.0395e-05 | 1 | 377 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1384 | 19080 | Lauder Flat | CB6576 | 2024-10-10 16:34 | 2024-10-10 16:52 | 0.0035552 | 0.00019751 | 19 | 342 | Unplanned | Adverse Environment | flooding | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1385 | 19051 | Roxburgh | CB4637 | 2024-10-10 16:54 | 2024-10-10 16:58 | 0.0046986 | 0.0011747 | 113 | 452 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1386 | 19142 | Roxburgh | CB4637 | 2024-10-10 16:54 | 2024-10-10 16:58 | 4.1581e-05 | 1.0395e-05 | 1 | 4 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1387 | 19087 | Omakau | CB656 | 2024-10-11 09:01 | 2024-10-11 17:25 | 0.45581 | 0.00090438 | 87 | 43848 | Unplanned | Adverse Environment | pole replacement - unplanned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1388 | 19088 | Omakau | CB656 | 2024-10-11 09:01 | 2024-10-11 17:17 | 0.87137 | 0.0017568 | 169 | 83824 | Unplanned | Adverse Environment | pole replacement - unplanned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1389 | 19082 | Queensberry | CB2424 | 2024-10-11 09:03 | 2024-10-11 12:36 | 0.017713 | 8.3162e-05 | 8 | 1704 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1390 | 19089 | Omakau | CB656 | 2024-10-11 09:04 | 2024-10-11 16:18 | 0.95644 | 0.0022038 | 212 | 92008 | Unplanned | Adverse Environment | pole replacement - unplanned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1391 | 19101 | East Taieri | ET3 | 2024-10-11 09:27 | 2024-10-11 10:52 | 0.00088359 | 1.0395e-05 | 1 | 85 | Unplanned | Defective Equipment | faulty pothead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1392 | 19115 | Ward Street | WS4 | 2024-10-11 13:53 | 2024-10-11 13:56 | 3.1186e-05 | 1.0395e-05 | 1 | 3 | Unplanned | Adverse Environment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1393 | 19093 | Omakau | CB656 | 2024-10-11 17:06 | 2024-10-11 17:19 | 0.011352 | 0.00094597 | 91 | 1092 | Unplanned | Adverse Environment | pole replacement - unplanned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1394 | 19092 | Omakau | CB656 | 2024-10-11 17:06 | 2024-10-11 17:17 | 0.014179 | 0.001289 | 124 | 1364 | Unplanned | Adverse Environment | pole replacement - unplanned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1395 | 19094 | Omakau | CB656 | 2024-10-11 17:07 | 2024-10-11 17:18 | 0.0045739 | 0.00041581 | 40 | 440 | Unplanned | Adverse Environment | pole replacement - unplanned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1396 | 19090 | Omakau | CB656 | 2024-10-11 17:14 | 2024-10-11 17:16 | 0.0040333 | 0.0020167 | 194 | 388 | Unplanned | Adverse Environment | pole replacement - unplanned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1397 | 19091 | Omakau | CB656 | 2024-10-11 18:11 | 2024-10-11 18:14 | 0.00059253 | 0.00019751 | 19 | 57 | Unplanned | Adverse Environment | pole replacement - unplanned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1398 | 19046 | Roxburgh | CB4637 | 2024-10-12 17:21 | 2024-10-12 17:24 | 3.1186e-05 | 1.0395e-05 | 1 | 3 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1399 | 19084 | Wanaka | CB2756 | 2024-10-14 08:34 | 2024-10-14 17:25 | 0.14352 | 0.00027028 | 26 | 13806 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1400 | 19083 | Wanaka | CB2756 | 2024-10-14 08:34 | 2024-10-14 17:14 | 0.31893 | 0.00061332 | 59 | 30680 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1401 | 19117 | Wanaka | CB2754 | 2024-10-15 08:02 | 2024-10-15 16:52 | 0.0055095 | 1.0395e-05 | 1 | 530 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1402 | 19118 | Wanaka | CB2754 | 2024-10-15 08:02 | 2024-10-15 16:52 | 0.011019 | 2.079e-05 | 2 | 1060 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1403 | 19119 | Wanaka | CB2754 | 2024-10-15 08:02 | 2024-10-15 17:25 | 0.011705 | 2.079e-05 | 2 | 1126 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1404 | 19116 | Wanaka | CB2754 | 2024-10-15 08:02 | 2024-10-15 16:52 | 0.65563 | 0.001237 | 119 | 63070 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1405 | 19120 | Wanaka | CB2754 | 2024-10-15 08:02 | 2024-10-15 16:52 | 0.0055095 | 1.0395e-05 | 1 | 530 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1406 | 19113 | East Taieri | ET3 | 2024-10-15 08:08 | 2024-10-15 09:16 | 0.030396 | 0.00044699 | 43 | 2924 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1407 | 19106 | Cromwell | CB821 | 2024-10-15 08:32 | 2024-10-15 11:52 | 0.13514 | 0.00067569 | 65 | 13000 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1408 | 19194 | Kaikorai Valley | KV7 | 2024-10-15 08:34 | 2024-10-15 12:38 | 0.15472 | 0.00063411 | 61 | 14884 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1409 | 19103 | Arrowtown | CB7662 | 2024-10-15 09:03 | 2024-10-15 13:48 | 0.20738 | 0.00072767 | 70 | 19950 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1410 | 19105 | Outram | OT2 | 2024-10-15 09:05 | 2024-10-15 16:26 | 0.0045843 | 1.0395e-05 | 1 | 441 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1411 | 19104 | Outram | OT2 | 2024-10-15 09:05 | 2024-10-15 16:12 | 0.78122 | 0.0018296 | 176 | 75152 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1412 | 19138 | Frankton | CB7784 | 2024-10-16 08:01 | 2024-10-16 14:34 | 0.27372 | 0.00069648 | 67 | 26331 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1413 | 19137 | Frankton | CB7784 | 2024-10-16 08:01 | 2024-10-16 14:34 | 0.44121 | 0.0011227 | 108 | 42444 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1414 | 19139 | Frankton | CB7784 | 2024-10-16 08:01 | 2024-10-16 16:45 | 2.7181 | 0.0051872 | 499 | 261476 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1415 | 19140 | Frankton | CB7784 | 2024-10-16 08:01 | 2024-10-16 16:45 | 0.0054471 | 1.0395e-05 | 1 | 524 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1416 | 19122 | Halfway Bush | HB4 | 2024-10-16 08:03 | 2024-10-16 16:27 | 1.0719 | 0.002131 | 205 | 103115 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1417 | 19125 | Wanaka | CB2751 | 2024-10-16 09:06 | 2024-10-16 14:03 | 0.35505 | 0.0011955 | 115 | 34155 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1418 | 19123 | Cromwell | CB822 | 2024-10-16 09:18 | 2024-10-16 15:11 | 0.0036695 | 1.0395e-05 | 1 | 353 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1419 | 19179 | Dalefield | CB7828 | 2024-10-16 15:16 | 2024-10-16 19:05 | 0.50229 | 0.0021934 | 211 | 48319 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1420 | 19178 | Dalefield | CB7828 | 2024-10-16 15:16 | 2024-10-16 17:29 | 0.31108 | 0.0023389 | 225 | 29925 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1421 | 19133 | Queenstown | CB5212 | 2024-10-16 16:52 | 2024-10-16 16:55 | 0.0042828 | 0.0021414 | 206 | 412 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1422 | 19131 | Wanaka | CB2758 | 2024-10-17 08:53 | 2024-10-17 09:02 | 0.0006549 | 7.2767e-05 | 7 | 63 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1423 | 19127 | Cromwell | CB822 | 2024-10-17 09:04 | 2024-10-17 15:03 | 0.085833 | 0.00023909 | 23 | 8257 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1424 | 19128 | Outram | OT2 | 2024-10-17 09:05 | 2024-10-17 15:51 | 0.74702 | 0.00184 | 177 | 71862 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1425 | 19129 | Cromwell | CB821 | 2024-10-17 09:10 | 2024-10-17 15:59 | 0.017007 | 4.1581e-05 | 4 | 1636 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1426 | 19195 | Kaikorai Valley | KV7 | 2024-10-17 16:15 | 2024-10-17 16:16 | 0.00063411 | 0.00063411 | 61 | 61 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1427 | 19340 | Frankton | CB7783 | 2024-10-17 22:58 | 2024-10-18 00:17 | 0.00082122 | 1.0395e-05 | 1 | 79 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1428 | 19151 | Frankton | CB7783 | 2024-10-17 22:58 | 2024-10-18 00:18 | 0.13879 | 0.0017568 | 169 | 13351 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1429 | 19149 | Nth East Valley | NV4 | 2024-10-18 08:36 | 2024-10-18 16:57 | 0.1927 | 0.00038462 | 37 | 18537 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1430 | 19150 | Roxburgh | CB4633 | 2024-10-18 09:31 | 2024-10-18 14:48 | 0.0098859 | 3.1186e-05 | 3 | 951 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1431 | 19166 | Ward Street | WS7 | 2024-10-21 09:04 | 2024-10-21 16:03 | 0.14373 | 0.00034304 | 33 | 13827 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1432 | 19168 | Cromwell | CB821 | 2024-10-21 09:07 | 2024-10-21 15:40 | 0.0040853 | 1.0395e-05 | 1 | 393 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1433 | 19167 | Cromwell | CB821 | 2024-10-21 09:08 | 2024-10-21 15:30 | 0.003971 | 1.0395e-05 | 1 | 382 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1434 | 19180 | Dalefield | CB7828 | 2024-10-21 22:30 | 2024-10-21 23:44 | 0.16231 | 0.0021934 | 211 | 15614 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1435 | 19171 | Roxburgh | CB4637 | 2024-10-22 08:08 | 2024-10-22 08:09 | 0.00011435 | 0.00011435 | 11 | 11 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1436 | 19175 | Roxburgh | CB4637 | 2024-10-22 08:14 | 2024-10-22 16:27 | 0.11275 | 0.00022869 | 22 | 10846 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1437 | 19172 | Roxburgh | CB4637 | 2024-10-22 08:14 | 2024-10-22 15:45 | 0.22504 | 0.00049897 | 48 | 21648 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1438 | 19169 | Cromwell | CB821 | 2024-10-22 08:32 | 2024-10-22 15:43 | 0.013441 | 3.1186e-05 | 3 | 1293 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1439 | 19164 | Carisbrook | CK8 | 2024-10-22 08:39 | 2024-10-22 17:18 | 0.32371 | 0.00062371 | 60 | 31140 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1440 | 19192 | Frankton | CB7782 | 2024-10-22 08:54 | 2024-10-22 16:40 | 0.014533 | 3.1186e-05 | 3 | 1398 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1441 | 19190 | Frankton | CB7782 | 2024-10-22 08:54 | 2024-10-22 09:08 | 0.00072767 | 5.1976e-05 | 5 | 70 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1442 | 19191 | Frankton | CB7782 | 2024-10-22 08:54 | 2024-10-22 16:40 | 0.16955 | 0.00036383 | 35 | 16310 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1443 | 19165 | Outram | OT2 | 2024-10-22 09:07 | 2024-10-22 17:07 | 0.099794 | 0.0002079 | 20 | 9600 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1444 | 19177 | Commonage | CB5730 | 2024-10-22 10:09 | 2024-10-22 14:27 | 0.24138 | 0.00093557 | 90 | 23220 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1445 | 19184 | Willowbank | WB3 | 2024-10-22 11:45 | 2024-10-22 13:28 | 0.0010707 | 1.0395e-05 | 1 | 103 | Unplanned | Defective Equipment | failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1446 | 19170 | Cromwell | CB821 | 2024-10-22 15:00 | 2024-10-22 15:43 | 0.021903 | 0.00050937 | 49 | 2107 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1447 | 19173 | Roxburgh | CB4637 | 2024-10-22 16:18 | 2024-10-22 16:24 | 0.00068608 | 0.00011435 | 11 | 66 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1448 | 19193 | Frankton | CB7782 | 2024-10-22 16:33 | 2024-10-22 16:40 | 0.00036383 | 5.1976e-05 | 5 | 35 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1449 | 19257 | Andersons Bay | AB8 | 2024-10-23 08:31 | 2024-10-23 16:57 | 0.3682 | 0.00072767 | 70 | 35420 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1450 | 19203 | Port Chalmers | PC7 | 2024-10-23 08:33 | 2024-10-23 15:51 | 0.027319 | 6.2371e-05 | 6 | 2628 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1451 | 19258 | Andersons Bay | AB8 | 2024-10-23 08:33 | 2024-10-23 17:00 | 0.20027 | 0.00039502 | 38 | 19266 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1452 | 19209 | Cromwell | CB821 | 2024-10-23 09:03 | 2024-10-23 15:16 | 0.0038774 | 1.0395e-05 | 1 | 373 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1453 | 19210 | Cromwell | CB821 | 2024-10-23 09:03 | 2024-10-23 15:40 | 0.016508 | 4.1581e-05 | 4 | 1588 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1454 | 19208 | Cromwell | CB821 | 2024-10-23 09:03 | 2024-10-23 15:05 | 0.026342 | 7.2767e-05 | 7 | 2534 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1455 | 19206 | Cromwell | CB821 | 2024-10-23 09:04 | 2024-10-23 13:36 | 0.0028275 | 1.0395e-05 | 1 | 272 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1456 | 19205 | Cromwell | CB821 | 2024-10-23 09:04 | 2024-10-23 13:35 | 0.016903 | 6.2371e-05 | 6 | 1626 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1457 | 19211 | Alexandra | CB163 | 2024-10-23 09:04 | 2024-10-23 13:43 | 0.31903 | 0.0011435 | 110 | 30690 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1458 | 19207 | Ward Street | WS7 | 2024-10-23 09:12 | 2024-10-23 16:03 | 0.14099 | 0.00034304 | 33 | 13563 | Planned | Planned interruption | tree trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1459 | 19202 | Lauder Flat | CB6576 | 2024-10-23 13:01 | 2024-10-23 14:07 | 0.032246 | 0.00048858 | 47 | 3102 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1460 | 19204 | Roxburgh | CB4637 | 2024-10-24 08:16 | 2024-10-24 12:42 | 0.0027651 | 1.0395e-05 | 1 | 266 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1461 | 19254 | Outram | OT2 | 2024-10-24 09:05 | 2024-10-24 14:41 | 0.038421 | 0.00011435 | 11 | 3696 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1462 | 19253 | Outram | OT2 | 2024-10-24 09:05 | 2024-10-24 14:36 | 0.068816 | 0.0002079 | 20 | 6620 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1463 | 19259 | Andersons Bay | AB8 | 2024-10-24 16:53 | 2024-10-24 17:09 | 0.0063203 | 0.00039502 | 38 | 608 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1464 | 19223 | Alexandra | CB168 | 2024-10-26 09:26 | 2024-10-26 16:46 | 0.12807 | 0.00029107 | 28 | 12320 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1465 | 19222 | Alexandra | CB168 | 2024-10-26 09:26 | 2024-10-26 11:04 | 0.109 | 0.0011123 | 107 | 10486 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1466 | 19271 | Mosgiel | MG4 | 2024-10-26 13:20 | 2024-10-26 14:01 | 0.013212 | 0.00032225 | 31 | 1271 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1467 | 19226 | Alexandra | CB168 | 2024-10-26 13:29 | 2024-10-26 15:18 | 0.052122 | 0.00047818 | 46 | 5014 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1468 | 19225 | Alexandra | CB168 | 2024-10-26 13:29 | 2024-10-26 15:06 | 0.0605 | 0.00062371 | 60 | 5820 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1469 | 19227 | Alexandra | CB168 | 2024-10-26 13:29 | 2024-10-26 17:24 | 0.38597 | 0.0016424 | 158 | 37130 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1470 | 19230 | Arrowtown | CB7632 | 2024-10-26 13:49 | 2024-10-26 14:56 | 0.013233 | 0.00019751 | 19 | 1273 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1471 | 19229 | Arrowtown | CB7632 | 2024-10-26 13:49 | 2024-10-26 14:41 | 0.030811 | 0.00059253 | 57 | 2964 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1472 | 19274 | Wanaka | CB2754 | 2024-10-26 14:13 | 2024-10-26 17:43 | 0.028379 | 0.00013514 | 13 | 2730 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1473 | 19272 | Wanaka | CB2754 | 2024-10-26 14:13 | 2024-10-26 15:04 | 0.012724 | 0.00024949 | 24 | 1224 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1474 | 19273 | Wanaka | CB2754 | 2024-10-26 14:13 | 2024-10-26 17:35 | 0.10079 | 0.00049897 | 48 | 9696 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1475 | 19232 | Arrowtown | CB7632 | 2024-10-26 14:41 | 2024-10-26 21:08 | 0.056176 | 0.00014553 | 14 | 5404 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1476 | 19231 | Arrowtown | CB7632 | 2024-10-26 14:41 | 2024-10-26 14:56 | 0.0062579 | 0.00044699 | 43 | 602 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1477 | 19233 | Arrowtown | CB7632 | 2024-10-26 14:56 | 2024-10-26 21:08 | 0.23911 | 0.0006445 | 62 | 23002 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1478 | 19238 | Halfway Bush | HB13 | 2024-10-26 19:07 | 2024-10-26 21:30 | 0.016352 | 0.00011435 | 11 | 1573 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1479 | 19237 | Halfway Bush | HB13 | 2024-10-26 19:07 | 2024-10-26 19:55 | 0.33082 | 0.006892 | 663 | 31824 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1480 | 19283 | East Taieri | ET6 | 2024-10-27 02:01 | 2024-10-27 04:10 | 0.069731 | 0.00054055 | 52 | 6708 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1481 | 19247 | Arrowtown | CB7632 | 2024-10-27 11:45 | 2024-10-27 17:49 | 0.037839 | 0.00010395 | 10 | 3640 | Unplanned | Defective Equipment | broken pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1482 | 19246 | Arrowtown | CB7632 | 2024-10-27 11:45 | 2024-10-27 12:19 | 0.02262 | 0.00066529 | 64 | 2176 | Unplanned | Defective Equipment | broken pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1483 | 19245 | Arrowtown | CB7632 | 2024-10-27 12:13 | 2024-10-27 12:19 | 0.00010395 | 2.079e-05 | 2 | 10 | Unplanned | Defective Equipment | broken pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1484 | 19248 | Arrowtown | CB7632 | 2024-10-27 17:28 | 2024-10-27 17:31 | 6.2371e-05 | 2.079e-05 | 2 | 6 | Unplanned | Defective Equipment | broken pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1485 | 19249 | Arrowtown | CB7632 | 2024-10-27 17:28 | 2024-10-27 17:49 | 0.013971 | 0.00066529 | 64 | 1344 | Unplanned | Defective Equipment | broken pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1486 | 19250 | Arrowtown | CB7632 | 2024-10-27 17:46 | 2024-10-27 17:49 | 6.2371e-05 | 2.079e-05 | 2 | 6 | Unplanned | Defective Equipment | broken pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1487 | 19284 | East Taieri | ET6 | 2024-10-28 11:24 | 2024-10-28 12:38 | 0.040001 | 0.00054055 | 52 | 3848 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1488 | 19264 | Corstorphine | CO6 | 2024-10-29 05:01 | 2024-10-29 05:39 | 0.031206 | 0.00082122 | 79 | 3002 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1489 | 19263 | Cromwell | CB821 | 2024-10-29 09:02 | 2024-10-29 16:01 | 0.0043556 | 1.0395e-05 | 1 | 419 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1490 | 19261 | Cromwell | CB821 | 2024-10-29 09:02 | 2024-10-29 15:41 | 0.078806 | 0.00019751 | 19 | 7581 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1491 | 19268 | Dalefield | CB7828 | 2024-10-29 09:04 | 2024-10-29 09:24 | 0.010187 | 0.00050937 | 49 | 980 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1492 | 19266 | Fernhill | CB5308 | 2024-10-29 09:05 | 2024-10-29 14:01 | 0.20924 | 0.00070688 | 68 | 20128 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1493 | 19260 | Berwick | BK2 | 2024-10-29 09:08 | 2024-10-29 11:05 | 0.021892 | 0.00018711 | 18 | 2106 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1494 | 19267 | Berwick | BK2 | 2024-10-29 12:35 | 2024-10-29 14:15 | 0.010395 | 0.00010395 | 10 | 1000 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1495 | 19265 | Corstorphine | CO6 | 2024-10-29 18:23 | 2024-10-29 18:34 | 0.0090335 | 0.00082122 | 79 | 869 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1496 | 19275 | Frankton | CB7783 | 2024-10-29 22:44 | 2024-10-30 00:30 | 0.02314 | 0.0002183 | 21 | 2226 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1497 | 19279 | Roxburgh | CB4637 | 2024-10-30 08:04 | 2024-10-30 15:12 | 0.048941 | 0.00011435 | 11 | 4708 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1498 | 19276 | Cromwell | CB822 | 2024-10-30 09:03 | 2024-10-30 14:50 | 0.19839 | 0.00057174 | 55 | 19085 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1499 | 19277 | Berwick | BK2 | 2024-10-30 09:31 | 2024-10-30 13:06 | 0.12516 | 0.00058213 | 56 | 12040 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1500 | 19285 | East Taieri | ET6 | 2024-10-30 15:58 | 2024-10-30 16:05 | 0.0037839 | 0.00054055 | 52 | 364 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1501 | 19287 | Lindis Crossing | CB2086 | 2024-10-31 08:34 | 2024-10-31 15:45 | 0.049284 | 0.00011435 | 11 | 4741 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1502 | 19291 | Ettrick | CB480 | 2024-10-31 09:02 | 2024-10-31 16:07 | 0.013254 | 3.1186e-05 | 3 | 1275 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1503 | 19290 | Ettrick | CB480 | 2024-10-31 09:02 | 2024-10-31 15:57 | 0.04314 | 0.00010395 | 10 | 4150 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1504 | 19294 | Outram | OT2 | 2024-10-31 09:04 | 2024-10-31 17:07 | 0.060251 | 0.00012474 | 12 | 5796 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1505 | 19295 | Outram | OT2 | 2024-10-31 09:04 | 2024-10-31 17:33 | 0.39684 | 0.00077964 | 75 | 38175 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1506 | 19292 | Outram | OT2 | 2024-10-31 09:04 | 2024-10-31 17:07 | 0.44686 | 0.00092518 | 89 | 42987 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1507 | 19289 | Outram | OT3 | 2024-10-31 09:05 | 2024-10-31 13:41 | 0.0028691 | 1.0395e-05 | 1 | 276 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1508 | 19288 | Outram | OT3 | 2024-10-31 09:05 | 2024-10-31 13:40 | 0.051456 | 0.00018711 | 18 | 4950 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1509 | 19296 | Camp Hill | CB2008 | 2024-10-31 09:28 | 2024-10-31 16:11 | 0.0041893 | 1.0395e-05 | 1 | 403 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1510 | 19297 | Camp Hill | CB2008 | 2024-10-31 09:28 | 2024-10-31 16:11 | 0.0083786 | 2.079e-05 | 2 | 806 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1511 | 19301 | Willowbank | WB3 | 2024-11-01 08:34 | 2024-11-01 15:04 | 0.10135 | 0.00025988 | 25 | 9750 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1512 | 19303 | Ward Street | WS12 | 2024-11-01 17:30 | 2024-11-01 19:12 | 0.025448 | 0.00024949 | 24 | 2448 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1513 | 19333 | Wanaka | CB2752 | 2024-11-01 21:02 | 2024-11-02 00:08 | 0.007734 | 4.1581e-05 | 4 | 744 | Unplanned | Defective Equipment | faulty lightning arrestor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1514 | 19302 | Ward Street | WS12 | 2024-11-02 08:03 | 2024-11-02 15:15 | 0.0089815 | 2.079e-05 | 2 | 864 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1515 | 19306 | Green Island | GI11 | 2024-11-02 08:38 | 2024-11-02 15:55 | 0.0045427 | 1.0395e-05 | 1 | 437 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1516 | 19313 | Roxburgh | CB4635 | 2024-11-02 14:10 | 2024-11-02 20:58 | 0.093079 | 0.00022869 | 22 | 8954 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1517 | 19312 | Roxburgh | CB4635 | 2024-11-02 14:10 | 2024-11-02 16:04 | 0.24649 | 0.0021622 | 208 | 23712 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1518 | 19671 | Commonage | CB5732 | 2024-11-02 15:21 | 2024-11-02 15:48 | 0.0028067 | 0.00010395 | 10 | 270 | Unplanned | Defective Equipment | broken fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1519 | 19318 | Alexandra | CB656 | 2024-11-03 01:40 | 2024-11-03 07:39 | 0.14886 | 0.00041581 | 40 | 14320 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1520 | 19316 | Alexandra | CB656 | 2024-11-03 01:40 | 2024-11-03 05:55 | 0.12938 | 0.00050937 | 49 | 12446 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1521 | 19319 | Alexandra | CB656 | 2024-11-03 01:40 | 2024-11-03 07:40 | 0.21645 | 0.00060292 | 58 | 20822 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1522 | 19320 | Alexandra | CB656 | 2024-11-03 01:40 | 2024-11-03 07:41 | 0.34055 | 0.00094597 | 91 | 32760 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1523 | 19317 | Alexandra | CB656 | 2024-11-03 01:40 | 2024-11-03 07:35 | 1.7296 | 0.0048858 | 470 | 166380 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1524 | 19322 | Alexandra | CB656 | 2024-11-03 07:50 | 2024-11-03 08:08 | 0.014668 | 0.0008628 | 83 | 1411 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1525 | 19321 | Alexandra | CB656 | 2024-11-03 07:50 | 2024-11-03 07:57 | 0.009231 | 0.0015385 | 148 | 888 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1526 | 19323 | Alexandra | CB656 | 2024-11-03 10:02 | 2024-11-03 10:05 | 0.0015281 | 0.00050937 | 49 | 147 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1527 | 19324 | Alexandra | CB656 | 2024-11-03 10:08 | 2024-11-03 11:15 | 0.032038 | 0.00047818 | 46 | 3082 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1528 | 19325 | Alexandra | CB656 | 2024-11-03 11:50 | 2024-11-03 11:56 | 0.013535 | 0.0022558 | 217 | 1302 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1529 | 19326 | Alexandra | CB656 | 2024-11-03 11:50 | 2024-11-03 11:57 | 0.016029 | 0.0026716 | 257 | 1542 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1530 | 19328 | Alexandra | CB656 | 2024-11-03 11:52 | 2024-11-03 12:05 | 0.0054055 | 0.00041581 | 40 | 520 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1531 | 19327 | Alexandra | CB656 | 2024-11-03 11:52 | 2024-11-03 11:56 | 0.00605 | 0.0020167 | 194 | 582 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1532 | 19329 | Alexandra | CB656 | 2024-11-03 11:52 | 2024-11-03 12:06 | 0.031217 | 0.0024013 | 231 | 3003 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1533 | 19337 | Outram | OT3 | 2024-11-04 15:57 | 2024-11-04 19:38 | 0.018296 | 8.3162e-05 | 8 | 1760 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1534 | 19336 | Outram | OT3 | 2024-11-04 15:57 | 2024-11-04 17:21 | 0.20103 | 0.0024221 | 233 | 19339 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1535 | 19338 | Outram | OT3 | 2024-11-04 19:35 | 2024-11-04 19:38 | 0.0048442 | 0.0024221 | 233 | 466 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1536 | 19390 | Frankton | CB7783 | 2024-11-05 08:12 | 2024-11-05 18:43 | 1.6464 | 0.0026092 | 251 | 158381 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1537 | 19350 | Andersons Bay | AB7 | 2024-11-05 08:34 | 2024-11-05 15:43 | 0.14717 | 0.00034304 | 33 | 14157 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1538 | 19389 | Frankton | CB7783 | 2024-11-05 08:35 | 2024-11-05 16:25 | 0.22474 | 0.00047818 | 46 | 21620 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1539 | 19388 | Frankton | CB7783 | 2024-11-05 08:35 | 2024-11-05 16:25 | 0.45926 | 0.00097715 | 94 | 44180 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1540 | 19349 | Andersons Bay | AB7 | 2024-11-05 08:44 | 2024-11-05 15:35 | 0.25635 | 0.00062371 | 60 | 24660 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1541 | 19342 | Outram | OT2 | 2024-11-05 09:01 | 2024-11-05 16:42 | 0.84343 | 0.0018296 | 176 | 81136 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1542 | 19448 | Nth East Valley | NV6 | 2024-11-06 03:23 | 2024-11-06 06:05 | 0.14314 | 0.00088359 | 85 | 13770 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1543 | 19368 | Cromwell | CB823 | 2024-11-06 07:08 | 2024-11-06 07:44 | 0.018337 | 0.00050937 | 49 | 1764 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1544 | 19369 | Cromwell | CB823 | 2024-11-06 07:46 | 2024-11-06 08:09 | 0.00526 | 0.00022869 | 22 | 506 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1545 | 19351 | Port Chalmers | PC6 | 2024-11-06 09:03 | 2024-11-06 10:40 | 0.2057 | 0.0021206 | 204 | 19788 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1546 | 19362 | Queensberry | CB2423 | 2024-11-06 09:05 | 2024-11-06 12:59 | 0.21406 | 0.00091478 | 88 | 20592 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1547 | 19391 | Ettrick | CB480 | 2024-11-06 09:06 | 2024-11-06 15:04 | 0.048379 | 0.00013514 | 13 | 4654 | Planned | Planned interruption | tree trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1548 | 19459 | Commonage | CB5732 | 2024-11-06 14:24 | 2024-11-06 15:31 | 0.0069648 | 0.00010395 | 10 | 670 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1549 | 19435 | Green Island | GI10 | 2024-11-06 15:14 | 2024-11-06 15:57 | 0.30868 | 0.0073494 | 707 | 29694 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1550 | 19424 | Green Island | GI10 | 2024-11-06 15:21 | 2024-11-06 22:25 | 0.088152 | 0.0002079 | 20 | 8480 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1551 | 19449 | Nth East Valley | NV6 | 2024-11-06 15:31 | 2024-11-06 15:44 | 0.011487 | 0.00088359 | 85 | 1105 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1552 | 19429 | Green Island | GI10 | 2024-11-06 17:32 | 2024-11-06 22:25 | 0.0030458 | 1.0395e-05 | 1 | 293 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1553 | 19425 | Green Island | GI10 | 2024-11-06 17:32 | 2024-11-06 22:24 | 0.0091062 | 3.1186e-05 | 3 | 876 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1554 | 19427 | Green Island | GI10 | 2024-11-06 17:32 | 2024-11-06 22:25 | 0.012183 | 4.1581e-05 | 4 | 1172 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1555 | 19426 | Green Island | GI10 | 2024-11-06 17:32 | 2024-11-06 22:25 | 0.027412 | 9.3557e-05 | 9 | 2637 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1556 | 19428 | Green Island | GI10 | 2024-11-06 17:32 | 2024-11-06 22:25 | 0.03655 | 0.00012474 | 12 | 3516 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1557 | 19430 | Green Island | GI10 | 2024-11-06 22:22 | 2024-11-06 22:24 | 0.0068401 | 0.0068401 | 658 | 658 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1558 | 19412 | Queensberry | CB2423 | 2024-11-07 08:32 | 2024-11-07 16:39 | 0.0050625 | 1.0395e-05 | 1 | 487 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1559 | 19413 | Queensberry | CB2423 | 2024-11-07 08:32 | 2024-11-07 16:47 | 0.0051456 | 1.0395e-05 | 1 | 495 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1560 | 19411 | Queensberry | CB2423 | 2024-11-07 08:32 | 2024-11-07 16:32 | 0.2894 | 0.00060292 | 58 | 27840 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1561 | 19374 | Alexandra | CB169 | 2024-11-07 09:01 | 2024-11-07 11:55 | 0.094056 | 0.00054055 | 52 | 9048 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1562 | 19367 | Outram | OT2 | 2024-11-07 09:04 | 2024-11-07 16:45 | 0.038338 | 8.3162e-05 | 8 | 3688 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1563 | 19366 | Outram | OT2 | 2024-11-07 09:04 | 2024-11-07 16:42 | 0.31899 | 0.00069648 | 67 | 30686 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1564 | 19414 | Queensberry | CB2423 | 2024-11-07 11:21 | 2024-11-07 17:33 | 0.003867 | 1.0395e-05 | 1 | 372 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1565 | 19437 | East Taieri | ET4 | 2024-11-07 17:22 | 2024-11-07 17:58 | 0.0018711 | 5.1976e-05 | 5 | 180 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1566 | 19370 | Cromwell | CB823 | 2024-11-07 17:23 | 2024-11-07 17:36 | 0.002973 | 0.00022869 | 22 | 286 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1567 | 19372 | Cromwell | CB823 | 2024-11-07 17:38 | 2024-11-07 18:10 | 0.0163 | 0.00050937 | 49 | 1568 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1568 | 19408 | Kaikorai Valley | KV4 | 2024-11-07 18:37 | 2024-11-07 22:54 | 0.040074 | 0.00015593 | 15 | 3855 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1569 | 19410 | Camp Hill | CB2006 | 2024-11-08 09:15 | 2024-11-08 14:19 | 0.094804 | 0.00031186 | 30 | 9120 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1570 | 19409 | Camp Hill | CB2006 | 2024-11-08 09:15 | 2024-11-08 14:11 | 0.16923 | 0.00057174 | 55 | 16280 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1571 | 19406 | Camp Hill | CB2006 | 2024-11-11 09:32 | 2024-11-11 14:18 | 0.0089191 | 3.1186e-05 | 3 | 858 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1572 | 19464 | Mosgiel | MG4 | 2024-11-12 08:15 | 2024-11-12 16:34 | 0.0051872 | 1.0395e-05 | 1 | 499 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1573 | 19476 | Outram | OT2 | 2024-11-12 09:01 | 2024-11-12 16:59 | 0.37267 | 0.00077964 | 75 | 35850 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1574 | 19465 | Arrowtown | CB7642 | 2024-11-12 09:05 | 2024-11-12 13:41 | 0.0028691 | 1.0395e-05 | 1 | 276 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1575 | 19466 | Wanaka | CB2751 | 2024-11-12 09:25 | 2024-11-12 14:23 | 0.44918 | 0.0015073 | 145 | 43210 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1576 | 19471 | Cromwell | CB832 | 2024-11-12 09:28 | 2024-11-12 15:01 | 0.0034616 | 1.0395e-05 | 1 | 333 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1577 | 19472 | Cromwell | CB832 | 2024-11-12 09:28 | 2024-11-12 15:02 | 0.031248 | 9.3557e-05 | 9 | 3006 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1578 | 19470 | Cromwell | CB832 | 2024-11-12 09:28 | 2024-11-12 15:01 | 0.062309 | 0.00018711 | 18 | 5994 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1579 | 19482 | Roxburgh | HSB33 | 2024-11-13 08:23 | 2024-11-13 16:14 | 0.0048962 | 1.0395e-05 | 1 | 471 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1580 | 19483 | Roxburgh | HSB33 | 2024-11-13 08:23 | 2024-11-13 16:14 | 0.0048962 | 1.0395e-05 | 1 | 471 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1581 | 19477 | Arrowtown | CB7632 | 2024-11-13 10:01 | 2024-11-13 11:00 | 0.16376 | 0.0027755 | 267 | 15753 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1582 | 19517 | Wanaka | CB2753 | 2024-11-13 19:11 | 2024-11-14 05:06 | 0.50718 | 0.00085241 | 82 | 48790 | Unplanned | Defective Equipment | fire/smoke | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1583 | 19492 | Roxburgh | CB4637 | 2024-11-14 08:09 | 2024-11-14 14:35 | 0.0040126 | 1.0395e-05 | 1 | 386 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1584 | 19495 | Roxburgh | CB4637 | 2024-11-14 08:09 | 2024-11-14 14:50 | 0.008337 | 2.079e-05 | 2 | 802 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1585 | 19491 | Roxburgh | CB4637 | 2024-11-14 08:09 | 2024-11-14 14:31 | 0.035739 | 9.3557e-05 | 9 | 3438 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1586 | 19494 | Roxburgh | CB4637 | 2024-11-14 08:09 | 2024-11-14 14:45 | 0.090563 | 0.00022869 | 22 | 8712 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1587 | 19493 | Roxburgh | CB4637 | 2024-11-14 08:09 | 2024-11-14 14:40 | 0.1951 | 0.00049897 | 48 | 18768 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1588 | 19490 | Roxburgh | CB4637 | 2024-11-14 08:10 | 2024-11-14 14:32 | 0.071478 | 0.00018711 | 18 | 6876 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1589 | 19489 | Clyde-Earnscleugh | CB195 | 2024-11-14 08:33 | 2024-11-14 13:36 | 0.015749 | 5.1976e-05 | 5 | 1515 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1590 | 19506 | Clyde-Earnscleugh | CB195 | 2024-11-14 08:36 | 2024-11-14 16:03 | 0.0046467 | 1.0395e-05 | 1 | 447 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1591 | 19484 | Arrowtown | CB7652 | 2024-11-14 09:07 | 2024-11-14 12:32 | 0.04262 | 0.0002079 | 20 | 4100 | Planned | Planned interruption | network extension | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1592 | 19486 | Outram | OT2 | 2024-11-14 09:09 | 2024-11-14 17:03 | 0.0098547 | 2.079e-05 | 2 | 948 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1593 | 19487 | Outram | OT2 | 2024-11-14 09:09 | 2024-11-14 17:05 | 0.0098963 | 2.079e-05 | 2 | 952 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1594 | 19485 | Outram | OT2 | 2024-11-14 09:09 | 2024-11-14 16:53 | 0.053057 | 0.00011435 | 11 | 5104 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1595 | 19488 | East Taieri | ET5 | 2024-11-14 12:42 | 2024-11-14 13:40 | 0.017485 | 0.00030146 | 29 | 1682 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1596 | 19500 | Alexandra | CB167 | 2024-11-14 18:06 | 2024-11-14 19:02 | 0.0075677 | 0.00013514 | 13 | 728 | Unplanned | Third-party Interference | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1597 | 19497 | Commonage | CB5731 | 2024-11-14 23:04 | 2024-11-15 05:06 | 0.11666 | 0.00032225 | 31 | 11222 | Unplanned | Defective Equipment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1598 | 19502 | Willowbank | WB3 | 2024-11-15 08:05 | 2024-11-15 16:06 | 0.185 | 0.00038462 | 37 | 17797 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1599 | 19501 | Willowbank | WB3 | 2024-11-15 08:05 | 2024-11-15 15:45 | 0.43036 | 0.00093557 | 90 | 41400 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1600 | 19504 | Willowbank | WB3 | 2024-11-15 08:12 | 2024-11-15 14:38 | 0.048151 | 0.00012474 | 12 | 4632 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1601 | 19510 | Omakau | CB656 | 2024-11-15 21:56 | 2024-11-16 04:39 | 0.025073 | 6.2371e-05 | 6 | 2412 | Unplanned | Defective Equipment | failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1602 | 19509 | Omakau | CB656 | 2024-11-15 21:56 | 2024-11-15 23:57 | 0.097299 | 0.00081083 | 78 | 9360 | Unplanned | Defective Equipment | failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1603 | 19511 | Omakau | CB656 | 2024-11-15 21:56 | 2024-11-16 04:49 | 0.36404 | 0.00088359 | 85 | 35020 | Unplanned | Defective Equipment | failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1604 | 19512 | Omakau | CB656 | 2024-11-15 21:56 | 2024-11-16 04:49 | 0.37689 | 0.00091478 | 88 | 36256 | Unplanned | Defective Equipment | failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1605 | 19515 | Omakau | CB656 | 2024-11-16 00:02 | 2024-11-16 04:39 | 0.22379 | 0.00081083 | 78 | 21528 | Unplanned | Defective Equipment | failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1606 | 19518 | Alexandra | CB162 | 2024-11-16 09:03 | 2024-11-16 09:07 | 0.0023701 | 0.00059253 | 57 | 228 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1607 | 19519 | Alexandra | CB162 | 2024-11-16 09:30 | 2024-11-16 14:45 | 0.18665 | 0.00059253 | 57 | 17955 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1608 | 19503 | Carisbrook | CK5 | 2024-11-16 12:11 | 2024-11-16 15:37 | 0.69168 | 0.0033577 | 323 | 66538 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1609 | 19521 | Ward Street | WS6 | 2024-11-18 08:00 | 2024-11-18 08:17 | 0.00035344 | 2.079e-05 | 2 | 34 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1610 | 19525 | Lauder Flat | CB6576 | 2024-11-18 08:33 | 2024-11-18 15:23 | 0.17901 | 0.0004366 | 42 | 17220 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1611 | 19581 | Lauder Flat | CB6576 | 2024-11-18 08:33 | 2024-11-18 09:25 | 0.00054055 | 1.0395e-05 | 1 | 52 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1612 | 19579 | Lauder Flat | CB6576 | 2024-11-18 08:33 | 2024-11-18 09:04 | 0.0006445 | 2.079e-05 | 2 | 62 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1613 | 19580 | Lauder Flat | CB6576 | 2024-11-18 08:33 | 2024-11-18 09:23 | 0.0010395 | 2.079e-05 | 2 | 100 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1614 | 19533 | Green Island | GI2 | 2024-11-18 21:32 | 2024-11-18 22:29 | 0.12739 | 0.002235 | 215 | 12255 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1615 | 19585 | Arrowtown | CB7632 | 2024-11-19 07:59 | 2024-11-19 08:07 | 8.3162e-05 | 1.0395e-05 | 1 | 8 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1616 | 19586 | Arrowtown | CB7632 | 2024-11-19 08:00 | 2024-11-19 08:20 | 0.00041581 | 2.079e-05 | 2 | 40 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1617 | 19587 | Arrowtown | CB7632 | 2024-11-19 08:02 | 2024-11-19 08:20 | 0.00037423 | 2.079e-05 | 2 | 36 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1618 | 19589 | Arrowtown | CB7632 | 2024-11-19 08:37 | 2024-11-19 16:06 | 0.014002 | 3.1186e-05 | 3 | 1347 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1619 | 19588 | Arrowtown | CB7632 | 2024-11-19 08:37 | 2024-11-19 08:48 | 0.0044596 | 0.00040541 | 39 | 429 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1620 | 19538 | Clyde-Earnscleugh | CB192 | 2024-11-19 08:49 | 2024-11-19 10:54 | 0.006497 | 5.1976e-05 | 5 | 625 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1621 | 19527 | Camp Hill | CB2008 | 2024-11-19 09:03 | 2024-11-19 16:03 | 0.008732 | 2.079e-05 | 2 | 840 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1622 | 19570 | Outram | OT2 | 2024-11-19 09:03 | 2024-11-19 17:10 | 0.010125 | 2.079e-05 | 2 | 974 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1623 | 19569 | Outram | OT2 | 2024-11-19 09:03 | 2024-11-19 17:10 | 0.065812 | 0.00013514 | 13 | 6331 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1624 | 19523 | Roxburgh | CB4635 | 2024-11-19 09:04 | 2024-11-19 17:11 | 0.015187 | 3.1186e-05 | 3 | 1461 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1625 | 19522 | Roxburgh | CB4635 | 2024-11-19 09:04 | 2024-11-19 16:41 | 0.20903 | 0.00045739 | 44 | 20108 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1626 | 19524 | Arrowtown | CB7632 | 2024-11-19 09:07 | 2024-11-19 17:14 | 0.035437 | 7.2767e-05 | 7 | 3409 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1627 | 19526 | Ettrick | CB480 | 2024-11-19 09:30 | 2024-11-19 16:02 | 0.097798 | 0.00024949 | 24 | 9408 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1628 | 19539 | Arrowtown | CB7662 | 2024-11-19 14:38 | 2024-11-19 14:54 | 0.029606 | 0.0018504 | 178 | 2848 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1629 | 19540 | Arrowtown | CB7662 | 2024-11-19 14:38 | 2024-11-19 15:41 | 0.19581 | 0.0031082 | 299 | 18837 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1630 | 19534 | Green Island | GI2 | 2024-11-19 15:30 | 2024-11-19 15:40 | 0.0084201 | 0.00084201 | 81 | 810 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1631 | 19541 | Arrowtown | CB7662 | 2024-11-19 15:31 | 2024-11-19 15:41 | 0.018504 | 0.0018504 | 178 | 1780 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1632 | 19590 | Arrowtown | CB7632 | 2024-11-19 15:56 | 2024-11-19 16:06 | 0.0040541 | 0.00040541 | 39 | 390 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1633 | 19591 | Arrowtown | CB7632 | 2024-11-19 16:07 | 2024-11-19 16:17 | 0.00010395 | 1.0395e-05 | 1 | 10 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1634 | 19592 | Arrowtown | CB7632 | 2024-11-19 16:08 | 2024-11-19 16:21 | 0.00027028 | 2.079e-05 | 2 | 26 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1635 | 19593 | Arrowtown | CB7632 | 2024-11-19 16:09 | 2024-11-19 16:25 | 0.00033265 | 2.079e-05 | 2 | 32 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1636 | 19535 | Alexandra | CB169 | 2024-11-19 19:30 | 2024-11-19 22:10 | 0.0016632 | 1.0395e-05 | 1 | 160 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1637 | 19548 | Green Island | GI4 | 2024-11-20 08:01 | 2024-11-20 15:28 | 0.078993 | 0.00017672 | 17 | 7599 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1638 | 19547 | Arrowtown | CB7662 | 2024-11-20 09:24 | 2024-11-20 14:28 | 0.23701 | 0.00077964 | 75 | 22800 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1639 | 19550 | Ettrick | CB480 | 2024-11-20 09:30 | 2024-11-20 15:59 | 0.09705 | 0.00024949 | 24 | 9336 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1640 | 19549 | Wanaka | CB2751 | 2024-11-20 10:03 | 2024-11-20 14:07 | 0.010146 | 4.1581e-05 | 4 | 976 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1641 | 19545 | Arrowtown | CB7652 | 2024-11-20 22:02 | 2024-11-20 22:49 | 0.048858 | 0.0010395 | 100 | 4700 | Planned | Planned interruption | safety disconnection - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1642 | 19546 | Ward Street | WS6 | 2024-11-21 07:43 | 2024-11-21 07:44 | 2.079e-05 | 2.079e-05 | 2 | 2 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1643 | 19595 | Arrowtown | CB7632 | 2024-11-21 08:00 | 2024-11-21 08:13 | 0.00027028 | 2.079e-05 | 2 | 26 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1644 | 19594 | Arrowtown | CB7632 | 2024-11-21 08:01 | 2024-11-21 08:04 | 3.1186e-05 | 1.0395e-05 | 1 | 3 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1645 | 19598 | Arrowtown | CB7632 | 2024-11-21 08:42 | 2024-11-21 16:00 | 0.013659 | 3.1186e-05 | 3 | 1314 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1646 | 19572 | Outram | OT2 | 2024-11-21 09:05 | 2024-11-21 16:43 | 0.009522 | 2.079e-05 | 2 | 916 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1647 | 19573 | Outram | OT2 | 2024-11-21 09:05 | 2024-11-21 16:44 | 0.014314 | 3.1186e-05 | 3 | 1377 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1648 | 19571 | Outram | OT2 | 2024-11-21 09:05 | 2024-11-21 16:43 | 0.04761 | 0.00010395 | 10 | 4580 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1649 | 19557 | Alexandra | CB168 | 2024-11-21 09:55 | 2024-11-21 19:22 | 0.0058941 | 1.0395e-05 | 1 | 567 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1650 | 19558 | Alexandra | CB168 | 2024-11-21 09:55 | 2024-11-21 19:46 | 0.012287 | 2.079e-05 | 2 | 1182 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1651 | 19556 | Alexandra | CB168 | 2024-11-21 09:55 | 2024-11-21 18:49 | 0.31641 | 0.00059253 | 57 | 30438 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1652 | 19601 | Arrowtown | CB7632 | 2024-11-21 16:11 | 2024-11-21 16:20 | 0.00018711 | 2.079e-05 | 2 | 18 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1653 | 19602 | Arrowtown | CB7632 | 2024-11-21 16:11 | 2024-11-21 16:23 | 0.00024949 | 2.079e-05 | 2 | 24 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1654 | 20082 | Willowbank | WB3 | 2024-11-22 00:30 | 2024-11-22 03:13 | 0.060999 | 0.00037423 | 36 | 5868 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1655 | 19568 | Roxburgh | CB4635 | 2024-11-22 09:12 | 2024-11-22 17:03 | 0.014688 | 3.1186e-05 | 3 | 1413 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1656 | 19582 | Lauder Flat | CB6576 | 2024-11-22 09:41 | 2024-11-22 10:42 | 0.0012682 | 2.079e-05 | 2 | 122 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1657 | 19559 | Queensberry | CB2423 | 2024-11-22 10:15 | 2024-11-22 14:00 | 0.0023389 | 1.0395e-05 | 1 | 225 | Planned | Planned interruption | network extension | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1658 | 19563 | Queensberry | CB2423 | 2024-11-22 10:15 | 2024-11-22 14:21 | 0.010229 | 4.1581e-05 | 4 | 984 | Planned | Planned interruption | network extension | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1659 | 19561 | Queensberry | CB2423 | 2024-11-22 10:15 | 2024-11-22 14:05 | 0.016736 | 7.2767e-05 | 7 | 1610 | Planned | Planned interruption | network extension | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1660 | 19583 | Lauder Flat | CB6576 | 2024-11-22 10:42 | 2024-11-22 10:43 | 2.079e-05 | 2.079e-05 | 2 | 2 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1661 | 19567 | Green Island | GI10 | 2024-11-23 08:00 | 2024-11-23 14:14 | 0.16673 | 0.00044699 | 43 | 16039 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1662 | 19578 | Arrowtown | CB7632 | 2024-11-24 15:21 | 2024-11-24 20:26 | 0.022194 | 7.2767e-05 | 7 | 2135 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1663 | 19604 | Outram | OT3 | 2024-11-25 08:33 | 2024-11-25 15:50 | 0.20896 | 0.00047818 | 46 | 20102 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1664 | 19603 | Ettrick | CB480 | 2024-11-25 09:35 | 2024-11-25 15:03 | 0.030687 | 9.3557e-05 | 9 | 2952 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1665 | 19629 | Wanaka | CB2758 | 2024-11-25 10:09 | 2024-11-25 12:40 | 0.04709 | 0.00031186 | 30 | 4530 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1666 | 19628 | Wanaka | CB2758 | 2024-11-25 10:09 | 2024-11-25 12:39 | 0.16996 | 0.0011331 | 109 | 16350 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1667 | 19605 | Dalefield | CB7830 | 2024-11-25 13:31 | 2024-11-25 14:10 | 0.00040541 | 1.0395e-05 | 1 | 39 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1668 | 19622 | Kaikorai Valley | KV4 | 2024-11-25 18:03 | 2024-11-26 00:33 | 0.028379 | 7.2767e-05 | 7 | 2730 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1669 | 19617 | Mosgiel | MG6 | 2024-11-26 08:13 | 2024-11-26 16:15 | 0.030063 | 6.2371e-05 | 6 | 2892 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1670 | 19612 | Mosgiel | MG6 | 2024-11-26 08:13 | 2024-11-26 08:17 | 0.00033265 | 8.3162e-05 | 8 | 32 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1671 | 19613 | Mosgiel | MG6 | 2024-11-26 08:13 | 2024-11-26 16:09 | 0.40575 | 0.00085241 | 82 | 39032 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1672 | 19673 | Mosgiel | MG6 | 2024-11-26 08:13 | 2024-11-26 16:09 | 0.0049481 | 1.0395e-05 | 1 | 476 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1673 | 19619 | Wanaka | CB2754 | 2024-11-26 08:20 | 2024-11-26 15:06 | 0.09285 | 0.00022869 | 22 | 8932 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1674 | 19620 | Alexandra | CB169 | 2024-11-26 08:33 | 2024-11-26 15:45 | 0.23352 | 0.00054055 | 52 | 22464 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1675 | 19623 | Frankton | CB7789 | 2024-11-26 09:03 | 2024-11-26 14:44 | 0.0035448 | 1.0395e-05 | 1 | 341 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1676 | 19655 | Outram | OT2 | 2024-11-26 09:09 | 2024-11-26 16:30 | 0.045843 | 0.00010395 | 10 | 4410 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1677 | 19621 | Roxburgh | CB4635 | 2024-11-26 09:11 | 2024-11-26 14:38 | 0.010198 | 3.1186e-05 | 3 | 981 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1678 | 19615 | Mosgiel | MG6 | 2024-11-26 16:02 | 2024-11-26 16:09 | 0.00058213 | 8.3162e-05 | 8 | 56 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1679 | 19633 | Outram | OT1 | 2024-11-27 00:24 | 2024-11-27 03:30 | 0.21075 | 0.0011331 | 109 | 20274 | Unplanned | Defective Equipment | failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1680 | 19634 | Outram | OT1 | 2024-11-27 03:31 | 2024-11-27 03:59 | 0.0098963 | 0.00035344 | 34 | 952 | Unplanned | Defective Equipment | failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1681 | 19635 | Outram | OT1 | 2024-11-27 03:31 | 2024-11-27 04:26 | 0.04288 | 0.00077964 | 75 | 4125 | Unplanned | Defective Equipment | failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1682 | 19636 | Outram | OT1 | 2024-11-27 03:59 | 2024-11-27 05:08 | 0.012017 | 0.00017672 | 17 | 1156 | Unplanned | Defective Equipment | failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1683 | 19637 | Outram | OT1 | 2024-11-27 03:59 | 2024-11-27 06:49 | 0.029865 | 0.00017672 | 17 | 2873 | Unplanned | Defective Equipment | failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1684 | 19631 | Outram | OT3 | 2024-11-27 08:12 | 2024-11-27 15:55 | 0.17327 | 0.00037423 | 36 | 16668 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1685 | 19649 | Cromwell | CB821 | 2024-11-27 09:02 | 2024-11-27 14:08 | 0.0668 | 0.0002183 | 21 | 6426 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1686 | 19630 | Cromwell | CB822 | 2024-11-27 09:03 | 2024-11-27 14:11 | 0.016009 | 5.1976e-05 | 5 | 1540 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1687 | 19643 | Lauder Flat | CB6576 | 2024-11-27 15:17 | 2024-11-27 17:49 | 0.16325 | 0.0010811 | 104 | 15704 | Unplanned | Wildlife | bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1688 | 19642 | Lauder Flat | CB6576 | 2024-11-27 15:17 | 2024-11-27 17:25 | 0.16766 | 0.0013202 | 127 | 16129 | Unplanned | Wildlife | bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1689 | 19668 | Ettrick | CB480 | 2024-11-28 08:01 | 2024-11-28 16:35 | 0.40608 | 0.00079004 | 76 | 39064 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1690 | 19651 | Carisbrook | CK13 | 2024-11-28 08:05 | 2024-11-28 08:24 | 0.00019751 | 1.0395e-05 | 1 | 19 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1691 | 19653 | Carisbrook | CK13 | 2024-11-28 08:05 | 2024-11-28 17:06 | 0.0056238 | 1.0395e-05 | 1 | 541 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1692 | 19652 | Carisbrook | CK13 | 2024-11-28 08:05 | 2024-11-28 17:00 | 0.45048 | 0.00084201 | 81 | 43335 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1693 | 19681 | Roxburgh | HSB33 | 2024-11-28 08:11 | 2024-11-28 14:48 | 0.0082538 | 2.079e-05 | 2 | 794 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1694 | 19645 | Nth East Valley | NV7 | 2024-11-28 08:31 | 2024-11-28 16:03 | 0.0093765 | 2.079e-05 | 2 | 902 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1695 | 19644 | Nth East Valley | NV7 | 2024-11-28 08:31 | 2024-11-28 15:57 | 0.27293 | 0.00061332 | 59 | 26255 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1696 | 19658 | Omakau | CB656 | 2024-11-28 08:35 | 2024-11-28 14:53 | 0.0078588 | 2.079e-05 | 2 | 756 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1697 | 19657 | Omakau | CB656 | 2024-11-28 08:35 | 2024-11-28 14:52 | 0.18419 | 0.00048858 | 47 | 17719 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1698 | 19646 | Nth East Valley | NV7 | 2024-11-28 08:36 | 2024-11-28 16:21 | 0.12568 | 0.00027028 | 26 | 12090 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1699 | 19669 | Ettrick | CB480 | 2024-11-28 08:59 | 2024-11-28 16:36 | 0.29454 | 0.0006445 | 62 | 28334 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1700 | 19670 | Ettrick | CB480 | 2024-11-28 08:59 | 2024-11-28 16:37 | 0.53323 | 0.0011643 | 112 | 51296 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1701 | 19661 | Clyde-Earnscleugh | CB190 | 2024-11-28 09:23 | 2024-11-28 09:30 | 0.076041 | 0.010863 | 1045 | 7315 | Unplanned | Human Error | switching error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1702 | 19664 | Frankton | CB7790 | 2024-11-28 18:26 | 2024-11-28 20:43 | 0.0014241 | 1.0395e-05 | 1 | 137 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1703 | 19689 | Andersons Bay | AB4 | 2024-11-28 23:16 | 2024-11-29 02:17 | 0.0094077 | 5.1976e-05 | 5 | 905 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1704 | 19675 | Halfway Bush | HB1 | 2024-11-29 08:22 | 2024-11-29 14:16 | 0.0184 | 5.1976e-05 | 5 | 1770 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1705 | 19676 | Lauder Flat | CB6576 | 2024-11-29 11:05 | 2024-11-29 15:00 | 0.0024429 | 1.0395e-05 | 1 | 235 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1706 | 19674 | Mosgiel | MG7 | 2024-11-30 08:00 | 2024-11-30 15:05 | 0.004418 | 1.0395e-05 | 1 | 425 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1707 | 19679 | East Taieri | ET3 | 2024-12-01 13:41 | 2024-12-01 19:44 | 0.060375 | 0.00016632 | 16 | 5808 | Unplanned | Defective Equipment | faulty transformer bushing | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1708 | 19688 | Outram | OT2 | 2024-12-02 08:04 | 2024-12-02 15:44 | 0.023909 | 5.1976e-05 | 5 | 2300 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1709 | 19687 | Outram | OT2 | 2024-12-02 08:04 | 2024-12-02 15:36 | 0.037589 | 8.3162e-05 | 8 | 3616 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1710 | 19684 | Alexandra | CB169 | 2024-12-02 09:07 | 2024-12-02 10:10 | 0.0013098 | 2.079e-05 | 2 | 126 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1711 | 19685 | Alexandra | CB169 | 2024-12-02 11:04 | 2024-12-02 12:05 | 0.00063411 | 1.0395e-05 | 1 | 61 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1712 | 19686 | Alexandra | CB169 | 2024-12-02 13:03 | 2024-12-02 13:33 | 0.00031186 | 1.0395e-05 | 1 | 30 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1713 | 19692 | Frankton | CB7786 | 2024-12-03 06:36 | 2024-12-03 06:42 | 0.075844 | 0.012641 | 1216 | 7296 | Unplanned | Human Error | switching error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1714 | 19718 | Cromwell | CB831 | 2024-12-03 07:07 | 2024-12-03 07:25 | 0.010291 | 0.00057174 | 55 | 990 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1715 | 19694 | Lauder Flat | CB6576 | 2024-12-03 07:21 | 2024-12-03 09:35 | 0.0027859 | 2.079e-05 | 2 | 268 | Unplanned | Wildlife | animal in equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1716 | 19724 | Roxburgh | CB4637 | 2024-12-03 08:19 | 2024-12-03 14:13 | 0.22079 | 0.00062371 | 60 | 21240 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1717 | 19715 | Cromwell | CB831 | 2024-12-03 08:34 | 2024-12-03 17:04 | 0.13784 | 0.00027028 | 26 | 13260 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1718 | 19717 | Cromwell | CB831 | 2024-12-03 08:35 | 2024-12-03 09:12 | 0.011154 | 0.00030146 | 29 | 1073 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1719 | 19716 | Cromwell | CB831 | 2024-12-03 08:38 | 2024-12-03 09:13 | 0.0061852 | 0.00017672 | 17 | 595 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1720 | 19727 | Outram | OT2 | 2024-12-03 08:46 | 2024-12-03 15:43 | 0.0043348 | 1.0395e-05 | 1 | 417 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1721 | 19728 | Outram | OT2 | 2024-12-03 08:46 | 2024-12-03 15:44 | 0.0086904 | 2.079e-05 | 2 | 836 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1722 | 19726 | Outram | OT2 | 2024-12-03 08:46 | 2024-12-03 15:19 | 0.18384 | 0.00046779 | 45 | 17685 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1723 | 19768 | East Taieri | ET5 | 2024-12-03 09:07 | 2024-12-03 15:41 | 0.065532 | 0.00016632 | 16 | 6304 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1724 | 19767 | East Taieri | ET5 | 2024-12-03 09:07 | 2024-12-03 15:41 | 0.17612 | 0.00044699 | 43 | 16942 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1725 | 19766 | East Taieri | ET5 | 2024-12-03 09:07 | 2024-12-03 15:29 | 0.55197 | 0.0014449 | 139 | 53098 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1726 | 19713 | Cromwell | CB821 | 2024-12-03 11:35 | 2024-12-03 17:32 | 0.0074222 | 2.079e-05 | 2 | 714 | Unplanned | Adverse Environment | flooding | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1727 | 19712 | Outram | OT2 | 2024-12-03 12:04 | 2024-12-03 20:11 | 0.35437 | 0.00072767 | 70 | 34090 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1728 | 19719 | Cromwell | CB831 | 2024-12-03 16:37 | 2024-12-03 16:53 | 0.0091478 | 0.00057174 | 55 | 880 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1729 | 19703 | Ettrick | CB480 | 2024-12-03 16:40 | 2024-12-03 19:24 | 0.0084721 | 5.1976e-05 | 5 | 815 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1730 | 19704 | Ettrick | CB480 | 2024-12-03 16:40 | 2024-12-03 19:29 | 0.022703 | 0.00013514 | 13 | 2184 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1731 | 19697 | Ettrick | CB480 | 2024-12-03 16:40 | 2024-12-03 18:07 | 0.018774 | 0.0002183 | 21 | 1806 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1732 | 19701 | Ettrick | CB480 | 2024-12-03 16:40 | 2024-12-03 18:25 | 0.027028 | 0.00025988 | 25 | 2600 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1733 | 19700 | Ettrick | CB480 | 2024-12-03 16:40 | 2024-12-03 18:14 | 0.029315 | 0.00031186 | 30 | 2820 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1734 | 19702 | Ettrick | CB480 | 2024-12-03 16:40 | 2024-12-03 19:20 | 0.054544 | 0.00034304 | 33 | 5247 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1735 | 19699 | Ettrick | CB480 | 2024-12-03 16:40 | 2024-12-03 18:13 | 0.13728 | 0.0014761 | 142 | 13206 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1736 | 19698 | Ettrick | CB480 | 2024-12-03 16:40 | 2024-12-03 18:13 | 0.15015 | 0.0016321 | 157 | 14444 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1737 | 19730 | Wanaka | CB2755 | 2024-12-04 08:03 | 2024-12-04 13:16 | 0.078089 | 0.00024949 | 24 | 7512 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1738 | 19731 | Nth East Valley | NV5 | 2024-12-04 08:12 | 2024-12-04 11:47 | 0.12739 | 0.00059253 | 57 | 12255 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1739 | 19770 | Wanaka | CB2755 | 2024-12-04 09:00 | 2024-12-04 14:39 | 1.3814 | 0.0040749 | 392 | 132888 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1740 | 19769 | Wanaka | CB2755 | 2024-12-04 09:03 | 2024-12-04 14:37 | 0.027776 | 8.3162e-05 | 8 | 2672 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1741 | 19771 | Wanaka | CB2755 | 2024-12-04 09:03 | 2024-12-04 14:37 | 0.003472 | 1.0395e-05 | 1 | 334 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1742 | 19729 | Lindis Crossing | CB2086 | 2024-12-04 09:06 | 2024-12-04 13:46 | 0.060906 | 0.0002183 | 21 | 5859 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1743 | 19855 | Wanaka | CB2754 | 2024-12-04 10:07 | 2024-12-04 15:09 | 0.0031394 | 1.0395e-05 | 1 | 302 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1744 | 19720 | Wanaka | CB2754 | 2024-12-04 10:07 | 2024-12-04 10:10 | 0.00049897 | 0.00024949 | 24 | 48 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1745 | 19721 | Wanaka | CB2754 | 2024-12-04 10:07 | 2024-12-04 15:09 | 0.18836 | 0.00062371 | 60 | 18120 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1746 | 19709 | Camp Hill | CB2006 | 2024-12-04 10:54 | 2024-12-04 11:52 | 0.074066 | 0.0012994 | 125 | 7125 | Unplanned | Human Error | tree trimming error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1747 | 19710 | Camp Hill | CB2006 | 2024-12-04 15:08 | 2024-12-04 16:37 | 0.10454 | 0.0011747 | 113 | 10057 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1748 | 19723 | Wanaka | CB2754 | 2024-12-04 15:08 | 2024-12-04 15:09 | 0.00024949 | 0.00024949 | 24 | 24 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1749 | 19735 | Green Island | GI11 | 2024-12-04 21:00 | 2024-12-05 14:57 | 0.011196 | 1.0395e-05 | 1 | 1077 | Unplanned | Defective Equipment | faulty transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1750 | 19774 | East Taieri | ET5 | 2024-12-05 09:14 | 2024-12-05 16:19 | 0.070688 | 0.00016632 | 16 | 6800 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1751 | 19773 | East Taieri | ET5 | 2024-12-05 09:14 | 2024-12-05 16:19 | 0.18997 | 0.00044699 | 43 | 18275 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1752 | 19772 | East Taieri | ET5 | 2024-12-05 09:14 | 2024-12-05 16:11 | 0.60254 | 0.0014449 | 139 | 57963 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1753 | 19742 | Ettrick | CB480 | 2024-12-05 11:26 | 2024-12-06 16:27 | 0.018098 | 1.0395e-05 | 1 | 1741 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1754 | 19740 | Ettrick | CB480 | 2024-12-05 11:26 | 2024-12-05 20:30 | 0.01131 | 2.079e-05 | 2 | 1088 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1755 | 19741 | Ettrick | CB480 | 2024-12-05 11:26 | 2024-12-05 20:30 | 0.01131 | 2.079e-05 | 2 | 1088 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1756 | 19738 | Ettrick | CB480 | 2024-12-05 11:26 | 2024-12-05 13:20 | 0.029626 | 0.00025988 | 25 | 2850 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1757 | 19739 | Ettrick | CB480 | 2024-12-05 11:26 | 2024-12-05 14:53 | 0.098983 | 0.00047818 | 46 | 9522 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1758 | 19737 | Ettrick | CB480 | 2024-12-05 11:26 | 2024-12-05 12:40 | 0.26924 | 0.0036383 | 350 | 25900 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1759 | 19744 | Ettrick | CB480 | 2024-12-05 14:09 | 2024-12-05 14:12 | 0.0077964 | 0.0038982 | 375 | 750 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1760 | 19754 | Halfway Bush | HB1 | 2024-12-05 17:27 | 2024-12-05 21:05 | 0.02946 | 0.00013514 | 13 | 2834 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1761 | 19753 | Halfway Bush | HB1 | 2024-12-05 17:27 | 2024-12-05 18:32 | 0.030406 | 0.00046779 | 45 | 2925 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1762 | 19755 | Outram | OT3 | 2024-12-05 18:25 | 2024-12-05 19:25 | 0.0012474 | 2.079e-05 | 2 | 120 | Unplanned | Defective Equipment | faulty fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1763 | 19759 | Cromwell | CB821 | 2024-12-05 18:34 | 2024-12-05 20:43 | 0.002682 | 2.079e-05 | 2 | 258 | Unplanned | Third-party Interference | accidental contact | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1764 | 19758 | Cromwell | CB821 | 2024-12-05 18:34 | 2024-12-05 20:41 | 0.026404 | 0.0002079 | 20 | 2540 | Unplanned | Third-party Interference | accidental contact | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1765 | 19757 | Cromwell | CB821 | 2024-12-05 18:34 | 2024-12-05 20:20 | 0.15977 | 0.0015073 | 145 | 15370 | Unplanned | Third-party Interference | accidental contact | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1766 | 19756 | Cromwell | CB821 | 2024-12-05 18:34 | 2024-12-05 20:19 | 0.69747 | 0.0066425 | 639 | 67095 | Unplanned | Third-party Interference | accidental contact | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1767 | 19748 | Berwick | BK1 | 2024-12-05 20:17 | 2024-12-06 02:47 | 0.0040541 | 1.0395e-05 | 1 | 390 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1768 | 19734 | Alexandra | CB162 | 2024-12-06 09:04 | 2024-12-06 14:08 | 0.28441 | 0.00093557 | 90 | 27360 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1769 | 19732 | Ettrick | CB480 | 2024-12-06 09:18 | 2024-12-06 10:06 | 0.0034928 | 7.2767e-05 | 7 | 336 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1770 | 19733 | Ettrick | CB480 | 2024-12-06 10:37 | 2024-12-06 11:47 | 0.00072767 | 1.0395e-05 | 1 | 70 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1771 | 19745 | Ettrick | CB480 | 2024-12-06 10:37 | 2024-12-06 11:47 | 0.00072767 | 1.0395e-05 | 1 | 70 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1772 | 19746 | Ettrick | CB480 | 2024-12-06 16:00 | 2024-12-06 16:27 | 0.00056134 | 2.079e-05 | 2 | 54 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1773 | 19747 | Ettrick | CB480 | 2024-12-06 16:03 | 2024-12-06 16:27 | 0.00049897 | 2.079e-05 | 2 | 48 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1774 | 19804 | Ettrick | CB480 | 2024-12-07 15:57 | 2024-12-07 16:29 | 0.00099794 | 3.1186e-05 | 3 | 96 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1775 | 19790 | Riverbank | CB2424 | 2024-12-08 12:35 | 2024-12-08 13:09 | 0.0091894 | 0.00027028 | 26 | 884 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1776 | 19789 | Riverbank | CB2423 | 2024-12-08 12:35 | 2024-12-08 13:08 | 0.13516 | 0.0040957 | 394 | 13002 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1777 | 19791 | Roxburgh | CB4637 | 2024-12-08 12:38 | 2024-12-08 13:21 | 0.22216 | 0.0051664 | 497 | 21371 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1778 | 19792 | Roxburgh | CB4637 | 2024-12-08 13:22 | 2024-12-08 13:23 | 0.0051664 | 0.0051664 | 497 | 497 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1779 | 19793 | Roxburgh | CB4637 | 2024-12-08 13:24 | 2024-12-08 13:36 | 0.061997 | 0.0051664 | 497 | 5964 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1780 | 19806 | Roxburgh | CB4633 | 2024-12-08 13:24 | 2024-12-08 13:32 | 0.0045739 | 0.00057174 | 55 | 440 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1781 | 19807 | Roxburgh | CB4635 | 2024-12-08 13:24 | 2024-12-08 13:32 | 0.019127 | 0.0023909 | 230 | 1840 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1782 | 19808 | Roxburgh | CB4639 | 2024-12-08 13:24 | 2024-12-08 13:37 | 0.017568 | 0.0013514 | 130 | 1690 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1783 | 19799 | Wanaka | CB2751 | 2024-12-09 06:20 | 2024-12-09 07:24 | 0.00066529 | 1.0395e-05 | 1 | 64 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1784 | 19787 | Ettrick | CB480 | 2024-12-09 09:03 | 2024-12-09 12:39 | 0.053889 | 0.00024949 | 24 | 5184 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1785 | 19786 | Arrowtown | CB7632 | 2024-12-09 09:06 | 2024-12-09 13:45 | 0.084108 | 0.00030146 | 29 | 8091 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1786 | 19784 | Wanaka | CB2754 | 2024-12-09 11:00 | 2024-12-09 13:50 | 0.0088359 | 5.1976e-05 | 5 | 850 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1787 | 19782 | Wanaka | CB2754 | 2024-12-09 11:26 | 2024-12-09 13:24 | 0.0049065 | 4.1581e-05 | 4 | 472 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1788 | 19819 | Port Chalmers | PC3 | 2024-12-10 08:36 | 2024-12-10 17:00 | 0.0052392 | 1.0395e-05 | 1 | 504 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1789 | 19820 | Port Chalmers | PC3 | 2024-12-10 08:36 | 2024-12-10 17:07 | 0.031872 | 6.2371e-05 | 6 | 3066 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1790 | 19810 | Lindis Crossing | CB2086 | 2024-12-10 08:50 | 2024-12-10 15:12 | 0.011913 | 3.1186e-05 | 3 | 1146 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1791 | 19809 | Lindis Crossing | CB2086 | 2024-12-10 08:50 | 2024-12-10 15:03 | 0.16673 | 0.00044699 | 43 | 16039 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1792 | 19816 | Port Chalmers | PC3 | 2024-12-10 09:02 | 2024-12-10 16:48 | 0.0048442 | 1.0395e-05 | 1 | 466 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1793 | 19817 | Port Chalmers | PC3 | 2024-12-10 09:02 | 2024-12-10 16:50 | 0.014595 | 3.1186e-05 | 3 | 1404 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1794 | 19818 | Port Chalmers | PC3 | 2024-12-10 09:02 | 2024-12-10 16:52 | 0.12703 | 0.00027028 | 26 | 12220 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1795 | 19815 | Port Chalmers | PC3 | 2024-12-10 09:02 | 2024-12-10 16:43 | 0.92489 | 0.0020063 | 193 | 88973 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1796 | 19812 | Omakau | CB656 | 2024-12-10 11:44 | 2024-12-10 12:42 | 0.0012058 | 2.079e-05 | 2 | 116 | Unplanned | Defective Equipment | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1797 | 20088 | Andersons Bay | AB9 | 2024-12-10 21:50 | 2024-12-10 23:55 | 0.0012994 | 1.0395e-05 | 1 | 125 | Unplanned | Wildlife | bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1798 | 20089 | Andersons Bay | AB9 | 2024-12-10 23:54 | 2024-12-10 23:55 | 1.0395e-05 | 1.0395e-05 | 1 | 1 | Unplanned | Wildlife | bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1799 | 20090 | Andersons Bay | AB9 | 2024-12-11 00:04 | 2024-12-11 00:47 | 0.00089399 | 2.079e-05 | 2 | 86 | Unplanned | Wildlife | bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1800 | 19823 | Frankton | CB7788 | 2024-12-11 05:20 | 2024-12-11 05:50 | 0.0034304 | 0.00011435 | 11 | 330 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1801 | 19827 | Frankton | CB7788 | 2024-12-11 05:20 | 2024-12-11 06:35 | 0.014034 | 0.00018711 | 18 | 1350 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1802 | 19825 | Frankton | CB7788 | 2024-12-11 05:20 | 2024-12-11 06:25 | 0.033109 | 0.00050937 | 49 | 3185 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1803 | 19824 | Frankton | CB7788 | 2024-12-11 05:20 | 2024-12-11 06:15 | 0.02973 | 0.00054055 | 52 | 2860 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1804 | 19838 | Outram | OT2 | 2024-12-11 08:01 | 2024-12-11 15:08 | 0.21306 | 0.00049897 | 48 | 20496 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1805 | 19829 | Frankton | CB7788 | 2024-12-11 08:05 | 2024-12-11 17:27 | 0.10516 | 0.00018711 | 18 | 10116 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1806 | 19822 | Cromwell | CB831 | 2024-12-11 09:03 | 2024-12-11 16:15 | 0.0044907 | 1.0395e-05 | 1 | 432 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1807 | 19821 | Cromwell | CB831 | 2024-12-11 09:03 | 2024-12-11 16:08 | 0.11487 | 0.00027028 | 26 | 11050 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1808 | 19839 | Lindis Crossing | CB2086 | 2024-12-11 09:19 | 2024-12-11 17:30 | 0.0051041 | 1.0395e-05 | 1 | 491 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1809 | 19830 | Frankton | CB7788 | 2024-12-11 18:13 | 2024-12-11 19:40 | 0.047028 | 0.00054055 | 52 | 4524 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1810 | 19834 | Frankton | CB7788 | 2024-12-11 18:46 | 2024-12-11 19:50 | 0.0073182 | 0.00011435 | 11 | 704 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1811 | 19836 | Frankton | CB7788 | 2024-12-11 19:00 | 2024-12-11 19:50 | 0.0093557 | 0.00018711 | 18 | 900 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1812 | 19832 | Frankton | CB7788 | 2024-12-11 19:16 | 2024-12-11 19:40 | 0.012225 | 0.00050937 | 49 | 1176 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1813 | 19840 | Omakau | CB656 | 2024-12-11 20:41 | 2024-12-11 21:25 | 0.00045739 | 1.0395e-05 | 1 | 44 | Unplanned | Defective Equipment | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1814 | 19842 | Camp Hill | CB2004 | 2024-12-12 09:03 | 2024-12-12 15:31 | 0.0080667 | 2.079e-05 | 2 | 776 | Planned | Planned interruption | network extension | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1815 | 19843 | Camp Hill | CB2004 | 2024-12-12 09:03 | 2024-12-12 15:32 | 0.028306 | 7.2767e-05 | 7 | 2723 | Planned | Planned interruption | network extension | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1816 | 19848 | Nth East Valley | NV7 | 2024-12-12 09:04 | 2024-12-12 17:10 | 0.050417 | 0.00010395 | 10 | 4850 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1817 | 19847 | Nth East Valley | NV7 | 2024-12-12 09:04 | 2024-12-12 16:30 | 0.23592 | 0.00053016 | 51 | 22695 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1818 | 19849 | Lindis Crossing | CB2086 | 2024-12-12 09:06 | 2024-12-12 12:10 | 0.040167 | 0.0002183 | 21 | 3864 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1819 | 19850 | Clyde-Earnscleugh | CB195 | 2024-12-12 09:06 | 2024-12-12 15:02 | 0.011102 | 3.1186e-05 | 3 | 1068 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1820 | 19844 | Omakau | CB656 | 2024-12-12 09:10 | 2024-12-12 13:13 | 0.002526 | 1.0395e-05 | 1 | 243 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1821 | 19845 | Nth East Valley | NV7 | 2024-12-12 09:13 | 2024-12-12 16:29 | 1.0243 | 0.0023493 | 226 | 98536 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1822 | 19932 | Nth East Valley | NV7 | 2024-12-12 09:13 | 2024-12-12 16:29 | 0.0045323 | 1.0395e-05 | 1 | 436 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1823 | 19854 | St. Kilda | SK9 | 2024-12-12 16:54 | 2024-12-12 17:14 | 0.0010395 | 5.1976e-05 | 5 | 100 | Unplanned | Adverse Environment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1824 | 19885 | Outram | OT2 | 2024-12-13 08:21 | 2024-12-13 14:57 | 0.01235 | 3.1186e-05 | 3 | 1188 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1825 | 19886 | Outram | OT2 | 2024-12-13 08:21 | 2024-12-13 16:14 | 0.014751 | 3.1186e-05 | 3 | 1419 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1826 | 19884 | Outram | OT2 | 2024-12-13 08:21 | 2024-12-13 14:57 | 0.13584 | 0.00034304 | 33 | 13068 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1827 | 19857 | Lindis Crossing | CB2086 | 2024-12-13 09:03 | 2024-12-13 10:33 | 0.0084201 | 9.3557e-05 | 9 | 810 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1828 | 19865 | Clyde-Earnscleugh | CB195 | 2024-12-13 09:12 | 2024-12-13 15:57 | 0.01263 | 3.1186e-05 | 3 | 1215 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1829 | 19866 | Clyde-Earnscleugh | CB195 | 2024-12-13 09:12 | 2024-12-13 16:00 | 0.15269 | 0.00037423 | 36 | 14688 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1830 | 19863 | Clyde-Earnscleugh | CB195 | 2024-12-13 09:12 | 2024-12-13 15:50 | 0.26479 | 0.00066529 | 64 | 25472 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1831 | 19901 | Clyde-Earnscleugh | CB195 | 2024-12-13 09:12 | 2024-12-13 16:00 | 0.021206 | 5.1976e-05 | 5 | 2040 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1832 | 19861 | East Taieri | ET5 | 2024-12-14 09:02 | 2024-12-14 17:45 | 0.0054367 | 1.0395e-05 | 1 | 523 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1833 | 19858 | East Taieri | ET5 | 2024-12-14 09:13 | 2024-12-14 10:30 | 0.005603 | 7.2767e-05 | 7 | 539 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1834 | 19869 | Wanaka | CB2754 | 2024-12-14 11:20 | 2024-12-14 12:45 | 0.00088359 | 1.0395e-05 | 1 | 85 | Unplanned | Wildlife | bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1835 | 19882 | East Taieri | ET5 | 2024-12-14 15:43 | 2024-12-14 17:34 | 0.0080771 | 7.2767e-05 | 7 | 777 | Unplanned | Defective Equipment | faulty lightning arrestor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1836 | 19859 | East Taieri | ET5 | 2024-12-14 16:30 | 2024-12-14 17:34 | 0.0046571 | 7.2767e-05 | 7 | 448 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1837 | 19871 | Willowbank | WB3 | 2024-12-14 18:21 | 2024-12-14 19:43 | 0.00085241 | 1.0395e-05 | 1 | 82 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1838 | 19872 | Outram | OT1 | 2024-12-14 18:26 | 2024-12-14 23:32 | 0.0063619 | 2.079e-05 | 2 | 612 | Unplanned | Lightning | lightning strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1839 | 19874 | Alexandra | CB169 | 2024-12-14 23:08 | 2024-12-15 01:06 | 0.16784 | 0.0014345 | 138 | 16146 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1840 | 19873 | Alexandra | CB169 | 2024-12-14 23:08 | 2024-12-15 00:42 | 0.17305 | 0.0018607 | 179 | 16647 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1841 | 19878 | Alexandra | CB169 | 2024-12-15 00:42 | 2024-12-15 05:23 | 0.011684 | 4.1581e-05 | 4 | 1124 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1842 | 19876 | Alexandra | CB169 | 2024-12-15 00:42 | 2024-12-15 01:06 | 0.0093245 | 0.00040541 | 39 | 897 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1843 | 19875 | Alexandra | CB169 | 2024-12-15 00:42 | 2024-12-15 00:53 | 0.0062891 | 0.00057174 | 55 | 605 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1844 | 19877 | Alexandra | CB169 | 2024-12-15 00:42 | 2024-12-15 01:58 | 0.063993 | 0.00084201 | 81 | 6156 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1845 | 19879 | Alexandra | CB169 | 2024-12-15 01:04 | 2024-12-15 01:06 | 0.00057174 | 0.00057174 | 55 | 55 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1846 | 19896 | Corstorphine | CO7 | 2024-12-16 08:17 | 2024-12-16 12:39 | 0.1498 | 0.00057174 | 55 | 14410 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1847 | 19895 | Corstorphine | CO7 | 2024-12-16 08:17 | 2024-12-16 12:39 | 0.26418 | 0.0010083 | 97 | 25414 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1848 | 19887 | Camp Hill | CB2006 | 2024-12-16 09:00 | 2024-12-16 11:53 | 0.06654 | 0.00038462 | 37 | 6401 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1849 | 19894 | Lauder Flat | CB6576 | 2024-12-16 09:30 | 2024-12-16 11:25 | 0.0011955 | 1.0395e-05 | 1 | 115 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1850 | 19893 | Port Chalmers | PC5 | 2024-12-16 17:32 | 2024-12-16 18:25 | 0.023691 | 0.00044699 | 43 | 2279 | Unplanned | Defective Equipment | failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1851 | 19892 | Camp Hill | CB2006 | 2024-12-16 17:49 | 2024-12-16 18:09 | 0.0033265 | 0.00016632 | 16 | 320 | Unplanned | Defective Equipment | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1852 | 19954 | Outram | OT2 | 2024-12-17 08:25 | 2024-12-17 15:17 | 0.14133 | 0.00034304 | 33 | 13596 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1853 | 19929 | Camp Hill | CB2008 | 2024-12-17 08:35 | 2024-12-17 15:21 | 0.0042205 | 1.0395e-05 | 1 | 406 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1854 | 19928 | Camp Hill | CB2008 | 2024-12-17 08:35 | 2024-12-17 15:21 | 0.042205 | 0.00010395 | 10 | 4060 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1855 | 19904 | Camp Hill | CB2004 | 2024-12-17 09:02 | 2024-12-17 13:22 | 0.010811 | 4.1581e-05 | 4 | 1040 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1856 | 19912 | Roxburgh | CB4635 | 2024-12-17 09:09 | 2024-12-17 13:23 | 0.010562 | 4.1581e-05 | 4 | 1016 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1857 | 19911 | Roxburgh | CB4635 | 2024-12-17 09:09 | 2024-12-17 13:15 | 0.048587 | 0.00019751 | 19 | 4674 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1858 | 19906 | Outram | OT2 | 2024-12-18 08:04 | 2024-12-18 13:39 | 0.038306 | 0.00011435 | 11 | 3685 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1859 | 19907 | Outram | OT2 | 2024-12-18 08:04 | 2024-12-18 14:28 | 0.1477 | 0.00038462 | 37 | 14208 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1860 | 19905 | North City | NC12 | 2024-12-18 08:12 | 2024-12-18 15:28 | 0.0045323 | 1.0395e-05 | 1 | 436 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1861 | 19930 | Wanaka | CB2752 | 2024-12-18 09:01 | 2024-12-18 15:35 | 0.0040957 | 1.0395e-05 | 1 | 394 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1862 | 19931 | Wanaka | CB2752 | 2024-12-18 09:01 | 2024-12-18 15:44 | 0.0041893 | 1.0395e-05 | 1 | 403 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1863 | 19903 | Camp Hill | CB2008 | 2024-12-18 09:02 | 2024-12-18 14:41 | 0.003524 | 1.0395e-05 | 1 | 339 | Planned | Planned interruption | network extension | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1864 | 19902 | Arrowtown | CB7632 | 2024-12-18 09:10 | 2024-12-18 13:35 | 0.0082642 | 3.1186e-05 | 3 | 795 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1865 | 19948 | Arrowtown | CB7632 | 2024-12-18 09:40 | 2024-12-18 12:20 | 0.0016632 | 1.0395e-05 | 1 | 160 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1866 | 19917 | Queensberry | CB2423 | 2024-12-18 11:39 | 2024-12-18 13:21 | 0.0031809 | 3.1186e-05 | 3 | 306 | Unplanned | Defective Equipment | burnt fuse jaw | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1867 | 19918 | Queensberry | CB2423 | 2024-12-18 11:54 | 2024-12-18 13:21 | 0.0018088 | 2.079e-05 | 2 | 174 | Unplanned | Defective Equipment | burnt fuse jaw | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1868 | 20064 | Carisbrook | CK13 | 2024-12-19 08:01 | 2024-12-19 13:29 | 0.3546 | 0.0010811 | 104 | 34112 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1869 | 20066 | Carisbrook | CK13 | 2024-12-19 08:01 | 2024-12-19 13:29 | 0.0034096 | 1.0395e-05 | 1 | 328 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1870 | 19942 | Berwick | BK1 | 2024-12-19 08:32 | 2024-12-19 10:50 | 0.025822 | 0.00018711 | 18 | 2484 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1871 | 19935 | Mosgiel | MG4 | 2024-12-19 08:34 | 2024-12-19 15:55 | 0.09627 | 0.0002183 | 21 | 9261 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1872 | 19933 | Mosgiel | MG4 | 2024-12-19 08:36 | 2024-12-19 15:46 | 0.0044699 | 1.0395e-05 | 1 | 430 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1873 | 19937 | Mosgiel | MG4 | 2024-12-19 08:37 | 2024-12-19 16:03 | 0.14372 | 0.00032225 | 31 | 13826 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1874 | 19939 | Mosgiel | MG4 | 2024-12-19 08:40 | 2024-12-19 16:07 | 0.0092933 | 2.079e-05 | 2 | 894 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1875 | 19943 | Cardrona | CB2881 | 2024-12-19 09:00 | 2024-12-19 13:31 | 0.0056342 | 2.079e-05 | 2 | 542 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1876 | 19952 | Wanaka | CB2752 | 2024-12-19 09:01 | 2024-12-19 15:00 | 0.0037319 | 1.0395e-05 | 1 | 359 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1877 | 19953 | Wanaka | CB2752 | 2024-12-19 09:01 | 2024-12-19 15:10 | 0.0038358 | 1.0395e-05 | 1 | 369 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1878 | 19944 | Frankton | CB7782 | 2024-12-19 09:02 | 2024-12-19 09:54 | 0.063245 | 0.0012162 | 117 | 6084 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1879 | 19945 | Frankton | CB7782 | 2024-12-19 09:02 | 2024-12-19 15:18 | 0.9068 | 0.0024117 | 232 | 87232 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1880 | 19941 | Arrowtown | CB7632 | 2024-12-19 09:04 | 2024-12-19 13:01 | 0.0024637 | 1.0395e-05 | 1 | 237 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1881 | 20091 | Port Chalmers | PC3 | 2024-12-19 12:33 | 2024-12-19 13:05 | 0.00066529 | 2.079e-05 | 2 | 64 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1882 | 19949 | Omakau | CB656 | 2024-12-19 13:38 | 2024-12-19 15:51 | 0.067746 | 0.00050937 | 49 | 6517 | Unplanned | Defective Equipment | failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1883 | 19950 | Omakau | CB656 | 2024-12-19 14:55 | 2024-12-19 16:15 | 0.019959 | 0.00024949 | 24 | 1920 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1884 | 19951 | Omakau | CB656 | 2024-12-19 14:55 | 2024-12-19 17:02 | 0.083827 | 0.00066529 | 64 | 8064 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1885 | 19946 | Frankton | CB7782 | 2024-12-19 16:16 | 2024-12-19 16:57 | 0.049866 | 0.0012162 | 117 | 4797 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1886 | 19978 | Commonage | CB5730 | 2024-12-28 21:13 | 2024-12-28 21:16 | 0.0020894 | 0.00069648 | 67 | 201 | Unplanned | Adverse Environment | fire/smoke | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1887 | 19979 | Commonage | CB5730 | 2024-12-28 21:16 | 2024-12-28 23:47 | 0.018836 | 0.00012474 | 12 | 1812 | Unplanned | Adverse Environment | fire/smoke | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1888 | 19980 | Commonage | CB5730 | 2024-12-28 23:47 | 2024-12-28 23:49 | 0.001393 | 0.00069648 | 67 | 134 | Unplanned | Adverse Environment | fire/smoke | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1889 | 20021 | Camp Hill | CB2006 | 2024-12-30 05:40 | 2024-12-30 06:47 | 0.80889 | 0.012256 | 1179 | 77814 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1890 | 20023 | Camp Hill | CB2006 | 2024-12-30 06:47 | 2024-12-30 09:21 | 0.1809 | 0.0011747 | 113 | 17402 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1891 | 20022 | Camp Hill | CB2006 | 2024-12-30 06:47 | 2024-12-30 06:49 | 0.022163 | 0.011081 | 1066 | 2132 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1892 | 20024 | Camp Hill | CB2006 | 2024-12-30 06:49 | 2024-12-30 08:31 | 0.0031498 | 3.1186e-05 | 3 | 303 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1893 | 20031 | Camp Hill | CB2006 | 2024-12-30 06:49 | 2024-12-30 14:53 | 0.050209 | 0.00010395 | 10 | 4830 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1894 | 20026 | Camp Hill | CB2006 | 2024-12-30 06:49 | 2024-12-30 09:21 | 0.034533 | 0.00022869 | 22 | 3322 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1895 | 20029 | Camp Hill | CB2006 | 2024-12-30 06:49 | 2024-12-30 11:00 | 0.072767 | 0.00029107 | 28 | 7000 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1896 | 20032 | Camp Hill | CB2006 | 2024-12-30 06:49 | 2024-12-30 16:45 | 0.17937 | 0.00030146 | 29 | 17255 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1897 | 20025 | Camp Hill | CB2006 | 2024-12-30 06:49 | 2024-12-30 08:56 | 0.072039 | 0.00057174 | 55 | 6930 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1898 | 20028 | Camp Hill | CB2006 | 2024-12-30 06:49 | 2024-12-30 10:21 | 0.3992 | 0.0018919 | 182 | 38402 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1899 | 20030 | Camp Hill | CB2006 | 2024-12-30 06:49 | 2024-12-30 11:14 | 0.94131 | 0.0035656 | 343 | 90552 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1900 | 20027 | Camp Hill | CB2006 | 2024-12-30 06:49 | 2024-12-30 09:40 | 0.69627 | 0.0040957 | 394 | 66980 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1901 | 20033 | Camp Hill | CB2006 | 2024-12-31 16:49 | 2024-12-31 17:00 | 0.0011435 | 0.00010395 | 10 | 110 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1902 | 20034 | Camp Hill | CB2006 | 2024-12-31 16:59 | 2024-12-31 17:00 | 0.00030146 | 0.00030146 | 29 | 29 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1903 | 19988 | Green Island | GI2 | 2025-01-01 22:18 | 2025-01-01 23:01 | 0.096104 | 0.002235 | 215 | 9245 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1904 | 19993 | Port Chalmers | PC3 | 2025-01-04 03:47 | 2025-01-04 05:14 | 0.14125 | 0.0016424 | 158 | 13588 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1905 | 19994 | Port Chalmers | PC3 | 2025-01-04 03:47 | 2025-01-04 06:18 | 0.63258 | 0.0041893 | 403 | 60853 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1906 | 20000 | Port Chalmers | PC3 | 2025-01-04 07:02 | 2025-01-04 11:15 | 0.12312 | 0.00048858 | 47 | 11844 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1907 | 19998 | Port Chalmers | PC3 | 2025-01-04 07:02 | 2025-01-04 08:43 | 0.11654 | 0.0011539 | 111 | 11211 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1908 | 19999 | Port Chalmers | PC3 | 2025-01-04 07:02 | 2025-01-04 11:14 | 1.0557 | 0.0041893 | 403 | 101556 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1909 | 20001 | Port Chalmers | PC3 | 2025-01-04 09:36 | 2025-01-04 10:03 | 0.031154 | 0.0011539 | 111 | 2997 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1910 | 20002 | Port Chalmers | PC3 | 2025-01-04 10:21 | 2025-01-04 10:25 | 0.0046155 | 0.0011539 | 111 | 444 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1911 | 20010 | Ward Street | WS4 | 2025-01-07 08:34 | 2025-01-07 15:37 | 0.03078 | 7.2767e-05 | 7 | 2961 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1912 | 20038 | Green Island | GI2 | 2025-01-07 09:20 | 2025-01-07 09:31 | 0.024585 | 0.002235 | 215 | 2365 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1913 | 20016 | Alexandra | CB169 | 2025-01-07 18:41 | 2025-01-07 19:02 | 0.0045843 | 0.0002183 | 21 | 441 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1914 | 20040 | Ward Street | WS10 | 2025-01-08 08:06 | 2025-01-08 16:21 | 0.051456 | 0.00010395 | 10 | 4950 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1915 | 20039 | Ward Street | WS10 | 2025-01-08 08:06 | 2025-01-08 15:51 | 0.13535 | 0.00029107 | 28 | 13020 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1916 | 20041 | St. Kilda | SK8 | 2025-01-08 08:34 | 2025-01-08 18:23 | 0.74698 | 0.0012682 | 122 | 71858 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1917 | 20054 | St. Kilda | SK8 | 2025-01-08 08:34 | 2025-01-08 18:23 | 0.0061228 | 1.0395e-05 | 1 | 589 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1918 | 20044 | Cromwell | CB831 | 2025-01-08 09:04 | 2025-01-08 12:20 | 0.046862 | 0.00023909 | 23 | 4508 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1919 | 20042 | St. Kilda | SK11 | 2025-01-09 08:20 | 2025-01-09 18:17 | 0.012412 | 2.079e-05 | 2 | 1194 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1920 | 20043 | Ettrick | CB480 | 2025-01-09 09:06 | 2025-01-09 13:09 | 0.065677 | 0.00027028 | 26 | 6318 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1921 | 20035 | Camp Hill | CB2006 | 2025-01-10 09:45 | 2025-01-10 10:46 | 0.02473 | 0.00040541 | 39 | 2379 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1922 | 20049 | Alexandra | CB169 | 2025-01-12 07:55 | 2025-01-12 09:00 | 0.00067569 | 1.0395e-05 | 1 | 65 | Unplanned | Wildlife | bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1923 | 20052 | Port Chalmers | PC4 | 2025-01-12 10:05 | 2025-01-12 12:57 | 0.0053639 | 3.1186e-05 | 3 | 516 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1924 | 20051 | Port Chalmers | PC4 | 2025-01-12 10:05 | 2025-01-12 10:53 | 0.39369 | 0.0082018 | 789 | 37872 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1925 | 20059 | Arrowtown | CB7632 | 2025-01-13 02:30 | 2025-01-13 03:39 | 0.054513 | 0.00079004 | 76 | 5244 | Unplanned | Wildlife | possum on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1926 | 20057 | Corstorphine | CO6 | 2025-01-13 08:32 | 2025-01-13 17:46 | 0.34554 | 0.00062371 | 60 | 33240 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1927 | 20056 | Corstorphine | CO6 | 2025-01-13 08:32 | 2025-01-13 10:02 | 0.17495 | 0.0019439 | 187 | 16830 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1928 | 20062 | Cromwell | CB821 | 2025-01-13 15:36 | 2025-01-13 16:55 | 0.054201 | 0.00068608 | 66 | 5214 | Unplanned | Wildlife | bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1929 | 20063 | Cromwell | CB821 | 2025-01-13 15:36 | 2025-01-13 17:28 | 0.091977 | 0.00082122 | 79 | 8848 | Unplanned | Wildlife | bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1930 | 20073 | Arrowtown | CB7632 | 2025-01-13 15:53 | 2025-01-13 16:51 | 0.0029626 | 5.1976e-05 | 5 | 285 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1931 | 20076 | Cromwell | CB823 | 2025-01-14 06:03 | 2025-01-14 06:34 | 0.003867 | 0.00012474 | 12 | 372 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1932 | 20071 | Wanaka | CB2755 | 2025-01-14 08:02 | 2025-01-14 17:03 | 0.32618 | 0.00060292 | 58 | 31378 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1933 | 20070 | Wanaka | CB2755 | 2025-01-14 08:02 | 2025-01-14 16:54 | 0.32629 | 0.00061332 | 59 | 31388 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1934 | 20072 | Roxburgh | CB4637 | 2025-01-14 09:06 | 2025-01-14 14:57 | 0.080272 | 0.00022869 | 22 | 7722 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1935 | 20083 | Cromwell | CB823 | 2025-01-14 21:18 | 2025-01-14 21:32 | 0.0017464 | 0.00012474 | 12 | 168 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1936 | 20084 | St. Kilda | SK12 | 2025-01-15 08:02 | 2025-01-15 17:09 | 0.04549 | 8.3162e-05 | 8 | 4376 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1937 | 20077 | Port Chalmers | PC3 | 2025-01-15 09:06 | 2025-01-15 14:01 | 0.12573 | 0.0004262 | 41 | 12095 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1938 | 20079 | Ettrick | CB480 | 2025-01-15 10:30 | 2025-01-15 13:32 | 0.056758 | 0.00031186 | 30 | 5460 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1939 | 20078 | Ettrick | CB480 | 2025-01-15 10:30 | 2025-01-15 13:32 | 0.26718 | 0.0014761 | 142 | 25702 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1940 | 20085 | Roxburgh | CB4633 | 2025-01-16 08:06 | 2025-01-16 13:48 | 0.014221 | 4.1581e-05 | 4 | 1368 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1941 | 20098 | Frankton | CB7784 | 2025-01-16 08:40 | 2025-01-16 16:20 | 0.0047818 | 1.0395e-05 | 1 | 460 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1942 | 20100 | Frankton | CB7784 | 2025-01-16 09:01 | 2025-01-16 16:22 | 0.0045843 | 1.0395e-05 | 1 | 441 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1943 | 20097 | Frankton | CB7784 | 2025-01-16 09:01 | 2025-01-16 16:10 | 0.0089191 | 2.079e-05 | 2 | 858 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1944 | 20114 | Roxburgh | CB4639 | 2025-01-16 11:01 | 2025-01-16 12:01 | 0.00062371 | 1.0395e-05 | 1 | 60 | Unplanned | Defective Equipment | broken fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1945 | 21041 | Arrowtown | CB7632 | 2025-01-16 12:56 | 2025-01-16 14:09 | 0.010624 | 0.00014553 | 14 | 1022 | Unplanned | Defective Equipment | broken tie wire (floater) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1946 | 20096 | Green Island | GI12 | 2025-01-17 08:06 | 2025-01-17 16:36 | 0.22797 | 0.00044699 | 43 | 21930 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1947 | 20117 | Andersons Bay | AB7 | 2025-01-17 09:05 | 2025-01-17 14:17 | 0.016217 | 5.1976e-05 | 5 | 1560 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1948 | 20116 | Andersons Bay | AB7 | 2025-01-17 09:05 | 2025-01-17 13:51 | 0.092164 | 0.00032225 | 31 | 8866 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1949 | 20106 | Riverbank | CB6342 | 2025-01-18 19:38 | 2025-01-18 21:07 | 0.18387 | 0.0020894 | 201 | 17688 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1950 | 20107 | Lauder Flat | CB6576 | 2025-01-18 21:08 | 2025-01-18 22:47 | 0.085574 | 0.0008732 | 84 | 8232 | Unplanned | Defective Equipment | broken tie wire (floater) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1951 | 20108 | Lauder Flat | CB6576 | 2025-01-18 22:53 | 2025-01-18 23:13 | 0.0041477 | 0.0002183 | 21 | 399 | Unplanned | Defective Equipment | broken tie wire (floater) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1952 | 20109 | Lauder Flat | CB6576 | 2025-01-18 22:53 | 2025-01-19 00:34 | 0.066145 | 0.0006549 | 63 | 6363 | Unplanned | Defective Equipment | broken tie wire (floater) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1953 | 20124 | South City | SC12 | 2025-01-20 15:33 | 2025-01-20 15:54 | 0.016372 | 0.00077964 | 75 | 1575 | Unplanned | Defective Equipment | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1954 | 20125 | Camp Hill | CB2006 | 2025-01-20 16:24 | 2025-01-20 16:38 | 0.0066945 | 0.00047818 | 46 | 644 | Unplanned | Defective Equipment | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1955 | 20162 | Roxburgh | CB4633 | 2025-01-21 08:30 | 2025-01-21 08:38 | 8.3162e-05 | 1.0395e-05 | 1 | 8 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1956 | 20165 | Roxburgh | CB4633 | 2025-01-21 08:30 | 2025-01-21 17:10 | 0.0054055 | 1.0395e-05 | 1 | 520 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1957 | 20168 | Roxburgh | CB4633 | 2025-01-21 08:30 | 2025-01-21 17:17 | 0.0054783 | 1.0395e-05 | 1 | 527 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1958 | 20164 | Roxburgh | CB4633 | 2025-01-21 08:30 | 2025-01-21 17:10 | 0.010811 | 2.079e-05 | 2 | 1040 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1959 | 20166 | Roxburgh | CB4633 | 2025-01-21 08:30 | 2025-01-21 17:13 | 0.010873 | 2.079e-05 | 2 | 1046 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1960 | 20170 | Roxburgh | CB4633 | 2025-01-21 08:30 | 2025-01-21 17:23 | 0.011081 | 2.079e-05 | 2 | 1066 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1961 | 20169 | Roxburgh | CB4633 | 2025-01-21 08:30 | 2025-01-21 17:19 | 0.016497 | 3.1186e-05 | 3 | 1587 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1962 | 20167 | Roxburgh | CB4633 | 2025-01-21 08:30 | 2025-01-21 17:17 | 0.038348 | 7.2767e-05 | 7 | 3689 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1963 | 20171 | Roxburgh | CB4633 | 2025-01-21 08:30 | 2025-01-21 17:36 | 0.085137 | 0.00015593 | 15 | 8190 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1964 | 20163 | Roxburgh | CB4633 | 2025-01-21 08:30 | 2025-01-21 15:53 | 0.096707 | 0.0002183 | 21 | 9303 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1965 | 20128 | East Taieri | ET3 | 2025-01-21 08:30 | 2025-01-21 16:23 | 0.78505 | 0.0016632 | 160 | 75520 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1966 | 20129 | Lauder Flat | CB6576 | 2025-01-21 08:31 | 2025-01-21 14:54 | 0.051758 | 0.00013514 | 13 | 4979 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1967 | 20137 | Lauder Flat | CB6576 | 2025-01-22 00:38 | 2025-01-22 02:55 | 0.11963 | 0.0008732 | 84 | 11508 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1968 | 20136 | Lauder Flat | CB6576 | 2025-01-22 00:38 | 2025-01-22 02:53 | 0.2091 | 0.0015489 | 149 | 20115 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1969 | 20147 | Alexandra | CB167 | 2025-01-22 08:34 | 2025-01-22 18:26 | 0.56001 | 0.00094597 | 91 | 53872 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1970 | 20263 | Alexandra | CB167 | 2025-01-22 08:34 | 2025-01-22 18:26 | 0.012308 | 2.079e-05 | 2 | 1184 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1971 | 20143 | Nth East Valley | NV6 | 2025-01-22 08:36 | 2025-01-22 13:44 | 0.20811 | 0.00067569 | 65 | 20020 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1972 | 20142 | Nth East Valley | NV6 | 2025-01-22 08:36 | 2025-01-22 13:44 | 0.7332 | 0.0023805 | 229 | 70532 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1973 | 20174 | Andersons Bay | AB9 | 2025-01-23 08:34 | 2025-01-23 16:56 | 0.015655 | 3.1186e-05 | 3 | 1506 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1974 | 20175 | Andersons Bay | AB9 | 2025-01-23 08:36 | 2025-01-23 16:58 | 0.015655 | 3.1186e-05 | 3 | 1506 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1975 | 20173 | Andersons Bay | AB9 | 2025-01-23 08:36 | 2025-01-23 16:43 | 0.075937 | 0.00015593 | 15 | 7305 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1976 | 20262 | Andersons Bay | AB9 | 2025-01-23 08:36 | 2025-01-23 16:43 | 0.025312 | 5.1976e-05 | 5 | 2435 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1977 | 20148 | Alexandra | CB167 | 2025-01-23 08:39 | 2025-01-23 16:19 | 0.7364 | 0.0016009 | 154 | 70840 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1978 | 20201 | Alexandra | CB167 | 2025-01-23 08:39 | 2025-01-23 16:19 | 0.0047818 | 1.0395e-05 | 1 | 460 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1979 | 20145 | Ettrick | CB480 | 2025-01-23 09:27 | 2025-01-23 11:57 | 0.27132 | 0.0018088 | 174 | 26100 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1980 | 20160 | Queensberry | CB2423 | 2025-01-23 11:48 | 2025-01-23 12:14 | 0.00027028 | 1.0395e-05 | 1 | 26 | Unplanned | Defective Equipment | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1981 | 20161 | Alexandra | CB169 | 2025-01-23 14:42 | 2025-01-23 15:03 | 0.0002183 | 1.0395e-05 | 1 | 21 | Unplanned | Defective Equipment | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1982 | 20245 | Green Island | GI2 | 2025-01-23 16:17 | 2025-01-23 17:46 | 0.044824 | 0.00050937 | 49 | 4312 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1983 | 20244 | Green Island | GI2 | 2025-01-23 16:17 | 2025-01-23 17:28 | 0.12079 | 0.0017256 | 166 | 11620 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1984 | 20159 | Green Island | GI4 | 2025-01-23 18:02 | 2025-01-23 18:40 | 0.029626 | 0.00077964 | 75 | 2850 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1985 | 20183 | Commonage | CB5731 | 2025-01-23 23:05 | 2025-01-24 00:43 | 0.032599 | 0.00033265 | 32 | 3136 | Unplanned | Defective Equipment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1986 | 20180 | Omakau | CB656 | 2025-01-24 05:56 | 2025-01-24 09:29 | 0.026445 | 0.00012474 | 12 | 2544 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1987 | 20179 | Omakau | CB656 | 2025-01-24 05:56 | 2025-01-24 08:27 | 0.020271 | 0.00013514 | 13 | 1950 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1988 | 20181 | Omakau | CB656 | 2025-01-24 05:56 | 2025-01-24 09:58 | 0.050105 | 0.0002079 | 20 | 4820 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1989 | 20178 | Omakau | CB656 | 2025-01-24 05:56 | 2025-01-24 08:06 | 0.056758 | 0.0004366 | 42 | 5460 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1990 | 20188 | Andersons Bay | AB11 | 2025-01-24 08:12 | 2025-01-24 11:06 | 0.0036175 | 2.079e-05 | 2 | 348 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1991 | 20182 | Omakau | CB656 | 2025-01-24 08:55 | 2025-01-24 09:01 | 0.0034304 | 0.00057174 | 55 | 330 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1992 | 20186 | Commonage | CB5731 | 2025-01-24 09:02 | 2025-01-24 09:46 | 0.0086904 | 0.00019751 | 19 | 836 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 1993 | 20230 | Commonage | CB5731 | 2025-01-24 09:02 | 2025-01-24 09:46 | 0.0018296 | 4.1581e-05 | 4 | 176 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1994 | 20185 | Omakau | CB656 | 2025-01-24 09:04 | 2025-01-24 14:19 | 0.013098 | 4.1581e-05 | 4 | 1260 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1995 | 20200 | Camp Hill | CB2006 | 2025-01-24 10:25 | 2025-01-24 10:53 | 0.013971 | 0.00049897 | 48 | 1344 | Unplanned | Defective Equipment | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1996 | 20195 | Camp Hill | CB2006 | 2025-01-25 14:47 | 2025-01-25 14:59 | 0.0019959 | 0.00016632 | 16 | 192 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1997 | 20196 | Camp Hill | CB2006 | 2025-01-25 14:47 | 2025-01-25 16:57 | 0.14617 | 0.0011331 | 109 | 14061 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 1998 | 20197 | Cromwell | CB832 | 2025-01-26 11:18 | 2025-01-26 11:26 | 0.00074846 | 9.3557e-05 | 9 | 72 | Unplanned | Wildlife | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 1999 | 20209 | East Taieri | ET2 | 2025-01-27 00:36 | 2025-01-27 02:08 | 0.090813 | 0.00099794 | 96 | 8736 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2000 | 20208 | East Taieri | ET2 | 2025-01-27 00:36 | 2025-01-27 01:31 | 0.05445 | 0.0010083 | 97 | 5238 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2001 | 20210 | East Taieri | ET2 | 2025-01-27 02:06 | 2025-01-27 02:08 | 0.0010083 | 0.0010083 | 97 | 97 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2002 | 20211 | Ward Street | WS4 | 2025-01-27 03:35 | 2025-01-27 04:28 | 0.00055095 | 1.0395e-05 | 1 | 53 | Unplanned | Third-party Interference | accidental contact | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2003 | 20212 | Ward Street | WS4 | 2025-01-27 03:35 | 2025-01-27 06:21 | 0.53666 | 0.0032329 | 311 | 51626 | Unplanned | Third-party Interference | accidental contact | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2004 | 20213 | Ward Street | WS4 | 2025-01-27 05:28 | 2025-01-27 06:21 | 0.00055095 | 1.0395e-05 | 1 | 53 | Unplanned | Third-party Interference | accidental contact | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2005 | 20221 | St. Kilda | SK4 | 2025-01-27 08:02 | 2025-01-27 08:30 | 0.0049481 | 0.00017672 | 17 | 476 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2006 | 20203 | Port Chalmers | PC3 | 2025-01-27 09:09 | 2025-01-27 14:20 | 0.13255 | 0.0004262 | 41 | 12751 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2007 | 20217 | Lindis Crossing | CB2084 | 2025-01-28 07:37 | 2025-01-28 13:36 | 0.0074638 | 2.079e-05 | 2 | 718 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2008 | 20207 | Roxburgh | HSB33 | 2025-01-28 08:01 | 2025-01-28 17:27 | 0.011767 | 2.079e-05 | 2 | 1132 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2009 | 20205 | Roxburgh | CB4633 | 2025-01-28 09:04 | 2025-01-28 17:27 | 0.04183 | 8.3162e-05 | 8 | 4024 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2010 | 20206 | Frankton | CB7790 | 2025-01-28 09:04 | 2025-01-28 13:35 | 0.29861 | 0.0011019 | 106 | 28726 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2011 | 20220 | North City | NC6 | 2025-01-29 08:05 | 2025-01-29 14:44 | 0.24057 | 0.00060292 | 58 | 23142 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2012 | 20228 | Port Chalmers | PC3 | 2025-01-29 08:35 | 2025-01-29 15:15 | 0.062371 | 0.00015593 | 15 | 6000 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2013 | 20227 | Port Chalmers | PC3 | 2025-01-29 08:35 | 2025-01-29 15:10 | 0.10676 | 0.00027028 | 26 | 10270 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2014 | 20219 | Queenstown | CB5262 | 2025-01-29 09:00 | 2025-01-29 16:03 | 0.10993 | 0.00025988 | 25 | 10575 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2015 | 20222 | St. Kilda | SK4 | 2025-01-29 14:22 | 2025-01-29 16:27 | 0.02209 | 0.00017672 | 17 | 2125 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2016 | 20239 | Arrowtown | CB7632 | 2025-01-30 05:44 | 2025-01-30 07:52 | 0.10112 | 0.00079004 | 76 | 9728 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2017 | 20238 | Arrowtown | CB7632 | 2025-01-30 05:44 | 2025-01-30 07:50 | 0.19647 | 0.0015593 | 150 | 18900 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2018 | 20237 | Arrowtown | CB7632 | 2025-01-30 05:44 | 2025-01-30 06:57 | 0.12218 | 0.0016736 | 161 | 11753 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2019 | 20240 | Arrowtown | CB7632 | 2025-01-30 05:44 | 2025-01-30 07:55 | 0.38266 | 0.0029211 | 281 | 36811 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2020 | 20233 | Lindis Crossing | CB2084 | 2025-01-30 08:17 | 2025-01-30 13:14 | 0.0030874 | 1.0395e-05 | 1 | 297 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2021 | 20231 | Lindis Crossing | CB2084 | 2025-01-30 08:36 | 2025-01-30 13:02 | 0.027651 | 0.00010395 | 10 | 2660 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2022 | 20249 | Ettrick | CB480 | 2025-01-31 05:20 | 2025-01-31 07:26 | 0.038982 | 0.00031186 | 30 | 3750 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2023 | 20248 | Ettrick | CB480 | 2025-01-31 05:20 | 2025-01-31 07:04 | 0.15204 | 0.0014761 | 142 | 14626 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2024 | 20308 | Port Chalmers | PC3 | 2025-01-31 08:35 | 2025-01-31 14:42 | 0.057226 | 0.00015593 | 15 | 5505 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2025 | 20309 | Port Chalmers | PC3 | 2025-01-31 08:35 | 2025-01-31 14:47 | 0.10054 | 0.00027028 | 26 | 9672 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2026 | 20246 | Green Island | GI2 | 2025-01-31 15:23 | 2025-01-31 15:46 | 0.00095636 | 4.1581e-05 | 4 | 92 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2027 | 20253 | Ettrick | CB480 | 2025-02-01 00:25 | 2025-02-01 01:05 | 0.00083162 | 2.079e-05 | 2 | 80 | Unplanned | Wildlife | possum on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2028 | 20259 | Roxburgh | CB4639 | 2025-02-01 14:15 | 2025-02-01 16:05 | 0.0022869 | 2.079e-05 | 2 | 220 | Unplanned | Defective Equipment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2029 | 20261 | Green Island | GI4 | 2025-02-01 18:49 | 2025-02-01 21:36 | 0.006944 | 4.1581e-05 | 4 | 668 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2030 | 20260 | Green Island | GI4 | 2025-02-01 18:49 | 2025-02-01 19:50 | 0.045022 | 0.00073806 | 71 | 4331 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2031 | 20268 | Frankton GXP | CB7784 | 2025-02-02 07:06 | 2025-02-02 08:32 | 0.011622 | 0.00013514 | 13 | 1118 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2032 | 20269 | Frankton GXP | CB7784 | 2025-02-02 07:06 | 2025-02-02 09:10 | 0.71798 | 0.0057901 | 557 | 69068 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2033 | 20270 | Frankton GXP | CB7784 | 2025-02-02 09:16 | 2025-02-02 09:37 | 0.098755 | 0.0049377 | 475 | 9500 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2034 | 20271 | Green Island | GI2 | 2025-02-02 23:32 | 2025-02-03 00:12 | 0.087164 | 0.002235 | 215 | 8385 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2035 | 20279 | Green Island | GI2 | 2025-02-03 04:41 | 2025-02-03 04:49 | 0.0019127 | 0.00023909 | 23 | 184 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2036 | 20280 | Green Island | GI2 | 2025-02-03 04:41 | 2025-02-03 04:49 | 0.0029938 | 0.00037423 | 36 | 288 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2037 | 20281 | Green Island | GI2 | 2025-02-03 04:41 | 2025-02-03 04:50 | 0.0054263 | 0.00060292 | 58 | 522 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2038 | 20283 | Green Island | GI2 | 2025-02-03 04:41 | 2025-02-03 04:50 | 0.007391 | 0.00082122 | 79 | 711 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2039 | 20282 | Green Island | GI2 | 2025-02-03 04:41 | 2025-02-03 04:50 | 0.0078588 | 0.0008732 | 84 | 756 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2040 | 20285 | Green Island | GI2 | 2025-02-03 04:41 | 2025-02-03 04:50 | 0.0080459 | 0.00089399 | 86 | 774 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2041 | 20284 | Green Island | GI2 | 2025-02-03 04:41 | 2025-02-03 04:50 | 0.0083266 | 0.00092518 | 89 | 801 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2042 | 20278 | Green Island | GI2 | 2025-02-03 04:41 | 2025-02-03 04:49 | 0.0083993 | 0.0010499 | 101 | 808 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2043 | 20328 | East Taieri | ET5 | 2025-02-03 09:13 | 2025-02-07 10:39 | 0.06077 | 1.0395e-05 | 1 | 5846 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2044 | 20326 | East Taieri | ET5 | 2025-02-03 09:13 | 2025-02-03 14:09 | 0.046155 | 0.00015593 | 15 | 4440 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2045 | 20265 | St. Kilda | SK4 | 2025-02-03 16:00 | 2025-02-03 16:23 | 0.0040645 | 0.00017672 | 17 | 391 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2046 | 20302 | Outram | OT1 | 2025-02-04 08:28 | 2025-02-04 10:36 | 0.022443 | 0.00017672 | 17 | 2159 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2047 | 20303 | Outram | OT1 | 2025-02-04 08:28 | 2025-02-04 10:45 | 0.13007 | 0.00095636 | 92 | 12512 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2048 | 20291 | Andersons Bay | AB6 | 2025-02-04 09:05 | 2025-02-04 11:08 | 0.09206 | 0.00074846 | 72 | 8856 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2049 | 20296 | Wanaka | CB2758 | 2025-02-04 09:06 | 2025-02-04 09:11 | 0.02578 | 0.005156 | 496 | 2480 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2050 | 20322 | Wanaka | CB2758 | 2025-02-04 09:06 | 2025-02-04 09:11 | 5.1976e-05 | 1.0395e-05 | 1 | 5 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2051 | 20305 | Cromwell | CB821 | 2025-02-04 11:32 | 2025-02-04 12:11 | 0.00081083 | 2.079e-05 | 2 | 78 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2052 | 20292 | Roxburgh | CB4635 | 2025-02-04 12:02 | 2025-02-04 14:32 | 0.0015593 | 1.0395e-05 | 1 | 150 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2053 | 20307 | Port Chalmers | PC4 | 2025-02-04 12:55 | 2025-02-04 13:50 | 0.00057174 | 1.0395e-05 | 1 | 55 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2054 | 20298 | Wanaka | CB2758 | 2025-02-04 17:01 | 2025-02-04 17:14 | 0.067028 | 0.005156 | 496 | 6448 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2055 | 20323 | Wanaka | CB2758 | 2025-02-04 17:01 | 2025-02-04 17:14 | 0.00013514 | 1.0395e-05 | 1 | 13 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2056 | 20316 | Lindis Crossing | CB2084 | 2025-02-04 17:10 | 2025-02-04 20:26 | 0.0061124 | 3.1186e-05 | 3 | 588 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2057 | 20306 | Lindis Crossing | CB2084 | 2025-02-04 18:31 | 2025-02-04 19:23 | 0.021622 | 0.00041581 | 40 | 2080 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2058 | 20304 | Lindis Crossing | CB2084 | 2025-02-04 20:02 | 2025-02-04 20:20 | 0.0044907 | 0.00024949 | 24 | 432 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2059 | 20318 | Camp Hill | CB2006 | 2025-02-04 22:08 | 2025-02-04 23:32 | 0.10915 | 0.0012994 | 125 | 10500 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2060 | 20317 | Camp Hill | CB2006 | 2025-02-04 22:08 | 2025-02-04 23:30 | 0.89843 | 0.011092 | 1067 | 86427 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2061 | 20330 | Wanaka | CB2751 | 2025-02-05 07:00 | 2025-02-05 09:16 | 0.0014138 | 1.0395e-05 | 1 | 136 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2062 | 20315 | Wanaka | CB2755 | 2025-02-05 08:31 | 2025-02-05 17:00 | 0.08995 | 0.00017672 | 17 | 8653 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2063 | 20314 | Port Chalmers | PC3 | 2025-02-05 09:31 | 2025-02-05 11:50 | 0.067912 | 0.00048858 | 47 | 6533 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2064 | 20321 | Green Island | GI4 | 2025-02-06 15:54 | 2025-02-06 19:05 | 0.0099274 | 5.1976e-05 | 5 | 955 | Unplanned | Third-party Interference | machinery contact | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2065 | 20320 | Green Island | GI4 | 2025-02-06 15:54 | 2025-02-06 17:02 | 0.016965 | 0.00024949 | 24 | 1632 | Unplanned | Third-party Interference | machinery contact | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2066 | 20333 | Arrowtown | CB7652 | 2025-02-07 18:27 | 2025-02-07 19:58 | 0.20863 | 0.0023181 | 223 | 20070 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2067 | 20334 | Arrowtown | CB7652 | 2025-02-07 18:27 | 2025-02-07 19:59 | 0.31751 | 0.0034512 | 332 | 30544 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2068 | 20335 | Alexandra | CB169 | 2025-02-08 11:00 | 2025-02-08 11:42 | 0.023441 | 0.00057174 | 55 | 2255 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2069 | 20336 | Alexandra | CB169 | 2025-02-08 11:00 | 2025-02-08 11:50 | 0.06445 | 0.001289 | 124 | 6200 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2070 | 20337 | Alexandra | CB169 | 2025-02-08 11:00 | 2025-02-08 12:39 | 0.14202 | 0.0014345 | 138 | 13662 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2071 | 20340 | East Taieri | ET3 | 2025-02-10 08:11 | 2025-02-10 15:18 | 0.19087 | 0.00044699 | 43 | 18361 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2072 | 20404 | Corstorphine | CO11 | 2025-02-10 08:57 | 2025-02-10 10:36 | 0.043223 | 0.0004366 | 42 | 4158 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2073 | 20403 | Corstorphine | CO11 | 2025-02-10 08:57 | 2025-02-10 09:36 | 0.40379 | 0.010354 | 996 | 38844 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2074 | 20342 | Andersons Bay | AB9 | 2025-02-10 09:05 | 2025-02-10 12:03 | 0.024055 | 0.00013514 | 13 | 2314 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2075 | 20592 | South City | SC4 | 2025-02-10 15:00 | 2025-02-10 17:22 | 0.055698 | 0.00039502 | 38 | 5358 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2076 | 20371 | Frankton | CB7787 | 2025-02-11 09:03 | 2025-02-11 14:37 | 0.56246 | 0.001684 | 162 | 54108 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2077 | 20373 | Ettrick | CB480 | 2025-02-11 09:03 | 2025-02-11 15:36 | 0.12256 | 0.00031186 | 30 | 11790 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2078 | 20372 | Ettrick | CB480 | 2025-02-11 09:03 | 2025-02-11 15:35 | 0.57864 | 0.0014761 | 142 | 55664 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2079 | 20355 | Alexandra | CB162 | 2025-02-11 09:05 | 2025-02-11 14:22 | 0.6327 | 0.0019959 | 192 | 60864 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2080 | 20376 | Ettrick | CB480 | 2025-02-11 09:09 | 2025-02-11 15:58 | 0.02551 | 6.2371e-05 | 6 | 2454 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2081 | 20374 | Ettrick | CB480 | 2025-02-11 09:09 | 2025-02-11 15:36 | 0.28161 | 0.00072767 | 70 | 27090 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2082 | 20368 | Remarkables | CB710 | 2025-02-11 11:09 | 2025-02-11 12:38 | 0.017578 | 0.00019751 | 19 | 1691 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2083 | 20377 | Omakau | CB656 | 2025-02-11 14:45 | 2025-02-11 17:04 | 0.0014449 | 1.0395e-05 | 1 | 139 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2084 | 20378 | Frankton | CB7787 | 2025-02-11 15:11 | 2025-02-11 15:16 | 0.0014553 | 0.00029107 | 28 | 140 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2085 | 20369 | Ettrick | CB480 | 2025-02-11 18:02 | 2025-02-11 20:44 | 0.050521 | 0.00031186 | 30 | 4860 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2086 | 20357 | Nth East Valley | NV3 | 2025-02-12 08:01 | 2025-02-12 14:39 | 0.56267 | 0.0014138 | 136 | 54128 | Planned | Planned interruption | tree trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2087 | 20353 | Queensberry | CB2424 | 2025-02-12 08:28 | 2025-02-12 10:28 | 0.0099794 | 8.3162e-05 | 8 | 960 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2088 | 20370 | East Taieri | ET7 | 2025-02-12 11:06 | 2025-02-12 11:51 | 0.00046779 | 1.0395e-05 | 1 | 45 | Unplanned | Defective Equipment | emergency isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2089 | 20382 | Mosgiel | MG6 | 2025-02-13 07:00 | 2025-02-13 07:12 | 0.0032433 | 0.00027028 | 26 | 312 | Planned | Planned interruption | tree trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2090 | 20384 | Mosgiel | MG6 | 2025-02-13 08:00 | 2025-02-13 16:16 | 0.14952 | 0.00030146 | 29 | 14384 | Planned | Planned interruption | tree trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2091 | 20383 | Mosgiel | MG6 | 2025-02-13 08:00 | 2025-02-13 08:57 | 0.040884 | 0.00071727 | 69 | 3933 | Planned | Planned interruption | tree trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2092 | 20348 | Andersons Bay | AB9 | 2025-02-13 08:30 | 2025-02-13 15:56 | 0.19429 | 0.0004366 | 42 | 18690 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2093 | 20358 | Roxburgh | CB4635 | 2025-02-13 09:03 | 2025-02-13 15:18 | 0.0038982 | 1.0395e-05 | 1 | 375 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2094 | 20387 | Mosgiel | MG6 | 2025-02-13 17:01 | 2025-02-13 17:05 | 0.0010811 | 0.00027028 | 26 | 104 | Planned | Planned interruption | tree trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2095 | 20389 | Roxburgh | CB4639 | 2025-02-14 08:35 | 2025-02-14 14:29 | 0.033119 | 9.3557e-05 | 9 | 3186 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2096 | 20398 | Omakau | CB656 | 2025-02-14 15:02 | 2025-02-14 15:48 | 0.0019127 | 4.1581e-05 | 4 | 184 | Unplanned | Defective Equipment | burning link | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2097 | 20397 | Alexandra | CB167 | 2025-02-14 17:16 | 2025-02-14 18:17 | 0.0082434 | 0.00013514 | 13 | 793 | Unplanned | Defective Equipment | faulty transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2098 | 20636 | Camp Hill | CB2008 | 2025-02-16 20:46 | 2025-02-16 21:44 | 0.02472 | 0.0004262 | 41 | 2378 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2099 | 20405 | Roxburgh | CB4635 | 2025-02-16 23:44 | 2025-02-17 01:48 | 0.29647 | 0.0023909 | 230 | 28520 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2100 | 20412 | Andersons Bay | AB7 | 2025-02-17 07:25 | 2025-02-17 15:21 | 0.019793 | 4.1581e-05 | 4 | 1904 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2101 | 20402 | Port Chalmers | PC4 | 2025-02-17 09:06 | 2025-02-17 14:42 | 0.059378 | 0.00017672 | 17 | 5712 | Planned | Planned interruption | tree trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2102 | 20506 | Port Chalmers | PC4 | 2025-02-17 09:06 | 2025-02-17 14:42 | 0.010478 | 3.1186e-05 | 3 | 1008 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2103 | 20424 | Roxburgh | CB480 | 2025-02-17 09:14 | 2025-02-17 09:53 | 0.00081083 | 2.079e-05 | 2 | 78 | Unplanned | Defective Equipment | incorrect protection settings | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2104 | 20423 | Roxburgh | CB480 | 2025-02-17 09:14 | 2025-02-17 09:48 | 0.15127 | 0.0044492 | 428 | 14552 | Unplanned | Defective Equipment | incorrect protection settings | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2105 | 20409 | Camp Hill | CB2006 | 2025-02-17 18:50 | 2025-02-17 19:59 | 0.089659 | 0.0012994 | 125 | 8625 | Unplanned | Defective Equipment | broken crossarm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2106 | 20425 | Alexandra | CB167 | 2025-02-18 00:16 | 2025-02-18 02:00 | 1.853 | 0.017817 | 1714 | 178256 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2107 | 20417 | Roxburgh | CB4639 | 2025-02-18 08:53 | 2025-02-18 17:38 | 0.02183 | 4.1581e-05 | 4 | 2100 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2108 | 20416 | Roxburgh | CB4639 | 2025-02-18 08:53 | 2025-02-18 16:34 | 0.16773 | 0.00036383 | 35 | 16135 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2109 | 20421 | Andersons Bay | AB4 | 2025-02-18 09:03 | 2025-02-18 13:55 | 0.036425 | 0.00012474 | 12 | 3504 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2110 | 20418 | Alexandra | CB162 | 2025-02-18 09:34 | 2025-02-18 16:13 | 0.79636 | 0.0019959 | 192 | 76608 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2111 | 20427 | Alexandra | CB162 | 2025-02-18 09:34 | 2025-02-18 16:13 | 0.012443 | 3.1186e-05 | 3 | 1197 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2112 | 20420 | Queensberry | CB2423 | 2025-02-18 10:13 | 2025-02-18 14:20 | 0.0051352 | 2.079e-05 | 2 | 494 | Planned | Planned interruption | network extension | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2113 | 20419 | Queensberry | CB2423 | 2025-02-18 10:14 | 2025-02-18 14:11 | 0.0049273 | 2.079e-05 | 2 | 474 | Planned | Planned interruption | network extension | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2114 | 20428 | Arrowtown | CB7652 | 2025-02-18 13:50 | 2025-02-18 14:17 | 0.093183 | 0.0034512 | 332 | 8964 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2115 | 20429 | East Taieri | ET3 | 2025-02-18 16:49 | 2025-02-18 17:49 | 0.0062371 | 0.00010395 | 10 | 600 | Unplanned | Defective Equipment | burning crossarm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2116 | 20443 | Ettrick | CB480 | 2025-02-18 17:03 | 2025-02-18 17:30 | 0.11568 | 0.0044492 | 428 | 11128 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2117 | 20444 | Roxburgh | CB4631 | 2025-02-18 17:03 | 2025-02-18 17:24 | 0.00083162 | 4.1581e-05 | 4 | 80 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2118 | 20445 | Roxburgh | CB4631 | 2025-02-18 17:03 | 2025-02-18 17:24 | 0.18088 | 0.0090438 | 870 | 17400 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2119 | 20446 | Roxburgh | HSB33 | 2025-02-18 17:03 | 2025-02-18 17:44 | 0.00085241 | 2.079e-05 | 2 | 82 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2120 | 20440 | Green Island | GI10 | 2025-02-19 07:16 | 2025-02-19 12:41 | 0.067569 | 0.0002079 | 20 | 6500 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2121 | 20439 | Green Island | GI10 | 2025-02-19 07:16 | 2025-02-19 10:47 | 0.083349 | 0.00039502 | 38 | 8018 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2122 | 20434 | Clyde-Earnscleugh | CB195 | 2025-02-19 08:09 | 2025-02-19 17:11 | 0.022537 | 4.1581e-05 | 4 | 2168 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2123 | 20432 | Alexandra | CB167 | 2025-02-19 09:03 | 2025-02-19 15:05 | 0.015052 | 4.1581e-05 | 4 | 1448 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2124 | 20431 | Alexandra | CB167 | 2025-02-19 09:03 | 2025-02-19 14:08 | 0.076093 | 0.00024949 | 24 | 7320 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2125 | 20433 | Camp Hill | CB2008 | 2025-02-19 09:04 | 2025-02-19 13:18 | 0.023763 | 9.3557e-05 | 9 | 2286 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2126 | 20436 | Port Chalmers | PC4 | 2025-02-19 09:05 | 2025-02-19 11:02 | 0.020676 | 0.00017672 | 17 | 1989 | Planned | Planned interruption | tree trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2127 | 20507 | Port Chalmers | PC4 | 2025-02-19 09:05 | 2025-02-19 11:02 | 0.0036487 | 3.1186e-05 | 3 | 351 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2128 | 20441 | Green Island | GI10 | 2025-02-19 12:37 | 2025-02-19 12:41 | 0.0015801 | 0.00039502 | 38 | 152 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2129 | 20454 | Alexandra | CB162 | 2025-02-20 08:05 | 2025-02-20 12:08 | 0.037891 | 0.00015593 | 15 | 3645 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2130 | 20459 | Ettrick | CB480 | 2025-02-20 08:30 | 2025-02-20 16:32 | 0.065136 | 0.00013514 | 13 | 6266 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2131 | 20462 | Ettrick | CB480 | 2025-02-20 08:30 | 2025-02-20 16:45 | 0.1235 | 0.00024949 | 24 | 11880 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2132 | 20458 | Ettrick | CB480 | 2025-02-20 08:30 | 2025-02-20 08:50 | 0.015011 | 0.00079004 | 76 | 1444 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2133 | 20463 | Ettrick | CB480 | 2025-02-20 08:30 | 2025-02-20 16:45 | 0.70495 | 0.0014241 | 137 | 67815 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2134 | 20453 | Andersons Bay | AB7 | 2025-02-20 09:07 | 2025-02-20 10:34 | 0.032558 | 0.00037423 | 36 | 3132 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2135 | 20452 | Carisbrook | CK13 | 2025-02-20 09:10 | 2025-02-20 16:58 | 0.73947 | 0.0015801 | 152 | 71136 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2136 | 20460 | Ettrick | CB480 | 2025-02-20 16:01 | 2025-02-20 16:32 | 0.024491 | 0.00079004 | 76 | 2356 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2137 | 20468 | Andersons Bay | AB7 | 2025-02-21 08:35 | 2025-02-21 12:52 | 0.072132 | 0.00028067 | 27 | 6939 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2138 | 20482 | Omakau | CB656 | 2025-02-21 18:37 | 2025-02-21 20:48 | 0.0013618 | 1.0395e-05 | 1 | 131 | Unplanned | Defective Equipment | burning crossarm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2139 | 20466 | East Taieri | ET4 | 2025-02-22 08:25 | 2025-02-22 17:12 | 0.1531 | 0.00029107 | 28 | 14728 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2140 | 20469 | Cromwell | CB823 | 2025-02-22 09:04 | 2025-02-22 12:26 | 0.10289 | 0.00050937 | 49 | 9898 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2141 | 20476 | Frankton GXP | CB2842 | 2025-02-22 09:47 | 2025-02-22 10:02 | 0.085605 | 0.005707 | 549 | 8235 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2142 | 20477 | Frankton GXP | CB7632 | 2025-02-22 09:47 | 2025-02-22 10:03 | 0.099794 | 0.0066529 | 640 | 9600 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2143 | 20481 | Port Chalmers | PC7 | 2025-02-22 09:57 | 2025-02-22 11:39 | 0.0084825 | 8.3162e-05 | 8 | 816 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2144 | 20480 | Port Chalmers | PC7 | 2025-02-22 09:57 | 2025-02-22 10:17 | 0.15208 | 0.0080043 | 770 | 14630 | Unplanned | Defective Equipment | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2145 | 20487 | Kaikorai Valley | KV6 | 2025-02-24 09:01 | 2025-02-24 13:25 | 0.13173 | 0.00049897 | 48 | 12672 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2146 | 20488 | Ettrick | CB480 | 2025-02-24 13:52 | 2025-02-24 15:34 | 0.031498 | 0.00031186 | 30 | 3030 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2147 | 20489 | Ettrick | CB480 | 2025-02-25 07:51 | 2025-02-25 10:14 | 0.0014761 | 1.0395e-05 | 1 | 142 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2148 | 20486 | Willowbank | WB3 | 2025-02-25 08:09 | 2025-02-25 15:59 | 0.17589 | 0.00037423 | 36 | 16920 | Planned | Planned interruption | tree trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2149 | 20494 | East Taieri | ET8 | 2025-02-25 08:31 | 2025-02-25 16:56 | 0.0052496 | 1.0395e-05 | 1 | 505 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2150 | 20493 | East Taieri | ET8 | 2025-02-25 08:31 | 2025-02-25 16:54 | 0.010458 | 2.079e-05 | 2 | 1006 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2151 | 20495 | East Taieri | ET8 | 2025-02-25 08:31 | 2025-02-25 17:03 | 0.010645 | 2.079e-05 | 2 | 1024 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2152 | 20496 | East Taieri | ET8 | 2025-02-25 08:31 | 2025-02-25 17:19 | 0.021955 | 4.1581e-05 | 4 | 2112 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2153 | 20492 | East Taieri | ET8 | 2025-02-25 08:31 | 2025-02-25 16:43 | 0.63419 | 0.001289 | 124 | 61008 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2154 | 20485 | Roxburgh | CB4639 | 2025-02-25 08:46 | 2025-02-25 13:58 | 0.012973 | 4.1581e-05 | 4 | 1248 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2155 | 20484 | Wanaka | CB2758 | 2025-02-25 09:31 | 2025-02-25 13:13 | 0.048463 | 0.0002183 | 21 | 4662 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2156 | 20537 | Ettrick | CB480 | 2025-02-25 10:04 | 2025-02-25 10:05 | 7.2767e-05 | 7.2767e-05 | 7 | 7 | Unplanned | Defective Equipment | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2157 | 20497 | Willowbank | WB3 | 2025-02-26 08:20 | 2025-02-26 13:55 | 0.010447 | 3.1186e-05 | 3 | 1005 | Planned | Planned interruption | tree trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2158 | 20503 | Dalefield | CB7830 | 2025-02-26 09:05 | 2025-02-26 12:58 | 0.0048442 | 2.079e-05 | 2 | 466 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2159 | 20504 | Dalefield | CB7830 | 2025-02-26 09:08 | 2025-02-26 12:58 | 0.011955 | 5.1976e-05 | 5 | 1150 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2160 | 20505 | Dalefield | CB7830 | 2025-02-26 09:12 | 2025-02-26 12:58 | 0.0023493 | 1.0395e-05 | 1 | 226 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2161 | 20498 | Arrowtown | CB7662 | 2025-02-26 09:45 | 2025-02-26 11:30 | 0.0010915 | 1.0395e-05 | 1 | 105 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2162 | 20502 | Omakau | CB656 | 2025-02-26 10:16 | 2025-02-26 13:13 | 0.00184 | 1.0395e-05 | 1 | 177 | Unplanned | Defective Equipment | burning crossarm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2163 | 20501 | Queensberry | CB2423 | 2025-02-26 10:36 | 2025-02-26 13:39 | 0.0019023 | 1.0395e-05 | 1 | 183 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2164 | 20499 | Dalefield | CB7830 | 2025-02-26 16:50 | 2025-02-26 18:20 | 0.0046779 | 5.1976e-05 | 5 | 450 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2165 | 20500 | St. Kilda | SK1 | 2025-02-26 17:46 | 2025-02-26 18:11 | 0.0038982 | 0.00015593 | 15 | 375 | Unplanned | Defective Equipment | burnt fuse jaw | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2166 | 20518 | Dalefield | CB7830 | 2025-02-27 08:06 | 2025-02-27 16:21 | 0.015437 | 3.1186e-05 | 3 | 1485 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2167 | 20517 | Dalefield | CB7830 | 2025-02-27 08:06 | 2025-02-27 16:04 | 0.17888 | 0.00037423 | 36 | 17208 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2168 | 20532 | Roxburgh | CB4635 | 2025-02-27 08:32 | 2025-02-27 16:47 | 0.061748 | 0.00012474 | 12 | 5940 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2169 | 20531 | Roxburgh | CB4635 | 2025-02-27 08:32 | 2025-02-27 16:16 | 0.16882 | 0.00036383 | 35 | 16240 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2170 | 20514 | Dalefield | CB7830 | 2025-02-27 09:01 | 2025-02-27 15:31 | 0.0040541 | 1.0395e-05 | 1 | 390 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2171 | 20509 | Dalefield | CB7830 | 2025-02-27 09:01 | 2025-02-27 09:08 | 0.00058213 | 8.3162e-05 | 8 | 56 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2172 | 20510 | Dalefield | CB7830 | 2025-02-27 09:01 | 2025-02-27 15:16 | 0.093557 | 0.00024949 | 24 | 9000 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2173 | 20546 | Kaikorai Valley | KV9 | 2025-02-27 09:01 | 2025-02-27 17:25 | 0.057631 | 0.00011435 | 11 | 5544 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2174 | 20547 | Kaikorai Valley | KV9 | 2025-02-27 09:01 | 2025-02-27 18:35 | 0.35204 | 0.00061332 | 59 | 33866 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2175 | 20545 | Kaikorai Valley | KV9 | 2025-02-27 09:01 | 2025-02-27 17:16 | 0.46311 | 0.00093557 | 90 | 44550 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2176 | 20508 | Alexandra | CB167 | 2025-02-27 09:06 | 2025-02-27 14:58 | 0.10246 | 0.00029107 | 28 | 9856 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2177 | 20512 | Dalefield | CB7830 | 2025-02-27 15:08 | 2025-02-27 15:16 | 0.00066529 | 8.3162e-05 | 8 | 64 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2178 | 20520 | South City | SC4 | 2025-02-27 17:59 | 2025-02-27 23:15 | 0.078837 | 0.00024949 | 24 | 7584 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2179 | 20524 | Queenstown | CB5212 | 2025-02-28 03:41 | 2025-02-28 09:26 | 0.0035864 | 1.0395e-05 | 1 | 345 | Unplanned | Defective Equipment | faulty transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2180 | 20525 | Queenstown | CB5212 | 2025-02-28 03:41 | 2025-02-28 10:00 | 0.0039398 | 1.0395e-05 | 1 | 379 | Unplanned | Defective Equipment | faulty transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2181 | 20534 | Lindis Crossing | CB2084 | 2025-02-28 08:41 | 2025-02-28 13:48 | 0.0031913 | 1.0395e-05 | 1 | 307 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2182 | 20533 | Lindis Crossing | CB2084 | 2025-02-28 08:41 | 2025-02-28 13:36 | 0.036799 | 0.00012474 | 12 | 3540 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2183 | 20522 | Cardrona | CB2882 | 2025-02-28 09:04 | 2025-02-28 13:31 | 0.0055511 | 2.079e-05 | 2 | 534 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2184 | 20521 | Cardrona | CB2881 | 2025-02-28 09:22 | 2025-02-28 13:45 | 0.010936 | 4.1581e-05 | 4 | 1052 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2185 | 20530 | Clyde-Earnscleugh | CB192 | 2025-02-28 10:53 | 2025-02-28 15:49 | 0.003077 | 1.0395e-05 | 1 | 296 | Unplanned | Defective Equipment | faulty transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2186 | 20526 | Queenstown | CB5212 | 2025-02-28 13:38 | 2025-02-28 14:15 | 0.041539 | 0.0011227 | 108 | 3996 | Unplanned | Defective Equipment | faulty transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2187 | 20535 | Omakau | CB656 | 2025-03-01 13:06 | 2025-03-01 13:34 | 0.00029107 | 1.0395e-05 | 1 | 28 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2188 | 20528 | Roxburgh | HSB33 | 2025-03-02 01:26 | 2025-03-02 01:52 | 0.00054055 | 2.079e-05 | 2 | 52 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2189 | 20541 | Roxburgh | HSB33 | 2025-03-02 12:57 | 2025-03-02 16:08 | 0.0019855 | 1.0395e-05 | 1 | 191 | Unplanned | Defective Equipment | faulty lightning arrestor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2190 | 20542 | Roxburgh | HSB33 | 2025-03-02 13:56 | 2025-03-02 16:08 | 0.0013722 | 1.0395e-05 | 1 | 132 | Unplanned | Defective Equipment | faulty lightning arrestor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2191 | 20538 | South City | SC9 | 2025-03-03 08:04 | 2025-03-03 13:57 | 0.18715 | 0.00053016 | 51 | 18003 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2192 | 20548 | Arrowtown | CB7692 | 2025-03-04 08:12 | 2025-03-04 08:19 | 7.2767e-05 | 1.0395e-05 | 1 | 7 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2193 | 20553 | Roxburgh | CB4639 | 2025-03-04 08:42 | 2025-03-04 14:41 | 0.033587 | 9.3557e-05 | 9 | 3231 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2194 | 20549 | Arrowtown | CB7692 | 2025-03-04 09:01 | 2025-03-04 15:02 | 0.0075054 | 2.079e-05 | 2 | 722 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2195 | 20555 | Outram | OT2 | 2025-03-04 10:16 | 2025-03-04 10:22 | 0.016009 | 0.0032017 | 308 | 1540 | Unplanned | Human Error | switching error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2196 | 20611 | Cromwell | CB838 | 2025-03-04 10:21 | 2025-03-04 12:27 | 0.053276 | 0.0004262 | 41 | 5125 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2197 | 20610 | Cromwell | CB838 | 2025-03-04 10:21 | 2025-03-04 12:11 | 0.065719 | 0.00060292 | 58 | 6322 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2198 | 20609 | Cromwell | CB838 | 2025-03-04 10:21 | 2025-03-04 11:21 | 0.27722 | 0.0046986 | 452 | 26668 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2199 | 20612 | Cromwell | CB838 | 2025-03-04 10:21 | 2025-03-04 12:37 | 1.1451 | 0.0084825 | 816 | 110160 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2200 | 20556 | Outram | OT2 | 2025-03-04 10:22 | 2025-03-04 10:24 | 0.0064035 | 0.0032017 | 308 | 616 | Unplanned | Human Error | switching error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2201 | 20613 | Cromwell | CB838 | 2025-03-04 12:22 | 2025-03-04 12:27 | 0.021206 | 0.0053016 | 510 | 2040 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2202 | 20558 | Ettrick | CB480 | 2025-03-04 12:36 | 2025-03-04 13:43 | 0.03552 | 0.00053016 | 51 | 3417 | Unplanned | Defective Equipment | arm brace off | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2203 | 20550 | Arrowtown | CB7692 | 2025-03-04 16:07 | 2025-03-04 16:09 | 2.079e-05 | 1.0395e-05 | 1 | 2 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2204 | 20566 | South City | SC2 | 2025-03-05 08:02 | 2025-03-05 16:17 | 0.0051456 | 1.0395e-05 | 1 | 495 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2205 | 20564 | Corstorphine | CO7 | 2025-03-05 08:21 | 2025-03-05 15:40 | 0.44266 | 0.0010083 | 97 | 42583 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2206 | 20563 | Corstorphine | CO7 | 2025-03-05 08:26 | 2025-03-05 15:18 | 0.23556 | 0.00057174 | 55 | 22660 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2207 | 20567 | Frankton | CB7784 | 2025-03-05 08:33 | 2025-03-05 16:27 | 4.6071 | 0.0097195 | 935 | 443190 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2208 | 20591 | Frankton | CB7784 | 2025-03-05 08:33 | 2025-03-05 16:27 | 0.083765 | 0.00017672 | 17 | 8058 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2209 | 20578 | Roxburgh | CB4639 | 2025-03-05 08:43 | 2025-03-05 15:14 | 0.0040645 | 1.0395e-05 | 1 | 391 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2210 | 20577 | Roxburgh | CB4639 | 2025-03-05 08:43 | 2025-03-05 15:14 | 0.0081291 | 2.079e-05 | 2 | 782 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2211 | 20576 | Roxburgh | CB4639 | 2025-03-05 08:43 | 2025-03-05 14:46 | 0.13584 | 0.00037423 | 36 | 13068 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2212 | 20560 | Arrowtown | CB7692 | 2025-03-05 08:53 | 2025-03-05 08:57 | 0.00012474 | 3.1186e-05 | 3 | 12 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2213 | 20561 | Arrowtown | CB7692 | 2025-03-05 09:07 | 2025-03-05 14:32 | 0.14527 | 0.00044699 | 43 | 13975 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2214 | 20565 | Halfway Bush | HB8 | 2025-03-05 09:08 | 2025-03-05 15:00 | 0.25248 | 0.00071727 | 69 | 24288 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2215 | 20573 | Halfway Bush | HB1 | 2025-03-05 14:54 | 2025-03-05 18:00 | 0.11214 | 0.00060292 | 58 | 10788 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2216 | 20572 | Halfway Bush | HB1 | 2025-03-05 14:54 | 2025-03-05 17:59 | 0.175 | 0.00094597 | 91 | 16835 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2217 | 20570 | Halfway Bush | HB1 | 2025-03-05 14:54 | 2025-03-05 15:31 | 0.070771 | 0.0019127 | 184 | 6808 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2218 | 20571 | Halfway Bush | HB1 | 2025-03-05 14:54 | 2025-03-05 15:47 | 0.17796 | 0.0033577 | 323 | 17119 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2219 | 20562 | Arrowtown | CB7692 | 2025-03-05 15:20 | 2025-03-05 15:24 | 0.00012474 | 3.1186e-05 | 3 | 12 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2220 | 20584 | Andersons Bay | AB9 | 2025-03-05 19:20 | 2025-03-05 21:03 | 0.011778 | 0.00011435 | 11 | 1133 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2221 | 20585 | Andersons Bay | AB9 | 2025-03-05 21:22 | 2025-03-05 22:20 | 0.0066322 | 0.00011435 | 11 | 638 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2222 | 20581 | Arrowtown | CB7652 | 2025-03-05 22:04 | 2025-03-05 22:50 | 0.048774 | 0.0010603 | 102 | 4692 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2223 | 20608 | Arrowtown | CB7652 | 2025-03-05 22:04 | 2025-03-05 22:50 | 0.00095636 | 2.079e-05 | 2 | 92 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2224 | 20603 | Port Chalmers | PC4 | 2025-03-06 07:55 | 2025-03-06 08:09 | 0.0048026 | 0.00034304 | 33 | 462 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2225 | 20605 | Port Chalmers | PC4 | 2025-03-06 08:00 | 2025-03-06 16:55 | 0.033369 | 6.2371e-05 | 6 | 3210 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2226 | 20607 | Port Chalmers | PC4 | 2025-03-06 08:00 | 2025-03-06 17:24 | 0.23452 | 0.00041581 | 40 | 22560 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2227 | 20604 | Port Chalmers | PC4 | 2025-03-06 08:00 | 2025-03-06 16:47 | 0.53687 | 0.0010187 | 98 | 51646 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2228 | 20579 | Arrowtown | CB7692 | 2025-03-06 09:00 | 2025-03-06 14:32 | 0.058671 | 0.00017672 | 17 | 5644 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2229 | 20583 | Omakau | CB656 | 2025-03-06 09:20 | 2025-03-06 12:54 | 0.066737 | 0.00031186 | 30 | 6420 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2230 | 20587 | St. Kilda | SK4 | 2025-03-06 16:11 | 2025-03-06 16:43 | 0.045905 | 0.0014345 | 138 | 4416 | Unplanned | Human Error | incorrect installation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2231 | 20588 | St. Kilda | SK4 | 2025-03-06 16:57 | 2025-03-06 17:36 | 0.055947 | 0.0014345 | 138 | 5382 | Unplanned | Human Error | incorrect installation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2232 | 20606 | Port Chalmers | PC4 | 2025-03-06 17:08 | 2025-03-06 17:09 | 0.00034304 | 0.00034304 | 33 | 33 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2233 | 20589 | Roxburgh | CB4633 | 2025-03-06 17:10 | 2025-03-06 20:00 | 0.0017672 | 1.0395e-05 | 1 | 170 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2234 | 20593 | South City | SC4 | 2025-03-06 23:00 | 2025-03-06 23:09 | 0.0035552 | 0.00039502 | 38 | 342 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2235 | 21224 | Lindis Crossing | CB2084 | 2025-03-07 06:11 | 2025-03-07 08:36 | 0.036175 | 0.00024949 | 24 | 3480 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2236 | 21223 | Lindis Crossing | CB2084 | 2025-03-07 06:11 | 2025-03-07 08:08 | 0.04865 | 0.00041581 | 40 | 4680 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2237 | 20602 | Outram | OT3 | 2025-03-07 14:16 | 2025-03-07 15:32 | 0.0063203 | 8.3162e-05 | 8 | 608 | Unplanned | Defective Equipment | faulty transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2238 | 20601 | Wanaka | CB2752 | 2025-03-07 15:08 | 2025-03-07 16:05 | 0.0011851 | 2.079e-05 | 2 | 114 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2239 | 20600 | Wanaka | CB2752 | 2025-03-07 15:08 | 2025-03-07 15:55 | 0.0039086 | 8.3162e-05 | 8 | 376 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2240 | 20595 | Ettrick | CB480 | 2025-03-07 16:21 | 2025-03-07 18:00 | 0.0010291 | 1.0395e-05 | 1 | 99 | Unplanned | Vegetation | branch / tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2241 | 20616 | Ettrick | CB480 | 2025-03-10 14:36 | 2025-03-10 17:11 | 0.048338 | 0.00031186 | 30 | 4650 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2242 | 20632 | St. Kilda | SK12 | 2025-03-11 07:05 | 2025-03-11 07:15 | 0.00010395 | 1.0395e-05 | 1 | 10 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2243 | 20626 | Fernhill | CB5307 | 2025-03-11 08:19 | 2025-03-11 08:24 | 5.1976e-05 | 1.0395e-05 | 1 | 5 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2244 | 20634 | Wanaka | CB2751 | 2025-03-11 08:33 | 2025-03-11 16:20 | 0.36409 | 0.00077964 | 75 | 35025 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2245 | 20624 | Port Chalmers | PC7 | 2025-03-11 08:36 | 2025-03-11 14:52 | 0.14071 | 0.00037423 | 36 | 13536 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2246 | 20635 | Commonage | CB5730 | 2025-03-11 09:01 | 2025-03-11 14:42 | 0.51045 | 0.0014969 | 144 | 49104 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2247 | 20671 | Alexandra | CB167 | 2025-03-11 09:01 | 2025-03-11 18:08 | 0.32352 | 0.00059253 | 57 | 31122 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2248 | 20704 | Alexandra | CB167 | 2025-03-11 09:01 | 2025-03-11 18:07 | 0.0056758 | 1.0395e-05 | 1 | 546 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2249 | 20623 | Outram | OT1 | 2025-03-11 09:07 | 2025-03-11 13:06 | 0.017391 | 7.2767e-05 | 7 | 1673 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2250 | 20633 | St. Kilda | SK12 | 2025-03-11 18:37 | 2025-03-11 19:16 | 0.00040541 | 1.0395e-05 | 1 | 39 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2251 | 20638 | Berwick | BK1 | 2025-03-11 18:45 | 2025-03-11 21:30 | 0.0017152 | 1.0395e-05 | 1 | 165 | Unplanned | Defective Equipment | faulty transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2252 | 20639 | Berwick | BK1 | 2025-03-11 19:16 | 2025-03-12 00:22 | 0.015905 | 5.1976e-05 | 5 | 1530 | Unplanned | Defective Equipment | faulty transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2253 | 20657 | Berwick | BK1 | 2025-03-11 19:36 | 2025-03-11 21:30 | 0.0011851 | 1.0395e-05 | 1 | 114 | Unplanned | Defective Equipment | faulty transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2254 | 20622 | Frankton | CB7790 | 2025-03-12 09:01 | 2025-03-12 13:17 | 0.20757 | 0.00081083 | 78 | 19968 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2255 | 20640 | Camp Hill | CB2002 | 2025-03-12 09:17 | 2025-03-12 10:04 | 0.0086072 | 0.00018711 | 18 | 828 | Unplanned | Human Error | technician error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2256 | 20641 | Camp Hill | CB2004 | 2025-03-12 09:17 | 2025-03-12 10:05 | 0.058141 | 0.001237 | 119 | 5593 | Unplanned | Human Error | technician error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2257 | 20643 | Camp Hill | CB2008 | 2025-03-12 09:17 | 2025-03-12 10:06 | 0.34229 | 0.0071311 | 686 | 32928 | Unplanned | Human Error | technician error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2258 | 20642 | Camp Hill | CB2006 | 2025-03-12 09:17 | 2025-03-12 10:05 | 0.58727 | 0.012495 | 1202 | 56494 | Unplanned | Human Error | technician error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2259 | 20644 | Camp Hill | CB2008 | 2025-03-12 10:11 | 2025-03-12 13:58 | 0.0047194 | 2.079e-05 | 2 | 454 | Unplanned | Defective Equipment | broken lead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2260 | 20653 | Lindis Crossing | CB2084 | 2025-03-13 08:32 | 2025-03-13 16:03 | 0.30005 | 0.00066529 | 64 | 28864 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2261 | 20652 | Lindis Crossing | CB2084 | 2025-03-13 08:37 | 2025-03-13 15:58 | 0.16503 | 0.00037423 | 36 | 15876 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2262 | 20655 | East Taieri | ET2 | 2025-03-13 09:06 | 2025-03-13 13:47 | 0.0029211 | 1.0395e-05 | 1 | 281 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2263 | 20654 | Lindis Crossing | CB2084 | 2025-03-13 17:06 | 2025-03-13 17:11 | 0.00072767 | 0.00014553 | 14 | 70 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2264 | 20659 | Frankton | CB7789 | 2025-03-13 23:06 | 2025-03-13 23:20 | 0.00029107 | 2.079e-05 | 2 | 28 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2265 | 20658 | Frankton | CB7789 | 2025-03-13 23:30 | 2025-03-13 23:40 | 0.0002079 | 2.079e-05 | 2 | 20 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2266 | 20673 | Port Chalmers | PC4 | 2025-03-14 08:04 | 2025-03-14 15:25 | 0.21088 | 0.00047818 | 46 | 20286 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2267 | 20665 | Wanaka | CB2756 | 2025-03-14 14:36 | 2025-03-14 14:47 | 0.0020583 | 0.00018711 | 18 | 198 | Unplanned | Wildlife | animal in equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2268 | 20662 | Ettrick | CB480 | 2025-03-15 01:57 | 2025-03-15 04:41 | 0.26766 | 0.0016321 | 157 | 25748 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2269 | 21227 | Andersons Bay | AB4 | 2025-03-16 20:56 | 2025-03-17 00:05 | 0.0039294 | 2.079e-05 | 2 | 378 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2270 | 21228 | Andersons Bay | AB4 | 2025-03-17 00:05 | 2025-03-17 03:29 | 0.11239 | 0.00055095 | 53 | 10812 | Unplanned | Third-party Interference | vehicle v equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2271 | 20677 | Omakau | CB656 | 2025-03-17 04:01 | 2025-03-17 06:42 | 0.023285 | 0.00014553 | 14 | 2240 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2272 | 20676 | Omakau | CB656 | 2025-03-17 04:01 | 2025-03-17 04:44 | 0.011175 | 0.00025988 | 25 | 1075 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2273 | 20670 | Outram | OT1 | 2025-03-17 08:51 | 2025-03-17 14:46 | 0.033213 | 9.3557e-05 | 9 | 3195 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2274 | 20693 | Queenstown | CB5202 | 2025-03-17 18:01 | 2025-03-18 02:33 | 0.037256 | 7.2767e-05 | 7 | 3584 | Unplanned | Defective Equipment | broken lead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2275 | 20698 | Queenstown | CB5202 | 2025-03-17 18:24 | 2025-03-18 01:21 | 0.030271 | 7.2767e-05 | 7 | 2912 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2276 | 20697 | Queenstown | CB5202 | 2025-03-17 18:24 | 2025-03-17 21:30 | 0.025001 | 0.00013514 | 13 | 2405 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2277 | 20696 | Queenstown | CB5202 | 2025-03-17 18:24 | 2025-03-17 21:22 | 0.055199 | 0.00031186 | 30 | 5310 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2278 | 20699 | Queenstown | CB5202 | 2025-03-17 18:24 | 2025-03-18 01:33 | 0.15127 | 0.00035344 | 34 | 14552 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2279 | 20695 | Queenstown | CB5202 | 2025-03-17 18:24 | 2025-03-17 20:57 | 0.11535 | 0.00075885 | 73 | 11096 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2280 | 20694 | Queenstown | CB5202 | 2025-03-17 18:24 | 2025-03-17 20:50 | 0.43109 | 0.002973 | 286 | 41470 | Unplanned | Vegetation | line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2281 | 20686 | Alexandra | CB167 | 2025-03-18 07:34 | 2025-03-18 07:39 | 5.1976e-05 | 1.0395e-05 | 1 | 5 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2282 | 20683 | Arrowtown | CB7662 | 2025-03-18 08:32 | 2025-03-18 15:15 | 0.29325 | 0.00072767 | 70 | 28210 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2283 | 20700 | Arrowtown | CB7662 | 2025-03-18 08:32 | 2025-03-18 15:15 | 0.0041893 | 1.0395e-05 | 1 | 403 | Unplanned | Human Error | non-notified planned interruption | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2284 | 20690 | Alexandra | CB167 | 2025-03-18 08:33 | 2025-03-18 16:21 | 0.28217 | 0.00060292 | 58 | 27144 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2285 | 20682 | Arrowtown | CB7652 | 2025-03-18 09:07 | 2025-03-18 09:40 | 0.0075469 | 0.00022869 | 22 | 726 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2286 | 20692 | Frankton | CB7790 | 2025-03-18 09:24 | 2025-03-18 14:41 | 0.046134 | 0.00014553 | 14 | 4438 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2287 | 20687 | Alexandra | CB167 | 2025-03-18 18:23 | 2025-03-18 18:24 | 1.0395e-05 | 1.0395e-05 | 1 | 1 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2288 | 20711 | Cromwell GXP | CB2084 | 2025-03-18 22:29 | 2025-03-18 23:07 | 0.00039502 | 1.0395e-05 | 1 | 38 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2289 | 20715 | Cromwell GXP | CB2424 | 2025-03-18 22:29 | 2025-03-18 23:18 | 0.013244 | 0.00027028 | 26 | 1274 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2290 | 20714 | Cromwell GXP | CB2082 | 2025-03-18 22:29 | 2025-03-18 23:16 | 0.015146 | 0.00032225 | 31 | 1457 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2291 | 20713 | Cromwell GXP | CB2084 | 2025-03-18 22:29 | 2025-03-18 23:15 | 0.073162 | 0.0015905 | 153 | 7038 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2292 | 20712 | Cromwell GXP | CB2086 | 2025-03-18 22:29 | 2025-03-18 23:13 | 0.085532 | 0.0019439 | 187 | 8228 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2293 | 20717 | Cromwell GXP | CB1092 | 2025-03-18 22:29 | 2025-03-18 23:20 | 0.10709 | 0.0020998 | 202 | 10302 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2294 | 20722 | Cromwell GXP | CB2754 | 2025-03-18 22:29 | 2025-03-18 23:32 | 0.20826 | 0.0033057 | 318 | 20034 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2295 | 20716 | Cromwell GXP | CB2423 | 2025-03-18 22:29 | 2025-03-18 23:19 | 0.20531 | 0.0041061 | 395 | 19750 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2296 | 20723 | Cromwell GXP | CB2753 | 2025-03-18 22:29 | 2025-03-18 23:32 | 0.39228 | 0.0062267 | 599 | 37737 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2297 | 20718 | Cromwell GXP | CB2755 | 2025-03-18 22:29 | 2025-03-18 23:25 | 0.55361 | 0.0098859 | 951 | 53256 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2298 | 20725 | Cromwell GXP | CB2751 | 2025-03-18 22:29 | 2025-03-18 23:35 | 0.76979 | 0.011663 | 1122 | 74052 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2299 | 20719 | Cromwell GXP | CB2758 | 2025-03-18 22:29 | 2025-03-18 23:26 | 0.71459 | 0.012537 | 1206 | 68742 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2300 | 20720 | Cromwell GXP | CB2757 | 2025-03-18 22:29 | 2025-03-18 23:28 | 0.74764 | 0.012672 | 1219 | 71921 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2301 | 20721 | Cromwell GXP | CB2756 | 2025-03-18 22:29 | 2025-03-18 23:29 | 0.82205 | 0.013701 | 1318 | 79080 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2302 | 20724 | Cromwell GXP | CB2752 | 2025-03-18 22:29 | 2025-03-18 23:33 | 1.0312 | 0.016113 | 1550 | 99200 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2303 | 20706 | Cardrona | CB2881 | 2025-03-19 00:47 | 2025-03-19 01:40 | 0.04683 | 0.00088359 | 85 | 4505 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2304 | 20732 | Wanaka | CB2755 | 2025-03-19 08:32 | 2025-03-19 08:49 | 0.00035344 | 2.079e-05 | 2 | 34 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2305 | 20734 | Roxburgh | CB4639 | 2025-03-19 08:44 | 2025-03-19 16:02 | 0.43255 | 0.00098755 | 95 | 41610 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2306 | 20736 | Alexandra | CB163 | 2025-03-20 08:19 | 2025-03-20 14:57 | 0.29789 | 0.00074846 | 72 | 28656 | Planned | Planned interruption | pole replacement - planned | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2307 | 20739 | Halfway Bush | HB1 | 2025-03-20 09:03 | 2025-03-20 14:01 | 0.0061956 | 2.079e-05 | 2 | 596 | Planned | Planned interruption | transformer change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2308 | 20741 | Alexandra | CB168 | 2025-03-20 14:06 | 2025-03-20 16:34 | 0.0015385 | 1.0395e-05 | 1 | 148 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2309 | 21229 | Clyde-Earnscleugh | CB192 | 2025-03-20 14:48 | 2025-03-20 15:37 | 0.0020375 | 4.1581e-05 | 4 | 196 | Unplanned | Defective Equipment | faulty equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2310 | 20738 | Port Chalmers | PC3 | 2025-03-20 15:31 | 2025-03-20 18:09 | 0.0032849 | 2.079e-05 | 2 | 316 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2311 | 20733 | Wanaka | CB2755 | 2025-03-20 16:30 | 2025-03-20 16:40 | 0.0002079 | 2.079e-05 | 2 | 20 | Planned | Planned interruption | upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2312 | 20737 | Arrowtown | CB7652 | 2025-03-20 17:55 | 2025-03-20 18:03 | 0.0018296 | 0.00022869 | 22 | 176 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2313 | 20747 | Lauder Flat | CB6576 | 2025-03-23 07:31 | 2025-03-23 09:14 | 0.0021414 | 2.079e-05 | 2 | 206 | Unplanned | Wildlife | animal in equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2314 | 20755 | Outram | OT3 | 2025-03-25 17:16 | 2025-03-25 20:31 | 0.079056 | 0.00040541 | 39 | 7605 | Unplanned | Defective Equipment | broken fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2315 | 20756 | Alexandra | CB167 | 2025-03-25 20:14 | 2025-03-25 21:06 | 0.14433 | 0.0027755 | 267 | 13884 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2316 | 20768 | Lindis Crossing | CB2084 | 2025-03-26 06:01 | 2025-03-26 08:00 | 0.001237 | 1.0395e-05 | 1 | 119 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2317 | 20790 | Clyde-Earnscleugh | CB192 | 2025-03-26 08:32 | 2025-03-26 14:56 | 0.011975 | 3.1186e-05 | 3 | 1152 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2318 | 20791 | Clyde-Earnscleugh | CB192 | 2025-03-26 08:32 | 2025-03-26 14:56 | 0.011975 | 3.1186e-05 | 3 | 1152 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Queenstown | 2319 | 20759 | Commonage | CB5731 | 2025-03-26 09:02 | 2025-03-26 14:44 | 0.081769 | 0.00023909 | 23 | 7866 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2320 | 20758 | Port Chalmers | PC4 | 2025-03-26 09:04 | 2025-03-26 13:23 | 0.059232 | 0.00022869 | 22 | 5698 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2321 | 20757 | Mosgiel | MG6 | 2025-03-26 09:20 | 2025-03-26 10:19 | 0.0055199 | 9.3557e-05 | 9 | 531 | Planned | Planned interruption | tap change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2322 | 20764 | Wanaka | CB2755 | 2025-03-26 16:09 | 2025-03-26 16:44 | 0.04839 | 0.0013826 | 133 | 4655 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2323 | 20766 | Wanaka | CB2755 | 2025-03-26 16:09 | 2025-03-26 17:10 | 0.088141 | 0.0014449 | 139 | 8479 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2324 | 20763 | Wanaka | CB2755 | 2025-03-26 16:09 | 2025-03-26 16:41 | 0.093141 | 0.0029107 | 280 | 8960 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2325 | 20765 | Wanaka | CB2755 | 2025-03-26 16:09 | 2025-03-26 17:03 | 0.22341 | 0.0041373 | 398 | 21492 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2326 | 20774 | Andersons Bay | AB7 | 2025-03-27 08:00 | 2025-03-27 16:31 | 0.42496 | 0.00083162 | 80 | 40880 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2327 | 20775 | Alexandra | CB169 | 2025-03-27 09:04 | 2025-03-27 15:51 | 0.22 | 0.00054055 | 52 | 21164 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2328 | 20793 | Lindis Crossing | CB2086 | 2025-03-27 09:04 | 2025-03-27 15:41 | 0.082538 | 0.0002079 | 20 | 7940 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2329 | 20770 | Omakau | CB656 | 2025-03-27 11:34 | 2025-03-27 14:53 | 0.0020687 | 1.0395e-05 | 1 | 199 | Unplanned | Wildlife | bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2330 | 20794 | Lindis Crossing | CB2086 | 2025-03-27 15:29 | 2025-03-27 15:41 | 0.00012474 | 1.0395e-05 | 1 | 12 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2331 | 20785 | Camp Hill | CB2006 | 2025-03-29 16:35 | 2025-03-29 20:12 | 0.083079 | 0.00038462 | 37 | 7992 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2332 | 20783 | Camp Hill | CB2006 | 2025-03-29 16:35 | 2025-03-29 18:33 | 0.15203 | 0.0012994 | 125 | 14625 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2333 | 20784 | Camp Hill | CB2006 | 2025-03-29 16:35 | 2025-03-29 18:37 | 0.54464 | 0.0045011 | 433 | 52393 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2334 | 20782 | Camp Hill | CB2006 | 2025-03-29 16:35 | 2025-03-29 18:27 | 0.63694 | 0.0057382 | 552 | 61272 | Unplanned | Defective Equipment | cable faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2335 | 20786 | Ward Street | WS8 | 2025-03-29 19:26 | 2025-03-29 21:13 | 0.061176 | 0.00057174 | 55 | 5885 | Unplanned | Cause Unknown | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2336 | 21233 | Queensberry | CB2423 | 2025-03-30 11:03 | 2025-03-30 13:33 | 0.0031186 | 2.079e-05 | 2 | 300 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2337 | 21232 | Queensberry | CB2423 | 2025-03-30 11:03 | 2025-03-30 11:31 | 0.0017464 | 6.2371e-05 | 6 | 168 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2338 | 20788 | Riverbank | CB2424 | 2025-03-31 05:39 | 2025-03-31 05:45 | 0.0016217 | 0.00027028 | 26 | 156 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2339 | 20789 | Riverbank | CB2423 | 2025-03-31 05:39 | 2025-03-31 05:46 | 0.028816 | 0.0041165 | 396 | 2772 | Unplanned | Cause Unknown | line patrolled, nothing found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Dunedin | 2340 | 20796 | Willowbank | WB3 | 2025-03-31 08:18 | 2025-03-31 16:38 | 0.19231 | 0.00038462 | 37 | 18500 | Planned | Planned interruption | maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Aurora Energy | 2025 | Central Otago and Wanaka | 2341 | 20849 | Wanaka | CB2754 | 2025-03-31 15:20 | 2025-03-31 17:19 | 0.001237 | 1.0395e-05 | 1 | 119 | Unplanned | Defective Equipment | blown hv fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 9 | OR-10022 | Mt Rochfort, Section 6080, ABS135 - F66 | 28-WHA | 2024-04-03 09:01 | 2024-04-03 12:47 | 0.091591 | 0.00040527 | 2 | 226 | Planned | Planned Outage | Replace 11kV Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 10 | OR-10336 | Bulls Road, Cape Foulwind | 20-ADD | 2024-04-03 10:04 | 2024-04-03 11:57 | 0.068693 | 0.0006079 | 3 | 113 | Planned | Planned Outage | REPLACE STAY WIRE | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 11 | OR-11133 | Seddonville, Section 7260 , ABS56 - EOL | 42-SED | 2024-04-22 09:10 | 2024-04-22 11:51 | 1.7291 | 0.01074 | 53 | 161 | Planned | Planned Outage | Remove Trees | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 12 | OR-10088 | Between Deadmans Creek & Waimangaroa | 28-WHA | 2024-04-23 09:04 | 2024-04-23 15:29 | 1.0008 | 0.0026342 | 13 | 385 | Planned | Planned Outage | Replace 33kV CCT2 Arms & Straighten Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 13 | OR-10107 | Little Wanganui, Section 11240, F40 - EOL | 60-LIT | 2024-04-24 09:06 | 2024-04-24 13:04 | 0.19291 | 0.00081054 | 4 | 238 | Planned | Planned Outage | Fell trees around powerlines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 14 | OR-10093 | Wangapeka Road, Little Wanganui | 60-LIT | 2024-04-25 13:01 | 2024-04-25 21:15 | 3.2734 | 0.013779 | 68 | 494 | Unplanned | Defective Equipment | FAULT - CRACKED 11KV PIN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 15 | OR-10098 | Kohaihai Road, Karamea | 62-KAR | 2024-04-29 09:00 | 2024-04-29 13:00 | 0.27558 | 0.0042553 | 21 | 240 | Unplanned | Defective Equipment | Broken jumper 11kV | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 16 | OR-10063 | Karamea, Section 9060, ABS77 - EOL | 62-KAR | 2024-04-30 09:00 | 2024-04-30 14:23 | 2.8798 | 0.0089159 | 44 | 323 | Planned | Planned Outage | Trim & fell trees | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 17 | OR-10123 | Whareatea feeder | 26-DOM, 28-WHA | 2024-05-02 06:30 | 2024-05-02 08:24 | 2.7413 | 0.12948 | 639 | 114 | Unplanned | Unknown | FAULT 282 TRIPPED | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 18 | OR-10132 | Cape Foulwind | 20-ADD | 2024-05-02 08:36 | 2024-05-02 13:44 | 0.062411 | 0.00020263 | 1 | 308 | Planned | Planned Outage | Install 11kV term arms, disconnect 11kV span. Dig in stay anchors | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 19 | OR-10136 | Golf Links Road, Carters Beach | 20-ADD | 2024-05-03 11:09 | 2024-05-03 11:58 | 1.0028 | 0.020466 | 101 | 49 | Unplanned | Defective Equipment | FAULT-BROKEN 11KV PREFORM | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 20 | OR-10159 | 8175 TOTARA ROAD CHARLESTON | 20-ADD | 2024-05-03 11:00 | 2024-05-03 12:00 | 0.012158 | 0.00020263 | 1 | 60 | Unplanned | Unknown | REPLACE BLOWN HV FUSE | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 21 | OR-10156 | Waimea Terrace Drive, Westport | 20-ADD | 2024-05-06 09:01 | 2024-05-06 14:39 | 0.95887 | 0.0028369 | 14 | 338 | Planned | Planned Outage | Replace 11kV S730 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 22 | OR-10202 | Utopia Road, Westport | 28-WHA | 2024-05-09 08:33 | 2024-05-09 15:29 | 6.6594 | 0.016008 | 79 | 416 | Planned | Planned Outage | Replace poles, conductor and subs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 23 | OR-10058 | Little Wanganui | 60-LIT | 2024-05-15 09:39 | 2024-05-15 15:38 | 8.875 | 0.024721 | 122 | 359 | Planned | Planned Outage | Remove branches overhanging powerlines, Fell trees at Tidal Creek | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 24 | OR-10128 | Cape Foulwind | 20-ADD | 2024-05-23 09:06 | 2024-05-23 16:02 | 5.3106 | 0.012766 | 63 | 416 | Planned | Planned Outage | INSTALL 11KV POLES AND GENERAL LINE WORK | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 25 | OR-10209 | Cape Foulwind Road, Westport | 20-ADD | 2024-05-27 09:00 | 2024-05-27 15:43 | 3.8381 | 0.0095238 | 47 | 403 | Planned | Planned Outage | INSTALL 11KV POLES & GENERAL LINE WORK | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 26 | OR-10337 | Lower Buller Gorge | 20-ADD | 2024-06-04 10:30 | 2024-06-04 11:30 | 0.012158 | 0.00020263 | 1 | 60 | Unplanned | Unknown | REPLACE BLOWN HV FUSE | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 27 | OR-10338 | MT ROCHFORT | 28-WHA | 2024-06-04 19:13 | 2024-06-04 19:40 | 0.010942 | 0.00040527 | 2 | 27 | Unplanned | Unknown | REPLACE HV FUSES | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 28 | OR-10176 | Buller Road, Westport | 20-ADD | 2024-06-06 09:03 | 2024-06-06 14:24 | 3.6539 | 0.01155 | 57 | 321 | Planned | Planned Outage | Replace two inline 11kV poles with excavator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 29 | OR-10252 | Hector | 36-NGK/KON, 42-SED | 2024-06-11 08:31 | 2024-06-11 14:30 | 10.2389 | 0.032219 | 159 | 359 | Planned | Planned Outage | REPLACE 33/11 KV POLE, CONNECT 11KV SPURLINE & REMOVE SEC 5 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 30 | OR-10199 | Stephen Road, Westport | 28-WHA | 2024-06-13 09:01 | 2024-06-13 14:57 | 6.4559 | 0.018237 | 90 | 356 | Planned | Planned Outage | REPLACE DOUBLE POLE STRUCTURE WITH SINGLE BUSCK & REMOVE ABS 38 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 31 | OR-10333 | 109 NINE MILE ROAD (OLD PACKING PLANT) | 28-WHA | 2024-06-16 13:30 | 2024-06-16 14:30 | 0.048632 | 0.00081054 | 4 | 60 | Unplanned | Lightning | REPLACE BLOWN HV FUSES | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 32 | OR-10331 | MARS BEACH | 20-ADD | 2024-06-19 18:00 | 2024-06-19 18:30 | 0.006079 | 0.00020263 | 1 | 30 | Unplanned | Unknown | REPLACE BLOWN HV FUSES | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 33 | OR-10332 | SHADICK AVE CARTERS BEACH | 20-ADD | 2024-06-19 10:21 | 2024-06-19 13:30 | 0.36657 | 0.0042553 | 21 | 189 | Unplanned | Unknown | REPLACE BLOWN POLE FUSES | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 34 | OR-10230 | ST HELENS, MOKIHINUI | 42-SED | 2024-06-20 09:04 | 2024-06-20 12:19 | 0.23708 | 0.0012158 | 6 | 195 | Planned | Planned Outage | REPLACE LV POLE, INSTALL STAY AND BARRIER | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 35 | OR-10326 | Nine Mile Road, Westport | 28-WHA | 2024-06-21 07:53 | 2024-06-21 08:41 | 0.15562 | 0.0032421 | 16 | 48 | Unplanned | Unknown | REPLACE 2 X BLOWN HV FUSES | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 36 | OR-10329 | LITTLE Wanganui | 60-LIT | 2024-06-23 10:00 | 2024-06-23 12:30 | 1.6717 | 0.011145 | 55 | 150 | Unplanned | Unknown | REPLACE BLOWN HV FUSES | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 37 | OR-10279 | POLE 1804 BETWEEN MARTINS CREEK & BULLER BRIDGE | 20-ADD | 2024-06-24 00:57 | 2024-06-24 05:45 | 0.7003 | 0.0024316 | 12 | 288 | Unplanned | Third Party Interference | CAR VS POLE MARTINS BEND | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 38 | OR-10236 | Cains Road, Birchfield | 40-WAI | 2024-06-26 09:05 | 2024-06-26 14:03 | 0.30193 | 0.0010132 | 5 | 298 | Planned | Planned Outage | RESAG 11KV CONDUCTOR AND GENERAL MAINTENANCE | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 39 | OR-10285 | Nikau Road, Hector | 42-SED | 2024-06-26 09:02 | 2024-06-26 10:21 | 0.080041 | 0.0010132 | 5 | 79 | Planned | Planned Outage | Replace 30kVA sub 661 & earth rods | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 40 | OR-10305 | Reedys Road, Westport | 28-WHA | 2024-06-27 09:03 | 2024-06-27 10:57 | 0.1617 | 0.0014184 | 7 | 114 | Planned | Planned Outage | REPLACE 11KV CROSSARMS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 41 | OR-10299 | Utopia Road, Westport | 28-WHA | 2024-06-27 09:53 | 2024-06-27 11:18 | 0.034448 | 0.00040527 | 2 | 85 | Planned | Planned Outage | REPLACE DDOS & LIGHTNINING ARRESTORS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 42 | OR-10264 | Fox River | 20-ADD | 2024-07-04 09:00 | 2024-07-04 14:55 | 2.9909 | 0.0085106 | 42 | 355 | Planned | Planned Outage | Replace poles and general linework | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 43 | OR-10242 | Karamea | 62-KAR | 2024-07-10 11:36 | 2024-07-10 12:41 | 0.026342 | 0.00040527 | 2 | 65 | Planned | Planned Outage | REPLACE SUB 396 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 44 | OR-10271 | LITTLE WANGANUI | 60-LIT | 2024-07-11 09:00 | 2024-07-11 13:30 | 6.7295 | 0.024924 | 123 | 270 | Planned | Planned Outage | REPLACE POLES & 33KV INSULATORS & TRIM TREES | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 45 | OR-10370 | Fonblanque Street, Westport | 22-RUS | 2024-07-11 21:20 | 2024-07-11 22:42 | 0.016616 | 0.00020263 | 1 | 82 | Planned | Planned Outage | Tighten internal LV bushing SUB 474 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 46 | OR-10377 | Fairdown | 28-WHA | 2024-07-11 04:53 | 2024-07-11 15:20 | 6.8316 | 0.017629 | 87 | 627 | Unplanned | Unknown | CB1392 TRIP - REPLACE CROSSARMS AT POLE 50134 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 47 | OR-10248 | Karamea | 62-KAR | 2024-07-12 10:09 | 2024-07-12 11:18 | 0.097872 | 0.0014184 | 7 | 69 | Planned | Planned Outage | REPLACE SUB 411 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 48 | OR-10311 | Fairdown | 28-WHA | 2024-07-17 09:03 | 2024-07-17 13:30 | 4.707 | 0.017629 | 87 | 267 | Planned | Planned Outage | REPLACE 11KV CROSSARMS, INSTALL 11KV FUSES & NEW SUB | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 49 | OR-10382 | Oparara Road, Karamea | 62-KAR | 2024-07-19 09:01 | 2024-07-19 14:19 | 0.45106 | 0.0014184 | 7 | 318 | Planned | Planned Outage | REPLACE LV CROSSARMS, CONNECT NEW ABC TO SERVICE POLE | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 50 | OR-10459 | Shaddock ave, Carters Beach | 20-ADD | 2024-07-25 08:50 | 2024-07-25 09:30 | 0.17021 | 0.0042553 | 21 | 40 | Unplanned | Unknown | 2X BLOWN HT FUSES | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 51 | OR-10358 | McKenna Road, Westport | 28-WHA | 2024-07-30 08:15 | 2024-07-30 14:43 | 5.6608 | 0.01459 | 72 | 388 | Planned | Planned Outage | Reconductor 11kV & General Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 52 | OR-10441 | KARAMEA BLUFF | 36-NGK/KON | 2024-08-09 09:00 | 2024-08-09 14:39 | 0.20608 | 0.0006079 | 3 | 339 | Planned | Planned Outage | INSTALL LINKS AT POLE 70418, TRACK & TREE CUTTING | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 53 | OR-10464 | Peel Street, Westport | 23-DER | 2024-08-20 08:30 | 2024-08-20 16:12 | 16.738 | 0.036677 | 181 | 462 | Planned | Planned Outage | REPLACE SUB 158 WITH GROUNDMOUNT | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 54 | OR-10531 | 708 NIKAU ROAD | 42-SED | 2024-08-27 05:57 | 2024-08-27 12:47 | 0.24924 | 0.0006079 | 3 | 410 | Unplanned | Lightning | REPLACE 3 HV FUSES SUPPLYING SUB 321 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 55 | OR-10530 | MT ROCHFORT | 28-WHA | 2024-08-27 05:05 | 2024-08-27 12:25 | 0.17832 | 0.00040527 | 2 | 440 | Unplanned | Lightning | REPLACE BLOWN FUSES 57 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 56 | OR-10597 | Denniston | 28-WHA | 2024-08-27 05:05 | 2024-08-27 12:00 | 0.58865 | 0.0014184 | 7 | 415 | Unplanned | Lightning | NO POWER FAULT | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 57 | OR-10472 | Mokihinui | 42-SED | 2024-08-29 09:07 | 2024-08-29 14:43 | 3.5404 | 0.010537 | 52 | 336 | Planned | Planned Outage | REPLACE 11KV POLE | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 58 | OR-10551 | 8860 SH6 | 20-ADD | 2024-08-30 09:30 | 2024-08-30 11:00 | 0.036474 | 0.00040527 | 2 | 90 | Unplanned | Lightning | REPLACE BLOWN HV FUSE | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 59 | OR-10554 | 114 FLAXMILL ROAD, KARAMEA | 62-KAR | 2024-08-30 | 2024-08-30 10:30 | 0.12766 | 0.00020263 | 1 | 630 | Unplanned | Lightning | REPLACE BLOWN HV FUSE | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 60 | OR-10552 | 23/153 ALMA ROAD | 20-ADD | 2024-08-30 07:30 | 2024-08-30 10:00 | 0.030395 | 0.00020263 | 1 | 150 | Unplanned | Lightning | REPLACE BLOWN HV FUSE | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 61 | OR-10553 | Linehams Road, Karamea | 62-KAR | 2024-08-30 07:30 | 2024-08-30 11:30 | 0.048632 | 0.00020263 | 1 | 240 | Unplanned | Lightning | REPLACE BLOWN HV FUSE | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 62 | OR-10539 | MT ROCHFORT | 28-WHA | 2024-08-30 07:30 | 2024-08-30 14:00 | 0.18703 | 0.00081054 | 4 | 390 | Unplanned | Lightning | REPAIR BROKEN JUMPER FUSES 57 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 63 | OR-10544 | Fairdown | 20-ADD, 28-WHA | 2024-08-31 18:37 | 2024-09-01 18:00 | 5.2904 | 0.025329 | 125 | 1403 | Unplanned | Lightning | Broken 33kv pin on pole 50135 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 64 | OR-10545 | Caledonian Road, Westport | 28-WHA | 2024-08-31 23:04 | 2024-09-01 13:00 | 0.1694 | 0.00020263 | 1 | 836 | Unplanned | Lightning | REPLACE SUB 517 CALEDONIAN ROAD (BEAR HUNTER) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 65 | OR-10502 | Cape Foulwind | 20-ADD | 2024-09-04 09:03 | 2024-09-04 16:04 | 1.9465 | 0.0046606 | 23 | 421 | Planned | Planned Outage | REMOVE ABS 11 & 12 - REPLACE ABS 13 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 66 | OR-10611 | Nine Mile Road, Westport | 28-WHA | 2024-09-05 20:00 | 2024-09-05 21:45 | 0.34043 | 0.0032421 | 16 | 105 | Unplanned | Unknown | Blown HV Fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 67 | OR-10601 | Tauranga Bay Road, Cape Foulwind | 20-ADD | 2024-09-08 21:55 | 2024-09-08 23:55 | 0.19453 | 0.0016211 | 8 | 120 | Unplanned | Defective Equipment | REPAIR BURNT OUT CONNECTOR ON 11KV CABLE | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 68 | OR-10594 | NORTH BEACH, KARAMEA | 62-KAR | 2024-09-11 09:04 | 2024-09-11 14:50 | 1.4723 | 0.0042553 | 21 | 346 | Planned | Planned Outage | REPLACE POLES, CROSSARMS AND CONDUCTOR | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 69 | OR-10514 | Flaxmill Road, Karamea | 62-KAR | 2024-09-12 09:04 | 2024-09-12 14:14 | 0.062817 | 0.00020263 | 1 | 310 | Planned | Planned Outage | REPLACE 11KV TX POLE | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 70 | OR-10616 | Karamea | 62-KAR | 2024-09-15 08:40 | 2024-09-15 12:39 | 0.04843 | 0.00020263 | 1 | 239 | Unplanned | Defective Equipment | Replace Sub 442 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 71 | OR-10618 | Schadick Avenue, Carters Beach | 20-ADD | 2024-09-16 07:30 | 2024-09-16 09:15 | 0.44681 | 0.0042553 | 21 | 105 | Unplanned | Wildlife | Swan hit lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 72 | OR-10680 | NORTH BEACH, KARAMEA | 62-KAR | 2024-09-18 09:02 | 2024-09-18 14:35 | 1.417 | 0.0042553 | 21 | 333 | Planned | Planned Outage | REPLACE POLES, CROSSARMS AND CONDUCTOR | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 73 | OR-10645 | CNR SHADDICK AVE, GOLF LINKS RD | 20-ADD | 2024-09-19 03:45 | 2024-09-19 04:30 | 0.0091185 | 0.00020263 | 1 | 45 | Unplanned | Wildlife | PART POWER WESTREEF PUMP STATION | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 74 | OR-10556 | NORTH BEACH KARAMEA | 62-KAR | 2024-09-20 09:00 | 2024-09-20 15:22 | 1.6255 | 0.0042553 | 21 | 382 | Planned | Planned Outage | RECONDUCTOR 11KV | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 75 | OR-10317 | Powerhouse Road, Fairdown | 28-WHA | 2024-09-26 09:13 | 2024-09-26 10:58 | 0.2766 | 0.0026342 | 13 | 105 | Planned | Planned Outage | REPLACE SUB 568 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 76 | OR-10647 | KONGAHU STRAIGHT | 60-LIT | 2024-09-28 03:30 | 2024-09-28 06:30 | 0.072948 | 0.00040527 | 2 | 180 | Unplanned | Wildlife | NO POWER- SWAN HIT LINE | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 77 | OR-10669 | Domain Road, Cape Foulwind | 20-ADD | 2024-10-10 09:03 | 2024-10-10 14:44 | 0.89828 | 0.0026342 | 13 | 341 | Planned | Planned Outage | Domain rd LV upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 78 | OR-10677 | Domain Road, Cape Foulwind | 20-ADD | 2024-10-11 09:20 | 2024-10-11 10:10 | 0.34448 | 0.0068896 | 34 | 50 | Unplanned | Defective Equipment | SUB CHECK | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 79 | OR-10656 | Golf Course Road, Karamea | 62-KAR | 2024-10-16 09:43 | 2024-10-16 14:14 | 0.3844 | 0.0014184 | 7 | 271 | Planned | Planned Outage | Replace 11kV TX. Remove OH LV & hardware & install new cable | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 80 | OR-10637 | McKenna Road, Westport | 28-WHA | 2024-10-22 09:08 | 2024-10-22 12:24 | 1.9461 | 0.0099291 | 49 | 196 | Planned | Planned Outage | Replace 11kv jumpers | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 81 | OR-10697 | Pines Corner | 28-WHA | 2024-10-22 17:45 | 2024-10-22 23:31 | 6.5905 | 0.019048 | 94 | 346 | Unplanned | Third Party Interference | De-Energise Power for crane to lift rolled Truck & Crusher | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 82 | OR-10727 | KERRS CROSSING, GRANITY | 40-WAI | 2024-10-25 07:40 | 2024-10-25 08:30 | 0.020263 | 0.00040527 | 2 | 50 | Unplanned | Lightning | REPLACE 2 X BLOWN HV FUSES | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 83 | OR-10642 | Tauranga Bay Road, Cape Foulwind | 20-ADD | 2024-10-29 08:34 | 2024-10-29 16:52 | 5.4241 | 0.084296 | 416 | 498 | Planned | Planned Outage | General Line work and maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 84 | OR-10665 | Cape Foulwind | 20-ADD | 2024-10-31 08:30 | 2024-10-31 15:14 | 0.88916 | 0.054306 | 268 | 404 | Planned | Planned Outage | RECONDUCTOR 11KV FROM POLE 1134 TO 1155 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 85 | OR-10710 | Cape Foulwind | 20-ADD | 2024-11-27 08:29 | 2024-11-27 15:50 | 4.894 | 0.064843 | 320 | 441 | Planned | Planned Outage | RECONDUCTOR 11KV SEC 700 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 86 | OR-10738 | COAST ROAD | 20-ADD | 2024-12-04 08:30 | 2024-12-04 15:00 | 3.8723 | 0.0099291 | 49 | 390 | Planned | Planned Outage | REPLACE 3 X 11KV POLES | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 87 | OR-10801 | Granite Creek Road, Karamea | 62-KAR | 2024-12-10 14:30 | 2024-12-10 17:30 | 0.36474 | 0.0020263 | 10 | 180 | Unplanned | Wildlife | NO POWER GRANITE CREEK RD | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 88 | OR-10798 | Little Wanganui | 60-LIT | 2024-12-13 19:00 | 2024-12-13 23:10 | 1.9141 | 0.024924 | 123 | 250 | Unplanned | Defective Equipment | Replace DDO's Supplying Sub 632 Little Wanganui | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 89 | OR-10806 | 9225 SH6 | 20-ADD | 2024-12-16 06:00 | 2024-12-16 08:00 | 0.048632 | 0.00040527 | 2 | 120 | Unplanned | Lightning | REPLACE BLOWN DDO FUSE | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 90 | OR-10767 | Darkies Terrace Road, Charleston | 20-ADD | 2024-12-17 09:00 | 2024-12-17 12:35 | 0.1307 | 0.0006079 | 3 | 215 | Planned | Planned Outage | REMOVE FUSES 289, INSTALL SUB 867 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 91 | OR-10816 | SHADICK DRIVE CARTERS BEACH | 20-ADD | 2024-12-20 22:00 | 2024-12-20 22:45 | 0.19149 | 0.0042553 | 21 | 45 | Unplanned | Defective Equipment | BROKEN HV FUSE LINK | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 92 | OR-10815 | Stephen Road, Westport | 28-WHA | 2024-12-30 12:30 | 2024-12-30 14:00 | 0.036474 | 0.00040527 | 2 | 90 | Unplanned | Wildlife | BIRD STRIKE, 2 X BLOWN HV FUSES | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 93 | OR-10812 | Granite Creek Road, Karamea | 62-KAR | 2025-01-01 14:00 | 2025-01-01 15:30 | 0.18237 | 0.0020263 | 10 | 90 | Unplanned | Unknown | BLOWN HV FUSES | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 94 | OR-10751 | Birchfield | 36-NGK/KON, 38-STK, 40-WAI, 42-SED | 2025-01-03 08:20 | 2025-01-03 13:55 | 5.6322 | 0.21783 | 1075 | 335 | Planned | Planned Outage | 33KV ROB/NGK CCT CROSSINGS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 95 | OR-10923 | Millerton | 40-WAI | 2025-01-29 09:45 | 2025-01-29 13:24 | 1.3757 | 0.0062817 | 31 | 219 | Unplanned | Unknown | REC 22 TRIPPED | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 96 | OR-10933 | Karamea | 62-KAR | 2025-01-31 14:25 | 2025-01-31 16:25 | 1.1185 | 0.0093212 | 46 | 120 | Unplanned | Human Error | RECLOSER 11 TRIPPED A-C-E FAULT | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 97 | OR-10936 | Oparara Road, Karamea | 62-KAR | 2025-02-04 03:08 | 2025-02-04 09:30 | 3.6999 | 0.011348 | 56 | 382 | Unplanned | Vegetation | REC 21 Tripped | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 98 | OR-10955 | BUNNINGS ROAD | 20-ADD | 2025-02-06 20:30 | 2025-02-06 21:00 | 0.018237 | 0.0006079 | 3 | 30 | Unplanned | Wildlife | BIRD STRIKE | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 99 | OR-10954 | Granite Creek Road, Karamea | 62-KAR | 2025-02-07 22:00 | 2025-02-07 23:30 | 0.18237 | 0.0020263 | 10 | 90 | Unplanned | Wildlife | 2X Blown HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 100 | OR-10960 | Oparara Road, Karamea | 62-KAR | 2025-02-12 09:00 | 2025-02-12 13:15 | 0.15502 | 0.0006079 | 3 | 255 | Unplanned | Defective Equipment | HV FUSE DROPPED OUT (NOT BLOWN) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 101 | OR-10866 | KAWATIRI PLACE | 26-DOM | 2025-02-17 09:00 | 2025-02-17 09:09 | 0.093009 | 0.010334 | 51 | 9 | Planned | Planned Outage | DE ENERGISE SUB 640 TO CHANGE TAP POSITION | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 102 | OR-10831 | Ngakawau | 40-WAI | 2025-02-18 09:03 | 2025-02-18 15:54 | 0.58298 | 0.0014184 | 7 | 411 | Planned | Planned Outage | UNDER GROUND TYLER ROAD NGAKAWAU | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 103 | OR-10819 | Ngakawau | 42-SED | 2025-02-20 09:27 | 2025-02-20 15:37 | 7.8363 | 0.08227 | 406 | 370 | Planned | Planned Outage | 11KV MAINTENANCE NGAKAWAU | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 104 | OR-10981 | Palmerston Street, Westport | 22-RUS | 2025-02-21 14:30 | 2025-02-21 16:00 | 0.40122 | 0.004458 | 22 | 90 | Unplanned | Defective Equipment | Part Power - Shops on Palmerston Street | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 105 | OR-10825 | Ngakawau | 42-SED | 2025-02-25 09:01 | 2025-02-25 15:46 | 8.1759 | 0.08227 | 406 | 405 | Planned | Planned Outage | 11KV MAINTENANCE NGAKAWAU | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 106 | OR-10984 | 438 Okari Road, Cape Foulwind Sub34 | 20-ADD | 2025-02-28 12:30 | 2025-02-28 14:00 | 0.018237 | 0.00020263 | 1 | 90 | Unplanned | Defective Equipment | Part Power | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 107 | OR-10985 | Lighthouse Road, Cape Foulwind | 20-ADD | 2025-03-03 08:30 | 2025-03-03 09:30 | 0.44985 | 0.0074975 | 37 | 60 | Unplanned | Defective Equipment | Part Power - Lighthouse Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 108 | OR-11010 | Millerton | 40-WAI | 2025-03-08 06:40 | 2025-03-08 08:55 | 0.84802 | 0.0062817 | 31 | 135 | Unplanned | Unknown | Rec 22 tripped - No comms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 109 | OR-10908 | Okari Road, Cape Foulwind | 20-ADD | 2025-03-11 08:21 | 2025-03-11 15:31 | 1.6326 | 0.067072 | 331 | 430 | Planned | Planned Outage | REPLACE DOUBLE STRUCTURE | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 110 | OR-11014 | CB 1332 to ABS126 | 34-ROB/NGK-CCT2 | 2025-03-18 08:37 | 2025-03-18 14:49 | 0.0034448 | 0.00040527 | 2 | 372 | Planned | Planned Outage | Trim and fell trees around powerlines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 111 | OR-11074 | Bulls Road, Cape Foulwind | 20-ADD | 2025-03-25 08:37 | 2025-03-25 15:29 | 1.1664 | 0.0028369 | 14 | 412 | Planned | Planned Outage | REPLACE 2X POLES | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Buller Electricity | 2025 |  | 112 | OR-11050 | KARAMEA BLUFF | 36-NGK/KON | 2025-03-31 08:19 | 2025-03-31 14:46 | 0.23526 | 0.0006079 | 3 | 387 | Planned | Planned Outage | FLY IN GRAVEL TO POLE SITES, REPLACE 1 X POLE | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 9 | INC 417001795 | 46 - Cooks Tooth/Herbertville | 46 - Cooks Tooth/Herbertville | 2024-04-09 09:22 | 2024-04-09 15:18 | 0.075778 | 0.00021314 | 2 | 711.0667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 10 | INC 417001796 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-04-09 09:59 | 2024-04-09 15:29 | 0.1759 | 0.00053285 | 5 | 1650.5833 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 11 | INC 417001812 | 04 - Burnside/Pukeora | 01 - OngaOnga/Ashley Clinton | 2024-04-10 09:24 | 2024-04-10 15:09 | 0.27796 | 0.0075665 | 39 | 2608.2167 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 12 | INC 417001847 | 46 - Cooks Tooth/Herbertville | 46 - Cooks Tooth/Herbertville | 2024-04-11 09:25 | 2024-04-11 16:31 | 0.75142 | 0.0019183 | 18 | 7050.9167 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 13 | INC 417001869 | 46 - Cooks Tooth/Herbertville | 46 - Cooks Tooth/Herbertville | 2024-04-11 14:36 | 2024-04-11 18:15 | 1.6819 | 0.034742 | 325 | 15781.7165 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 14 | INC 417002005 | 17 - Cook St | 17 - Cook St | 2024-04-13 07:36 | 2024-04-13 18:57 | 0.072619 | 0.00010657 | 1 | 681.4167 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 15 | INC 417002055 | 17 - Cook St | 17 - Cook St | 2024-04-14 07:45 | 2024-04-14 16:03 | 0.053022 | 0.00010657 | 1 | 497.5333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 16 | INC 417002124 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2024-04-16 09:01 | 2024-04-16 14:04 | 0.77587 | 0.0025577 | 24 | 7280.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 17 | INC 417002129 | 15 - Waipukurau CBD | 15 - Waipukurau CBD | 2024-04-16 09:10 | 2024-04-16 15:48 | 2.2472 | 0.0056482 | 53 | 21086.9333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 18 | INC 417002207 | 46 - Cooks Tooth/Herbertville | 46 - Cooks Tooth/Herbertville | 2024-04-19 09:03 | 2024-04-19 13:26 | 0.084062 | 0.00031971 | 3 | 788.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 19 | INC 417002320 | 03 - Argyll/Ruataniwha | 03 - Argyll/Ruataniwha | 2024-04-23 09:01 | 2024-04-23 13:59 | 2.1081 | 0.0072468 | 68 | 19781.3667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 20 | INC 417002323 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2024-04-23 09:13 | 2024-04-23 16:10 | 0.48925 | 0.0011723 | 11 | 4590.85 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 21 | INC 417002351 | 15 - Waipukurau CBD | 15 - Waipukurau CBD | 2024-04-24 09:04 | 2024-04-24 14:39 | 1.0604 | 0.0063942 | 60 | 9950.65 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 22 | INC 417002427 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-04-26 10:14 | 2024-04-26 11:08 | 1.1586 | 0.057868 | 375 | 10871.483 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 23 | INC 417002427 | 83 - Omakere/Elsthorpe | 88 - Omakere/Pourerere | 2024-04-26 10:19 | 2024-04-26 10:21 | 0.06586 | 0.038365 | 360 | 617.9998 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 24 | INC 417002439 | 18 - Waipukurau South/Farm Rd | 18 - Waipukurau South/Farm Rd | 2024-04-26 16:10 | 2024-04-26 16:37 | 0.077029 | 0.0027708 | 26 | 722.8 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 25 | INC 417002462 | 13 - Tapairu/Mangatarata | 13 - Tapairu/Mangatarata | 2024-04-27 14:29 | 2024-04-29 15:16 | 0.62383 | 0.00021314 | 2 | 5853.7 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 26 | INC 417002510 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2024-04-30 09:10 | 2024-04-30 14:14 | 0.32396 | 0.0010657 | 10 | 3039.8333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 27 | INC 417002514 | 46 - Cooks Tooth/Herbertville | 46 - Cooks Tooth/Herbertville | 2024-04-30 09:16 | 2024-04-30 13:59 | 0.030154 | 0.00010657 | 1 | 282.95 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 28 | INC 417002560 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2024-05-02 00:03 | 2024-05-02 03:41 | 0.87268 | 0.04039 | 199 | 8188.7665 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 29 | INC 417002572 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2024-05-02 09:09 | 2024-05-02 14:20 | 0.33086 | 0.0010657 | 10 | 3104.6667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 30 | INC 417002722 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2024-05-07 09:25 | 2024-05-07 13:47 | 0.50284 | 0.0019183 | 18 | 4718.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 31 | INC 417002788 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2024-05-13 09:12 | 2024-05-13 13:44 | 0.49212 | 0.0018117 | 17 | 4617.7667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 32 | INC 417002791 | 75 - Paget Rd/Burnside | 75 - Paget Rd/Burnside | 2024-05-13 09:28 | 2024-05-13 10:32 | 0.047793 | 0.00074599 | 7 | 448.4667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 33 | INC 417002821 | 19 - Hatuma/Wanstead | 45 - Porangahau/Wallingford | 2024-05-14 09:09 | 2024-05-14 16:21 | 0.8853 | 0.0021314 | 20 | 8307.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 34 | INC 417002823 | 78 - Hinerangi | 78 - Hinerangi | 2024-05-14 09:14 | 2024-05-14 12:08 | 0.11126 | 0.00063942 | 6 | 1044 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 35 | INC 417002932 | 76 - Maharakeke | 76 - Maharakeke | 2024-05-16 09:19 | 2024-05-16 15:31 | 1.5069 | 0.0040497 | 38 | 14139.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 36 | INC 417003058 | 02 - Wakarara/Tikokino | 02 - Wakarara/Tikokino | 2024-05-20 09:13 | 2024-05-20 12:39 | 0.021918 | 0.00010657 | 1 | 205.6667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 37 | INC 417003184 | 88 - Omakere/Pourerere | 88 - Omakere/Pourerere | 2024-06-19 09:24 | 2024-06-19 13:28 | 0.76371 | 0.019502 | 104 | 7166.2499 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 38 | INC 417003227 | 85 - Waipawa Urban | 85 - Waipawa Urban | 2024-06-22 14:56 | 2024-06-22 15:52 | 3.9664 | 0.085043 | 798 | 37218.5998 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 39 | INC 417003279 | 03 - Argyll/Ruataniwha | 03 - Argyll/Ruataniwha | 2024-06-24 09:46 | 2024-06-24 11:43 | 0.012463 | 0.00010657 | 1 | 116.95 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 40 | INC 417003393 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2024-06-26 17:56 | 2024-06-26 17:57 | 0.0097352 | 0.0092716 | 87 | 91.35 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 41 | INC 417003462 | 15 - Waipukurau CBD | 15 - Waipukurau CBD | 2024-06-29 09:53 | 2024-06-29 12:34 | 1.2207 | 0.0075665 | 71 | 11454.6666 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 42 | INC 417003477 | 17 - Cook St | 15 - Waipukurau CBD | 2024-06-29 09:52 | 2024-06-29 12:39 | 1.936 | 0.011723 | 110 | 18166 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 43 | INC 417003597 | Wilder Rd | 45 - Porangahau/Wallingford | 2024-07-02 10:40 | 2024-07-02 12:30 | 1.6174 | 0.087387 | 410 | 15176.8331 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 44 | INC 417003597 | Wilder Rd | 46 - Cooks Tooth/Herbertville | 2024-07-02 10:40 | 2024-07-02 12:34 | 1.4815 | 0.072681 | 341 | 13901.4331 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 45 | INC 417003639 | 13 - Tapairu/Mangatarata | 13 - Tapairu/Mangatarata | 2024-07-03 09:16 | 2024-07-03 14:04 | 2.3949 | 0.0085256 | 79 | 22472.7833 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 46 | INC 417003740 | 13 - Tapairu/Mangatarata | 13 - Tapairu/Mangatarata | 2024-07-05 09:20 | 2024-07-05 12:10 | 1.1207 | 0.0066073 | 62 | 10516.2333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 47 | INC 417003891 | 13 - Tapairu/Mangatarata | 13 - Tapairu/Mangatarata | 2024-07-09 09:04 | 2024-07-09 12:34 | 0.58344 | 0.0027708 | 26 | 5474.7333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 48 | INC 417003894 | 88 - Omakere/Pourerere | 88 - Omakere/Pourerere | 2024-07-09 09:16 | 2024-07-09 13:54 | 0.3857 | 0.0013854 | 13 | 3619.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 49 | INC 417004040 | 88 - Omakere/Pourerere | 83 - Omakere/Elsthorpe | 2024-07-12 09:10 | 2024-07-12 12:19 | 0.020119 | 0.00010657 | 1 | 188.7833 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 50 | INC 417004191 | 91 - Te Kura | 91 - Te Kura | 2024-07-16 09:05 | 2024-07-16 13:03 | 0.12698 | 0.00053285 | 5 | 1191.5167 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 51 | INC 417004194 | 83 - Omakere/Elsthorpe | 88 - Omakere/Pourerere | 2024-07-16 09:57 | 2024-07-16 14:25 | 0.028646 | 0.00010657 | 1 | 268.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 52 | INC 417004202 | 18 - Waipukurau South/Farm Rd | 18 - Waipukurau South/Farm Rd | 2024-07-19 21:25 | 2024-07-19 21:41 | 0.044168 | 0.0028774 | 27 | 414.45 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 53 | INC 417004222 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2024-07-21 00:33 | 2024-07-21 01:56 | 0.24727 | 0.002984 | 28 | 2320.2666 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 54 | INC 417004290 | 85 - Waipawa Urban | 85 - Waipawa Urban | 2024-07-23 09:08 | 2024-07-23 16:06 | 2.4794 | 0.043267 | 223 | 23265.3332 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 55 | INC 417004291 | 88 - Omakere/Pourerere | 88 - Omakere/Pourerere | 2024-07-23 09:40 | 2024-07-23 15:36 | 0.36394 | 0.002238 | 15 | 3415.05 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 56 | INC 417004368 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-07-25 09:02 | 2024-07-25 14:33 | 0.95277 | 0.0028774 | 27 | 8940.2833 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 57 | INC 417004528 | 88 - Omakere/Pourerere | 88 - Omakere/Pourerere | 2024-07-30 09:14 | 2024-07-30 12:50 | 0.023032 | 0.00010657 | 1 | 216.1167 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 58 | INC 417004557 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-08-01 10:24 | 2024-08-01 12:24 | 0.38057 | 0.0036234 | 34 | 3571.0833 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 59 | INC 417004558 | 76 - Maharakeke | 76 - Maharakeke | 2024-08-01 10:37 | 2024-08-01 11:57 | 0.016955 | 0.00021314 | 2 | 159.1 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 60 | INC 417004670 | 14 - Waipukurau Urban | 14 - Waipukurau Urban | 2024-08-05 09:37 | 2024-08-05 15:52 | 0.079881 | 0.00021314 | 2 | 749.5667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 61 | INC 417004724 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-08-06 09:08 | 2024-08-06 14:43 | 0.95852 | 0.002984 | 28 | 8994.2833 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 62 | INC 417004818 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-08-08 09:27 | 2024-08-08 15:35 | 3.4526 | 0.013321 | 107 | 32397.0166 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 63 | INC 417004822 | 91 - Te Kura | 91 - Te Kura | 2024-08-08 11:56 | 2024-08-08 12:21 | 0.007721 | 0.00031971 | 3 | 72.45 | Unplanned | Other cause | Tap change for voltage | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 64 | INC 417004850 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2024-08-09 09:07 | 2024-08-09 15:48 | 1.2519 | 0.0031971 | 30 | 11746.75 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 65 | INC 417004898 | 75 - Paget Rd/Burnside | 75 - Paget Rd/Burnside | 2024-08-11 00:03 | 2024-08-11 00:27 | 0.61236 | 0.030053 | 282 | 5746.0498 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 66 | INC 417004899 | 75 - Paget Rd/Burnside | 75 - Paget Rd/Burnside | 2024-08-11 02:29 | 2024-08-11 07:04 | 0.24716 | 0.030586 | 282 | 2319.2165 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 67 | INC 417004931 | Wilder Rd | 45 - Porangahau/Wallingford | 2024-08-12 08:21 | 2024-08-12 08:31 | 0.46361 | 0.044013 | 413 | 4350.2665 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 68 | INC 417004931 | Wilder Rd | 46 - Cooks Tooth/Herbertville | 2024-08-12 08:21 | 2024-08-12 08:34 | 0.4998 | 0.03666 | 344 | 4689.8666 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 69 | INC 417004965 | 74 - Takapau Urban/Otawhao | 74 - Takapau Urban/Otawhao | 2024-08-12 17:53 | 2024-08-12 20:11 | 5.1579 | 0.043907 | 412 | 48398.7332 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 70 | INC 417004988 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-08-12 21:32 | 2024-08-12 22:08 | 0.02852 | 0.00085256 | 8 | 267.6167 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 71 | INC 417005010 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-08-13 09:08 | 2024-08-13 14:46 | 1.0075 | 0.002984 | 28 | 9453.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 72 | INC 417005023 | 04 - Burnside/Pukeora | 75 - Paget Rd/Burnside | 2024-08-13 11:57 | 2024-08-13 15:03 | 0.039601 | 0.00021314 | 2 | 371.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 73 | INC 417005096 | 75 - Paget Rd/Burnside | 75 - Paget Rd/Burnside | 2024-08-15 09:02 | 2024-08-15 17:33 | 0.25175 | 0.00095913 | 9 | 2362.25 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 74 | INC 417005097 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-08-15 09:18 | 2024-08-15 14:21 | 0.064738 | 0.00021314 | 2 | 607.4667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 75 | INC 417005266 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-08-19 09:16 | 2024-08-19 12:00 | 0.034987 | 0.00021314 | 2 | 328.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 76 | INC 417005312 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2024-08-19 18:59 | 2024-08-19 20:26 | 0.0093178 | 0.00010657 | 1 | 87.4333 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 77 | INC 417005328 | 14 - Waipukurau Urban | 14 - Waipukurau Urban | 2024-08-20 09:07 | 2024-08-20 13:54 | 2.4354 | 0.034742 | 282 | 22852.8332 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 78 | INC 417005424 | 75 - Paget Rd/Burnside | 75 - Paget Rd/Burnside | 2024-08-23 09:08 | 2024-08-23 12:52 | 0.45309 | 0.0020248 | 19 | 4251.5667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 79 | INC 417005467 | 13 - Tapairu/Mangatarata | 13 - Tapairu/Mangatarata | 2024-08-25 00:34 | 2024-08-25 02:21 | 0.45927 | 0.0044759 | 42 | 4309.55 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 80 | INC 417005556 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-08-27 09:15 | 2024-08-27 15:01 | 1.2154 | 0.0035168 | 33 | 11405.1333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 81 | INC 417005585 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-08-28 08:37 | 2024-08-28 12:24 | 0.024193 | 0.00010657 | 1 | 227.0167 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 82 | INC 417005613 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2024-08-29 09:13 | 2024-08-29 13:44 | 0.49015 | 0.0018117 | 17 | 4599.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 83 | INC 417005615 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-08-29 09:42 | 2024-08-29 12:47 | 0.019712 | 0.00010657 | 1 | 184.9667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 84 | INC 417005765 | 46 - Cooks Tooth/Herbertville | 46 - Cooks Tooth/Herbertville | 2024-09-01 16:07 | 2024-09-02 06:52 | 0.094346 | 0.00010657 | 1 | 885.3 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 85 | INC 417005777 | 88 - Omakere/Pourerere | 88 - Omakere/Pourerere | 2024-09-01 23:05 | 2024-09-01 23:50 | 0.0095274 | 0.00021314 | 2 | 89.4 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 86 | INC 417005839 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-09-03 09:01 | 2024-09-03 11:10 | 0.013756 | 0.00010657 | 1 | 129.0833 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 87 | INC 417005841 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-09-03 09:07 | 2024-09-03 12:07 | 0.019163 | 0.00010657 | 1 | 179.8167 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 88 | INC 417005843 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-09-03 09:23 | 2024-09-03 14:50 | 1.1849 | 0.0036234 | 34 | 11118.5666 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 89 | INC 417005913 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-09-04 09:07 | 2024-09-04 10:52 | 0.022362 | 0.00021314 | 2 | 209.8333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 90 | INC 417005952 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-09-05 09:30 | 2024-09-05 15:39 | 0.66851 | 0.0018117 | 17 | 6273 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 91 | INC 417006115 | 18 - Waipukurau South/Farm Rd | 18 - Waipukurau South/Farm Rd | 2024-09-11 09:39 | 2024-09-11 12:55 | 0.38533 | 0.0146 | 137 | 3615.7667 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 92 | INC 417006118 | 75 - Paget Rd/Burnside | 75 - Paget Rd/Burnside | 2024-09-11 09:03 | 2024-09-11 14:07 | 0.29178 | 0.00095913 | 9 | 2737.95 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 93 | INC 417006265 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-09-17 09:12 | 2024-09-17 10:24 | 0.015375 | 0.00021314 | 2 | 144.2667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 94 | INC 417006317 | 13 - Tapairu/Mangatarata | 13 - Tapairu/Mangatarata | 2024-09-18 06:15 | 2024-09-18 06:41 | 0.25868 | 0.009911 | 93 | 2427.3 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 95 | INC 417006371 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2024-09-19 09:13 | 2024-09-19 12:59 | 0.67447 | 0.002984 | 28 | 6328.9333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 96 | INC 417006403 | 74 - Takapau Urban/Otawhao | 74 - Takapau Urban/Otawhao | 2024-09-19 22:57 | 2024-09-20 03:48 | 1.8754 | 0.02952 | 129 | 17597.4832 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 97 | INC 417006414 | 91 - Te Kura | 91 - Te Kura | 2024-09-20 07:35 | 2024-09-20 10:23 | 0.071771 | 0.00042628 | 4 | 673.4667 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 98 | INC 417006443 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-09-20 19:19 | 2024-09-20 22:00 | 0.78299 | 0.0082059 | 77 | 7347.2 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 99 | INC 417006516 | 86 - Otane/Pukehou | 86 - Otane/Pukehou | 2024-09-24 08:33 | 2024-09-24 17:32 | 3.3434 | 0.037832 | 207 | 31372.3666 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 100 | INC 417006529 | 46 - Cooks Tooth/Herbertville | 46 - Cooks Tooth/Herbertville | 2024-09-24 09:53 | 2024-09-24 12:58 | 0.028422 | 0.00042628 | 2 | 266.7 | Unplanned | Other cause | Tap change for voltage | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 101 | INC 417006538 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2024-09-24 12:49 | 2024-09-24 16:39 | 2.5512 | 0.061278 | 414 | 23938.8665 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 102 | INC 417006540 | 46 - Cooks Tooth/Herbertville | 46 - Cooks Tooth/Herbertville | 2024-09-24 12:56 | 2024-09-24 12:58 | 0.043829 | 0.021207 | 199 | 411.2665 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 103 | INC 417006541 | 03 - Argyll/Ruataniwha | 03 - Argyll/Ruataniwha | 2024-09-24 13:06 | 2024-09-24 16:29 | 0.89502 | 0.0058614 | 55 | 8398.45 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 104 | INC 417006579 | 46 - Cooks Tooth/Herbertville | 46 - Cooks Tooth/Herbertville | 2024-09-24 17:57 | 2024-09-24 21:01 | 0.23458 | 0.0012788 | 12 | 2201.2 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 105 | INC 417006658 | 03 - Argyll/Ruataniwha | 03 - Argyll/Ruataniwha | 2024-09-26 09:38 | 2024-09-26 13:16 | 1.0421 | 0.0047957 | 45 | 9778.25 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 106 | INC 417006784 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-10-01 09:11 | 2024-10-01 14:24 | 1.4528 | 0.0047957 | 45 | 13632.05 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 107 | INC 417006784 | 83 - Omakere/Elsthorpe | 88 - Omakere/Pourerere | 2024-10-01 09:00 | 2024-10-01 14:35 | 11.9436 | 0.035808 | 336 | 112072.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 108 | INC 417006945 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-11-12 09:11 | 2024-11-12 14:19 | 0.65647 | 0.0021314 | 20 | 6160 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 109 | INC 417007023 | 91 - Te Kura | 91 - Te Kura | 2024-11-14 10:04 | 2024-11-14 13:08 | 0.039122 | 0.00021314 | 2 | 367.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 110 | INC 417007033 | 75 - Paget Rd/Burnside | 75 - Paget Rd/Burnside | 2024-11-14 14:24 | 2024-11-14 14:28 | 0.00042628 | 0.00010657 | 1 | 4 | Unplanned | Other cause | Tap change for voltage | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 111 | INC 417007076 | 73 - Silver Fern 2 | 71 - Silver Fern 1 | 2024-11-15 11:03 | 2024-11-15 12:30 | 0.0021829 | 0.00021314 | 1 | 20.4833 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 112 | INC 417007290 | 46 - Cooks Tooth/Herbertville | 46 - Cooks Tooth/Herbertville | 2024-11-23 10:54 | 2024-11-23 11:10 | 0.16325 | 0.021207 | 199 | 1531.85 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 113 | INC 417007293 | 76 - Maharakeke | 76 - Maharakeke | 2024-11-23 12:25 | 2024-11-23 12:30 | 0.0009911 | 0.00021314 | 2 | 9.3 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 114 | INC 417007329 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2024-11-24 13:09 | 2024-11-24 13:11 | 0.1027 | 0.044013 | 413 | 963.6665 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 115 | INC 417007329 | 45 - Porangahau/Wallingford | 46 - Cooks Tooth/Herbertville | 2024-11-24 13:00 | 2024-11-24 17:37 | 1.196 | 0.041562 | 199 | 11223.0332 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 116 | INC 417007387 | 76 - Maharakeke | 76 - Maharakeke | 2024-11-26 09:17 | 2024-11-26 15:32 | 0.194 | 0.00053285 | 5 | 1820.3667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 117 | INC 417007426 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-11-27 09:03 | 2024-11-27 14:51 | 1.0774 | 0.0031971 | 30 | 10110.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 118 | INC 417007485 | 46 - Cooks Tooth/Herbertville | 46 - Cooks Tooth/Herbertville | 2024-11-29 00:34 | 2024-11-29 00:36 | 0.016648 | 0.0096979 | 91 | 156.2166 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 119 | INC 417007500 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-11-29 09:09 | 2024-11-29 11:32 | 0.030326 | 0.00021314 | 2 | 284.5667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 120 | INC 417007504 | 46 - Cooks Tooth/Herbertville | 46 - Cooks Tooth/Herbertville | 2024-11-29 09:45 | 2024-11-29 19:37 | 0.063161 | 0.00010657 | 1 | 592.6667 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 121 | INC 417007511 | 75 - Paget Rd/Burnside | 75 - Paget Rd/Burnside | 2024-11-29 11:18 | 2024-11-29 11:59 | 0.0088418 | 0.00021314 | 2 | 82.9667 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 122 | INC 417007520 | 91 - Te Kura | 91 - Te Kura | 2024-11-29 13:53 | 2024-11-29 17:14 | 0.39709 | 0.0020248 | 19 | 3726.1167 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 123 | INC 417007527 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2024-07-02 10:40 | 2024-11-29 17:59 | 1.3257 | 0.015879 | 143 | 12439.7666 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 124 | INC 417007595 | 03 - Argyll/Ruataniwha | 03 - Argyll/Ruataniwha | 2024-12-02 09:36 | 2024-12-02 12:52 | 0.062583 | 0.00031971 | 3 | 587.25 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 125 | INC 417007614 | 46 - Cooks Tooth/Herbertville | 46 - Cooks Tooth/Herbertville | 2024-12-04 14:31 | 2024-12-04 17:38 | 0.35801 | 0.0019183 | 18 | 3359.4 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 126 | INC 417007646 | 85 - Waipawa Urban | 85 - Waipawa Urban | 2024-12-05 09:06 | 2024-12-05 12:18 | 1.3581 | 0.0072468 | 68 | 12744.05 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 127 | INC 417007648 | 18 - Waipukurau South/Farm Rd | 15 - Waipukurau CBD | 2024-12-05 09:07 | 2024-12-05 16:41 | 3.9013 | 0.011616 | 109 | 36607.7666 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 128 | INC 417007732 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2024-12-06 15:47 | 2024-12-06 17:40 | 0.21603 | 0.0019183 | 18 | 2027.1 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 129 | INC 417007797 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-12-09 09:09 | 2024-12-09 14:01 | 0.82424 | 0.002984 | 28 | 7734.2167 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 130 | INC 417007809 | 15 - Waipukurau CBD | 15 - Waipukurau CBD | 2024-12-09 12:24 | 2024-12-09 14:33 | 0.53879 | 0.0041562 | 39 | 5055.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 131 | INC 417007846 | 85 - Waipawa Urban | 85 - Waipawa Urban | 2024-12-10 09:21 | 2024-12-10 14:31 | 2.6479 | 0.0085256 | 80 | 24846.6666 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 132 | INC 417007895 | 88 - Omakere/Pourerere | 88 - Omakere/Pourerere | 2024-12-11 09:09 | 2024-12-11 14:34 | 6.8267 | 0.021421 | 201 | 64058.3665 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 133 | INC 417007928 | 46 - Cooks Tooth/Herbertville | 46 - Cooks Tooth/Herbertville | 2024-12-12 09:05 | 2024-12-12 13:40 | 0.38053 | 0.0013854 | 13 | 3570.6667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 134 | INC 417007930 | 01 - OngaOnga/Ashley Clinton | 01 - OngaOnga/Ashley Clinton | 2024-12-12 09:12 | 2024-12-12 11:32 | 0.014964 | 0.00010657 | 1 | 140.4167 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 135 | INC 417007974 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-12-13 09:18 | 2024-12-13 11:24 | 0.14765 | 0.0011723 | 11 | 1385.45 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 136 | INC 417007979 | 01 - OngaOnga/Ashley Clinton | 01 - OngaOnga/Ashley Clinton | 2024-12-13 12:24 | 2024-12-13 12:59 | 0.003698 | 0.00010657 | 1 | 34.7 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 137 | INC 417008091 | 02 - Wakarara/Tikokino | 02 - Wakarara/Tikokino | 2024-12-16 22:54 | 2024-12-17 03:27 | 0.97072 | 0.010337 | 63 | 9108.7166 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 138 | INC 417008121 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2024-12-17 09:10 | 2024-12-17 15:05 | 0.37912 | 0.0010657 | 10 | 3557.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 139 | INC 417008254 | 88 - Omakere/Pourerere | 88 - Omakere/Pourerere | 2024-12-19 09:06 | 2024-12-19 10:13 | 0.035923 | 0.00053285 | 5 | 337.0833 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 140 | INC 417008258 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2024-12-19 09:22 | 2024-12-19 12:11 | 0.035918 | 0.00021314 | 2 | 337.0333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 141 | INC 417008267 | 88 - Omakere/Pourerere | 88 - Omakere/Pourerere | 2024-12-19 10:07 | 2024-12-19 12:30 | 0.16479 | 0.0055416 | 29 | 1546.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 142 | INC 417008367 | 03 - Argyll/Ruataniwha | 03 - Argyll/Ruataniwha | 2024-12-21 15:50 | 2024-12-21 15:55 | 0.059811 | 0.01833 | 172 | 561.2333 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 143 | INC 417008422 | 02 - Wakarara/Tikokino | 02 - Wakarara/Tikokino | 2024-12-21 22:12 | 2024-12-22 13:31 | 0.17745 | 0.0028774 | 14 | 1665.1 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 144 | INC 417008599 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2024-12-27 | 2024-12-27 05:45 | 1.1093 | 0.016625 | 97 | 10409.2832 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 145 | INC 417008600 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2024-12-27 00:07 | 2024-12-27 00:10 | 0.048766 | 0.01524 | 143 | 457.6 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 146 | INC 417008604 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2024-12-27 02:14 | 2024-12-27 02:20 | 0.066914 | 0.010764 | 101 | 627.8833 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 147 | INC 417008674 | 02 - Wakarara/Tikokino | 02 - Wakarara/Tikokino | 2024-12-27 16:19 | 2024-12-27 19:18 | 0.7803 | 0.0043694 | 41 | 7321.9167 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 148 | INC 417008776 | 86 - Otane/Pukehou | 86 - Otane/Pukehou | 2024-12-30 08:29 | 2024-12-30 09:06 | 0.0038845 | 0.00010657 | 1 | 36.45 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 149 | INC 417008896 | 88 - Omakere/Pourerere | 88 - Omakere/Pourerere | 2025-01-02 12:33 | 2025-01-02 13:24 | 0.0054599 | 0.00010657 | 1 | 51.2333 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 150 | INC 417008963 | 88 - Omakere/Pourerere | 88 - Omakere/Pourerere | 2025-01-04 17:35 | 2025-01-04 20:09 | 0.081881 | 0.00053285 | 5 | 768.3333 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 151 | INC 417008996 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2025-01-06 09:09 | 2025-01-06 11:13 | 0.013115 | 0.00010657 | 1 | 123.0667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 152 | INC 417009086 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2025-01-17 09:03 | 2025-01-17 13:30 | 0.45501 | 0.0017051 | 16 | 4269.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 153 | INC 417009138 | 74 - Takapau Urban/Otawhao | 74 - Takapau Urban/Otawhao | 2025-02-28 11:03 | 2025-02-28 12:07 | 0.095586 | 0.001492 | 14 | 896.9333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 154 | INC 417009170 | 76 - Maharakeke | 76 - Maharakeke | 2025-03-01 16:50 | 2025-03-01 16:53 | 0.00072468 | 0.00021314 | 2 | 6.8 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 155 | INC 417009253 | 74 - Takapau Urban/Otawhao | 74 - Takapau Urban/Otawhao | 2025-03-06 09:05 | 2025-03-06 13:16 | 0.21421 | 0.00085256 | 8 | 2010 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 156 | INC 417009255 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2025-03-06 09:20 | 2025-03-06 14:57 | 0.93254 | 0.012575 | 71 | 8750.4999 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 157 | INC 417009293 | 19 - Hatuma/Wanstead | 45 - Porangahau/Wallingford | 2025-03-07 10:48 | 2025-03-07 11:25 | 0.0039733 | 0.00010657 | 1 | 37.2833 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 158 | INC 417009385 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2025-03-11 09:51 | 2025-03-11 15:53 | 3.6994 | 0.010231 | 96 | 34713.65 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 159 | INC 417009429 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2025-03-12 09:30 | 2025-03-12 15:20 | 0.95936 | 0.012575 | 71 | 9002.1167 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 160 | INC 417009462 | 46 - Cooks Tooth/Herbertville | 46 - Cooks Tooth/Herbertville | 2025-03-12 21:44 | 2025-03-13 03:14 | 4.3212 | 0.021207 | 199 | 40548.2666 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 161 | INC 417009498 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2025-03-14 06:23 | 2025-03-14 06:26 | 0.06861 | 0.044227 | 415 | 643.7998 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 162 | INC 417009507 | 74 - Takapau Urban/Otawhao | 74 - Takapau Urban/Otawhao | 2025-03-14 10:46 | 2025-03-14 11:54 | 0.0072787 | 0.00010657 | 1 | 68.3 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 163 | INC 417009538 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2025-03-15 12:37 | 2025-03-15 15:54 | 0.69287 | 0.0035168 | 33 | 6501.55 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 164 | INC 417009544 | 85 - Waipawa Urban | 85 - Waipawa Urban | 2025-03-16 07:22 | 2025-03-16 08:47 | 3.4009 | 0.085789 | 805 | 31912.3829 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 165 | INC 417009574 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2025-03-17 09:28 | 2025-03-17 13:45 | 0.41088 | 0.0015986 | 15 | 3855.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 166 | INC 417009606 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2025-03-18 09:47 | 2025-03-18 11:51 | 0.026419 | 0.00021314 | 2 | 247.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 167 | INC 417009639 | 03 - Argyll/Ruataniwha | 03 - Argyll/Ruataniwha | 2025-03-19 08:47 | 2025-03-19 09:50 | 0.02704 | 0.00042628 | 4 | 253.7333 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 168 | INC 417009669 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2025-03-20 01:17 | 2025-03-20 01:32 | 0.20979 | 0.04039 | 379 | 1968.5665 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 169 | INC 417009765 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2025-03-22 09:28 | 2025-03-22 14:46 | 0.86147 | 0.012575 | 71 | 8083.5666 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 170 | INC 417009767 | 74 - Takapau Urban/Otawhao | 74 - Takapau Urban/Otawhao | 2025-03-22 10:32 | 2025-03-22 13:15 | 0.97297 | 0.0059679 | 56 | 9129.8666 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 171 | INC 417009811 | 46 - Cooks Tooth/Herbertville | 46 - Cooks Tooth/Herbertville | 2025-03-24 09:49 | 2025-03-24 10:09 | 0.040632 | 0.0020248 | 19 | 381.2667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 172 | INC 417009835 | 19 - Hatuma/Wanstead | 45 - Porangahau/Wallingford | 2025-03-26 09:10 | 2025-03-26 13:25 | 0.51647 | 0.0020248 | 19 | 4846.2667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 173 | INC 417009908 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2025-03-28 09:09 | 2025-03-28 11:48 | 0.01695 | 0.00010657 | 1 | 159.05 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 174 | INC 417009912 | 13 - Tapairu/Mangatarata | 13 - Tapairu/Mangatarata | 2025-03-28 13:10 | 2025-03-28 16:07 | 0.13193 | 0.010764 | 101 | 1237.9333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 175 | INC 421003346 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2024-04-03 09:10 | 2024-04-03 12:51 | 0.58996 | 0.0033037 | 31 | 5535.8667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 176 | INC 421003381 | 46 - Cooks Tooth/Herbertville | 46 - Cooks Tooth/Herbertville | 2024-04-04 09:02 | 2024-04-04 14:16 | 0.066979 | 0.00021314 | 2 | 628.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 177 | INC 421003383 | 02 - Wakarara/Tikokino | 02 - Wakarara/Tikokino | 2024-04-04 09:20 | 2024-04-04 14:07 | 0.76422 | 0.0047957 | 45 | 7171.0667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 178 | INC 421003507 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-04-08 09:15 | 2024-04-08 15:42 | 1.1951 | 0.0030905 | 29 | 11213.8167 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 179 | INC 421003511 | 13 - Tapairu/Mangatarata | 13 - Tapairu/Mangatarata | 2024-04-08 10:09 | 2024-04-08 12:42 | 0.0163 | 0.00010657 | 1 | 152.95 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 180 | INC 421003531 | 46 - Cooks Tooth/Herbertville | 46 - Cooks Tooth/Herbertville | 2024-04-17 09:03 | 2024-04-17 14:19 | 3.099 | 0.0098044 | 92 | 29079.6666 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 181 | INC 421003584 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2024-05-08 09:19 | 2024-05-08 13:39 | 0.38881 | 0.001492 | 14 | 3648.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 182 | INC 421003619 | 18 - Waipukurau South/Farm Rd | 18 - Waipukurau South/Farm Rd | 2024-05-09 09:07 | 2024-05-09 13:07 | 0.051072 | 0.00021314 | 2 | 479.2333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 183 | INC 421003621 | 78 - Hinerangi | 78 - Hinerangi | 2024-05-09 09:11 | 2024-05-09 13:31 | 0.24906 | 0.00095913 | 9 | 2337.0333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 184 | INC 421003623 | 02 - Wakarara/Tikokino | 02 - Wakarara/Tikokino | 2024-05-09 09:18 | 2024-05-09 14:36 | 1.5573 | 0.0049022 | 46 | 14612.6666 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 185 | INC 421003663 | 78 - Hinerangi | 78 - Hinerangi | 2024-05-10 09:13 | 2024-05-10 15:08 | 0.45473 | 0.0012788 | 12 | 4266.9667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 186 | INC 421003784 | 76 - Maharakeke | 78 - Hinerangi | 2024-05-22 09:12 | 2024-05-22 14:33 | 0.21116 | 0.00074599 | 7 | 1981.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 187 | INC 421003786 | 02 - Wakarara/Tikokino | 02 - Wakarara/Tikokino | 2024-05-22 09:13 | 2024-05-22 11:48 | 0.7254 | 0.0046891 | 44 | 6806.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 188 | INC 421003790 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2024-05-22 09:23 | 2024-05-22 13:27 | 0.026033 | 0.00010657 | 1 | 244.2833 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 189 | INC 421003928 | 91 - Te Kura | 91 - Te Kura | 2024-05-24 09:03 | 2024-05-24 11:32 | 0.015851 | 0.00010657 | 1 | 148.7333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 190 | INC 421004089 | 88 - Omakere/Pourerere | 88 - Omakere/Pourerere | 2024-05-28 08:32 | 2024-05-28 09:34 | 0.0065647 | 0.00010657 | 1 | 61.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 191 | INC 421004132 | 13 - Tapairu/Mangatarata | 13 - Tapairu/Mangatarata | 2024-05-29 02:29 | 2024-05-29 03:22 | 0.30331 | 0.0059679 | 56 | 2846.0833 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 192 | INC 421004139 | 03 - Argyll/Ruataniwha | 03 - Argyll/Ruataniwha | 2024-05-29 09:04 | 2024-05-29 12:59 | 0.70307 | 0.002984 | 28 | 6597.2666 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 193 | INC 421004141 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2024-05-29 09:05 | 2024-05-29 12:33 | 0.20579 | 0.0036234 | 22 | 1931.0667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 194 | INC 421004219 | 04 - Burnside/Pukeora | 04 - Burnside/Pukeora | 2024-05-30 09:00 | 2024-05-30 11:49 | 0.2689 | 0.0020248 | 19 | 2523.25 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 195 | INC 421004229 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2024-05-30 10:31 | 2024-05-30 12:50 | 0.23664 | 0.0017051 | 16 | 2220.5333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 196 | INC 421004257 | 86 - Otane/Pukehou | 86 - Otane/Pukehou | 2024-05-31 09:00 | 2024-05-31 12:41 | 0.0534 | 0.0063942 | 60 | 501.0833 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 197 | INC 421004258 | 18 - Waipukurau South/Farm Rd | 18 - Waipukurau South/Farm Rd | 2024-05-31 09:01 | 2024-05-31 11:02 | 0.33379 | 0.0027708 | 26 | 3132.1333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 198 | INC 421004262 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2024-05-31 09:51 | 2024-05-31 15:47 | 0.64481 | 0.0018117 | 17 | 6050.5833 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 199 | INC 421004317 | 88 - Omakere/Pourerere | 88 - Omakere/Pourerere | 2024-06-02 09:01 | 2024-06-02 10:15 | 0.24325 | 0.019502 | 104 | 2282.5666 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 200 | INC 421004419 | 91 - Te Kura | 91 - Te Kura | 2024-06-05 09:04 | 2024-06-05 14:20 | 1.5125 | 0.0047957 | 45 | 14192.25 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 201 | INC 421004423 | 88 - Omakere/Pourerere | 88 - Omakere/Pourerere | 2024-06-05 09:29 | 2024-06-05 14:46 | 0.43881 | 0.0013854 | 13 | 4117.5333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 202 | INC 421004424 | 18 - Waipukurau South/Farm Rd | 18 - Waipukurau South/Farm Rd | 2024-06-05 09:33 | 2024-06-05 11:42 | 0.47986 | 0.00373 | 35 | 4502.75 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 203 | INC 421004460 | 18 - Waipukurau South/Farm Rd | 19 - Hatuma/Wanstead | 2024-06-06 09:11 | 2024-06-06 16:14 | 1.0818 | 0.0025577 | 24 | 10151.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 204 | INC 421004496 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-06-07 09:22 | 2024-06-07 13:05 | 0.57207 | 0.0025577 | 24 | 5368 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 205 | INC 421004613 | 03 - Argyll/Ruataniwha | 03 - Argyll/Ruataniwha | 2024-06-11 09:01 | 2024-06-11 12:07 | 1.1332 | 0.0060745 | 57 | 10633.35 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 206 | INC 421004615 | 88 - Omakere/Pourerere | 88 - Omakere/Pourerere | 2024-06-11 09:20 | 2024-06-11 14:21 | 0.2028 | 0.0082059 | 40 | 1903 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 207 | INC 421004640 | 88 - Omakere/Pourerere | 88 - Omakere/Pourerere | 2024-06-12 09:11 | 2024-06-12 13:29 | 0.85378 | 0.0033037 | 31 | 8011.4333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 208 | INC 421004734 | 88 - Omakere/Pourerere | 88 - Omakere/Pourerere | 2024-06-14 09:20 | 2024-06-14 11:30 | 0.16655 | 0.0012788 | 12 | 1562.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 209 | INC 421004742 | 91 - Te Kura | 91 - Te Kura | 2024-06-14 10:38 | 2024-06-14 12:39 | 0.012865 | 0.00010657 | 1 | 120.7167 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 210 | INC 421004771 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2024-06-14 15:36 | 2024-06-14 15:38 | 0.0043907 | 0.0025577 | 24 | 41.2 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 211 | INC 421004882 | 91 - Te Kura | 91 - Te Kura | 2024-06-17 08:43 | 2024-06-17 10:01 | 0.10701 | 0.0015986 | 15 | 1004.1167 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 212 | INC 421004920 | 13 - Tapairu/Mangatarata | 03 - Argyll/Ruataniwha | 2024-06-18 09:06 | 2024-06-18 15:02 | 0.037907 | 0.00010657 | 1 | 355.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 213 | INC 421004920 | 13 - Tapairu/Mangatarata | 13 - Tapairu/Mangatarata | 2024-06-18 09:21 | 2024-06-18 14:53 | 0.56624 | 0.0017051 | 16 | 5313.3333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 214 | INC 421004961 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2024-06-20 10:12 | 2024-06-20 11:45 | 0.19955 | 0.002984 | 28 | 1872.5 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 215 | INC 421004993 | 88 - Omakere/Pourerere | 88 - Omakere/Pourerere | 2024-06-21 09:10 | 2024-06-21 11:35 | 0.046374 | 0.00031971 | 3 | 435.15 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 216 | INC 421004994 | 88 - Omakere/Pourerere | 88 - Omakere/Pourerere | 2024-06-21 09:11 | 2024-06-21 12:32 | 0.1072 | 0.00053285 | 5 | 1005.9167 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 217 | INC 421005038 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2024-07-17 09:23 | 2024-07-17 14:54 | 0.38734 | 0.0011723 | 11 | 3634.5833 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 218 | INC 421005040 | 75 - Paget Rd/Burnside | 75 - Paget Rd/Burnside | 2024-07-17 09:46 | 2024-07-17 13:57 | 0.50763 | 0.0020248 | 19 | 4763.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 219 | INC 421005070 | 88 - Omakere/Pourerere | 88 - Omakere/Pourerere | 2024-07-18 09:14 | 2024-07-18 13:54 | 0.18601 | 0.0026643 | 15 | 1745.4333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 220 | INC 421005097 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-07-19 09:11 | 2024-07-19 13:04 | 0.27267 | 0.0011723 | 11 | 2558.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 221 | INC 421005148 | Wilder Rd | 45 - Porangahau/Wallingford | 2024-08-01 00:32 | 2024-08-01 00:48 | 0.70927 | 0.044013 | 413 | 6655.4164 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 222 | INC 421005148 | Wilder Rd | 46 - Cooks Tooth/Herbertville | 2024-08-01 00:32 | 2024-08-01 00:55 | 0.83707 | 0.03666 | 344 | 7854.6666 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 223 | INC 421005183 | 85 - Waipawa Urban | 85 - Waipawa Urban | 2024-08-21 09:07 | 2024-08-21 11:20 | 1.1335 | 0.0085256 | 80 | 10636 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 224 | INC 421005198 | 86 - Otane/Pukehou | 86 - Otane/Pukehou | 2024-10-02 09:02 | 2024-10-02 16:05 | 1.2691 | 0.0090585 | 60 | 11908.7167 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 225 | INC 421005202 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2024-10-02 09:09 | 2024-10-02 10:21 | 0.13824 | 0.0019183 | 18 | 1297.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 226 | INC 421005205 | 46 - Cooks Tooth/Herbertville | 46 - Cooks Tooth/Herbertville | 2024-10-02 09:22 | 2024-10-02 12:27 | 0.01974 | 0.00010657 | 1 | 185.2333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 227 | INC 421005242 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-10-03 06:26 | 2024-10-03 14:16 | 1.8947 | 0.06277 | 379 | 17779.2 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 228 | INC 421005243 | 88 - Omakere/Pourerere | 88 - Omakere/Pourerere | 2024-10-03 06:27 | 2024-10-03 06:47 | 0.43673 | 0.038685 | 363 | 4098.0498 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 229 | INC 421005351 | 03 - Argyll/Ruataniwha | 03 - Argyll/Ruataniwha | 2024-10-09 12:20 | 2024-10-09 12:42 | 0.0048205 | 0.00021314 | 2 | 45.2333 | Unplanned | Other cause | No cause detail captured | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 230 | INC 421005419 | 86 - Otane/Pukehou | 86 - Otane/Pukehou | 2024-10-09 09:01 | 2024-10-09 14:20 | 1.0893 | 0.0063942 | 60 | 10221.2166 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 231 | INC 421005421 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-10-09 09:02 | 2024-10-09 13:46 | 0.66452 | 0.0023445 | 22 | 6235.5333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 232 | INC 421005456 | 46 - Cooks Tooth/Herbertville | 46 - Cooks Tooth/Herbertville | 2024-10-10 09:21 | 2024-10-10 12:57 | 4.5805 | 0.021207 | 199 | 42980.6833 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 233 | INC 421005575 | 75 - Paget Rd/Burnside | 75 - Paget Rd/Burnside | 2024-10-14 22:10 | 2024-10-14 22:20 | 0.0010675 | 0.00010657 | 1 | 10.0167 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 234 | INC 421005606 | 74 - Takapau Urban/Otawhao | 74 - Takapau Urban/Otawhao | 2024-10-14 21:26 | 2024-10-14 21:44 | 0.0038827 | 0.00021314 | 2 | 36.4333 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 235 | INC 421005620 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-10-15 09:03 | 2024-10-15 13:23 | 0.30533 | 0.0011723 | 11 | 2865.0667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 236 | INC 421005663 | 85 - Waipawa Urban | 13 - Tapairu/Mangatarata | 2024-10-16 09:06 | 2024-10-16 13:14 | 0.13224 | 0.00053285 | 5 | 1240.9167 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 237 | INC 421005663 | 85 - Waipawa Urban | 85 - Waipawa Urban | 2024-10-16 09:17 | 2024-10-16 13:05 | 0.24316 | 0.0010657 | 10 | 2281.6667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 238 | INC 421005665 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-10-16 09:07 | 2024-10-16 11:08 | 0.012881 | 0.00010657 | 1 | 120.8667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 239 | INC 421005700 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-10-17 09:05 | 2024-10-17 12:31 | 0.043949 | 0.00021314 | 2 | 412.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 240 | INC 421005808 | 86 - Otane/Pukehou | 86 - Otane/Pukehou | 2024-10-22 08:34 | 2024-10-22 15:19 | 2.7122 | 0.037832 | 207 | 25450.1333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 241 | INC 421005843 | 02 - Wakarara/Tikokino | 02 - Wakarara/Tikokino | 2024-10-23 09:29 | 2024-10-23 15:28 | 0.038275 | 0.00010657 | 1 | 359.15 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 242 | INC 421005848 | 15 - Waipukurau CBD | 15 - Waipukurau CBD | 2024-10-23 10:12 | 2024-10-23 11:32 | 4.4855 | 0.10082 | 882 | 42089.3994 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 243 | INC 421005953 | 46 - Cooks Tooth/Herbertville | 46 - Cooks Tooth/Herbertville | 2024-10-27 14:30 | 2024-10-27 14:31 | 0.025577 | 0.021314 | 200 | 240 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 244 | INC 421006024 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-10-30 09:35 | 2024-10-30 11:45 | 0.041775 | 0.00031971 | 3 | 392 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 245 | INC 421006053 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-10-31 09:01 | 2024-10-31 14:52 | 1.3858 | 0.0039431 | 37 | 13003.65 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 246 | INC 421006085 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-11-01 09:45 | 2024-11-01 15:36 | 0.63544 | 0.0018117 | 17 | 5962.6833 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 247 | INC 421006170 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2024-11-04 17:09 | 2024-11-04 17:36 | 0.0028934 | 0.00010657 | 1 | 27.15 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 248 | INC 421006177 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2024-11-05 00:27 | 2024-11-05 15:49 | 4.134 | 0.10359 | 635 | 38791.1328 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 249 | INC 421006188 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-11-05 09:02 | 2024-11-05 13:26 | 0.1124 | 0.00042628 | 4 | 1054.7333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 250 | INC 421006216 | 18 - Waipukurau South/Farm Rd | 18 - Waipukurau South/Farm Rd | 2024-11-06 21:51 | 2024-11-06 22:07 | 0.045271 | 0.0028774 | 27 | 424.8 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 251 | INC 421006223 | 18 - Waipukurau South/Farm Rd | 18 - Waipukurau South/Farm Rd | 2024-11-07 08:47 | 2024-11-07 13:57 | 2.0885 | 0.010231 | 78 | 19597.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 252 | INC 421006345 | 83 - Omakere/Elsthorpe | 83 - Omakere/Elsthorpe | 2024-11-11 09:21 | 2024-11-11 12:30 | 0.060436 | 0.00031971 | 3 | 567.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 253 | INC 421006392 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2024-12-03 09:01 | 2024-12-03 11:33 | 0.032301 | 0.00021314 | 2 | 303.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 254 | INC 421006393 | 46 - Cooks Tooth/Herbertville | 46 - Cooks Tooth/Herbertville | 2024-12-03 09:04 | 2024-12-03 12:56 | 0.024714 | 0.00010657 | 1 | 231.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 255 | INC 421006398 | 15 - Waipukurau CBD | 15 - Waipukurau CBD | 2024-12-03 09:12 | 2024-12-03 15:52 | 3.1992 | 0.0079928 | 75 | 30019.6833 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 256 | INC 421006431 | 86 - Otane/Pukehou | 86 - Otane/Pukehou | 2024-12-04 05:55 | 2024-12-04 18:45 | 0.027555 | 0.00021314 | 1 | 258.5667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 257 | INC 421006447 | 85 - Waipawa Urban | 85 - Waipawa Urban | 2024-12-04 09:26 | 2024-12-04 13:57 | 2.3038 | 0.0085256 | 80 | 21617.3333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 258 | INC 421006595 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2025-01-10 09:06 | 2025-01-10 11:36 | 0.015954 | 0.00010657 | 1 | 149.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 259 | INC 421006691 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2025-01-14 09:08 | 2025-01-14 13:17 | 0.053015 | 0.00021314 | 2 | 497.4667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 260 | INC 421006693 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2025-01-14 09:14 | 2025-01-14 13:25 | 0.026747 | 0.00010657 | 1 | 250.9833 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 261 | INC 421006694 | 03 - Argyll/Ruataniwha | 03 - Argyll/Ruataniwha | 2025-01-14 09:17 | 2025-01-14 11:45 | 0.01576 | 0.00010657 | 1 | 147.8833 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 262 | INC 421006759 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2025-01-16 09:19 | 2025-01-16 13:38 | 0.55182 | 0.0021314 | 20 | 5178 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 263 | INC 421006761 | 03 - Argyll/Ruataniwha | 03 - Argyll/Ruataniwha | 2025-01-16 09:26 | 2025-01-16 10:36 | 0.022268 | 0.00031971 | 3 | 208.95 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 264 | INC 421006793 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2025-01-21 09:16 | 2025-01-21 12:07 | 0.43903 | 0.0025577 | 24 | 4119.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 265 | INC 421006824 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2025-01-22 09:24 | 2025-01-22 14:16 | 0.9655 | 0.0033037 | 31 | 9059.75 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 266 | INC 421006864 | 04 - Burnside/Pukeora | 04 - Burnside/Pukeora | 2025-01-23 19:03 | 2025-01-23 19:16 | 0.0042735 | 0.00031971 | 3 | 40.1 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 267 | INC 421006878 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2025-01-24 09:27 | 2025-01-24 13:45 | 0.11025 | 0.00042628 | 4 | 1034.5333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 268 | INC 421006899 | 20 - Ovation | 20 - Ovation | 2025-01-25 07:00 | 2025-01-25 16:20 | 0.059656 | 0.00010657 | 1 | 559.7833 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 269 | INC 421007035 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2025-01-29 09:00 | 2025-01-29 13:46 | 0.1669 | 0.012575 | 61 | 1566.0833 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 270 | INC 421007084 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2025-01-30 09:18 | 2025-01-30 14:52 | 0.39143 | 0.0011723 | 11 | 3672.9833 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 271 | INC 421007292 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2025-02-04 09:06 | 2025-02-04 14:36 | 0.49061 | 0.001492 | 14 | 4603.65 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 272 | INC 421007341 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2025-02-05 09:26 | 2025-02-05 12:02 | 0.033236 | 0.00021314 | 2 | 311.8667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 273 | INC 421007493 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2025-02-10 08:58 | 2025-02-10 12:23 | 0.02182 | 0.00010657 | 1 | 204.75 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 274 | INC 421007533 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2025-02-11 09:04 | 2025-02-11 13:18 | 0.027101 | 0.00010657 | 1 | 254.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 275 | INC 421007535 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2025-02-11 09:05 | 2025-02-11 10:23 | 0.0082698 | 0.00010657 | 1 | 77.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 276 | INC 421007541 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2025-02-11 09:28 | 2025-02-11 12:43 | 0.020721 | 0.00010657 | 1 | 194.4333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 277 | INC 421007591 | 19 - Hatuma/Wanstead | 45 - Porangahau/Wallingford | 2025-02-13 09:09 | 2025-02-13 13:35 | 0.53864 | 0.0020248 | 19 | 5054.3667 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 278 | INC 421007621 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2025-02-14 09:12 | 2025-02-14 12:32 | 0.1069 | 0.00053285 | 5 | 1003.0833 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 279 | INC 421007682 | 46 - Cooks Tooth/Herbertville | 46 - Cooks Tooth/Herbertville | 2025-02-17 08:04 | 2025-02-17 09:04 | 0.084118 | 0.0013854 | 13 | 789.3167 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 280 | INC 421007790 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2025-02-19 11:36 | 2025-02-19 16:22 | 0.030484 | 0.00010657 | 1 | 286.05 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 281 | INC 421007792 | 74 - Takapau Urban/Otawhao | 74 - Takapau Urban/Otawhao | 2025-02-19 12:57 | 2025-02-19 13:42 | 0.0048454 | 0.00010657 | 1 | 45.4667 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 282 | INC 421007829 | 74 - Takapau Urban/Otawhao | 74 - Takapau Urban/Otawhao | 2025-02-20 13:03 | 2025-02-20 13:36 | 0.032259 | 0.00095913 | 9 | 302.7 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 283 | INC 421007902 | 88 - Omakere/Pourerere | 88 - Omakere/Pourerere | 2025-02-22 19:57 | 2025-02-22 20:12 | 0.16847 | 0.011083 | 104 | 1580.8 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 284 | INC 421007908 | 03 - Argyll/Ruataniwha | 03 - Argyll/Ruataniwha | 2025-02-23 07:40 | 2025-02-23 07:45 | 0.052443 | 0.01833 | 172 | 492.1 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 285 | INC 421007977 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2025-02-25 09:13 | 2025-02-25 14:47 | 2.5251 | 0.0075665 | 71 | 23693.8833 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 286 | INC 421008002 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2025-02-26 09:00 | 2025-02-26 14:37 | 1.4226 | 0.01492 | 89 | 13349.0666 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 287 | INC 421008038 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2025-02-27 09:13 | 2025-02-27 15:12 | 0.98895 | 0.012575 | 71 | 9279.85 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 288 | INC 421008043 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2025-02-27 09:45 | 2025-02-27 15:06 | 0.034157 | 0.00010657 | 1 | 320.5167 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 289 | INC 421008076 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2025-02-28 09:33 | 2025-02-28 16:21 | 0.13048 | 0.00031971 | 3 | 1224.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 290 | INC 421008125 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2025-03-04 09:11 | 2025-03-04 14:22 | 0.87564 | 0.012575 | 71 | 8216.5999 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 291 | INC 421008126 | 18 - Waipukurau South/Farm Rd | 18 - Waipukurau South/Farm Rd | 2025-03-04 09:11 | 2025-03-04 10:02 | 0.15188 | 0.002984 | 28 | 1425.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 292 | INC 421008165 | 19 - Hatuma/Wanstead | 19 - Hatuma/Wanstead | 2025-03-05 09:02 | 2025-03-05 13:29 | 0.59339 | 0.002238 | 21 | 5568.05 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Centralines | 2025 |  | 293 | INC 421008203 | 45 - Porangahau/Wallingford | 45 - Porangahau/Wallingford | 2025-03-25 09:00 | 2025-03-25 13:33 | 0.78428 | 0.0028774 | 27 | 7359.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 9 | NF011748 | Kaiaua | Kaiaua | 2024-04-02 08:40 | 2024-04-02 14:04 | 0.092552 | 0.0008048 | 39 | 4485 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 10 | CP00095131 | Drury | Drury | 2024-04-02 09:05 | 2024-04-02 13:07 | 0.13983 | 0.00057781 | 28 | 6776 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 11 | NF011749 | Hunua | Kaiaua | 2024-04-02 12:10 | 2024-04-02 12:49 | 0.00080482 | 2.0636e-05 | 1 | 39 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 12 | NF011752 | Glenbrook | Glenbrook | 2024-04-03 10:22 | 2024-04-03 13:30 | 0.0070988 | 0.00016509 | 8 | 344 | Unplanned | Human Error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 13 | NF011753 | Port Waikato | Port Waikato | 2024-04-03 21:52 | 2024-04-03 22:10 | 0.022287 | 0.0012382 | 60 | 1080 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 14 | CP00095985 | Pukekohe West | Pukekohe West | 2024-04-07 22:09 | 2024-04-08 06:35 | 2.9759 | 0.0058813 | 285 | 144716 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 15 | CP00095988 | Anchor Factory | Anchor Factory | 2024-04-07 22:09 | 2024-04-08 06:36 | 1.0881 | 0.0021461 | 104 | 49686 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 16 | CP00096004 | Pukekohe West | Pukekohe West | 2024-04-07 22:09 | 2024-04-08 06:32 | 2.5016 | 0.0049733 | 241 | 121223 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 17 | NF011758 | Glen Murray | Glen Murray | 2024-04-08 10:44 | 2024-04-08 12:00 | 0.020388 | 0.00026827 | 13 | 988 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 18 | NF011760 | Cape Hill | Cape Hill | 2024-04-08 15:11 | 2024-04-08 15:28 | 0.011928 | 0.00070162 | 34 | 578 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 19 | CP00096731 | Te Hihi | Te Hihi | 2024-04-09 08:59 | 2024-04-09 12:48 | 0.018903 | 8.2544e-05 | 4 | 229 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 20 | CP00097271 | Whangarata | Whangarata | 2024-04-09 09:00 | 2024-04-09 11:00 | 0.12134 | 0.0010112 | 49 | 5880 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 21 | CP00096808 | Glenbrook | Glenbrook | 2024-04-09 10:12 | 2024-04-09 13:54 | 0.073299 | 0.00033018 | 16 | 3552 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 22 | CP00096725 | Railway | Railway | 2024-04-10 08:04 | 2024-04-10 13:35 | 0.49863 | 0.0015064 | 73 | 22177 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 23 | NF011778 | Glen Murray | Glen Murray | 2024-04-10 13:42 | 2024-04-10 16:18 | 0.0096576 | 6.1908e-05 | 3 | 468 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 24 | NF011762 | Hunua | Hunua | 2024-04-11 02:22 | 2024-04-11 08:16 | 0.89364 | 0.011597 | 562 | 43305 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 25 | NF011795 | Manukau Heads | Manukau Heads | 2024-04-11 06:28 | 2024-04-11 09:22 | 0.0032192 | 0.00024763 | 12 | 156 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 26 | CP00096773 | Waiau Pa | Waiau Pa | 2024-04-11 09:14 | 2024-04-11 15:06 | 0.82082 | 0.0023319 | 113 | 40128 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 27 | CP00097404 | Manukau Heads | Manukau Heads | 2024-04-11 09:38 | 2024-04-11 12:31 | 0.01785 | 0.00010318 | 5 | 865 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 28 | NF011783 | Manukau Heads | Te Toro | 2024-04-11 11:48 | 2024-04-11 12:13 | 0.030417 | 0.0013826 | 67 | 1474 | Unplanned | Human Error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 29 | NF011783 | Manukau Heads | Manukau Heads | 2024-04-11 11:48 | 2024-04-11 12:13 | 0.019872 | 0.0066242 | 321 | 963 | Unplanned | Human Error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 30 | NF011808 | Glenbrook | Waiau Pa | 2024-04-11 13:18 | 2024-04-11 14:17 | 0.231 | 0.027363 | 1326 | 11194 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 31 | NF011808 | Glenbrook | Glenbrook | 2024-04-11 13:18 | 2024-04-11 14:17 | 0.15712 | 0.0078004 | 378 | 7614 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 32 | NF011782 | Manukau Heads | Manukau Heads | 2024-04-11 14:02 | 2024-04-11 14:19 | 0.13119 | 0.0086879 | 421 | 6357 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 33 | NF011782 | Manukau Heads | Te Toro | 2024-04-11 14:02 | 2024-04-11 14:19 | 0.023505 | 0.0013826 | 67 | 1139 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 34 | NF011784 | Te Hihi | Te Hihi | 2024-04-11 14:20 | 2024-04-11 17:45 | 0.42302 | 0.015023 | 728 | 20499 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 35 | NF011769 | Railway | Railway | 2024-04-11 15:04 | 2024-04-11 19:01 | 0.1076 | 0.000454 | 22 | 5214 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 36 | NF011764 | Te Hihi | Te Hihi | 2024-04-11 19:13 | 2024-04-11 21:06 | 0.38957 | 0.023566 | 744 | 18878 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 37 | NF011792 | Pakington | Pakington | 2024-04-11 21:00 | 2024-04-11 23:02 | 0.27694 | 0.00227 | 110 | 13420 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 38 | NF011765 | Kaiaua | Kaiaua | 2024-04-11 21:11 | 2024-04-12 08:07 | 8.0779 | 0.040942 | 1057 | 391447 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 39 | NF011794 | Waiau Pa | Waiau Pa | 2024-04-12 05:23 | 2024-04-12 06:46 | 1.8833 | 0.043728 | 1495 | 91261 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 40 | NF011768 | Waiau Pa | Waiau Pa | 2024-04-12 05:55 | 2024-04-12 08:51 | 0.069007 | 0.00039208 | 19 | 3344 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 41 | NF011796 | Kaiaua | Kaiaua | 2024-04-12 08:28 | 2024-04-12 12:07 | 0.022596 | 0.00010318 | 5 | 1095 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 42 | CP00097385 | Drury | Drury | 2024-04-12 10:05 | 2024-04-12 14:09 | 0.66968 | 0.0027446 | 133 | 32452 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 43 | CP00097385 | Drury | Pukekohe East | 2024-04-12 10:05 | 2024-04-12 14:09 | 0.11077 | 0.00045399 | 22 | 5368 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 44 | NF011779 | Kaiaua | Kaiaua | 2024-04-12 12:07 | 2024-04-12 18:40 | 2.4099 | 0.023216 | 1057 | 116779 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 45 | NF011780 | Drury | Drury | 2024-04-13 07:24 | 2024-04-13 08:52 | 1.1788 | 0.026992 | 1308 | 57125 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 46 | NF011776 | Manukau Heads | Te Toro | 2024-04-13 08:52 | 2024-04-13 12:58 | 0.068408 | 0.012609 | 544 | 3315 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 47 | NF011776 | Manukau Heads | Manukau Heads | 2024-04-13 08:52 | 2024-04-13 12:58 | 0.72577 | 0.011907 | 421 | 35170 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 48 | NF011771 | Railway | Railway | 2024-04-13 11:20 | 2024-04-13 17:46 | 0.12679 | 0.0019811 | 96 | 6144 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 49 | NF011773 | Te Toro | Te Toro | 2024-04-13 14:28 | 2024-04-13 21:15 | 1.0073 | 0.021255 | 1030 | 48811 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 50 | CP00097529 | Pakington | Pakington | 2024-04-15 09:55 | 2024-04-15 12:24 | 0.046121 | 0.00030954 | 15 | 2235 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 51 | CP00096508 | Pukekawa | Pukekawa | 2024-04-16 08:35 | 2024-04-16 15:50 | 0.66427 | 0.0015271 | 74 | 32190 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 52 | CP00096803 | Titi Mauku | Titi Mauku | 2024-04-16 09:01 | 2024-04-16 15:02 | 0.12664 | 0.00035081 | 17 | 6137 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 53 | CP00096408 | Pukekohe West | Pukekohe West | 2024-04-17 08:34 | 2024-04-17 15:14 | 3.4586 | 0.0086465 | 419 | 104000 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 54 | CP00096884 | Glenbrook | Glenbrook | 2024-04-17 09:08 | 2024-04-17 14:46 | 0.96255 | 0.0028478 | 138 | 46644 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 55 | CP00096884 | Glenbrook | Waiuku South | 2024-04-17 09:08 | 2024-04-17 14:46 | 0.006975 | 2.0636e-05 | 1 | 338 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 56 | NF011799 | Kaiaua | Kaiaua | 2024-04-17 14:49 | 2024-04-17 22:55 | 0.27074 | 0.00066035 | 32 | 13120 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 57 | CP00096794 | Railway | Railway | 2024-04-18 08:33 | 2024-04-18 15:44 | 1.1118 | 0.0025795 | 125 | 53875 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 58 | CP00096794 | Railway | Razorback | 2024-04-18 08:33 | 2024-04-18 15:44 | 0.38245 | 0.00088735 | 43 | 18533 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 59 | CP00096529 | Drury Hills | Drury Hills | 2024-04-18 09:05 | 2024-04-18 15:25 | 0.15683 | 0.00041272 | 20 | 7600 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 60 | CP00096894 | Hunua | Hunua | 2024-04-18 09:12 | 2024-04-18 13:50 | 1.4858 | 0.0053447 | 259 | 72002 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 61 | CP00097857 | Drury | Drury | 2024-04-18 12:00 | 2024-04-18 13:10 | 0.021668 | 0.00030954 | 15 | 1050 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 62 | NF011797 | Otaua | Otaua | 2024-04-18 20:16 | 2024-04-19 01:30 | 0.070018 | 0.00059844 | 29 | 3393 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 63 | CP00096985 | Kaiaua | Kaiaua | 2024-04-19 09:15 | 2024-04-19 14:25 | 0.39662 | 0.0012794 | 62 | 19220 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 64 | CP00097942 | Glen Murray | Glen Murray | 2024-04-19 09:48 | 2024-04-19 14:22 | 0.14136 | 0.0005159 | 25 | 6302 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 65 | NF011800 | Anchor Factory | Anchor Factory | 2024-04-19 12:32 | 2024-04-19 14:13 | 0.52723 | 0.0062527 | 303 | 25549 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 66 | NF011802 | Pakington | Pakington | 2024-04-22 21:31 | 2024-04-22 22:05 | 0.013909 | 0.00035082 | 17 | 674 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 67 | CP00096959 | Glen Murray | Glen Murray | 2024-04-23 08:36 | 2024-04-23 11:12 | 0.054727 | 0.00035081 | 17 | 2652 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 68 | CP00096990 | Titi Mauku | Titi Mauku | 2024-04-23 09:08 | 2024-04-23 14:19 | 0.1091 | 0.00035081 | 17 | 5287 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 69 | NF011804 | Whangarata | Whangarata | 2024-04-24 07:09 | 2024-04-24 12:53 | 0.44008 | 0.004705 | 180 | 21326 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 70 | CP00096875 | Onewhero | Onewhero | 2024-04-24 09:04 | 2024-04-24 12:34 | 0.043336 | 0.00020636 | 10 | 2100 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 71 | CP00097236 | Otaua | Otaua | 2024-04-24 09:13 | 2024-04-24 14:44 | 0.020492 | 6.1908e-05 | 3 | 993 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 72 | CP00097239 | Kaiaua | Kaiaua | 2024-04-24 09:30 | 2024-04-24 15:39 | 0.32743 | 0.00088735 | 43 | 15867 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 73 | CP00098230 | Glenbrook | Glenbrook | 2024-04-24 09:35 | 2024-04-24 13:11 | 0.0044574 | 2.0636e-05 | 1 | 216 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 74 | CP00097515 | Otaua | Otaua | 2024-04-26 09:04 | 2024-04-26 14:42 | 0.50917 | 0.0015064 | 73 | 22984 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 75 | CP00097516 | Otaua | Otaua | 2024-04-26 09:04 | 2024-04-26 12:42 | 0.31041 | 0.0014239 | 69 | 15042 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 76 | NF011806 | Titi Mauku | Te Hihi | 2024-04-26 10:20 | 2024-04-26 11:07 | 0.00096991 | 2.0636e-05 | 1 | 47 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 77 | NF011811 | Onewhero | Onewhero | 2024-04-29 17:27 | 2024-04-30 01:40 | 0.17908 | 0.00053654 | 22 | 8678 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 78 | CP00097464 | Titi Mauku | Titi Mauku | 2024-04-30 09:09 | 2024-04-30 13:11 | 0.33959 | 0.0014032 | 68 | 16456 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 79 | CP00097469 | Razorback | Razorback | 2024-04-30 10:08 | 2024-04-30 13:33 | 0.038073 | 0.00018572 | 9 | 1845 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 80 | NF011817 | Glen Murray | Glen Murray | 2024-04-30 13:15 | 2024-04-30 16:23 | 0.072124 | 0.0063147 | 304 | 3495 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 81 | NF011813 | Drury | Drury | 2024-05-01 00:08 | 2024-05-01 01:11 | 0.47906 | 0.0076042 | 369 | 23247 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 82 | NF011814 | Anchor Factory | Anchor Factory | 2024-05-01 01:59 | 2024-05-01 02:29 | 0.19907 | 0.0066356 | 322 | 9660 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 83 | CP00097467 | Anchor Factory | Anchor Factory | 2024-05-01 09:06 | 2024-05-01 16:30 | 0.57642 | 0.0012982 | 63 | 27972 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 84 | NF011815 | Whangarata | Whangarata | 2024-05-01 19:42 | 2024-05-01 19:46 | 0.010881 | 0.0027201 | 132 | 528 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 85 | CP00097449 | Waiau Pa | Waiau Pa | 2024-05-02 08:28 | 2024-05-02 15:51 | 0.73032 | 0.0016486 | 80 | 30567 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 86 | CP00097122 | Drury Hills | Drury Hills | 2024-05-02 09:04 | 2024-05-02 15:12 | 2.8134 | 0.0076452 | 371 | 127696 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 87 | CP00098335 | Te Hihi | Te Hihi | 2024-05-02 10:05 | 2024-05-02 16:08 | 0.082284 | 0.00022668 | 11 | 3993 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 88 | NF011821 | Port Waikato | Port Waikato | 2024-05-02 12:07 | 2024-05-02 15:34 | 0.02986 | 0.00014425 | 7 | 1449 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 89 | NF011823 | River Road | River Road | 2024-05-03 08:10 | 2024-05-03 16:55 | 1.103 | 0.0056257 | 273 | 53524 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 90 | CP00097772 | Manukau Heads | Manukau Heads | 2024-05-03 09:14 | 2024-05-03 12:30 | 0.056546 | 0.0002885 | 14 | 2744 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 91 | CP00097664 | Paparata | Paparata | 2024-05-03 09:40 | 2024-05-03 14:12 | 0.82956 | 0.0030498 | 148 | 38896 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 92 | CP00098741 | Waiau Pa | Waiau Pa | 2024-05-06 09:16 | 2024-05-06 17:18 | 0.79461 | 0.0016486 | 80 | 38560 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 93 | NF011822 | Glen Murray | Glen Murray | 2024-05-06 09:31 | 2024-05-06 14:26 | 0.032395 | 0.00024729 | 12 | 1572 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 94 | CP00098052 | Port Waikato | Port Waikato | 2024-05-07 09:03 | 2024-05-07 15:59 | 0.077153 | 0.00018546 | 9 | 3744 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 95 | CP00097686 | Kaiaua | Kaiaua | 2024-05-07 09:07 | 2024-05-07 15:23 | 0.30993 | 0.00082428 | 40 | 15040 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 96 | CP00097684 | Waiau Pa | Waiau Pa | 2024-05-08 09:04 | 2024-05-08 15:42 | 0.65613 | 0.0016486 | 80 | 31840 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 97 | CP00098988 | Waiau Pa | Waiau Pa | 2024-05-08 09:04 | 2024-05-08 15:42 | 0.27065 | 0.00068003 | 33 | 13134 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 98 | CP00097657 | Blackbridge | Blackbridge | 2024-05-08 09:06 | 2024-05-08 15:24 | 0.46737 | 0.0012364 | 60 | 23436 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 99 | CP00097765 | Manukau Heads | Manukau Heads | 2024-05-09 08:31 | 2024-05-09 15:25 | 0.39244 | 0.00094793 | 46 | 15732 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 100 | CP00097741 | Kaiaua | Kaiaua | 2024-05-09 09:09 | 2024-05-09 15:15 | 0.10559 | 0.0002885 | 14 | 5124 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 101 | CP00097662 | Railway | Railway | 2024-05-10 09:05 | 2024-05-10 15:40 | 0.51281 | 0.0012982 | 63 | 24885 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 102 | NF012057 | Railway | Railway | 2024-05-11 16:40 | 2024-05-11 21:22 | 0.010386 | 8.243e-05 | 4 | 504 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 103 | NF011767 | Anchor Factory | Anchor Factory | 2024-05-12 06:50 | 2024-05-12 13:40 | 0.036598 | 0.00037093 | 18 | 1776 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 104 | CP00099135 | Glen Murray | Glen Murray | 2024-05-13 09:29 | 2024-05-13 12:09 | 0.056051 | 0.00035032 | 17 | 2720 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 105 | CP00097172 | Kaiaua | Kaiaua | 2024-05-14 08:45 | 2024-05-14 16:14 | 3.4154 | 0.0076452 | 370 | 157150 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 106 | NF012391 | Glenbrook | Glenbrook | 2024-05-16 00:58 | 2024-05-16 12:28 | 0.72294 | 0.024358 | 379 | 35082 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 107 | NF012163 | Onewhero | Onewhero | 2024-05-16 07:43 | 2024-05-16 08:25 | 0.25458 | 0.016444 | 798 | 12354 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 108 | CP00097808 | Pukekohe West | Pukekohe West | 2024-05-16 22:00 | 2024-05-17 05:59 | 3.3363 | 0.0069652 | 338 | 71371 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 109 | CP00097848 | Pukekohe West | Pukekohe West | 2024-05-16 22:00 | 2024-05-17 05:59 | 2.7737 | 0.0057906 | 281 | 66581 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 110 | CP00099340 | Drury | Drury | 2024-05-17 09:52 | 2024-05-17 12:45 | 0.01426 | 8.2428e-05 | 4 | 692 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 111 | NF012492 | Glenbrook | Glenbrook | 2024-05-19 21:16 | 2024-05-20 07:49 | 0.035547 | 0.00010304 | 5 | 1725 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 112 | CP00099139 | Glen Murray | Glen Murray | 2024-05-20 09:03 | 2024-05-20 13:46 | 0.099141 | 0.00035032 | 17 | 4811 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 113 | NF012160 | Railway | Railway | 2024-05-21 00:46 | 2024-05-21 02:47 | 0.22336 | 0.0063676 | 309 | 10839 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 114 | NF012162 | Mercer | Mercer | 2024-05-21 04:55 | 2024-05-21 11:12 | 0.14466 | 0.0026789 | 130 | 7020 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 115 | CP00098417 | Kaiaua | Kaiaua | 2024-05-21 09:08 | 2024-05-21 14:56 | 0.25099 | 0.00072125 | 35 | 12180 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 116 | CP00099331 | Kaiaua | Kaiaua | 2024-05-21 09:08 | 2024-05-21 14:56 | 0.30836 | 0.0008861 | 43 | 14964 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 117 | NF012165 | Hunua | Hunua | 2024-05-21 12:29 | 2024-05-21 17:13 | 0.084365 | 0.00094793 | 46 | 4094 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 118 | NF012164 | Great South Road | Great South Road | 2024-05-21 12:48 | 2024-05-21 13:37 | 0.21996 | 0.012344 | 584 | 10674 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 119 | CP00098440 | Kaiaua | Kaiaua | 2024-05-22 09:14 | 2024-05-22 12:35 | 0.02071 | 0.00010304 | 5 | 1005 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 120 | CP00098548 | Pakington | Pakington | 2024-05-22 09:15 | 2024-05-22 15:54 | 1.3649 | 0.0034208 | 166 | 66234 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 121 | NF012166 | Drury Hills | Drury Hills | 2024-05-22 12:40 | 2024-05-22 14:12 | 0.017063 | 0.00018546 | 9 | 828 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 122 | CP00098554 | Pukekohe West | Pukekohe West | 2024-05-23 08:44 | 2024-05-23 17:51 | 2.8969 | 0.005296 | 257 | 140579 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 123 | CP00098667 | Pukekohe West | Pukekohe West | 2024-05-23 08:44 | 2024-05-23 17:51 | 1.1397 | 0.0021225 | 243 | 55247 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 124 | CP00098679 | Pukekohe West | Pukekohe West | 2024-05-23 08:44 | 2024-05-23 17:51 | 1.8486 | 0.0033796 | 164 | 547 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 125 | NF012167 | Waiuku South | Waiuku South | 2024-05-23 08:46 | 2024-05-23 11:25 | 0.0068416 | 8.2428e-05 | 4 | 332 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 126 | NF012169 | Razorback | Razorback | 2024-05-23 09:34 | 2024-05-23 14:00 | 0.0046366 | 0.00010304 | 5 | 225 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 127 | NF012168 | Pukekohe East | Pukekohe East | 2024-05-23 10:10 | 2024-05-23 11:50 | 0.18341 | 0.0018341 | 89 | 8900 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 128 | CP00098436 | Kaiaua | Kaiaua | 2024-05-24 10:00 | 2024-05-24 12:03 | 0.0050693 | 4.1214e-05 | 2 | 246 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 129 | NF012251 | Manukau Heads | Manukau Heads | 2024-05-26 12:24 | 2024-05-26 16:38 | 0.0048427 | 0.00010304 | 5 | 235 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 130 | CP00098462 | Kaiaua | Kaiaua | 2024-05-28 09:59 | 2024-05-28 14:48 | 0.089332 | 0.00030911 | 15 | 4335 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 131 | CP00086990 | Churchill Road | Churchill Road | 2024-05-28 10:00 | 2024-05-28 15:50 | 0.014425 | 4.1214e-05 | 2 | 700 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 132 | NF012263 | Kaiaua | Kaiaua | 2024-05-29 00:10 | 2024-05-29 00:37 | 0.13465 | 0.0049869 | 242 | 6534 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 133 | NF012262 | Kaiaua | Kaiaua | 2024-05-29 08:32 | 2024-05-29 09:20 | 0.52681 | 0.012014 | 583 | 25564 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 134 | CP00098463 | Kaiaua | Kaiaua | 2024-05-29 09:08 | 2024-05-29 10:20 | 1.9161 | 0.0014837 | 72 | 4536 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 135 | NF012266 | Titi Mauku | Titi Mauku | 2024-05-29 09:32 | 2024-05-29 11:28 | 0.05737 | 0.00049457 | 24 | 2784 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 136 | NF012261 | Onewhero | Onewhero | 2024-05-29 09:40 | 2024-05-29 10:32 | 0.19775 | 0.016444 | 798 | 9596 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 137 | NF012370 | Glen Murray | Glen Murray | 2024-05-29 09:45 | 2024-05-30 16:11 | 0.61992 | 0.00024729 | 12 | 30082 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 138 | NF012259 | Ararimu | Ararimu | 2024-05-29 09:50 | 2024-05-29 12:17 | 1.1714 | 0.01527 | 508 | 56845 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 139 | NF012310 | Hunua | Hunua | 2024-05-29 09:55 | 2024-05-29 20:15 | 0.39318 | 0.0038947 | 189 | 19080 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 140 | NF012362 | Kaiaua | Kaiaua | 2024-05-29 10:01 | 2024-05-29 15:50 | 1.3858 | 0.027325 | 740 | 67250 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 141 | NF012348 | Waiuku South | Waiuku South | 2024-05-29 10:32 | 2024-05-29 14:24 | 0.349 | 0.0015043 | 73 | 16936 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 142 | NF012341 | Onewhero | Onewhero | 2024-05-29 11:00 | 2024-05-30 12:15 | 0.47023 | 0.00039153 | 19 | 22819 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 143 | NF012327 | Kaiaua | Kaiaua | 2024-05-29 11:04 | 2024-05-29 16:47 | 0.59662 | 0.0086138 | 242 | 28952 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 144 | NF012260 | Pukekohe East | Pukekohe East | 2024-05-29 11:56 | 2024-05-30 01:10 | 0.37221 | 0.0023698 | 115 | 18062 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 145 | NF012330 | Railway | Railway | 2024-05-29 11:59 | 2024-05-29 14:00 | 0.44262 | 0.0063676 | 309 | 21479 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 146 | NF012345 | Waiuku South | Waiuku South | 2024-05-29 12:00 | 2024-05-29 12:30 | 0.01051 | 0.00035032 | 17 | 510 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 147 | NF012308 | Blackbridge | Blackbridge | 2024-05-29 12:08 | 2024-05-30 17:55 | 4.0876 | 0.0022874 | 111 | 198357 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 148 | NF012273 | Otaua | Otaua | 2024-05-29 12:52 | 2024-05-29 14:24 | 0.013271 | 0.00014425 | 7 | 644 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 149 | NF012359 | Glenbrook | Glenbrook | 2024-05-29 13:05 | 2024-05-29 17:39 | 0.34218 | 0.0090259 | 379 | 16605 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 150 | NF012305 | Hunua | Hunua | 2024-05-29 13:20 | 2024-05-29 18:18 | 0.27236 | 0.0038947 | 189 | 13217 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 151 | NF012346 | Waiuku South | Waiuku South | 2024-05-29 13:20 | 2024-05-29 17:22 | 0.034908 | 0.00014425 | 7 | 1694 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 152 | NF012265 | Kaiaua | Kaiaua | 2024-05-29 13:29 | 2024-05-29 16:50 | 0.34206 | 0.0049869 | 242 | 16599 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 153 | NF012357 | Glen Murray | Glen Murray | 2024-05-29 14:05 | 2024-05-29 19:33 | 0.96441 | 0.012612 | 306 | 46800 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 154 | NF012342 | Railway | Railway | 2024-05-29 15:33 | 2024-05-29 17:06 | 0.40969 | 0.0063676 | 309 | 19881 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 155 | NF012367 | Pukekohe East | Pukekohe East | 2024-05-29 16:07 | 2024-05-30 17:19 | 0.15579 | 0.00010304 | 5 | 7560 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 156 | NF012350 | Hunua | Hunua | 2024-05-29 16:14 | 2024-05-29 21:40 | 0.053743 | 0.00016486 | 8 | 2608 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 157 | NF012368 | Waiuku South | Waiuku South | 2024-05-29 17:30 | 2024-05-29 19:10 | 0.018546 | 0.00018546 | 9 | 900 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 158 | NF012340 | Glen Murray | Glen Murray | 2024-05-29 18:49 | 2024-05-30 17:12 | 0.13838 | 0.00010304 | 5 | 6715 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 159 | NF012309 | Glenbrook | Glenbrook | 2024-05-29 18:59 | 2024-05-31 01:10 | 0.090815 | 0.00022668 | 7 | 4407 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 160 | NF012369 | Glen Murray | Glen Murray | 2024-05-29 19:33 | 2024-05-29 19:36 | 0.018918 | 0.0063059 | 306 | 918 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 161 | NF012314 | Kaiaua | Kaiaua | 2024-05-29 21:07 | 2024-05-30 15:48 | 0.026377 | 0.00020607 | 10 | 1280 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 162 | NF012356 | Pakington | Pakington | 2024-05-29 21:56 | 2024-05-30 16:10 | 0.40579 | 0.00037093 | 18 | 19692 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 163 | NF012363 | Pakington | Te Hihi | 2024-05-29 21:56 | 2024-05-30 16:00 | 0.10046 | 0.00010304 | 5 | 4875 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 164 | NF012270 | Patumahoe | Patumahoe | 2024-05-29 22:30 | 2024-05-29 23:59 | 0.020174 | 0.00022668 | 11 | 979 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 165 | NF012336 | Onewhero | Onewhero | 2024-05-29 23:14 | 2024-05-30 01:09 | 0.0094795 | 8.243e-05 | 4 | 460 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 166 | NF012334 | Otaua | Otaua | 2024-05-30 07:36 | 2024-05-30 13:30 | 0.0072125 | 0.0002885 | 14 | 350 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 167 | NF012353 | Glen Murray | Glen Murray | 2024-05-30 08:47 | 2024-05-30 13:05 | 0.23962 | 0.0063058 | 306 | 11628 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 168 | NF012349 | Waiuku South | Waiuku South | 2024-05-30 08:53 | 2024-05-31 12:00 | 0.20117 | 0.00012364 | 6 | 9762 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 169 | NF012277 | Glenbrook | Glenbrook | 2024-05-30 09:30 | 2024-05-30 09:45 | 0.023183 | 0.0015455 | 75 | 1125 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 170 | NF012303 | Hunua | Hunua | 2024-05-30 09:30 | 2024-05-30 18:23 | 0.14279 | 0.0002679 | 13 | 6929 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 171 | NF012358 | Waiuku South | Waiuku West | 2024-05-30 09:36 | 2024-05-30 12:00 | 0.050508 | 0.00039153 | 19 | 2451 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 172 | NF012364 | Te Toro | Te Toro | 2024-05-30 10:04 | 2024-05-31 12:55 | 0.58923 | 0.0005564 | 27 | 28593 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 173 | NF012365 | Glenbrook | Glenbrook | 2024-05-30 10:15 | 2024-05-30 11:37 | 0.18757 | 0.0022874 | 111 | 9102 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 174 | NF012354 | Ararimu | Ararimu | 2024-05-30 10:36 | 2024-05-30 20:38 | 0.07808 | 0.00018546 | 9 | 3789 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 175 | NF012278 | Manukau Heads | Manukau Heads | 2024-05-30 13:49 | 2024-05-30 14:50 | 0.0062852 | 0.00010304 | 5 | 305 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 176 | NF012317 | Te Toro | Te Toro | 2024-05-30 14:40 | 2024-05-30 16:27 | 0.01764 | 0.00016486 | 8 | 856 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 177 | NF012268 | Manukau Heads | Manukau Heads | 2024-05-30 17:00 | 2024-05-30 19:10 | 0.058937 | 0.00045337 | 22 | 2860 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 178 | NF012382 | Drury | Drury | 2024-05-31 08:25 | 2024-05-31 09:33 | 1.705 | 0.027222 | 1321 | 3480 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 179 | NF012338 | Anchor Factory | Anchor Factory | 2024-05-31 13:30 | 2024-05-31 16:28 | 0.011004 | 6.1821e-05 | 3 | 534 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 180 | NF012321 | Mercer | Mercer | 2024-06-01 12:37 | 2024-06-01 21:13 | 0.0070541 | 0.00014396 | 7 | 343 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 181 | NF012322 | Glenbrook | Glenbrook | 2024-06-03 05:20 | 2024-06-03 07:00 | 0.77739 | 0.0077739 | 378 | 37800 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 182 | NF012322 | Glenbrook | Waiau Pa | 2024-06-03 05:20 | 2024-06-03 07:00 | 0.38047 | 0.0038047 | 185 | 18500 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 183 | NF012360 | Tuakau | Tuakau | 2024-06-03 09:13 | 2024-06-03 11:57 | 1.2787 | 0.016082 | 782 | 62179 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 184 | NF012304 | Mercer | Pukekawa | 2024-06-03 10:55 | 2024-06-03 13:05 | 0.0080207 | 6.1698e-05 | 3 | 390 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 185 | NF012389 | Glenbrook | Glenbrook | 2024-06-04 14:32 | 2024-06-04 14:39 | 0.0064781 | 0.00092545 | 45 | 315 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 186 | CP00099056 | Hingaia | Hingaia | 2024-06-04 22:06 | 2024-06-05 05:31 | 0.10067 | 0.00022622 | 11 | 4895 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 187 | CP00099125 | Port Waikato | Port Waikato | 2024-06-05 09:00 | 2024-06-05 15:43 | 0.29008 | 0.00071979 | 35 | 14105 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 188 | CP00100035 | Blackbridge | Blackbridge | 2024-06-05 09:02 | 2024-06-05 15:28 | 0.46042 | 0.0011928 | 58 | 22388 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 189 | NF012390 | Glenbrook | Glenbrook | 2024-06-05 10:08 | 2024-06-05 10:29 | 0.012525 | 0.00059641 | 29 | 609 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 190 | CP00099137 | Port Waikato | Port Waikato | 2024-06-06 09:02 | 2024-06-06 16:20 | 1.8838 | 0.0043393 | 210 | 91542 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 191 | CP00099226 | Port Waikato | Port Waikato | 2024-06-06 09:02 | 2024-06-06 16:20 | 2.387 | 0.0054499 | 265 | 116070 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 192 | CP00099404 | Railway | Railway | 2024-06-06 09:17 | 2024-06-06 15:41 | 0.97925 | 0.0025501 | 124 | 47616 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 193 | CP00098995 | Beach Road | Beach Road | 2024-06-06 21:31 | 2024-06-07 04:08 | 0.15437 | 0.00061697 | 24 | 7543 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 194 | CP00099344 | Pukekawa | Pukekawa | 2024-06-07 09:06 | 2024-06-07 15:22 | 1.1986 | 0.0031877 | 155 | 58656 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 195 | CP00099988 | Port Waikato | Port Waikato | 2024-06-07 11:00 | 2024-06-07 13:20 | 0.057584 | 0.00041131 | 20 | 2800 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 196 | NF012378 | Port Waikato | Mercer | 2024-06-08 01:26 | 2024-06-08 09:02 | 0.090077 | 0.0030026 | 146 | 4380 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 197 | NF012378 | Port Waikato | Pukekawa | 2024-06-08 01:26 | 2024-06-08 09:02 | 0.28689 | 0.009563 | 465 | 13950 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 198 | NF012378 | Port Waikato | Port Waikato | 2024-06-08 01:26 | 2024-06-08 09:02 | 0.22419 | 0.0020977 | 99 | 10901 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 199 | NF012383 | Pukekawa | Mercer | 2024-06-09 18:38 | 2024-06-10 03:04 | 0.024021 | 0.0030026 | 146 | 1168 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 200 | NF012383 | Pukekawa | Pukekawa | 2024-06-09 18:38 | 2024-06-10 03:04 | 0.45619 | 0.0096864 | 471 | 22182 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 201 | NF012383 | Pukekawa | Port Waikato | 2024-06-09 18:38 | 2024-06-10 03:04 | 0.016288 | 0.002036 | 99 | 792 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 202 | CP00099143 | Keri Downs | Keri Downs | 2024-06-09 22:00 | 2024-06-10 01:39 | 0.29725 | 0.0013573 | 66 | 14454 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 203 | CP00099298 | Waiuku South | Waiuku South | 2024-06-10 09:38 | 2024-06-10 17:14 | 0.037512 | 8.2262e-05 | 4 | 1824 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 204 | NF012371 | Hunua | Hunua | 2024-06-10 11:00 | 2024-06-10 12:50 | 0.054293 | 0.00049357 | 24 | 2640 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 205 | NF012375 | Titi Mauku | Titi Mauku | 2024-06-10 15:44 | 2024-06-10 17:55 | 0.48494 | 0.0037018 | 180 | 23580 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 206 | NF012379 | Waiuku South | Waiuku South | 2024-06-10 16:33 | 2024-06-10 17:14 | 0.0033728 | 8.2262e-05 | 4 | 164 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 207 | CP00099399 | Ararimu | Ararimu | 2024-06-11 09:05 | 2024-06-11 15:45 | 1.563 | 0.0039075 | 190 | 76000 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 208 | NF012387 | Pakington | Pakington | 2024-06-11 09:06 | 2024-06-11 12:37 | 0.22998 | 0.00109 | 53 | 11183 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 209 | CP00099290 | Waiuku South | Waiuku South | 2024-06-11 09:11 | 2024-06-11 15:25 | 0.48457 | 0.0012956 | 63 | 23562 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 210 | CP00099174 | Otaua | Otaua | 2024-06-11 09:23 | 2024-06-11 15:11 | 0.014314 | 4.1131e-05 | 2 | 696 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 211 | CP00098727 | Beach Road | Beach Road | 2024-06-11 09:33 | 2024-06-11 09:39 | 0.02036 | 0.0033933 | 165 | 996 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 212 | CP00099345 | Beach Road | Beach Road | 2024-06-11 11:04 | 2024-06-11 11:22 | 0.0011105 | 6.1697e-05 | 3 | 54 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 213 | CP00098729 | Beach Road | Beach Road | 2024-06-11 15:02 | 2024-06-11 15:18 | 0.056596 | 0.0035373 | 172 | 2768 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 214 | NF012381 | Waiuku South | Waiuku South | 2024-06-11 23:06 | 2024-06-12 02:47 | 0.065604 | 0.0011311 | 55 | 3190 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 215 | CP00098730 | Hingaia | Hingaia | 2024-06-12 07:17 | 2024-06-12 07:33 | 0.033892 | 0.0021183 | 103 | 1664 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 216 | CP00099347 | Hingaia | Hingaia | 2024-06-12 09:02 | 2024-06-12 09:15 | 0.037429 | 0.0028792 | 140 | 1833 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 217 | CP00099396 | Waiuku South | Waiuku South | 2024-06-12 09:02 | 2024-06-12 14:38 | 0.39387 | 0.0011722 | 57 | 19152 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 218 | CP00099244 | Te Toro | Manukau Heads | 2024-06-12 09:20 | 2024-06-12 16:12 | 0.20335 | 0.00049357 | 24 | 9888 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 219 | CP00099244 | Te Toro | Te Toro | 2024-06-12 09:20 | 2024-06-12 16:12 | 0.22877 | 0.00055527 | 27 | 11124 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 220 | CP00099511 | Manukau Heads | Manukau Heads | 2024-06-12 09:29 | 2024-06-12 14:13 | 0.12265 | 0.00043188 | 21 | 5964 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 221 | CP00099561 | Ararimu | Ararimu | 2024-06-12 09:33 | 2024-06-12 14:20 | 0.088535 | 0.00030848 | 15 | 4305 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 222 | CP00099323 | Red Hill | Red Hill | 2024-06-13 08:48 | 2024-06-13 09:03 | 0.048123 | 0.0032082 | 156 | 2355 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 223 | CP00099192 | Otaua | Otaua | 2024-06-13 09:13 | 2024-06-13 14:45 | 0.49843 | 0.0015013 | 73 | 24236 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 224 | CP00099822 | Ararimu | Ararimu | 2024-06-13 09:16 | 2024-06-13 15:17 | 0.8612 | 0.0023856 | 116 | 41876 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 225 | CP00099402 | Hunua | Drury Hills | 2024-06-13 09:20 | 2024-06-13 14:18 | 0.012257 | 4.1131e-05 | 2 | 596 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 226 | CP00099402 | Hunua | Hunua | 2024-06-13 09:20 | 2024-06-13 14:18 | 1.1706 | 0.003928 | 191 | 56918 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 227 | CP00099329 | Te Hihi | Te Hihi | 2024-06-13 12:02 | 2024-06-13 12:23 | 0.014684 | 0.00069923 | 34 | 714 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 228 | CP00099668 | Drury Hills | Drury Hills | 2024-06-14 09:02 | 2024-06-14 12:52 | 0.080411 | 0.00034961 | 17 | 3910 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 229 | CP00099668 | Drury Hills | Drury | 2024-06-14 09:02 | 2024-06-14 12:52 | 0.0094602 | 4.1131e-05 | 2 | 460 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 230 | CP00099299 | Keri Downs | Keri Downs | 2024-06-15 08:05 | 2024-06-15 08:29 | 0.0024679 | 0.00010283 | 5 | 120 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 231 | CP00101007 | Glen Murray | Glen Murray | 2024-06-15 10:04 | 2024-06-15 13:19 | 0.0080206 | 4.1131e-05 | 2 | 390 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 232 | NF012392 | Drury | Drury | 2024-06-15 18:41 | 2024-06-15 19:09 | 0.65092 | 0.027208 | 1323 | 31651 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 233 | NF012394 | Kaiaua | Kaiaua | 2024-06-15 20:12 | 2024-06-15 21:39 | 0.24155 | 0.0027764 | 135 | 11745 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 234 | NF012393 | Railway | Railway | 2024-06-16 16:51 | 2024-06-16 18:08 | 0.07126 | 0.00092545 | 45 | 3465 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 235 | CP00099295 | Glen Murray | Glen Murray | 2024-06-17 09:31 | 2024-06-17 16:57 | 0.045861 | 0.00010283 | 5 | 2230 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 236 | CP00101396 | Blackbridge | Blackbridge | 2024-06-17 10:08 | 2024-06-17 11:24 | 0.068771 | 0.00090488 | 44 | 3344 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 237 | NF012602 | Pakington | Pakington | 2024-06-17 18:45 | 2024-06-17 21:34 | 0.031281 | 0.00018509 | 9 | 1521 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 238 | NF012395 | Kaiaua | Kaiaua | 2024-06-17 20:33 | 2024-06-17 21:03 | 0.36155 | 0.012052 | 586 | 17580 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 239 | CP00099386 | Glen Murray | Glen Murray | 2024-06-18 09:05 | 2024-06-18 14:35 | 0.13573 | 0.00041131 | 20 | 6600 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 240 | CP00099463 | Onewhero | Onewhero | 2024-06-18 09:05 | 2024-06-18 15:21 | 0.43303 | 0.0011517 | 56 | 21056 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 241 | CP00099512 | Waiuku South | Waiuku South | 2024-06-18 09:08 | 2024-06-18 15:20 | 0.83513 | 0.0022828 | 110 | 40548 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 242 | CP00099480 | Waiuku South | Waiuku South | 2024-06-19 09:05 | 2024-06-19 14:23 | 0.28121 | 0.00088432 | 43 | 13674 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 243 | NF012396 | Ararimu | Ararimu | 2024-06-19 09:35 | 2024-06-19 10:20 | 0.0074038 | 0.00016453 | 8 | 360 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 244 | NF012397 | Whangarata | Whangarata | 2024-06-19 10:40 | 2024-06-19 13:40 | 0.00691 | 6.1697e-05 | 3 | 336 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 245 | CP00099217 | Waiuku South | Waiuku South | 2024-06-20 09:04 | 2024-06-20 16:20 | 0.56489 | 0.0012956 | 63 | 27468 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 246 | NF012407 | Buckland | Buckland | 2024-06-20 20:06 | 2024-06-20 21:30 | 0.03455 | 0.00041131 | 20 | 1680 | Unplanned | Human Error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 247 | CP00099978 | Blackbridge | Blackbridge | 2024-06-20 21:00 | 2024-06-21 05:19 | 0.55416 | 0.0011105 | 54 | 27944 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 248 | NF012408 | Manukau Heads | Manukau Heads | 2024-06-21 02:30 | 2024-06-21 04:42 | 0.57443 | 0.012813 | 607 | 27931 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 249 | NF012408 | Manukau Heads | Te Toro | 2024-06-21 02:30 | 2024-06-21 04:42 | 0.056495 | 0.0013779 | 67 | 2747 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 250 | CP00099670 | Pakington | Pakington | 2024-06-21 09:04 | 2024-06-21 14:55 | 0.52695 | 0.0015013 | 73 | 25623 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 251 | CP00099526 | Kaiaua | Kaiaua | 2024-06-21 09:16 | 2024-06-21 15:10 | 0.45137 | 0.0012751 | 62 | 21948 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 252 | NF012405 | Waiuku South | Waiuku South | 2024-06-21 10:12 | 2024-06-21 18:38 | 1.6525 | 0.016555 | 805 | 80354 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 253 | NF012406 | Port Waikato | Port Waikato | 2024-06-24 13:01 | 2024-06-24 20:31 | 6.1697e-05 | 4.1131e-05 | 1 | 3 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 254 | NF012482 | Waiuku South | Waiuku South | 2024-06-25 02:36 | 2024-06-25 03:30 | 0.0044423 | 8.2264e-05 | 4 | 216 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 255 | CP00099843 | Pakington | Pakington | 2024-06-25 09:01 | 2024-06-25 16:17 | 2.3582 | 0.0054087 | 263 | 114668 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 256 | CP00099624 | Waiuku South | Waiuku South | 2024-06-26 09:01 | 2024-06-26 15:48 | 0.80354 | 0.0019743 | 96 | 32153 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 257 | NF012484 | Manukau Heads | Manukau Heads | 2024-06-26 09:32 | 2024-06-26 13:04 | 0.00654 | 4.1132e-05 | 2 | 318 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 258 | CP00100090 | Buckland | Buckland | 2024-06-26 21:30 | 2024-06-27 05:12 | 0.37055 | 0.00080206 | 39 | 18018 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 259 | CP00099673 | Drury Hills | Drury Hills | 2024-06-27 09:12 | 2024-06-27 15:06 | 0.1456 | 0.00041131 | 20 | 7080 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 260 | CP00099719 | Waiuku South | Waiuku South | 2024-06-27 09:34 | 2024-06-27 13:50 | 0.052648 | 0.00020566 | 10 | 2560 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 261 | NF012487 | Te Toro | Te Toro | 2024-06-29 14:06 | 2024-06-29 16:10 | 0.091805 | 0.00074036 | 36 | 4464 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 262 | NF012494 | Drury | Drury | 2024-07-01 23:28 | 2024-07-02 13:42 | 0.035053 | 4.1046e-05 | 2 | 1708 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 263 | CP00099937 | Waiuku South | Waiuku South | 2024-07-02 09:04 | 2024-07-02 14:00 | 0.10934 | 0.00036941 | 18 | 5624 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 264 | CP00100275 | Waiuku South | Waiuku South | 2024-07-02 09:21 | 2024-07-02 13:59 | 0.16545 | 0.00059515 | 29 | 8340 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 265 | CP00099893 | Pakington | Pakington | 2024-07-03 09:05 | 2024-07-03 15:33 | 0.17518 | 0.0004515 | 22 | 8536 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 266 | NF012498 | Hunua | Hunua | 2024-07-04 05:17 | 2024-07-04 16:35 | 0.0022575 | 2.0523e-05 | 1 | 110 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 267 | CP00100268 | Waiuku South | Titi Mauku | 2024-07-04 09:00 | 2024-07-04 15:15 | 0.0076959 | 2.0523e-05 | 1 | 375 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 268 | CP00100268 | Waiuku South | Waiuku South | 2024-07-04 09:00 | 2024-07-04 15:15 | 0.50024 | 0.001334 | 65 | 24375 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 269 | CP00099833 | Waiuku South | Waiuku South | 2024-07-04 09:08 | 2024-07-04 17:20 | 0.73709 | 0.0014981 | 73 | 35916 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 270 | NF012497 | Pukekawa | Pukekawa | 2024-07-04 12:21 | 2024-07-04 13:38 | 0.0047408 | 6.1569e-05 | 3 | 231 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 271 | NF012513 | Glenbrook | Glenbrook | 2024-07-04 19:37 | 2024-07-04 20:32 | 0.083527 | 0.0015187 | 74 | 4070 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 272 | NF012514 | Glenbrook | Glenbrook | 2024-07-04 21:30 | 2024-07-04 22:50 | 0.12149 | 0.0015187 | 74 | 5920 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 273 | NF012515 | Glenbrook | Glenbrook | 2024-07-05 00:03 | 2024-07-05 00:19 | 0.024299 | 0.0015187 | 74 | 1184 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 274 | NF012530 | Kaiaua | Kaiaua | 2024-07-05 05:32 | 2024-07-05 08:15 | 2.6606 | 0.021856 | 1065 | 129645 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 275 | CP00102579 | Te Hihi | Te Hihi | 2024-07-05 09:11 | 2024-07-05 11:58 | 0.010282 | 6.1568e-05 | 3 | 501 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 276 | NF012529 | Kaiaua | Kaiaua | 2024-07-05 13:15 | 2024-07-05 19:04 | 0.016254 | 0.00036941 | 18 | 792 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 277 | NF012527 | Drury Hills | Drury Hills | 2024-07-06 14:24 | 2024-07-06 22:30 | 0.10971 | 0.00022575 | 11 | 5346 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 278 | NF012541 | Te Hihi | Patumahoe | 2024-07-08 20:29 | 2024-07-09 00:22 | 0.04831 | 0.0004515 | 22 | 2354 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 279 | CP00099909 | Pakington | Pakington | 2024-07-10 09:04 | 2024-07-10 14:13 | 0.13951 | 0.0004515 | 22 | 6798 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 280 | CP00100258 | Waiuku South | Waiuku South | 2024-07-11 09:06 | 2024-07-11 14:09 | 0.18655 | 0.00061568 | 30 | 9090 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 281 | CP00099923 | Pakington | Pakington | 2024-07-11 09:09 | 2024-07-11 16:16 | 0.42939 | 0.0010056 | 49 | 20923 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 282 | CP00101081 | Anchor Factory | Anchor Factory | 2024-07-11 09:35 | 2024-07-11 15:58 | 0.070741 | 0.0001847 | 9 | 3447 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 283 | NF012582 | Pukekohe East | Pukekohe East | 2024-07-14 07:28 | 2024-07-14 08:18 | 0.10775 | 0.0021549 | 105 | 5250 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 284 | NF012583 | Manukau Heads | Manukau Heads | 2024-07-15 11:55 | 2024-07-15 13:36 | 0.01451 | 0.00014366 | 7 | 707 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 285 | NF012585 | Blackbridge | Blackbridge | 2024-07-15 21:36 | 2024-07-16 04:02 | 0.2341 | 0.0012519 | 61 | 11407 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 286 | CP00102119 | Pakington | Pakington | 2024-07-16 09:01 | 2024-07-16 15:23 | 0.38414 | 0.0010056 | 49 | 18718 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 287 | CP00100082 | Waiuku South | Waiuku South | 2024-07-16 09:05 | 2024-07-16 14:38 | 0.59456 | 0.0017855 | 87 | 28971 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 288 | CP00100009 | Waiuku South | Waiuku South | 2024-07-17 09:03 | 2024-07-17 15:03 | 0.22164 | 0.00061568 | 30 | 10800 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 289 | CP00101519 | Church Corner | Church Corner | 2024-07-17 09:07 | 2024-07-17 17:16 | 2.9805 | 0.0060952 | 297 | 90954 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 290 | CP00101531 | Church Corner | Church Corner | 2024-07-17 09:07 | 2024-07-17 17:16 | 2.7698 | 0.0056642 | 276 | 1956 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 291 | CP00101898 | Waiuku South | Waiuku South | 2024-07-17 09:32 | 2024-07-17 16:03 | 0.95489 | 0.0024422 | 119 | 46920 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 292 | CP00101534 | Pukekohe East | Pukekohe East | 2024-07-18 09:03 | 2024-07-18 15:00 | 0.79859 | 0.002237 | 109 | 38913 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 293 | CP00100262 | Otaua | Otaua | 2024-07-19 09:09 | 2024-07-19 15:09 | 0.50239 | 0.0013955 | 68 | 24480 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 294 | CP00100262 | Otaua | Waiuku South | 2024-07-19 09:09 | 2024-07-19 15:09 | 0.19209 | 0.00053359 | 26 | 9360 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 295 | NF012586 | Paparata | Paparata | 2024-07-21 21:33 | 2024-07-22 05:01 | 1.2326 | 0.011431 | 557 | 60062 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 296 | NF012590 | Pukekawa | Mercer | 2024-07-22 14:15 | 2024-07-22 14:55 | 0.012149 | 0.0030373 | 148 | 592 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 297 | NF012590 | Pukekawa | Pukekawa | 2024-07-22 14:15 | 2024-07-22 14:55 | 0.039157 | 0.010015 | 488 | 1908 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 298 | NF012589 | Railway | Railway | 2024-07-23 07:03 | 2024-07-23 08:34 | 0.0029552 | 0.00024627 | 12 | 144 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 299 | CP00102127 | Pakington | Pakington | 2024-07-23 09:08 | 2024-07-23 15:41 | 0.3952 | 0.0010056 | 49 | 19257 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 300 | CP00101207 | Waiuku South | Waiuku South | 2024-07-23 09:09 | 2024-07-23 14:54 | 0.75759 | 0.0021959 | 107 | 36915 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 301 | CP00101340 | Anchor Factory | Anchor Factory | 2024-07-24 09:03 | 2024-07-24 14:58 | 0.26228 | 0.00073881 | 36 | 12070 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 302 | CP00102128 | Pakington | Pakington | 2024-07-24 09:07 | 2024-07-24 16:10 | 0.22571 | 0.00053359 | 26 | 10998 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 303 | CP00101541 | Ararimu | Ararimu | 2024-07-24 09:37 | 2024-07-24 14:06 | 0.30915 | 0.0011493 | 56 | 15064 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 304 | NF012595 | Waiuku South | Waiuku South | 2024-07-25 11:49 | 2024-07-25 11:50 | 0.0030168 | 0.0030168 | 147 | 147 | Unplanned | Human Error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 305 | CP00101581 | Hingaia | Hingaia | 2024-07-25 21:32 | 2024-07-26 05:00 | 0.43212 | 0.00096456 | 215 | 10304 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 306 | NF012594 | Hingaia | Hingaia | 2024-07-29 21:32 | 2024-07-29 23:09 | 0.14134 | 0.0014571 | 71 | 6887 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 307 | CP00101602 | Pukekohe East | Pukekohe East | 2024-07-30 09:07 | 2024-07-30 15:25 | 0.69042 | 0.0018265 | 89 | 33642 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 308 | NF012598 | Glen Murray | Glen Murray | 2024-07-30 15:41 | 2024-07-30 19:13 | 0.017403 | 8.2092e-05 | 4 | 848 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 309 | NF012601 | Onewhero | Onewhero | 2024-07-31 08:11 | 2024-07-31 12:58 | 0.064339 | 0.00038994 | 19 | 3135 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 310 | CP00102650 | Anchor Factory | Anchor Factory | 2024-07-31 09:05 | 2024-07-31 13:30 | 0.065262 | 0.00024627 | 12 | 3180 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 311 | CP00101535 | Kaiaua | Kaiaua | 2024-07-31 09:06 | 2024-07-31 15:59 | 0.52086 | 0.0016418 | 71 | 25606 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 312 | CP00103736 | Anchor Factory | Anchor Factory | 2024-07-31 09:52 | 2024-07-31 14:12 | 0.053359 | 0.00020523 | 10 | 2600 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 313 | CP00102140 | Pakington | Pakington | 2024-08-01 09:02 | 2024-08-01 14:26 | 0.17258 | 0.00053266 | 26 | 8424 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 314 | NF012605 | Whangarata | Whangarata | 2024-08-02 05:16 | 2024-08-02 07:01 | 0.24498 | 0.0037081 | 181 | 11958 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 315 | NF012677 | Port Waikato | Port Waikato | 2024-08-02 08:33 | 2024-08-02 10:28 | 0.47546 | 0.015693 | 766 | 23208 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 316 | NF012604 | Whangarata | Port Waikato | 2024-08-02 09:42 | 2024-08-02 09:46 | 0.0010653 | 0.00026633 | 13 | 52 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 317 | CP00102267 | Pakington | Pakington | 2024-08-06 09:06 | 2024-08-06 15:42 | 0.39753 | 0.0010039 | 49 | 19404 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 318 | CP00102059 | Manukau Heads | Manukau Heads | 2024-08-06 09:34 | 2024-08-06 17:42 | 0.56986 | 0.0011677 | 57 | 21960 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 319 | NF012709 | Anchor Factory | Anchor Factory | 2024-08-06 12:00 | 2024-08-06 18:55 | 0.30452 | 0.0042204 | 104 | 14864 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 320 | CP00101962 | Great South Road | Great South Road | 2024-08-07 09:01 | 2024-08-07 10:25 | 0.12735 | 0.001516 | 74 | 6216 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 321 | CP00101962 | Great South Road | Pukekohe East | 2024-08-07 09:01 | 2024-08-07 10:25 | 0.01893 | 0.00022535 | 11 | 924 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 322 | CP00102613 | Paparata | Paparata | 2024-08-07 09:33 | 2024-08-07 12:59 | 0.17725 | 0.00086044 | 42 | 8652 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 323 | CP00098496 | Drury | Drury | 2024-08-08 09:07 | 2024-08-08 15:33 | 0.86196 | 0.0022331 | 109 | 38986 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 324 | NF012711 | Manukau Heads | Manukau Heads | 2024-08-08 16:56 | 2024-08-08 17:00 | 0.00032779 | 8.1947e-05 | 4 | 16 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 325 | CP00103563 | Pakington | Pakington | 2024-08-08 21:01 | 2024-08-09 01:52 | 0.98367 | 0.0033803 | 165 | 48015 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 326 | CP00101932 | Church Corner | Church Corner | 2024-08-08 21:02 | 2024-08-09 05:03 | 0.039417 | 8.1947e-05 | 4 | 1924 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 327 | NF012612 | Razorback | Razorback | 2024-08-09 03:11 | 2024-08-09 04:09 | 0.0059412 | 0.00010243 | 5 | 290 | Unplanned | Human Error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 328 | NF012707 | Titi Mauku | Titi Mauku | 2024-08-11 06:26 | 2024-08-11 11:52 | 0.89787 | 0.0080513 | 393 | 43827 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 329 | CP00104045 | Great South Road | Great South Road | 2024-08-13 08:08 | 2024-08-13 08:55 | 0.0096288 | 0.00020487 | 10 | 517 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 330 | CP00102546 | Waiuku South | Pakington | 2024-08-13 09:00 | 2024-08-13 15:50 | 0.21839 | 0.00053266 | 26 | 10608 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 331 | CP00102546 | Waiuku South | Titi Mauku | 2024-08-13 09:00 | 2024-08-13 15:50 | 0.47038 | 0.0011473 | 56 | 22850 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 332 | CP00102546 | Waiuku South | Waiuku South | 2024-08-13 09:00 | 2024-08-13 15:50 | 1.0667 | 0.0026018 | 127 | 51820 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 333 | CP00102997 | Pukekohe East | Pukekohe East | 2024-08-13 09:01 | 2024-08-13 16:05 | 0.13898 | 0.00032779 | 16 | 6784 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 334 | NF012714 | Waiau Pa | Waiau Pa | 2024-08-13 10:25 | 2024-08-13 10:30 | 0.0096288 | 0.0019258 | 94 | 470 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 335 | NF012715 | Waiau Pa | Waiau Pa | 2024-08-13 10:34 | 2024-08-13 10:37 | 0.0050397 | 0.0016799 | 82 | 246 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 336 | CP00103229 | Pukekohe Hill | Pukekohe Hill | 2024-08-14 08:35 | 2024-08-14 12:54 | 0.27061 | 0.0010448 | 51 | 13209 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 337 | CP00102996 | Te Toro | Te Toro | 2024-08-14 09:06 | 2024-08-14 15:41 | 2.282 | 0.0057773 | 282 | 110995 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 338 | CP00103555 | Drury | Drury | 2024-08-14 09:15 | 2024-08-14 15:03 | 0.23527 | 0.00067606 | 33 | 11484 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 339 | CP00102674 | Anchor Factory | Anchor Factory | 2024-08-15 09:34 | 2024-08-15 15:36 | 1.3053 | 0.0036057 | 176 | 60816 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 340 | CP00103151 | Hingaia | Hingaia | 2024-08-15 22:02 | 2024-08-16 05:24 | 1.4035 | 0.0031754 | 155 | 68510 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 341 | NF012728 | Great South Road | Great South Road | 2024-08-17 20:36 | 2024-08-17 21:31 | 0.26289 | 0.011985 | 585 | 12832 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 342 | NF012735 | Waiuku South | Titi Mauku | 2024-08-18 04:10 | 2024-08-18 05:38 | 0.032205 | 0.0080513 | 393 | 1572 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 343 | NF012735 | Waiuku South | Waiuku South | 2024-08-18 04:10 | 2024-08-18 05:38 | 0.53253 | 0.016492 | 805 | 25994 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 344 | NF012733 | Manukau Heads | Manukau Heads | 2024-08-18 09:29 | 2024-08-18 16:00 | 0.022945 | 0.00010243 | 5 | 1120 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 345 | NF012727 | Glen Murray | Glen Murray | 2024-08-18 11:33 | 2024-08-18 12:05 | 0.15146 | 0.0061051 | 298 | 7393 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 346 | NF012741 | Waiau Pa | Waiau Pa | 2024-08-19 01:54 | 2024-08-19 03:57 | 1.0288 | 0.027206 | 1328 | 50219 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 347 | NF012740 | Pukekawa | Pukekawa | 2024-08-19 05:45 | 2024-08-19 10:51 | 0.013419 | 0.00010244 | 5 | 655 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 348 | NF012720 | Waiuku South | Waiuku South | 2024-08-19 08:28 | 2024-08-19 15:34 | 0.071355 | 0.00088093 | 43 | 3483 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 349 | NF012744 | Railway | Railway | 2024-08-19 13:22 | 2024-08-19 14:34 | 0.14161 | 0.0019668 | 96 | 6912 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 350 | NF012723 | Manukau Heads | Manukau Heads | 2024-08-19 16:53 | 2024-08-19 19:30 | 0.022515 | 0.00014341 | 7 | 1099 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 351 | NF012724 | Titi Mauku | Titi Mauku | 2024-08-19 22:03 | 2024-08-19 23:20 | 0.01893 | 0.00024585 | 12 | 924 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 352 | CP00103271 | Cape Hill | Cape Hill | 2024-08-20 08:51 | 2024-08-20 12:47 | 0.14505 | 0.0006146 | 30 | 7080 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 353 | CP00103042 | Pukekohe East | Pukekohe East | 2024-08-20 09:06 | 2024-08-20 14:10 | 0.4235 | 0.0013931 | 68 | 20672 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 354 | NF012737 | Manukau Heads | Manukau Heads | 2024-08-20 14:18 | 2024-08-20 16:05 | 0.0065763 | 6.146e-05 | 3 | 321 | Unplanned | Human Error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 355 | CP00103096 | Waiuku South | Waiuku South | 2024-08-21 09:04 | 2024-08-21 15:27 | 0.74541 | 0.0019462 | 95 | 36385 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 356 | CP00103593 | Titi Mauku | Titi Mauku | 2024-08-21 09:08 | 2024-08-21 16:03 | 0.47611 | 0.0011473 | 56 | 23240 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 357 | CP00103701 | Waiau Pa | Waiau Pa | 2024-08-22 08:34 | 2024-08-22 14:51 | 0.90365 | 0.002397 | 117 | 44109 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 358 | CP00103881 | Port Waikato | Port Waikato | 2024-08-22 09:30 | 2024-08-22 12:33 | 0.059985 | 0.00032779 | 16 | 2928 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 359 | NF012747 | Kaiaua | Kaiaua | 2024-08-22 17:39 | 2024-08-22 21:24 | 0.059924 | 0.00026633 | 13 | 2925 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 360 | CP00103553 | Te Toro | Te Toro | 2024-08-23 09:04 | 2024-08-23 15:31 | 0.51534 | 0.0013316 | 65 | 25155 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 361 | CP00103586 | Hunua | Hunua | 2024-08-26 08:40 | 2024-08-26 15:35 | 0.34008 | 0.00081947 | 40 | 16600 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 362 | CP00102609 | Ararimu | Ararimu | 2024-08-26 10:15 | 2024-09-06 13:44 | 0.0086044 | 0.00028681 | 7 | 0 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 363 | CP00103795 | Waiuku South | Waiuku South | 2024-08-28 09:04 | 2024-08-28 15:11 | 0.65412 | 0.0017823 | 87 | 31929 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 364 | CP00103623 | Waiuku South | Waiuku South | 2024-08-28 09:09 | 2024-08-28 14:22 | 0.23726 | 0.00075801 | 37 | 11581 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 365 | CP00103849 | Pukekawa | Pukekawa | 2024-08-28 21:23 | 2024-08-29 04:48 | 0.63816 | 0.0018643 | 91 | 31595 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 366 | NF012760 | Manukau Heads | Manukau Heads | 2024-08-29 20:23 | 2024-08-30 07:58 | 0.056953 | 8.1947e-05 | 4 | 2780 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 367 | NF012761 | (Subtrans-33MO) | Otaua | 2024-08-29 20:47 | 2024-08-29 20:56 | 0.10233 | 0.01137 | 555 | 4995 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 368 | CP00103596 | Titi Mauku | Titi Mauku | 2024-08-30 09:04 | 2024-08-30 14:42 | 0.38777 | 0.0011473 | 56 | 18928 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 369 | NF012765 | Blackbridge | Blackbridge | 2024-08-31 08:57 | 2024-08-31 15:22 | 0.015775 | 4.0974e-05 | 2 | 770 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 370 | NF012764 | Anchor Factory | Anchor Factory | 2024-08-31 17:44 | 2024-08-31 22:50 | 0.39495 | 0.0012907 | 63 | 19278 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 371 | NF012769 | Drury | Drury | 2024-09-02 14:09 | 2024-09-02 15:37 | 0.0053978 | 6.1338e-05 | 3 | 264 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 372 | CP00103847 | Waiau Pa | Waiau Pa | 2024-09-03 08:21 | 2024-09-03 12:42 | 0.61419 | 0.0023532 | 115 | 30015 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 373 | CP00105303 | Pukekawa | Pukekawa | 2024-09-03 08:42 | 2024-09-03 10:49 | 0.070167 | 0.0005525 | 27 | 3429 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 374 | CP00104484 | Blackbridge | Blackbridge | 2024-09-04 09:02 | 2024-09-04 15:20 | 0.34807 | 0.00092083 | 45 | 17010 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 375 | CP00103626 | Pakington | Pakington | 2024-09-04 09:04 | 2024-09-04 15:04 | 0.5525 | 0.0015347 | 75 | 27000 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 376 | NF012782 | Port Waikato | Port Waikato | 2024-09-04 21:23 | 2024-09-04 22:14 | 0.06048 | 0.0011859 | 58 | 2958 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 377 | CP00103620 | Titi Mauku | Titi Mauku | 2024-09-05 09:06 | 2024-09-05 15:15 | 0.42284 | 0.0011459 | 56 | 20664 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 378 | CP00104332 | Railway | Railway | 2024-09-06 09:01 | 2024-09-06 15:49 | 1.0269 | 0.0025169 | 123 | 50184 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 379 | NF012780 | Anchor Factory | Anchor Factory | 2024-09-06 09:48 | 2024-09-06 16:58 | 0.76644 | 0.0018197 | 89 | 37486 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 380 | NF012777 | Otaua | Otaua | 2024-09-08 15:08 | 2024-09-08 22:14 | 1.2451 | 0.011348 | 555 | 60895 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 381 | CP00104230 | Racecourse | Racecourse | 2024-09-09 11:00 | 2024-09-09 11:20 | 0.013096 | 0.00065481 | 32 | 640 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 382 | CP00104231 | Pukekohe Town | Pukekohe Town | 2024-09-09 13:32 | 2024-09-09 13:46 | 0.036383 | 0.0025988 | 127 | 28 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 383 | CP00104232 | Railway | Railway | 2024-09-09 15:01 | 2024-09-09 15:19 | 0.0018417 | 0.00010231 | 5 | 90 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 384 | CP00104250 | Church Corner | Church Corner | 2024-09-10 08:34 | 2024-09-10 09:00 | 0.044159 | 0.0016984 | 83 | 2158 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 385 | CP00102887 | Pakington | Pakington | 2024-09-10 09:02 | 2024-09-10 13:42 | 0.63026 | 0.0022509 | 110 | 30800 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 386 | CP00104028 | River Road | River Road | 2024-09-10 09:04 | 2024-09-10 11:02 | 0.0096585 | 8.1851e-05 | 4 | 590 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 387 | CP00103812 | Pukekohe East | Pukekohe East | 2024-09-10 09:07 | 2024-09-10 15:10 | 0.40111 | 0.001105 | 54 | 19602 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 388 | CP00104252 | Cape Hill | Cape Hill | 2024-09-10 10:01 | 2024-09-10 10:20 | 0.043156 | 0.0022714 | 111 | 19 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 389 | CP00104255 | Cape Hill | Cape Hill | 2024-09-10 11:32 | 2024-09-10 11:56 | 0.060406 | 0.0025169 | 123 | 2976 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 390 | NF012773 | Drury Hills | Drury Hills | 2024-09-10 16:03 | 2024-09-10 19:06 | 0.078576 | 0.00042938 | 21 | 3843 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 391 | CP00105631 | Titi Mauku | Titi Mauku | 2024-09-11 08:30 | 2024-09-11 10:30 | 0.14488 | 0.0012073 | 59 | 7080 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 392 | CP00103629 | Waiuku South | Pakington | 2024-09-11 09:06 | 2024-09-11 14:36 | 0.17557 | 0.00053203 | 26 | 8580 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 393 | CP00103629 | Waiuku South | Waiuku South | 2024-09-11 09:06 | 2024-09-11 14:36 | 0.24985 | 0.00075713 | 37 | 12210 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 394 | CP00104346 | Paparata | Paparata | 2024-09-11 09:10 | 2024-09-11 15:30 | 0.10109 | 0.00026602 | 13 | 5320 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 395 | CP00104719 | Mercer | Mercer | 2024-09-12 09:03 | 2024-09-12 14:00 | 0.3768 | 0.0012687 | 62 | 18414 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 396 | CP00103630 | Pakington | Pakington | 2024-09-12 09:04 | 2024-09-12 15:42 | 0.39907 | 0.0010027 | 49 | 19502 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 397 | CP00103523 | Anchor Factory | Anchor Factory | 2024-09-15 22:00 | 2024-09-16 04:06 | 0.7789 | 0.0021281 | 104 | 38064 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 398 | CP00105945 | Hingaia | Hingaia | 2024-09-16 16:30 | 2024-09-16 16:52 | 0.035114 | 0.0015961 | 78 | 1716 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 399 | NF012787 | Waiau Pa | Waiau Pa | 2024-09-17 08:16 | 2024-09-17 20:04 | 0.063567 | 0.0002658 | 13 | 3109 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 400 | CP00105438 | Waiau Pa | Waiau Pa | 2024-09-17 09:07 | 2024-09-17 13:39 | 0.65121 | 0.0023942 | 117 | 31824 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 401 | CP00105329 | Te Toro | Te Toro | 2024-09-17 10:06 | 2024-09-17 13:52 | 1.2938 | 0.0057249 | 280 | 60342 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 402 | NF012786 | Kaiaua | Kaiaua | 2024-09-17 16:59 | 2024-09-17 18:14 | 0.027603 | 0.00036804 | 18 | 1350 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 403 | NF012790 | Beach Road | Beach Road | 2024-09-17 19:05 | 2024-09-17 21:11 | 0.43024 | 0.0034146 | 167 | 21042 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 404 | NF012791 | Anchor Factory | Anchor Factory | 2024-09-18 06:09 | 2024-09-18 07:14 | 0.43325 | 0.0066654 | 326 | 21190 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 405 | CP00104479 | Blackbridge | Blackbridge | 2024-09-18 08:41 | 2024-09-18 13:41 | 0.12892 | 0.00042972 | 21 | 6300 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 406 | CP00105134 | Pukekohe East | Pukekohe East | 2024-09-18 09:05 | 2024-09-18 15:44 | 0.44053 | 0.0011041 | 54 | 21546 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 407 | CP00104329 | Railway | Railway | 2024-09-18 09:09 | 2024-09-18 14:55 | 0.36787 | 0.0010632 | 52 | 19376 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 408 | CP00105378 | Ararimu | Ararimu | 2024-09-19 08:50 | 2024-09-19 14:35 | 0.035298 | 0.00010231 | 5 | 1725 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 409 | CP00105333 | Ararimu | Ararimu | 2024-09-19 09:39 | 2024-09-19 15:45 | 0.067405 | 0.00018417 | 9 | 3294 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 410 | CP00103954 | Drury | Drury | 2024-09-19 22:00 | 2024-09-20 04:50 | 2.3827 | 0.0058115 | 284 | 117260 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 411 | CP00104259 | Church Corner | Church Corner | 2024-09-19 23:31 | 2024-09-19 23:43 | 0.0029467 | 0.00024555 | 12 | 144 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 412 | CP00104260 | Buckland | Buckland | 2024-09-20 01:31 | 2024-09-20 01:52 | 0.025783 | 0.0012278 | 60 | 1260 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 413 | CP00104261 | Buckland | Buckland | 2024-09-20 02:31 | 2024-09-20 02:44 | 0.015163 | 0.0011664 | 57 | 741 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 414 | NF012794 | Waiau Pa | Waiau Pa | 2024-09-20 02:46 | 2024-09-20 11:43 | 0.034412 | 0.00022491 | 11 | 1683 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 415 | NF012792 | Razorback | Razorback | 2024-09-20 02:50 | 2024-09-20 04:34 | 0.014885 | 0.00014312 | 7 | 728 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 416 | NF012804 | Drury | Drury | 2024-09-20 03:20 | 2024-09-20 06:21 | 0.077716 | 0.00042937 | 21 | 3801 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 417 | CP00104263 | Pukekohe Town | Pukekohe Town | 2024-09-20 03:30 | 2024-09-20 03:41 | 0.046594 | 0.0042358 | 207 | 11 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 418 | NF012800 | Te Toro | Te Toro | 2024-09-20 03:46 | 2024-09-20 09:48 | 0.022205 | 6.1338e-05 | 3 | 1086 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 419 | NF012795 | Papakura South | Papakura South | 2024-09-20 04:57 | 2024-09-20 15:15 | 2.4777 | 0.041342 | 2022 | 121180 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 420 | NF012774 | Razorback | Razorback | 2024-09-20 06:33 | 2024-09-20 15:04 | 0.039666 | 0.00010223 | 5 | 1940 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 421 | CP00105170 | Kaiaua | Kaiaua | 2024-09-20 09:32 | 2024-09-20 10:56 | 0.056723 | 0.00067527 | 33 | 2772 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 422 | CP00105410 | Ararimu | Ararimu | 2024-09-20 13:38 | 2024-09-20 14:46 | 0.040353 | 0.00059342 | 29 | 1972 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 423 | CP00105986 | Hunua | Hunua | 2024-09-21 09:05 | 2024-09-21 13:26 | 0.085453 | 0.00032741 | 16 | 4176 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 424 | NF012805 | Drury | Drury | 2024-09-22 16:00 | 2024-09-22 16:10 | 0.0071561 | 0.00071561 | 35 | 350 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 425 | CP00106255 | Manukau Heads | Manukau Heads | 2024-09-23 10:08 | 2024-09-23 16:45 | 0.57679 | 0.0014529 | 71 | 28187 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 426 | NF012796 | Pukekawa | Mercer | 2024-09-23 10:15 | 2024-09-23 13:39 | 0.012513 | 6.1338e-05 | 3 | 612 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 427 | CP00105283 | Ararimu | Ararimu | 2024-09-24 08:35 | 2024-09-24 13:58 | 0.50893 | 0.0015756 | 77 | 23902 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 428 | CP00103998 | Anchor Factory | Anchor Factory | 2024-09-24 09:04 | 2024-09-24 15:53 | 0.52727 | 0.0012892 | 63 | 25767 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 429 | CP00104935 | Drury | Drury | 2024-09-24 09:10 | 2024-09-24 15:30 | 0.31881 | 0.00083898 | 41 | 15580 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 430 | NF012807 | Cape Hill | Cape Hill | 2024-09-24 09:18 | 2024-09-24 16:45 | 2.2569 | 0.060991 | 2983 | 110384 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 431 | NF012806 | Anchor Factory | Anchor Factory | 2024-09-24 16:38 | 2024-09-24 17:00 | 0.028338 | 0.0012881 | 63 | 1386 | Unplanned | Human Error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 432 | CP00105273 | Ararimu | Ararimu | 2024-09-25 09:00 | 2024-09-25 16:00 | 0.3094 | 0.00073666 | 36 | 15120 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 433 | CP00104949 | Drury | Drury | 2024-09-25 09:07 | 2024-09-25 14:59 | 0.36735 | 0.0010436 | 51 | 17952 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 434 | CP00106612 | Drury | Drury | 2024-09-25 09:07 | 2024-09-25 14:59 | 0.12245 | 0.00034787 | 17 | 5984 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 435 | CP00105442 | Anchor Factory | Anchor Factory | 2024-09-25 09:34 | 2024-09-25 16:00 | 0.094784 | 0.00024555 | 12 | 4632 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 436 | CP00105747 | Paparata | Paparata | 2024-09-26 08:37 | 2024-09-26 15:40 | 0.7444 | 0.0017598 | 86 | 36378 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 437 | CP00105738 | Ararimu | Ararimu | 2024-09-26 08:38 | 2024-09-26 15:17 | 0.50621 | 0.0012687 | 62 | 25536 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 438 | CP00104108 | Anchor Factory | Anchor Factory | 2024-09-26 09:02 | 2024-09-26 15:08 | 0.24715 | 0.00067527 | 33 | 12078 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 439 | CP00104351 | Pukekawa | Pukekawa | 2024-09-26 09:08 | 2024-09-26 13:10 | 0.034664 | 0.00014324 | 25 | 1694 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 440 | NF012809 | Railway | Railway | 2024-09-28 08:17 | 2024-09-28 12:29 | 0.096179 | 0.0019628 | 96 | 4704 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 441 | CP00106948 | Cape Hill | Cape Hill | 2024-09-29 09:02 | 2024-09-29 13:52 | 0.70024 | 0.0024146 | 118 | 34220 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 442 | CP00106955 | Cape Hill | Cape Hill | 2024-09-30 10:05 | 2024-09-30 11:04 | 0.091756 | 0.0015552 | 76 | 4484 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 443 | CP00106956 | Cape Hill | Cape Hill | 2024-09-30 12:48 | 2024-09-30 14:02 | 0.084798 | 0.0011459 | 56 | 4144 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 444 | CP00104527 | Kaiaua | Kaiaua | 2024-10-01 09:04 | 2024-10-01 12:48 | 1.3722 | 0.0061259 | 300 | 49952 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 445 | CP00105266 | Railway | Railway | 2024-10-01 09:14 | 2024-10-01 15:28 | 0.69497 | 0.0018582 | 91 | 34408 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 446 | CP00105192 | Te Toro | Te Toro | 2024-10-01 09:30 | 2024-10-01 14:21 | 0.0059422 | 2.042e-05 | 1 | 291 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 447 | CP00106574 | Glen Murray | Glen Murray | 2024-10-01 09:40 | 2024-10-01 14:16 | 0.09581 | 0.00034714 | 17 | 4692 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 448 | CP00105262 | Waiuku South | Waiuku South | 2024-10-02 09:02 | 2024-10-02 16:08 | 0.22617 | 0.00053092 | 26 | 11076 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 449 | CP00105143 | Pukekohe East | Pukekohe East | 2024-10-02 09:05 | 2024-10-02 15:15 | 0.58932 | 0.0015927 | 78 | 26640 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 450 | NF012811 | Kaiaua | Kaiaua | 2024-10-02 11:15 | 2024-10-02 14:56 | 0.0017766 | 0.00012252 | 3 | 87 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 451 | NF012815 | Te Hihi | Te Hihi | 2024-10-02 23:34 | 2024-10-03 08:56 | 1.4243 | 0.0146 | 715 | 69749 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 452 | CP00104349 | Te Hihi | Te Hihi | 2024-10-03 09:07 | 2024-10-03 13:59 | 0.16099 | 0.00055134 | 27 | 7884 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 453 | CP00105270 | Railway | Railway | 2024-10-03 09:09 | 2024-10-03 15:23 | 0.73315 | 0.0019603 | 96 | 35904 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 454 | CP00106838 | Ararimu | Ararimu | 2024-10-03 09:18 | 2024-10-03 09:40 | 0.0044924 | 0.0002042 | 10 | 220 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 455 | CP00106575 | Titi Mauku | Titi Mauku | 2024-10-03 22:13 | 2024-10-04 03:22 | 0.37227 | 0.0012048 | 59 | 18231 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 456 | CP00104096 | Anchor Factory | Anchor Factory | 2024-10-04 09:02 | 2024-10-04 14:41 | 0.47072 | 0.0013885 | 68 | 23052 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 457 | NF012817 | Otaua | Otaua | 2024-10-06 18:20 | 2024-10-06 23:40 | 0.033815 | 0.00036756 | 18 | 1656 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 458 | CP00106391 | Keri Downs | Keri Downs | 2024-10-06 22:00 | 2024-10-07 02:41 | 0.36723 | 0.0013069 | 64 | 17984 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 459 | CP00107017 | Blackbridge | Blackbridge | 2024-10-08 08:34 | 2024-10-08 15:31 | 0.59605 | 0.0014294 | 70 | 29190 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 460 | CP00106258 | Pukekohe East | Pukekohe East | 2024-10-08 09:06 | 2024-10-08 14:52 | 0.39565 | 0.0011435 | 56 | 16954 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 461 | CP00106081 | Pukekohe Town | Pukekohe Town | 2024-10-09 08:35 | 2024-10-09 19:36 | 3.3069 | 0.0050029 | 245 | 96506 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 462 | CP00106084 | Pukekohe Town | Pukekohe Town | 2024-10-09 08:35 | 2024-10-09 19:36 | 0.95832 | 0.0014498 | 71 | 46931 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 463 | NF012837 | Glen Murray | Glen Murray | 2024-10-09 08:58 | 2024-10-09 18:10 | 0.011272 | 2.042e-05 | 1 | 552 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 464 | CP00106095 | Waiau Pa | Waiau Pa | 2024-10-09 09:12 | 2024-10-09 16:45 | 0.31451 | 0.00069427 | 34 | 13590 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 465 | CP00106101 | Blackbridge | Blackbridge | 2024-10-10 08:35 | 2024-10-10 15:15 | 0.30221 | 0.00075553 | 37 | 14800 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 466 | CP00104954 | Te Hihi | Te Hihi | 2024-10-10 09:10 | 2024-10-10 14:18 | 0.16981 | 0.00055134 | 27 | 8316 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 467 | CP00106398 | Ararimu | Ararimu | 2024-10-10 09:36 | 2024-10-10 14:27 | 0.24363 | 0.00083721 | 41 | 11931 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 468 | CP00106403 | Ararimu | Ararimu | 2024-10-11 10:46 | 2024-10-11 14:14 | 0.18263 | 0.00087805 | 43 | 8944 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 469 | NF012825 | Glen Murray | Glen Murray | 2024-10-12 08:45 | 2024-10-12 18:44 | 0.012231 | 2.042e-05 | 1 | 599 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 470 | CP00106543 | Pakington | Glenbrook | 2024-10-14 09:01 | 2024-10-14 15:14 | 0.060933 | 0.00016336 | 8 | 2984 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 471 | CP00106543 | Pakington | Pakington | 2024-10-14 09:01 | 2024-10-14 15:14 | 0.23611 | 0.00063301 | 31 | 11563 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 472 | NF012830 | Otaua | Otaua | 2024-10-14 15:10 | 2024-10-14 15:33 | 0.0023483 | 0.0001021 | 5 | 115 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 473 | NF012827 | Otaua | Otaua | 2024-10-15 06:30 | 2024-10-15 10:10 | 0.07096 | 0.00051051 | 25 | 3475 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 474 | CP00106525 | Pukekohe East | Pukekohe East | 2024-10-15 09:07 | 2024-10-15 14:30 | 0.36935 | 0.0011435 | 56 | 18088 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 475 | CP00106408 | Ararimu | Ararimu | 2024-10-15 09:37 | 2024-10-15 15:09 | 0.14237 | 0.00042882 | 21 | 7304 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 476 | CP00106156 | Pukekawa | Pukekawa | 2024-10-16 09:04 | 2024-10-16 15:30 | 0.60692 | 0.0015723 | 77 | 29722 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 477 | CP00106404 | Ararimu | Ararimu | 2024-10-16 09:39 | 2024-10-16 15:42 | 0.40768 | 0.0011231 | 55 | 19965 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 478 | CP00106435 | Glen Murray | Glen Murray | 2024-10-17 09:01 | 2024-10-17 15:30 | 0.60369 | 0.0015519 | 76 | 29564 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 479 | CP00106542 | Te Hihi | Te Hihi | 2024-10-17 09:12 | 2024-10-17 14:55 | 0.18911 | 0.00055134 | 27 | 9261 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 480 | CP00107659 | Glenbrook | Glenbrook | 2024-10-17 10:01 | 2024-10-17 10:10 | 0.0060647 | 0.00067385 | 33 | 297 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 481 | NF012832 | Te Hihi | Te Hihi | 2024-10-17 13:35 | 2024-10-17 18:09 | 0.022381 | 8.1681e-05 | 4 | 1096 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 482 | CP00106617 | Blackbridge | Blackbridge | 2024-10-17 21:33 | 2024-10-18 03:51 | 1.0497 | 0.0027771 | 136 | 48762 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 483 | NF012834 | Onewhero | Onewhero | 2024-10-18 08:51 | 2024-10-18 10:53 | 0.77671 | 0.030814 | 798 | 38037 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 484 | CP00105790 | Pukekawa | Pukekawa | 2024-10-18 09:08 | 2024-10-18 15:17 | 0.54251 | 0.0014702 | 72 | 26937 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 485 | CP00106103 | Paparata | Paparata | 2024-10-21 09:08 | 2024-10-21 14:40 | 0.18304 | 0.00055134 | 27 | 8964 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 486 | CP00106409 | Paparata | Paparata | 2024-10-22 09:02 | 2024-10-22 14:50 | 0.28424 | 0.00081679 | 40 | 13920 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 487 | CP00107582 | Waiau Pa | Waiau Pa | 2024-10-22 09:02 | 2024-10-22 13:47 | 0.73328 | 0.0025729 | 126 | 35910 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 488 | CP00106388 | Pakington | Pakington | 2024-10-22 09:03 | 2024-10-22 16:24 | 0.63937 | 0.0014498 | 71 | 31311 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 489 | CP00107197 | Railway | Railway | 2024-10-23 09:00 | 2024-10-23 13:44 | 0.71331 | 0.0025116 | 123 | 34932 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 490 | CP00106462 | Pukekawa | Pukekawa | 2024-10-23 09:06 | 2024-10-23 15:02 | 0.45071 | 0.001266 | 62 | 22072 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 491 | CP00106459 | Glen Murray | Glen Murray | 2024-10-24 09:03 | 2024-10-24 15:02 | 0.095299 | 0.00026546 | 13 | 4667 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 492 | CP00106925 | Paparata | Paparata | 2024-10-24 09:09 | 2024-10-24 14:47 | 0.13114 | 0.00038798 | 19 | 6422 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 493 | NF012836 | Hingaia | Hingaia | 2024-10-24 22:50 | 2024-10-25 00:05 | 1.551 | 0.021073 | 1032 | 75956 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 494 | CP00106964 | Church Corner | Church Corner | 2024-10-25 08:30 | 2024-10-25 08:41 | 0.018643 | 0.0016948 | 83 | 913 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 495 | NF012839 | Drury Hills | Drury Hills | 2024-10-29 08:39 | 2024-10-29 09:43 | 0.014376 | 0.00022462 | 11 | 704 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 496 | CP00107610 | Titi Mauku | Titi Mauku | 2024-10-29 09:12 | 2024-10-29 16:12 | 0.40309 | 0.00095973 | 47 | 19740 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 497 | CP00107276 | Pukekohe East | Pukekohe East | 2024-10-30 09:04 | 2024-10-30 14:55 | 0.50888 | 0.0014498 | 71 | 24570 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 498 | CP00107583 | Port Waikato | Port Waikato | 2024-10-30 09:04 | 2024-10-30 14:20 | 0.058074 | 0.00018378 | 9 | 2844 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 499 | CP00107100 | Te Hihi | Te Hihi | 2024-10-31 09:00 | 2024-10-31 15:12 | 0.94193 | 0.0025321 | 124 | 46128 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 500 | NF012840 | Mercer | Mercer | 2024-10-31 12:45 | 2024-10-31 13:25 | 0.0024504 | 6.1259e-05 | 3 | 120 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 501 | CP00107734 | Tuakau | Tuakau | 2024-11-01 09:09 | 2024-11-01 14:09 | 0.1346 | 0.00044866 | 22 | 6900 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 502 | CP00106576 | Glen Murray | Glen Murray | 2024-11-01 09:11 | 2024-11-01 15:11 | 0.20557 | 0.00057102 | 28 | 10080 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 503 | CP00108268 | Port Waikato | Port Waikato | 2024-11-01 09:15 | 2024-11-01 13:09 | 0.076354 | 0.0003263 | 16 | 3744 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 504 | NF012841 | Waiuku South | Waiuku South | 2024-11-01 15:50 | 2024-11-01 18:11 | 0.084511 | 0.0015091 | 74 | 4144 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 505 | NF012843 | Railway | Railway | 2024-11-04 02:02 | 2024-11-04 04:44 | 0.021923 | 0.00050984 | 25 | 1075 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 506 | CP00106797 | Pukekohe East | Pukekohe East | 2024-11-04 09:01 | 2024-11-04 15:33 | 0.81664 | 0.0021209 | 103 | 39984 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 507 | CP00107931 | Te Hihi | Te Hihi | 2024-11-05 09:01 | 2024-11-05 16:48 | 0.18095 | 0.00038748 | 19 | 8873 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 508 | CP00107847 | Pukekohe East | Pukekohe East | 2024-11-05 09:04 | 2024-11-05 15:42 | 0.76297 | 0.001917 | 94 | 37412 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 509 | CP00107853 | Ararimu | Ararimu | 2024-11-06 09:06 | 2024-11-06 14:50 | 0.035077 | 0.00010197 | 5 | 1720 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 510 | CP00106860 | Glen Murray | Glen Murray | 2024-11-06 09:07 | 2024-11-06 14:58 | 0.18611 | 0.00053023 | 26 | 9126 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 511 | CP00107585 | Te Hihi | Te Hihi | 2024-11-07 09:01 | 2024-11-07 14:59 | 1.4383 | 0.0040175 | 197 | 70168 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 512 | CP00107859 | Pukekawa | Pukekawa | 2024-11-07 09:09 | 2024-11-07 14:40 | 0.57377 | 0.0017335 | 85 | 28466 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 513 | CP00106869 | Glen Murray | Glen Murray | 2024-11-08 09:08 | 2024-11-08 15:29 | 0.0777 | 0.00020394 | 10 | 3810 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 514 | CP00108104 | Ararimu | Ararimu | 2024-11-12 09:04 | 2024-11-12 15:42 | 0.39772 | 0.00099929 | 49 | 19502 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 515 | CP00107682 | Glenbrook | Glenbrook | 2024-11-12 09:06 | 2024-11-12 15:14 | 0.68294 | 0.0018558 | 91 | 33488 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 516 | CP00107934 | Drury Hills | Drury Hills | 2024-11-13 08:39 | 2024-11-13 15:35 | 0.084837 | 0.00020394 | 10 | 4160 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 517 | CP00107920 | Glen Murray | Glen Murray | 2024-11-13 09:07 | 2024-11-13 16:13 | 0.11294 | 0.00026512 | 13 | 5538 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 518 | NF012862 | Blackbridge | Blackbridge | 2024-11-13 19:39 | 2024-11-13 22:22 | 0.23261 | 0.0023249 | 114 | 11406 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 519 | CP00108234 | Manukau Heads | Manukau Heads | 2024-11-14 09:10 | 2024-11-14 12:12 | 0.04454 | 0.00024472 | 12 | 2184 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 520 | CP00107923 | Anchor Factory | Anchor Factory | 2024-11-14 09:12 | 2024-11-14 14:41 | 0.22141 | 0.00067299 | 33 | 10857 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 521 | CP00107687 | Glenbrook | Glenbrook | 2024-11-15 09:08 | 2024-11-15 14:14 | 0.037443 | 0.00012236 | 6 | 1836 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 522 | CP00107755 | Great South Road | Great South Road | 2024-11-16 08:32 | 2024-11-16 16:12 | 0.024472 | 0.00081574 | 20 | 0 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 523 | CP00107868 | Kaiaua | Kaiaua | 2024-11-16 09:02 | 2024-11-16 13:01 | 0.29732 | 0.001244 | 61 | 12906 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 524 | NF012867 | Manukau Heads | Manukau Heads | 2024-11-16 10:18 | 2024-11-16 10:35 | 0.0013868 | 8.1576e-05 | 4 | 68 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 525 | NF012868 | Pukekawa | Pukekawa | 2024-11-16 15:09 | 2024-11-16 22:58 | 0.69513 | 0.0017335 | 85 | 34085 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 526 | CP00107910 | Pukekohe East | Pukekohe East | 2024-11-18 09:05 | 2024-11-18 16:24 | 0.63565 | 0.0014479 | 71 | 31169 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 527 | NF012873 | Port Waikato | Port Waikato | 2024-11-18 09:10 | 2024-11-18 10:32 | 0.0016723 | 2.0394e-05 | 1 | 82 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 528 | CP00108682 | Pukekohe East | Pukekohe East | 2024-11-18 09:11 | 2024-11-18 15:05 | 0.15883 | 0.00044866 | 22 | 7788 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 529 | NF012870 | Paparata | Paparata | 2024-11-18 14:36 | 2024-11-18 23:16 | 0.44062 | 0.0051392 | 253 | 21606 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 530 | NF012874 | Pukekohe East | Pukekohe East | 2024-11-18 18:59 | 2024-11-18 23:17 | 0.015785 | 6.1181e-05 | 3 | 774 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 531 | CP00108287 | Pukekawa | Pukekawa | 2024-11-19 09:06 | 2024-11-19 15:02 | 0.24684 | 0.00069338 | 34 | 12104 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 532 | CP00108119 | Glenbrook | Glenbrook | 2024-11-19 09:08 | 2024-11-19 14:49 | 0.20167 | 0.00059141 | 29 | 9889 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 533 | NF012875 | Pukekohe East | Pukekohe East | 2024-11-19 09:10 | 2024-11-19 14:30 | 0.019578 | 6.1182e-05 | 3 | 960 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 534 | NF012879 | Helenslee Road | Helenslee Road | 2024-11-19 12:52 | 2024-11-19 17:12 | 1.5822 | 0.01607 | 788 | 77584 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 535 | NF012889 | Drury | Drury | 2024-11-20 06:51 | 2024-11-20 08:01 | 0.53105 | 0.0075864 | 372 | 26040 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 536 | NF012880 | Railway | Railway | 2024-11-21 04:24 | 2024-11-21 06:26 | 0.010401 | 0.00020394 | 10 | 510 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 537 | NF012881 | Waiau Pa | Waiau Pa | 2024-11-21 08:56 | 2024-11-21 10:59 | 0.0037524 | 0.00016315 | 8 | 184 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 538 | CP00107746 | Drury | Drury | 2024-11-21 22:08 | 2024-11-22 03:06 | 1.3248 | 0.0044458 | 218 | 65262 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 539 | CP00109057 | Te Toro | Te Toro | 2024-11-22 10:11 | 2024-11-22 10:20 | 0.0075252 | 0.00083614 | 41 | 369 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 540 | CP00109100 | Te Toro | Te Toro | 2024-11-22 11:05 | 2024-11-22 11:17 | 0.014928 | 0.001244 | 61 | 744 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 541 | CP00109104 | Te Toro | Te Toro | 2024-11-22 12:03 | 2024-11-22 12:16 | 0.0055675 | 0.00042827 | 21 | 273 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 542 | NF012883 | Te Hihi | Te Hihi | 2024-11-22 12:53 | 2024-11-22 13:05 | 0.04821 | 0.0037932 | 197 | 2364 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 543 | CP00109117 | Te Toro | Te Toro | 2024-11-22 14:09 | 2024-11-22 14:29 | 0.00081574 | 4.0787e-05 | 2 | 40 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 544 | CP00109119 | Te Toro | Te Toro | 2024-11-22 15:05 | 2024-11-22 15:17 | 0.0073417 | 0.00061181 | 30 | 360 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 545 | NF012888 | Drury | Drury | 2024-11-24 08:22 | 2024-11-24 08:45 | 0.17449 | 0.0075866 | 372 | 8556 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 546 | CP00108704 | Pakington | Glenbrook | 2024-11-25 09:41 | 2024-11-25 14:34 | 0.047803 | 0.00016315 | 8 | 2344 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 547 | CP00108704 | Pakington | Pakington | 2024-11-25 09:41 | 2024-11-25 14:34 | 0.18524 | 0.0006322 | 31 | 9083 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 548 | CP00109120 | Waiuku West | Waiuku West | 2024-11-26 08:43 | 2024-11-26 08:56 | 0.0047721 | 0.00036708 | 18 | 234 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 549 | CP00107981 | Drury | Drury | 2024-11-26 09:01 | 2024-11-26 14:19 | 0.090792 | 0.00028551 | 14 | 4452 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 550 | CP00108690 | Pukekohe East | Pukekohe East | 2024-11-26 09:33 | 2024-11-26 16:34 | 0.40353 | 0.0009585 | 47 | 15577 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 551 | CP00109125 | Waiuku West | Waiuku West | 2024-11-26 10:08 | 2024-11-26 10:31 | 0.011013 | 0.0011013 | 27 | 351 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 552 | CP00109127 | Hingaia | Hingaia | 2024-11-26 12:13 | 2024-11-26 12:22 | 0.0031202 | 0.00034669 | 17 | 153 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 553 | CP00109565 | Glenbrook | Glenbrook | 2024-11-27 08:07 | 2024-11-27 08:51 | 0.026022 | 0.00059141 | 29 | 1276 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 554 | CP00108569 | Glenbrook | Glenbrook | 2024-11-27 09:00 | 2024-11-27 14:48 | 0.48969 | 0.0014072 | 69 | 24012 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 555 | NF012901 | McDonald Road | McDonald Road | 2024-11-27 09:08 | 2024-11-27 10:11 | 0.024411 | 0.00034669 | 19 | 1197 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 556 | CP00108706 | Pukekawa | Pukekawa | 2024-11-27 09:13 | 2024-11-27 14:47 | 0.0068115 | 2.0394e-05 | 1 | 334 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 557 | NF012891 | Te Hihi | Te Hihi | 2024-11-28 02:43 | 2024-11-28 09:40 | 1.5198 | 0.015112 | 741 | 51550 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 558 | CP00108678 | Glen Murray | Glen Murray | 2024-11-28 09:00 | 2024-11-28 15:26 | 0.10234 | 0.00026512 | 13 | 5018 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 559 | CP00108698 | Pukekawa | Pukekawa | 2024-11-28 09:37 | 2024-11-28 16:11 | 0.24105 | 0.00061181 | 30 | 11820 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 560 | CP00108982 | Waiuku West | Waiuku West | 2024-11-28 09:43 | 2024-11-28 11:36 | 0.043785 | 0.00038748 | 19 | 2147 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 561 | NF012895 | Anchor Factory | Anchor Factory | 2024-11-28 15:30 | 2024-11-28 15:50 | 0.00040787 | 2.0394e-05 | 1 | 20 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 562 | CP00108771 | Mercer | Mercer | 2024-11-29 09:06 | 2024-11-29 15:37 | 1.0446 | 0.0026716 | 131 | 50830 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 563 | CP00109459 | Manukau Heads | Manukau Heads | 2024-11-29 09:44 | 2024-11-29 11:28 | 0.061507 | 0.00059141 | 29 | 3016 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 564 | NF012904 | Ararimu | Ararimu | 2024-11-30 16:32 | 2024-11-30 21:19 | 0.32777 | 0.001142 | 56 | 16072 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 565 | CP00108817 | Pakington | Pakington | 2024-12-02 09:06 | 2024-12-02 16:53 | 0.67459 | 0.0014445 | 71 | 33157 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 566 | NF012899 | Pukekawa | Pukekawa | 2024-12-02 16:59 | 2024-12-02 21:28 | 0.005473 | 2.0346e-05 | 1 | 269 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 567 | CP00108912 | Great South Road | Great South Road | 2024-12-03 09:10 | 2024-12-03 15:35 | 0.86946 | 0.0022583 | 111 | 41901 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 568 | CP00108912 | Great South Road | Pukekohe East | 2024-12-03 09:10 | 2024-12-03 15:35 | 0.7363 | 0.0019125 | 94 | 35483 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 569 | CP00109517 | Port Waikato | Port Waikato | 2024-12-03 09:42 | 2024-12-03 14:12 | 0.010987 | 4.0691e-05 | 2 | 540 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 570 | CP00108679 | Glen Murray | Glen Murray | 2024-12-04 09:01 | 2024-12-04 15:10 | 0.075075 | 0.00020345 | 10 | 3690 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 571 | CP00108927 | Mercer | Mercer | 2024-12-04 09:03 | 2024-12-04 14:40 | 0.19884 | 0.00059002 | 29 | 9773 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 572 | NF012905 | Manukau Heads | Manukau Heads | 2024-12-04 11:19 | 2024-12-04 13:35 | 0.038739 | 0.00028484 | 14 | 1904 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 573 | CP00108809 | Glenbrook | Glenbrook | 2024-12-05 09:11 | 2024-12-05 16:28 | 0.45344 | 0.0010376 | 51 | 21850 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 574 | CP00109086 | Pukekawa | Pukekawa | 2024-12-05 09:19 | 2024-12-05 15:37 | 0.60756 | 0.0016073 | 79 | 29862 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 575 | NF012910 | Otaua | Otaua | 2024-12-06 04:07 | 2024-12-06 11:14 | 0.012777 | 4.0691e-05 | 2 | 628 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 576 | CP00104137 | Waiuku South | Waiuku South | 2024-12-06 09:07 | 2024-12-06 15:27 | 0.57985 | 0.0015259 | 75 | 26220 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 577 | CP00108542 | Mercer | Mercer | 2024-12-06 09:08 | 2024-12-06 15:02 | 0.92189 | 0.0026042 | 128 | 45312 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 578 | CP00108872 | Otaua | Otaua | 2024-12-06 09:30 | 2024-12-06 13:34 | 0.0049643 | 2.0345e-05 | 1 | 244 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 579 | CP00108971 | Pukekawa | Pukekawa | 2024-12-07 09:07 | 2024-12-07 13:33 | 0.41672 | 0.0015666 | 77 | 20482 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 580 | NF012916 | Otaua | Otaua | 2024-12-08 03:55 | 2024-12-08 16:09 | 1.6881 | 0.011292 | 555 | 82970 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 581 | CP00108683 | Glen Murray | Glen Murray | 2024-12-10 09:01 | 2024-12-10 14:44 | 0.09072 | 0.00026449 | 13 | 4459 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 582 | NF012917 | Hunua | Hunua | 2024-12-10 12:38 | 2024-12-11 00:05 | 0.055909 | 8.1382e-05 | 4 | 2748 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 583 | CP00108292 | Anchor Factory | Anchor Factory | 2024-12-11 09:17 | 2024-12-11 14:19 | 0.39324 | 0.0013021 | 64 | 19328 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 584 | CP00108689 | Glen Murray | Glen Murray | 2024-12-12 09:10 | 2024-12-12 14:33 | 0.065716 | 0.00020345 | 10 | 3230 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 585 | NF012924 | Kaiaua | Kaiaua | 2024-12-13 05:06 | 2024-12-13 11:30 | 0.093754 | 0.00024415 | 12 | 4608 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 586 | NF012921 | Railway | Railway | 2024-12-13 07:18 | 2024-12-13 11:26 | 0.098045 | 0.0016073 | 79 | 4819 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 587 | CP00109589 | Drury Hills | Drury Hills | 2024-12-13 08:32 | 2024-12-13 17:03 | 0.96688 | 0.0018921 | 93 | 47523 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 588 | CP00108883 | Titi Mauku | Titi Mauku | 2024-12-13 09:07 | 2024-12-13 14:55 | 0.39649 | 0.0011393 | 56 | 19488 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 589 | CP00109989 | Waiau Pa | Waiau Pa | 2024-12-13 09:33 | 2024-12-13 18:05 | 0.54168 | 0.001058 | 52 | 26624 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 590 | CP00109109 | Razorback | Mercer | 2024-12-14 09:01 | 2024-12-14 14:14 | 0.50308 | 0.0016073 | 79 | 24498 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 591 | CP00109109 | Razorback | Razorback | 2024-12-14 09:01 | 2024-12-14 14:14 | 0.87243 | 0.0027873 | 137 | 42483 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 592 | CP00108974 | Kaiaua | Kaiaua | 2024-12-14 09:04 | 2024-12-14 15:24 | 0.41749 | 0.0010987 | 54 | 20520 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 593 | NF012927 | Hunua | Hunua | 2024-12-15 05:57 | 2024-12-15 13:15 | 0.071291 | 0.00016276 | 8 | 3504 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 594 | CP00110449 | Pukekawa | Pukekawa | 2024-12-15 09:01 | 2024-12-15 10:29 | 0.13786 | 0.0015666 | 77 | 6776 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 595 | NF012928 | Hunua | Hunua | 2024-12-16 06:15 | 2024-12-16 14:34 | 0.04476 | 0.00016276 | 8 | 2200 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 596 | NF012920 | Anchor Factory | Anchor Factory | 2024-12-16 08:50 | 2024-12-16 10:27 | 0.055421 | 0.00093589 | 46 | 2724 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 597 | CP00109615 | Glen Murray | Glen Murray | 2024-12-17 09:01 | 2024-12-17 14:13 | 0.063478 | 0.00020345 | 10 | 3120 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 598 | CP00108892 | Otaua | Otaua | 2024-12-17 09:08 | 2024-12-17 12:23 | 0.27772 | 0.0014242 | 70 | 13650 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 599 | CP00109471 | Manukau Heads | Manukau Heads | 2024-12-17 09:10 | 2024-12-17 13:37 | 0.16297 | 0.00061036 | 30 | 8010 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 600 | NF012954 | Te Toro | Te Toro | 2024-12-17 17:01 | 2024-12-17 19:40 | 0.00647 | 4.0692e-05 | 2 | 318 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 601 | CP00109377 | Drury Hills | Drury Hills | 2024-12-18 08:35 | 2024-12-18 15:34 | 0.085248 | 0.00020345 | 10 | 4190 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 602 | CP00109620 | Railway | Railway | 2024-12-18 09:10 | 2024-12-18 16:11 | 0.051393 | 0.00012207 | 6 | 2526 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 603 | NF012951 | Drury | Drury | 2024-12-19 05:14 | 2024-12-19 05:33 | 0.1438 | 0.0075687 | 372 | 7068 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 604 | NF012955 | Kaiaua | Kaiaua | 2024-12-19 05:48 | 2024-12-19 12:01 | 0.54204 | 0.0049033 | 243 | 26642 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 605 | NF012948 | Onewhero | Onewhero | 2024-12-21 11:48 | 2024-12-21 20:18 | 0.079714 | 0.00032553 | 10 | 3918 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 606 | NF012977 | Onewhero | Onewhero | 2024-12-23 11:36 | 2024-12-23 19:36 | 0.029989 | 0.00016276 | 8 | 1474 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 607 | NF012970 | Pakington | Pakington | 2024-12-27 13:43 | 2024-12-27 20:00 | 0.42555 | 0.0026042 | 128 | 20916 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 608 | NF012972 | Port Waikato | Port Waikato | 2024-12-28 01:58 | 2024-12-28 02:14 | 0.018881 | 0.0011801 | 58 | 928 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 609 | NF012944 | Razorback | Razorback | 2024-12-28 21:16 | 2024-12-29 13:30 | 0.17251 | 0.00077313 | 38 | 8479 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 610 | NF012943 | Whangarata | Whangarata | 2024-12-28 21:54 | 2024-12-29 05:00 | 0.13867 | 0.00032553 | 16 | 6816 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 611 | NF012937 | Manukau Heads | Pukekawa | 2024-12-31 17:06 | 2024-12-31 22:41 | 0.10224 | 0.00030518 | 15 | 5025 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 612 | NF012957 | Pukekohe East | Pukekohe East | 2025-01-02 08:33 | 2025-01-02 09:40 | 0.27067 | 0.0040398 | 199 | 13333 | Unplanned | Human Error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 613 | NF012958 | Pukekohe West | Anchor Factory | 2025-01-02 08:33 | 2025-01-02 16:57 | 0.026391 | 0.0065976 | 325 | 1300 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 614 | NF012958 | Pukekohe West | Pukekohe West | 2025-01-02 08:33 | 2025-01-02 16:57 | 7.0786 | 0.090499 | 3027 | 348690 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 615 | NF012941 | Pukekohe East | Pukekohe East | 2025-01-04 02:59 | 2025-01-04 05:45 | 0.38126 | 0.0040398 | 199 | 18781 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 616 | NF012956 | Manukau Heads | Manukau Heads | 2025-01-06 12:43 | 2025-01-06 23:22 | 0.2334 | 0.00056842 | 28 | 11497 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 617 | NF012959 | Glen Murray | Glen Murray | 2025-01-07 18:00 | 2025-01-08 03:50 | 0.03378 | 8.1202e-05 | 4 | 1664 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 618 | NF012962 | Blackbridge | Blackbridge | 2025-01-08 00:19 | 2025-01-08 14:03 | 0.083638 | 0.0001015 | 5 | 4120 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 619 | CP00108814 | Paparata | Paparata | 2025-01-08 09:16 | 2025-01-08 15:00 | 0.4609 | 0.0013398 | 66 | 22704 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 620 | NF012963 | Watercare Plant 3 | Pukekawa | 2025-01-08 09:55 | 2025-01-08 11:23 | 0.053593 | 0.00060901 | 30 | 2640 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 621 | NF012961 | Railway | Railway | 2025-01-08 19:48 | 2025-01-08 20:05 | 0.0017256 | 0.0001015 | 5 | 85 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 622 | CP00109778 | Waiuku South | Waiuku South | 2025-01-09 09:00 | 2025-01-09 12:08 | 0.099229 | 0.00052781 | 26 | 4888 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 623 | CP00109853 | Glenbrook | Glenbrook | 2025-01-09 09:02 | 2025-01-09 10:15 | 0.041494 | 0.00056841 | 28 | 2117 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 624 | NF012964 | Church Corner | Church Corner | 2025-01-09 14:50 | 2025-01-09 20:34 | 0.027933 | 8.1202e-05 | 4 | 1376 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 625 | NF012966 | Pakington | Pakington | 2025-01-10 02:41 | 2025-01-10 06:34 | 0.034409 | 0.00030451 | 15 | 1695 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 626 | CP00110361 | Mercer | Mercer | 2025-01-13 09:05 | 2025-01-13 14:45 | 0.20016 | 0.00058871 | 29 | 9860 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 627 | CP00109315 | Glen Murray | Glen Murray | 2025-01-14 09:01 | 2025-01-14 15:30 | 0.10266 | 0.00026391 | 13 | 5057 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 628 | CP00108945 | Paparata | Paparata | 2025-01-14 09:08 | 2025-01-14 15:28 | 0.20057 | 0.00052781 | 26 | 9880 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 629 | NF012982 | Drury | Drury | 2025-01-14 09:32 | 2025-01-14 10:54 | 0.0019489 | 0.00024361 | 12 | 96 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 630 | CP00110487 | Glen Murray | Glen Murray | 2025-01-15 09:00 | 2025-01-15 15:06 | 0.2972 | 0.00081202 | 40 | 14640 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 631 | CP00109452 | Glenbrook | Glenbrook | 2025-01-15 09:05 | 2025-01-15 16:21 | 1.8233 | 0.0041819 | 206 | 90249 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 632 | CP00109452 | Glenbrook | Waiuku South | 2025-01-15 09:05 | 2025-01-15 16:21 | 0.008851 | 2.03e-05 | 1 | 438 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 633 | NF012984 | Red Hill | Red Hill | 2025-01-16 08:57 | 2025-01-16 09:48 | 0.14805 | 0.002903 | 143 | 7293 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 634 | CP00108278 | Pukekohe East | Great South Road | 2025-01-16 09:02 | 2025-01-16 17:05 | 0.73538 | 0.0015225 | 75 | 36225 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 635 | CP00108278 | Pukekohe East | Pukekohe East | 2025-01-16 09:02 | 2025-01-16 17:05 | 1.9022 | 0.0039383 | 194 | 93702 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 636 | CP00109538 | Te Hihi | Te Hihi | 2025-01-16 09:05 | 2025-01-16 15:00 | 0.079273 | 0.0002233 | 11 | 3905 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 637 | CP00110524 | Glen Murray | Glen Murray | 2025-01-16 09:20 | 2025-01-16 15:15 | 0.2162 | 0.00060901 | 30 | 10650 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 638 | CP00109316 | Glen Murray | Glen Murray | 2025-01-17 09:05 | 2025-01-17 15:11 | 0.08173 | 0.0002233 | 11 | 4026 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 639 | NF013051 | Mercer | Mercer | 2025-01-21 09:27 | 2025-01-21 12:45 | 0.052254 | 0.00026391 | 13 | 2574 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 640 | NF013048 | Hunua | Hunua | 2025-01-21 17:43 | 2025-01-21 23:23 | 0.021194 | 0.0001218 | 6 | 1044 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 641 | NF013050 | Otaua | Otaua | 2025-01-21 18:46 | 2025-01-22 00:12 | 0.00077142 | 2.03e-05 | 1 | 38 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 642 | CP00110636 | Hunua | Hunua | 2025-01-22 08:35 | 2025-01-22 14:39 | 0.73155 | 0.0020097 | 99 | 36036 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 643 | CP00109483 | Pakington | Pakington | 2025-01-22 09:05 | 2025-01-22 14:43 | 1.1322 | 0.0033496 | 165 | 56108 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 644 | CP00111485 | Waiau Pa | Waiau Pa | 2025-01-23 08:41 | 2025-01-23 11:08 | 0.1313 | 0.00089322 | 44 | 6468 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 645 | CP00109814 | Port Waikato | Port Waikato | 2025-01-23 09:23 | 2025-01-23 16:11 | 0.16565 | 0.00040601 | 20 | 8160 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 646 | CP00110642 | Pukekohe East | Pukekohe East | 2025-01-23 09:30 | 2025-01-23 15:55 | 0.55491 | 0.0014413 | 71 | 27335 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 647 | CP00111766 | Pukekohe East | Pukekohe East | 2025-01-23 09:30 | 2025-01-23 15:55 | 0.17194 | 0.00044661 | 22 | 8470 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 648 | CP00109871 | Glen Murray | Glen Murray | 2025-01-24 09:04 | 2025-01-24 17:19 | 0.11054 | 0.0002233 | 11 | 5445 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 649 | NF013039 | Railway | Railway | 2025-01-25 05:39 | 2025-01-25 06:21 | 0.36289 | 0.020341 | 1002 | 17876 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 650 | NF013040 | Anchor Factory | Anchor Factory | 2025-01-26 14:32 | 2025-01-26 19:31 | 0.12377 | 0.0018473 | 91 | 6097 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 651 | CP00111566 | Waiau Pa | Waiau Pa | 2025-01-28 08:38 | 2025-01-28 11:39 | 0.040418 | 0.0002233 | 11 | 1991 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 652 | NF013059 | Pukekohe Hill | Anchor Factory | 2025-01-28 08:42 | 2025-01-28 08:53 | 0.002233 | 0.000203 | 10 | 110 | Unplanned | Human Error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 653 | NF013059 | Pukekohe Hill | Pukekohe Hill | 2025-01-28 08:42 | 2025-01-28 08:53 | 0.0031263 | 0.00028421 | 14 | 154 | Unplanned | Human Error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 654 | CP00109526 | Waiau Pa | Te Hihi | 2025-01-28 09:03 | 2025-01-28 15:17 | 0.068331 | 0.0001827 | 9 | 3366 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 655 | CP00109526 | Waiau Pa | Waiau Pa | 2025-01-28 09:03 | 2025-01-28 15:17 | 0.60739 | 0.001624 | 80 | 29920 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 656 | CP00110735 | Pukekawa | Pukekawa | 2025-01-28 09:03 | 2025-01-28 17:13 | 0.14921 | 0.00030451 | 15 | 7350 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 657 | CP00109522 | Pukekohe Hill | Pukekohe Hill | 2025-01-28 09:12 | 2025-01-28 16:12 | 2.0719 | 0.004933 | 243 | 63840 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 658 | CP00109525 | Pukekohe Hill | Pukekohe Hill | 2025-01-28 09:12 | 2025-01-28 16:12 | 0.8782 | 0.0020909 | 103 | 43260 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 659 | CP00110583 | Glen Murray | Glen Murray | 2025-01-28 09:48 | 2025-01-28 17:26 | 0.018595 | 4.0601e-05 | 2 | 916 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 660 | CP00111641 | Racecourse | Racecourse | 2025-01-29 08:33 | 2025-01-29 11:24 | 0.57278 | 0.0033496 | 165 | 28215 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 661 | CP00109958 | Glen Murray | Glen Murray | 2025-01-29 09:02 | 2025-01-29 14:28 | 0.072797 | 0.0002233 | 11 | 3586 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 662 | CP00111228 | Paparata | Paparata | 2025-01-30 09:14 | 2025-01-30 15:20 | 0.2229 | 0.00060901 | 30 | 10980 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 663 | NF013054 | Manukau Heads | Manukau Heads | 2025-01-30 12:34 | 2025-01-30 21:41 | 0.2314 | 0.0083841 | 413 | 11399 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 664 | CP00110419 | Kaiaua | Kaiaua | 2025-01-30 21:33 | 2025-01-31 04:47 | 1.7885 | 0.004121 | 203 | 87234 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 665 | CP00111507 | Waiau Pa | Waiau Pa | 2025-01-31 09:01 | 2025-01-31 14:24 | 0.63603 | 0.0019691 | 97 | 31008 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 666 | NF013056 | Hunua | Hunua | 2025-01-31 10:26 | 2025-01-31 10:36 | 0.0012181 | 0.00012181 | 6 | 60 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 667 | NF013061 | Te Toro | Te Toro | 2025-02-01 08:50 | 2025-02-01 12:43 | 0.075666 | 0.00032475 | 16 | 3728 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 668 | NF013162 | Hunua | Hunua | 2025-02-03 10:41 | 2025-02-03 12:26 | 0.58041 | 0.0056019 | 276 | 28596 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 669 | CP00111809 | Ararimu | Ararimu | 2025-02-04 08:47 | 2025-02-04 10:45 | 0.03353 | 0.00028415 | 14 | 1652 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 670 | CP00110737 | Pukekawa | Pukekawa | 2025-02-04 09:05 | 2025-02-04 14:16 | 0.094684 | 0.00030445 | 15 | 4665 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 671 | CP00110535 | Kaiaua | Kaiaua | 2025-02-04 09:18 | 2025-02-04 15:36 | 0.79791 | 0.0021109 | 104 | 39312 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 672 | NF013165 | Tuakau | Tuakau | 2025-02-04 20:30 | 2025-02-04 21:55 | 0.42095 | 0.0049524 | 244 | 20740 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 673 | CP00111277 | Titi Mauku | Titi Mauku | 2025-02-05 09:02 | 2025-02-05 15:56 | 0.96633 | 0.0023341 | 115 | 47610 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 674 | CP00110717 | Kaiaua | Kaiaua | 2025-02-05 09:08 | 2025-02-05 15:19 | 0.30873 | 0.00083217 | 41 | 15211 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 675 | CP00111285 | Pukekohe East | Pukekohe East | 2025-02-05 10:07 | 2025-02-05 14:17 | 0.015223 | 6.089e-05 | 3 | 750 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 676 | NF013166 | Blackbridge | Blackbridge | 2025-02-06 02:05 | 2025-02-06 14:56 | 0.56146 | 0.010433 | 514 | 27662 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 677 | NF013168 | Port Waikato | Port Waikato | 2025-02-07 01:01 | 2025-02-07 01:23 | 0.025899 | 0.0011772 | 58 | 1276 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 678 | CP00111454 | Pukekohe Hill | Pukekohe Hill | 2025-02-11 05:16 | 2025-02-11 07:00 | 0.0021109 | 2.0297e-05 | 206 | 7176 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 679 | CP00111829 | Manukau Heads | Manukau Heads | 2025-02-11 08:43 | 2025-02-11 14:00 | 0.10295 | 0.00032475 | 16 | 5072 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 680 | CP00111530 | Ararimu | Ararimu | 2025-02-11 09:04 | 2025-02-11 14:46 | 0.034707 | 0.00010148 | 5 | 1710 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 681 | CP00110645 | Pukekohe East | Pukekohe East | 2025-02-11 09:36 | 2025-02-11 15:13 | 0.48564 | 0.0014411 | 71 | 23927 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 682 | NF013195 | Titi Mauku | Titi Mauku | 2025-02-11 11:43 | 2025-02-12 00:24 | 0.12357 | 0.00016238 | 8 | 6088 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 683 | CP00111543 | Titi Mauku | Titi Mauku | 2025-02-12 09:03 | 2025-02-12 17:15 | 0.55922 | 0.0011366 | 56 | 27552 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 684 | CP00110736 | Kaiaua | Kaiaua | 2025-02-12 09:07 | 2025-02-12 16:12 | 0.89712 | 0.0021109 | 104 | 44200 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 685 | CP00111479 | Pukekawa | Pukekawa | 2025-02-12 09:37 | 2025-02-12 15:31 | 0.38799 | 0.001096 | 54 | 19116 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 686 | CP00111959 | Pukekawa | Pukekawa | 2025-02-12 09:37 | 2025-02-12 15:32 | 0.28101 | 0.00079157 | 39 | 13845 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 687 | NF013244 | Manukau Heads | Manukau Heads | 2025-02-12 21:40 | 2025-02-13 01:47 | 0.10528 | 0.00042623 | 21 | 5187 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 688 | NF013243 | Kaiaua | Kaiaua | 2025-02-13 00:24 | 2025-02-13 03:44 | 0.45503 | 0.0049524 | 246 | 22419 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 689 | CP00111951 | River Road | River Road | 2025-02-13 08:39 | 2025-02-13 09:52 | 0.022225 | 0.00030445 | 15 | 1095 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 690 | CP00110739 | Kaiaua | Kaiaua | 2025-02-13 09:06 | 2025-02-13 16:00 | 0.34452 | 0.00083217 | 41 | 16974 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 691 | NF013251 | Whangarata | Whangarata | 2025-02-13 16:22 | 2025-02-14 15:33 | 0.21133 | 0.0036534 | 176 | 10412 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 692 | CP00111459 | Pukekohe Hill | Pukekohe Hill | 2025-02-13 17:02 | 2025-02-13 18:20 | 0.0015831 | 2.0297e-05 | 206 | 5382 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 693 | CP00110203 | Razorback | Razorback | 2025-02-14 09:11 | 2025-02-14 15:05 | 0.007185 | 2.0297e-05 | 1 | 354 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 694 | CP00111572 | Manukau Heads | Manukau Heads | 2025-02-14 09:20 | 2025-02-14 14:46 | 0.099251 | 0.00030445 | 15 | 4890 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 695 | NF013246 | Titi Mauku | Titi Mauku | 2025-02-15 15:24 | 2025-02-15 18:56 | 0.016481 | 0.00014208 | 7 | 812 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 696 | NF013247 | Glen Murray | Glen Murray | 2025-02-16 14:02 | 2025-02-16 22:55 | 0.046602 | 0.00014208 | 7 | 2296 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 697 | CP00111846 | Onewhero | Onewhero | 2025-02-17 08:37 | 2025-02-17 16:01 | 1.6672 | 0.0037549 | 185 | 82140 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 698 | NF013253 | Te Toro | Te Toro | 2025-02-17 10:09 | 2025-02-17 14:32 | 0.080071 | 0.00030445 | 15 | 3945 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 699 | NF013252 | Port Waikato | Port Waikato | 2025-02-17 14:59 | 2025-02-17 16:56 | 0.70156 | 0.00684 | 337 | 34565 | Unplanned | Adverse Environment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 700 | CP00111921 | Razorback | Razorback | 2025-02-18 09:01 | 2025-02-18 14:12 | 0.72591 | 0.0023341 | 115 | 35765 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 701 | CP00111387 | Kaiaua | Kaiaua | 2025-02-18 09:05 | 2025-02-18 14:57 | 0.25006 | 0.00071039 | 35 | 12320 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 702 | NF013260 | Titi Mauku | Titi Mauku | 2025-02-18 19:45 | 2025-02-18 21:53 | 0.0077939 | 6.089e-05 | 3 | 384 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 703 | NF013261 | Waiuku South | Waiuku South | 2025-02-19 08:05 | 2025-02-19 08:30 | 0.0035519 | 0.00014208 | 7 | 175 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 704 | NF013259 | Te Toro | Te Toro | 2025-02-19 08:39 | 2025-02-19 12:23 | 0.027117 | 0.00016238 | 8 | 1336 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 705 | CP00111938 | Pukekohe West | Pukekohe West | 2025-02-19 08:53 | 2025-02-19 14:55 | 0.95516 | 0.0026386 | 130 | 47422 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 706 | CP00112002 | Glen Murray | Glen Murray | 2025-02-19 09:03 | 2025-02-19 15:52 | 0.34866 | 0.00085246 | 42 | 17178 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 707 | CP00111695 | Paparata | Paparata | 2025-02-19 09:06 | 2025-02-19 17:36 | 0.26913 | 0.00052772 | 26 | 13260 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 708 | NF013262 | Paparata | Paparata | 2025-02-19 16:48 | 2025-02-19 17:48 | 0.031664 | 0.00052773 | 26 | 1560 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 709 | NF013263 | Drury Hills | Drury | 2025-02-19 19:24 | 2025-02-20 10:00 | 0.0014208 | 6.089e-05 | 1 | 70 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 710 | NF013263 | Drury Hills | Drury Hills | 2025-02-19 19:24 | 2025-02-20 10:00 | 1.7188 | 0.048083 | 821 | 84684 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 711 | CP00111689 | Glen Murray | Glen Murray | 2025-02-20 09:04 | 2025-02-20 16:03 | 0.11056 | 0.00026386 | 13 | 4609 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 712 | CP00111777 | Pukekawa | Mercer | 2025-02-20 09:04 | 2025-02-20 15:47 | 0.35172 | 0.00087276 | 43 | 17446 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 713 | CP00111777 | Pukekawa | Pukekawa | 2025-02-20 09:04 | 2025-02-20 15:47 | 0.85886 | 0.0021312 | 105 | 42600 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 714 | CP00111632 | Kaiaua | Kaiaua | 2025-02-21 09:08 | 2025-02-21 14:55 | 0.30989 | 0.00089306 | 44 | 15268 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 715 | NF013265 | Titi Mauku | Titi Mauku | 2025-02-22 20:10 | 2025-02-22 20:45 | 0.00071039 | 2.0297e-05 | 1 | 35 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 716 | NF013267 | Port Waikato | Port Waikato | 2025-02-23 09:34 | 2025-02-23 10:02 | 0.032962 | 0.0011772 | 58 | 1624 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 717 | NF013268 | Pukekohe Hill | Pukekohe Hill | 2025-02-25 01:11 | 2025-02-25 02:01 | 1.2067 | 0.024133 | 1189 | 59450 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 718 | CP00113401 | Pukekohe West | Pukekohe West | 2025-02-25 08:33 | 2025-02-25 11:12 | 0.5228 | 0.0032881 | 162 | 25758 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 719 | CP00111924 | Kaiaua | Kaiaua | 2025-02-25 09:06 | 2025-02-25 14:35 | 0.23372 | 0.00071039 | 35 | 11515 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 720 | CP00112009 | Port Waikato | Glen Murray | 2025-02-25 09:07 | 2025-02-25 15:33 | 0.037783 | 0.00010539 | 5 | 1855 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 721 | CP00112009 | Port Waikato | Port Waikato | 2025-02-25 09:07 | 2025-02-25 15:33 | 0.15869 | 0.00044263 | 21 | 7794 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 722 | CP00111837 | Pukekawa | Pukekawa | 2025-02-25 09:33 | 2025-02-25 16:28 | 0.64016 | 0.0015426 | 76 | 31955 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 723 | NF013271 | Pukekohe Hill | Pukekohe Hill | 2025-02-25 11:20 | 2025-02-25 11:50 | 0.52818 | 0.024173 | 1191 | 26023 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 724 | CP00111694 | Ararimu | Ararimu | 2025-02-26 09:08 | 2025-02-26 16:29 | 0.82348 | 0.0018673 | 92 | 40131 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 725 | NF013272 | Manukau Heads | Manukau Heads | 2025-02-27 06:30 | 2025-02-27 16:40 | 0.7198 | 0.014695 | 413 | 35464 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 726 | CP00112049 | Paparata | Paparata | 2025-02-27 09:14 | 2025-02-27 15:32 | 0.099738 | 0.00026386 | 13 | 4914 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 727 | NF013277 | Port Waikato | Port Waikato | 2025-02-28 11:09 | 2025-02-28 12:35 | 0.0017456 | 2.0297e-05 | 1 | 86 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 728 | CP00114009 | Mercer | Mercer | 2025-03-01 08:34 | 2025-03-01 12:44 | 0.030406 | 0.00012162 | 6 | 1500 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 729 | CP00112914 | Te Toro | Manukau Heads | 2025-03-03 09:05 | 2025-03-03 15:25 | 0.10014 | 0.00026352 | 13 | 4940 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 730 | CP00112914 | Te Toro | Te Toro | 2025-03-03 09:05 | 2025-03-03 15:25 | 0.20797 | 0.0005473 | 27 | 10260 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 731 | CP00112097 | Kaiaua | Kaiaua | 2025-03-04 09:00 | 2025-03-04 15:34 | 0.64691 | 0.0016419 | 81 | 31520 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 732 | CP00113157 | Pukekawa | Pukekawa | 2025-03-04 09:00 | 2025-03-04 17:22 | 0.78353 | 0.0015608 | 77 | 34638 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 733 | NF013295 | Manukau Heads | Manukau Heads | 2025-03-04 20:13 | 2025-03-05 12:24 | 0.67533 | 0.027284 | 413 | 33316 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 734 | CP00113211 | Glenbrook | Glenbrook | 2025-03-05 08:49 | 2025-03-05 16:10 | 0.053635 | 0.00012162 | 6 | 2646 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 735 | CP00111698 | Glen Murray | Glen Murray | 2025-03-05 09:00 | 2025-03-05 17:08 | 0.70233 | 0.0014392 | 71 | 36112 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 736 | CP00113172 | Paparata | Paparata | 2025-03-05 09:25 | 2025-03-05 17:48 | 0.56078 | 0.0011149 | 55 | 27665 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 737 | CP00113908 | Pukekawa | Pukekawa | 2025-03-06 08:35 | 2025-03-06 12:40 | 0.014899 | 6.0811e-05 | 3 | 735 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 738 | CP00111734 | Pakington | Pakington | 2025-03-06 09:04 | 2025-03-06 15:41 | 0.60355 | 0.0015203 | 75 | 29775 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 739 | NF013284 | Otaua | Otaua | 2025-03-06 10:30 | 2025-03-06 12:30 | 0.017027 | 0.0001419 | 7 | 840 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 740 | CP00114250 | Pukekohe Hill | Pukekohe Hill | 2025-03-07 08:38 | 2025-03-07 13:12 | 1.4274 | 0.0052095 | 257 | 70418 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 741 | CP00114274 | Pukekohe Hill | Pukekohe Hill | 2025-03-07 08:38 | 2025-03-07 13:12 | 0.75536 | 0.0027568 | 136 | 37264 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 742 | CP00112098 | Kaiaua | Kaiaua | 2025-03-07 09:00 | 2025-03-07 13:13 | 0.40827 | 0.0020068 | 88 | 19481 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 743 | CP00111704 | Glen Murray | Glen Murray | 2025-03-07 09:07 | 2025-03-07 14:10 | 0.079845 | 0.00026352 | 13 | 3333 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 744 | CP00114327 | Pukekawa | Pukekawa | 2025-03-08 09:09 | 2025-03-08 12:40 | 0.12831 | 0.00060811 | 30 | 6330 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 745 | CP00113521 | Whangarata | Whangarata | 2025-03-10 09:08 | 2025-03-10 18:31 | 0.11412 | 0.0002027 | 10 | 5630 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 746 | CP00113410 | Blackbridge | Blackbridge | 2025-03-10 10:12 | 2025-03-10 11:37 | 0.16024 | 0.0018851 | 93 | 6375 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 747 | NF013285 | Onewhero | Onewhero | 2025-03-10 19:25 | 2025-03-10 19:57 | 0.007784 | 0.00024325 | 12 | 384 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 748 | CP00114030 | Hunua | Hunua | 2025-03-11 08:40 | 2025-03-11 12:10 | 0.034054 | 0.00016216 | 8 | 1680 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 749 | CP00113437 | Pukekawa | Pukekawa | 2025-03-11 09:04 | 2025-03-11 16:58 | 0.73983 | 0.0015608 | 77 | 32706 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 750 | CP00113141 | Ararimu | Ararimu | 2025-03-11 09:06 | 2025-03-11 15:20 | 0.27292 | 0.00072973 | 36 | 13464 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 751 | NF013287 | Te Toro | Manukau Heads | 2025-03-11 11:45 | 2025-03-11 11:49 | 0.0017838 | 0.00044595 | 22 | 88 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 752 | NF013286 | Onewhero | Onewhero | 2025-03-11 12:30 | 2025-03-11 12:40 | 0.002027 | 0.0002027 | 10 | 100 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 753 | CP00113524 | Glenbrook | Glenbrook | 2025-03-12 08:39 | 2025-03-12 15:12 | 0.39831 | 0.0010135 | 50 | 19650 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 754 | CP00113442 | Paparata | Paparata | 2025-03-12 09:05 | 2025-03-12 15:26 | 0.32437 | 0.00085136 | 42 | 16002 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 755 | CP00113297 | Kaiaua | Kaiaua | 2025-03-12 09:08 | 2025-03-12 15:17 | 0.60586 | 0.0016419 | 81 | 29889 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 756 | NF013319 | Manukau Heads | Manukau Heads | 2025-03-12 11:04 | 2025-03-12 22:42 | 0.68137 | 0.026737 | 413 | 33614 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 757 | NF013319 | Manukau Heads | Te Toro | 2025-03-12 11:04 | 2025-03-12 22:42 | 0.022419 | 0.01121 | 553 | 1106 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 758 | NF013320 | Manukau Heads | Manukau Heads | 2025-03-12 11:45 | 2025-03-12 17:42 | 0.0072367 | 2.0271e-05 | 1 | 357 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 759 | NF013321 | Manukau Heads | Manukau Heads | 2025-03-12 15:30 | 2025-03-12 20:11 | 0.051265 | 0.00018244 | 9 | 2529 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 760 | NF013322 | Te Toro | Te Toro | 2025-03-12 16:08 | 2025-03-12 16:57 | 0.12714 | 0.0025947 | 128 | 6272 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 761 | NF013297 | Manukau Heads | Manukau Heads | 2025-03-13 08:56 | 2025-03-13 10:40 | 0.0063245 | 6.0812e-05 | 3 | 312 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 762 | CP00113459 | Paparata | Paparata | 2025-03-13 09:04 | 2025-03-13 15:55 | 0.24993 | 0.00060811 | 30 | 12330 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 763 | CP00111868 | Pakington | Pakington | 2025-03-13 09:05 | 2025-03-13 16:59 | 0.93199 | 0.0019662 | 97 | 45978 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 764 | CP00111708 | Glen Murray | Glen Murray | 2025-03-14 09:08 | 2025-03-14 14:39 | 0.087224 | 0.00026352 | 13 | 3972 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 765 | CP00114592 | Manukau Heads | Manukau Heads | 2025-03-14 09:19 | 2025-03-14 15:22 | 0.14716 | 0.00040541 | 20 | 7260 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 766 | CP00111591 | Port Waikato | Port Waikato | 2025-03-14 09:30 | 2025-03-14 13:53 | 0.031987 | 0.00012162 | 6 | 1578 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 767 | NF013306 | Pukekohe East | Great South Road | 2025-03-14 15:00 | 2025-03-14 15:01 | 0.00010135 | 0.00010135 | 5 | 5 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 768 | NF013296 | Pukekawa | Pukekawa | 2025-03-14 15:26 | 2025-03-14 17:45 | 0.022541 | 0.00016216 | 8 | 1112 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 769 | NF013427 | Anchor Factory | Anchor Factory | 2025-03-15 06:02 | 2025-03-15 14:04 | 1.0861 | 0.0086555 | 324 | 53580 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 770 | NF013301 | Manukau Heads | Manukau Heads | 2025-03-17 01:27 | 2025-03-17 18:52 | 2.2151 | 0.065007 | 978 | 109278 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 771 | NF013301 | Manukau Heads | Te Toro | 2025-03-17 01:27 | 2025-03-17 18:52 | 0.047433 | 0.023716 | 1170 | 2340 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 772 | NF013302 | Pukekohe East | Great South Road | 2025-03-17 08:07 | 2025-03-17 09:20 | 0.0060811 | 0.0015203 | 75 | 300 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 773 | NF013302 | Pukekohe East | Pukekohe East | 2025-03-17 08:07 | 2025-03-17 09:20 | 0.095717 | 0.012811 | 632 | 4722 | Unplanned | Third Party Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 774 | CP00113583 | Hunua | Hunua | 2025-03-17 08:32 | 2025-03-17 15:34 | 1.5825 | 0.00375 | 185 | 78492 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 775 | CP00113438 | Pukekawa | Pukekawa | 2025-03-18 09:05 | 2025-03-18 15:28 | 0.59779 | 0.0015608 | 77 | 26427 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 776 | NF013298 | Patumahoe | Patumahoe | 2025-03-18 09:26 | 2025-03-18 11:39 | 0.0038919 | 0.00016216 | 8 | 192 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 777 | CP00113909 | Hunua | Hunua | 2025-03-19 09:04 | 2025-03-19 16:36 | 1.6767 | 0.0037095 | 183 | 82716 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 778 | NF013309 | Paparata | Paparata | 2025-03-19 16:03 | 2025-03-19 19:00 | 0.046642 | 0.00026352 | 13 | 2301 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 779 | CP00113855 | Glenbrook | Glenbrook | 2025-03-20 08:38 | 2025-03-20 12:01 | 0.20574 | 0.0010135 | 50 | 10150 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 780 | CP00113150 | Pukekohe West | Pukekohe West | 2025-03-20 09:00 | 2025-03-20 20:13 | 3.4514 | 0.0051284 | 253 | 169596 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 781 | CP00113147 | Pukekohe West | Pukekohe West | 2025-03-20 09:01 | 2025-03-20 20:13 | 3.3373 | 0.0049662 | 245 | 1344 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 782 | CP00113904 | Te Toro | Te Toro | 2025-03-20 09:33 | 2025-03-20 16:12 | 0.28308 | 0.00070946 | 35 | 13965 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 783 | CP00114600 | Hingaia | Hingaia | 2025-03-20 11:47 | 2025-03-20 12:02 | 0.0082095 | 0.0005473 | 27 | 15 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 784 | CP00114610 | Hingaia | Hingaia | 2025-03-20 13:36 | 2025-03-20 13:52 | 0.00064865 | 4.0541e-05 | 2 | 32 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 785 | NF013326 | Subtrans (33MO) | Otaua | 2025-03-20 15:28 | 2025-03-20 15:32 | 0.045244 | 0.011311 | 558 | 2232 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 786 | CP00114605 | Hingaia | Hingaia | 2025-03-20 17:39 | 2025-03-20 17:51 | 0.00072973 | 6.0811e-05 | 3 | 36 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 787 | CP00114628 | Hingaia | Hingaia | 2025-03-20 18:15 | 2025-03-20 18:33 | 0.00072973 | 4.0541e-05 | 2 | 36 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 788 | CP00114604 | Hingaia | Hingaia | 2025-03-21 07:44 | 2025-03-21 08:01 | 0.00068919 | 4.0541e-05 | 2 | 34 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 789 | CP00114129 | Waiau Pa | Waiau Pa | 2025-03-21 08:31 | 2025-03-21 17:08 | 3.3221 | 0.0064257 | 317 | 163889 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 790 | CP00114134 | Waiau Pa | Waiau Pa | 2025-03-21 08:31 | 2025-03-21 17:08 | 2.9553 | 0.0057163 | 282 | 98230 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 791 | CP00114135 | Waiau Pa | Waiau Pa | 2025-03-21 08:31 | 2025-03-21 17:08 | 2.861 | 0.0055338 | 273 | 85822 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 792 | NF013328 | Hunua | Hunua | 2025-03-21 08:44 | 2025-03-21 09:56 | 0.45489 | 0.011351 | 563 | 22441 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 793 | CP00113428 | Gateway | Gateway | 2025-03-21 09:50 | 2025-03-21 11:16 | 0.0017433 | 2.027e-05 | 1 | 86 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 794 | CP00114584 | Hingaia | Hingaia | 2025-03-21 10:01 | 2025-03-21 10:13 | 0.0012162 | 0.00010135 | 5 | 60 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 795 | CP00114603 | Hingaia | Hingaia | 2025-03-21 11:03 | 2025-03-21 11:22 | 0.0015406 | 8.1082e-05 | 4 | 76 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 796 | CP00114617 | Hingaia | Hingaia | 2025-03-21 11:45 | 2025-03-21 12:00 | 0.005473 | 0.00036487 | 18 | 270 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 797 | NF013304 | Kaiaua | Kaiaua | 2025-03-21 12:00 | 2025-03-21 15:00 | 0.00077028 | 4.0541e-05 | 2 | 38 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 798 | CP00114624 | Hingaia | Hingaia | 2025-03-21 13:00 | 2025-03-21 13:11 | 0.008919 | 0.00081082 | 40 | 440 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 799 | CP00114623 | Hingaia | Hingaia | 2025-03-21 13:34 | 2025-03-21 13:50 | 0.0051892 | 0.00032433 | 16 | 256 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 800 | CP00114619 | Hingaia | Hingaia | 2025-03-21 14:02 | 2025-03-21 14:14 | 0.015324 | 0.001277 | 63 | 756 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 801 | NF013305 | Hunua | Hunua | 2025-03-21 14:15 | 2025-03-21 14:34 | 0.00077029 | 4.0542e-05 | 2 | 38 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 802 | CP00114613 | Hingaia | Hingaia | 2025-03-21 16:35 | 2025-03-21 16:45 | 0.0024324 | 0.00024324 | 12 | 120 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 803 | CP00114626 | Hingaia | Hingaia | 2025-03-21 17:19 | 2025-03-21 17:31 | 0.00024324 | 2.027e-05 | 1 | 12 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 804 | CP00114585 | Hingaia | Hingaia | 2025-03-21 18:11 | 2025-03-21 18:12 | 2.027e-05 | 2.027e-05 | 1 | 1 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 805 | NF013308 | Te Toro | Te Toro | 2025-03-22 08:48 | 2025-03-22 13:00 | 0.0025135 | 2.027e-05 | 1 | 124 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 806 | CP00113944 | Te Hihi | Blackbridge | 2025-03-22 09:03 | 2025-03-22 16:15 | 0.324 | 0.00075001 | 37 | 15606 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 807 | CP00113944 | Te Hihi | Te Hihi | 2025-03-22 09:03 | 2025-03-22 16:15 | 2.268 | 0.00525 | 259 | 109242 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 808 | CP00113961 | Te Hihi | Te Hihi | 2025-03-22 09:03 | 2025-03-22 16:15 | 0.2627 | 0.00060811 | 30 | 12960 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 809 | CP00114724 | Anchor Factory | Anchor Factory | 2025-03-22 09:07 | 2025-03-22 15:18 | 0.74451 | 0.0020068 | 99 | 35987 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 810 | NF013310 | Te Toro | Te Toro | 2025-03-22 16:17 | 2025-03-23 02:33 | 0.080636 | 0.00024324 | 12 | 3978 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 811 | CP00114116 | Pukekohe Hill | Pukekohe Hill | 2025-03-23 07:01 | 2025-03-23 08:54 | 0.061845 | 0.0005473 | 27 | 3164 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 812 | CP00113301 | Kaiaua | Kaiaua | 2025-03-24 09:00 | 2025-03-24 16:12 | 1.5424 | 0.0036081 | 177 | 76032 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 813 | NF013314 | Glen Murray | Glen Murray | 2025-03-24 09:17 | 2025-03-24 11:41 | 0.0024325 | 8.1083e-05 | 4 | 120 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 814 | CP00111981 | Manukau Heads | Manukau Heads | 2025-03-24 09:35 | 2025-03-24 13:55 | 0.052703 | 0.0002027 | 10 | 2600 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 815 | NF013316 | Waiuku South | Waiuku South | 2025-03-24 16:02 | 2025-03-24 17:15 | 0.005919 | 8.1082e-05 | 4 | 292 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 816 | NF013317 | Te Hihi | Te Hihi | 2025-03-25 02:37 | 2025-03-25 16:05 | 0.60286 | 0.0014595 | 72 | 29741 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 817 | NF013318 | Mercer | Mercer | 2025-03-25 08:00 | 2025-03-25 13:49 | 0.10516 | 0.0013581 | 67 | 5188 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 818 | CP00113844 | Mercer | Mercer | 2025-03-25 08:34 | 2025-03-25 15:17 | 0.2369 | 0.00058784 | 29 | 11687 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 819 | CP00113432 | Razorback | Razorback | 2025-03-25 09:21 | 2025-03-25 16:11 | 0.066487 | 0.00016216 | 8 | 3280 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 820 | CP00113856 | Port Waikato | Port Waikato | 2025-03-25 09:31 | 2025-03-25 11:51 | 0.056757 | 0.00040541 | 20 | 2800 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 821 | CP00114240 | Keri Downs | Keri Downs | 2025-03-26 08:30 | 2025-03-26 15:59 | 0.14562 | 0.00032433 | 16 | 7184 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 822 | CP00114077 | Hunua | Hunua | 2025-03-26 09:00 | 2025-03-26 17:13 | 0.49967 | 0.0010135 | 50 | 25143 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 823 | CP00114254 | Ararimu | Ararimu | 2025-03-26 09:04 | 2025-03-26 15:53 | 1.3431 | 0.0032838 | 162 | 66258 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 824 | CP00114424 | Kaiaua | Kaiaua | 2025-03-26 09:31 | 2025-03-26 14:38 | 0.26137 | 0.00085136 | 42 | 12894 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 825 | CP00114201 | Railway | Railway | 2025-03-27 08:15 | 2025-03-27 15:57 | 0.1592 | 0.0003446 | 17 | 7854 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 826 | CP00114489 | Glen Murray | Glen Murray | 2025-03-27 08:31 | 2025-03-27 18:15 | 0.84049 | 0.0014392 | 71 | 40880 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 827 | CP00114477 | Pukekawa | Pukekawa | 2025-03-27 09:05 | 2025-03-27 15:17 | 0.40719 | 0.0010946 | 54 | 20088 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 828 | CP00115520 | Waiau Pa | Waiau Pa | 2025-03-28 08:30 | 2025-03-28 14:14 | 0.89255 | 0.0025946 | 128 | 37152 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 829 | CP00113520 | Kaiaua | Kaiaua | 2025-03-28 09:04 | 2025-03-28 14:40 | 0.81049 | 0.0024122 | 119 | 39984 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 830 | CP00115381 | Manukau Heads | Manukau Heads | 2025-03-28 09:09 | 2025-03-28 14:51 | 0.31889 | 0.00093244 | 46 | 15732 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 831 | NF013338 | Pukekawa | Pukekawa | 2025-03-30 15:44 | 2025-03-30 18:55 | 0.28263 | 0.0014797 | 73 | 13943 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 832 | NF013336 | Port Waikato | Port Waikato | 2025-03-31 01:39 | 2025-03-31 01:58 | 0.022338 | 0.0011757 | 58 | 1102 | Unplanned | Cause Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 833 | CP00114807 | Kaiaua | Kaiaua | 2025-03-31 09:53 | 2025-03-31 14:52 | 0.078791 | 0.00026352 | 13 | 3887 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Counties Energy | 2025 |  | 834 | NF013337 | Manukau Heads | Manukau Heads | 2025-03-31 17:00 | 2025-03-31 18:40 | 0.018568 | 0.0002027 | 10 | 916 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 9 | 46579 | Anama School Rd | SY02 Anama_22 | 2024-04-02 12:49 | 2024-04-02 16:05 | 0.17435 | 0.00088955 | 19 | 3724 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 10 | 46580 | Wolseley Rd. | OX03 Hatfield_22 | 2024-04-03 09:08 | 2024-04-03 15:56 | 0.49665 | 0.0012173 | 26 | 10608 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 11 | 46584 | Rakaia Barrhill Methven Rd. | OX03 Hatfield_22 | 2024-04-04 12:35 | 2024-04-04 13:54 | 0.08507 | 0.0010768 | 23 | 1817 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 12 | 46588 | Carters Tce. | YY02 Willowby_22 | 2024-04-05 08:48 | 2024-04-05 12:44 | 0.25413 | 0.0010768 | 23 | 5428 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 13 | 46589 | Farm Rd 74-A | TW07 Winchmore_11 | 2024-04-05 09:05 | 2024-04-05 12:03 | 0.041669 | 0.00023409 | 5 | 890 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 14 | 46590 | Cochranes Rd 401 | QY03 Cochranes Rd_22 | 2024-04-06 08:59 | 2024-04-06 11:52 | 0.59127 | 0.0034178 | 73 | 12629 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 15 | 46592 | Dobson St West 16 | TD26 Ashburton South_11 | 2024-04-06 13:21 | 2024-04-06 15:48 | 0.013765 | 9.3637e-05 | 2 | 294 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 16 | 46599 | Greens Rd | YW04 Flemington_22 | 2024-04-08 09:01 | 2024-04-08 10:31 | 0.016855 | 0.00018727 | 4 | 360 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 17 | 46600 | Rangitata Gorge | BI20 Montalto_11 | 2024-04-08 09:25 | 2024-04-08 14:38 | 0.71806 | 0.0022941 | 49 | 15337 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 18 | 46601 | Windermere | GW04 Winslow_22 | 2024-04-08 11:08 | 2024-04-08 12:15 | 0.015684 | 0.00023409 | 5 | 335 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 19 | 46603 | Methven Sub Line Rd Dolma St | SW04 Staveley_22 | 2024-04-09 09:03 | 2024-04-09 17:02 | 0.65036 | 0.0013577 | 29 | 13891 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 20 | 46622 | Baker & Normanby Rds. | OX03 Hatfield_22 | 2024-04-15 09:00 | 2024-04-15 14:35 | 0.078421 | 0.00023409 | 5 | 1675 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 21 | 46628 | Rakaia Barrhill Methven Rd | OX03 Hatfield_22 | 2024-04-16 09:08 | 2024-04-16 10:46 | 0.10094 | 0.00103 | 22 | 2156 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 22 | 46630 | Coplands Rd | OY02 Chertsey_22 | 2024-04-16 09:09 | 2024-04-16 13:06 | 0.033288 | 0.00014046 | 3 | 711 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 23 | 46632 | Blairs Rd. | KU06 Mayfield_22 | 2024-04-17 09:15 | 2024-04-17 16:02 | 0.03811 | 9.3637e-05 | 2 | 814 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 24 | 46645 | Rakaia Methven Barrhill Rd | OX03 Hatfield_22 | 2024-04-19 09:01 | 2024-04-19 11:02 | 0.1303 | 0.0010768 | 23 | 2783 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 25 | 46648 | Pudding Hill & Hobbs Rds. | VP11 - Methven Central_11 | 2024-04-22 09:00 | 2024-04-22 15:21 | 1.4092 | 0.0036987 | 79 | 30099 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 26 | 46674 | Pudding Hill Rd | BS83 Springfield | 2024-04-29 09:04 | 2024-04-29 15:53 | 0.99574 | 0.0024346 | 52 | 21268 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 27 | 46676 | Rakaia Barrhill Methven Rd. | OX03 Hatfield_22 | 2024-04-30 09:01 | 2024-04-30 16:00 | 0.45119 | 0.0010768 | 23 | 9637 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 28 | 46679 | Hinds Gorge Rd. | BI20 Montalto_11 | 2024-05-02 09:04 | 2024-05-02 14:17 | 0.60082 | 0.0019196 | 41 | 12833 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 29 | 46696 | Highbank Generation. | VG72 - Methven 66_HBK | 2024-05-07 08:30 | 2024-05-07 14:41 | 0.052109 | 0.00014046 | 3 | 1113 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 30 | 46697 | Rangitata Hwy, South Hinds. | JY02 Hinds South_22 | 2024-05-07 09:24 | 2024-05-07 14:14 | 0.52952 | 0.0018259 | 39 | 11310 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 31 | 46698 | Pole Rd. | UW04 Braemar_22 | 2024-05-07 09:44 | 2024-05-07 12:50 | 0.11321 | 0.00060864 | 13 | 2418 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 32 | 46699 | Tinwald Westerfield Mayfield Rd. | IN12 Tinwald Westerfield Mayfield Rd_22 | 2024-05-07 09:16 | 2024-05-07 12:05 | 0.21363 | 0.0012641 | 27 | 4563 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 33 | 46703 | Rangitata Gorge. | BI20 Montalto_11 | 2024-05-08 09:12 | 2024-05-08 15:58 | 0.93141 | 0.0022941 | 49 | 19894 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 34 | 46705 | Fords Rd. | YW04 Flemington_22 | 2024-05-08 13:04 | 2024-05-08 15:54 | 0.32633 | 0.0019196 | 41 | 6970 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 35 | 46716 | 4 mayfield Klondye Rd | KY02 Punawai_22 | 2024-05-10 09:27 | 2024-05-10 12:18 | 0.46435 | 0.0027155 | 58 | 9918 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 36 | 46717 | Ashburton Gorge Rd | SX03 Ashburton Gorge_22 | 2024-05-10 14:27 | 2024-05-10 16:22 | 0.31228 | 0.0027155 | 58 | 6670 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 37 | 46737 | Arundel Rakaia Gorge Rd. | SW04 Staveley_22 | 2024-05-17 09:09 | 2024-05-17 14:57 | 0.63542 | 0.0018259 | 39 | 13572 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 38 | 46750 | Thompsons Track | OX03 Hatfield_22 | 2024-05-21 09:06 | 2024-05-21 15:36 | 0.18259 | 0.00046819 | 10 | 3900 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 39 | 46752 | Wilkinsons Rd. | UX03 Mitcham_22 | 2024-05-22 09:00 | 2024-05-22 15:44 | 0.45395 | 0.0011236 | 24 | 9696 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 40 | 46753 | Company Rd. | FU06 Company Rd_11 | 2024-05-22 09:00 | 2024-05-22 11:34 | 0.37492 | 0.0024346 | 52 | 8008 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 41 | 46762 | Dawsons Rd | YW04 Flemington_22 | 2024-05-23 09:10 | 2024-05-23 15:51 | 0.28161 | 0.00070228 | 15 | 6015 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 42 | 46774 | Ealing Rd | JX03 Junction Rd_22 | 2024-05-27 09:08 | 2024-05-27 14:25 | 1.128 | 0.0035582 | 76 | 24092 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 43 | 46776 | Boundary & Isleworth Rds, plus Hinds Township. | JY02 Hinds South_22 | 2024-05-28 09:00 | 2024-05-28 14:52 | 0.84049 | 0.0023878 | 51 | 17952 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 44 | 46778 | Jamiesons Rd. | OY02 Chertsey_22 | 2024-05-28 09:33 | 2024-05-28 11:53 | 0.019664 | 0.00014046 | 3 | 420 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 45 | 46784 | Maronan Rd | KW04 Maronan_22 | 2024-05-29 09:06 | 2024-05-29 13:24 | 0.71267 | 0.0027623 | 59 | 15222 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 46 | 46785 | Winters Rd | PX03 Kyle_22 | 2024-05-29 09:21 | 2024-05-29 10:18 | 0.016012 | 0.00028091 | 6 | 342 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 47 | 46786 | Sheehans Rd | OX03 Hatfield_22 | 2024-05-30 09:07 | 2024-05-30 09:48 | 0.026874 | 0.00065546 | 14 | 574 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 48 | 46788 | Old Main South Rd. | JY02 Hinds South_22 | 2024-05-30 09:33 | 2024-05-30 15:33 | 0.65733 | 0.0018259 | 39 | 14040 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 49 | 46789 | Arundel Rakaia Gorge Rd. | KU06 Mayfield_22 | 2024-05-30 09:31 | 2024-05-30 12:22 | 0.064048 | 0.00037455 | 8 | 1368 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 50 | 46795 | Frasers Rd. | KT07 Westerfield_22 | 2024-05-31 09:00 | 2024-05-31 11:28 | 0.23559 | 0.0015918 | 34 | 5032 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 51 | 46796 | Winters Rd. | PV05 Christys Rd_22 | 2024-05-31 09:14 | 2024-05-31 13:46 | 0.20375 | 0.0007491 | 16 | 4352 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 52 | 46809 | Coldstream & Lloyds Rds. | JW04 Coldstream_22 | 2024-06-04 09:01 | 2024-06-04 15:25 | 1.0248 | 0.0026687 | 57 | 21888 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 53 | 46815 | Emersons Rd | JW04 Coldstream_22 | 2024-06-05 12:31 | 2024-06-05 15:06 | 0.12337 | 0.00079592 | 17 | 2635 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 54 | 46818 | Trevors Rd | NV05 Carew_22 | 2024-06-05 09:38 | 2024-06-05 11:50 | 0.074161 | 0.00056182 | 12 | 1584 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 55 | 46819 | Wrens Rd | JW04 Coldstream_22 | 2024-06-05 09:03 | 2024-06-05 11:07 | 0.66183 | 0.0053373 | 114 | 14136 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 56 | 46826 | Pyes Rd. | JV05 Poplar Rd_22 | 2024-06-07 09:00 | 2024-06-07 11:04 | 0.1103 | 0.00088955 | 19 | 2356 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 57 | 46827 | Darts Rd. | MW04 - Blackford rd feeder | 2024-06-07 12:36 | 2024-06-07 15:31 | 0.057353 | 0.00032773 | 7 | 1225 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 58 | 46828 | Isleworth Settlement Rd. | JV05 Poplar Rd_22 | 2024-06-07 13:06 | 2024-06-07 14:47 | 0.023643 | 0.00023409 | 5 | 505 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 59 | 46831 | Robinson St 9-A | TQ13 Industrial Estate_11 | 2024-06-09 08:00 | 2024-06-09 12:08 | 0.046444 | 0.00018727 | 4 | 992 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 60 | 46837 | Springburn Bushside Rd. | SW04 Staveley_22 | 2024-06-10 09:33 | 2024-06-10 11:22 | 0.056136 | 0.00051501 | 11 | 1199 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 61 | 46847 | Isleworth & Trig Pole Rds. | JW04 Coldstream_22 | 2024-06-11 09:02 | 2024-06-11 13:22 | 0.36519 | 0.0014046 | 30 | 7800 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 62 | 46848 | Fords Rd. | YY02 Willowby_22 | 2024-06-11 09:00 | 2024-06-11 10:52 | 0.031462 | 0.00028091 | 6 | 672 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 63 | 46849 | Hinds Gorge Rd. | BI20 Montalto_11 | 2024-06-12 08:47 | 2024-06-12 15:37 | 0.78702 | 0.0019196 | 41 | 16810 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 64 | 46855 | Frisbys, Old Main South, McConnells Rd North & Fields Rds. | JY02 Hinds South_22 | 2024-06-13 09:27 | 2024-06-13 16:18 | 1.4047 | 0.0034178 | 73 | 30003 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 65 | 46857 | Ashburton Gorge Rd | SX03 Ashburton Gorge_22 | 2024-06-14 13:17 | 2024-06-14 15:18 | 0.32857 | 0.0027155 | 58 | 7018 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 66 | 46863 | Boundary Rd | JY02 Hinds South_22 | 2024-06-14 09:05 | 2024-06-14 11:10 | 0.1346 | 0.0010768 | 23 | 2875 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 67 | 46870 | Longbeach Rd Bells Rd | YY02 Willowby_22 | 2024-06-17 09:00 | 2024-06-17 13:26 | 0.39852 | 0.0014982 | 32 | 8512 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 68 | 46875 | Westward Way | VZ01 Springfield_22 | 2024-06-17 14:04 | 2024-06-17 14:45 | 0.023035 | 0.00056182 | 12 | 492 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 69 | 46880 | Anama Settlement Rd | KU06 Mayfield_22 | 2024-06-18 09:34 | 2024-06-18 12:44 | 0.11564 | 0.00060864 | 13 | 2470 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 70 | 46881 | Hackthorne Rd | KV05 Hackthorne_22 | 2024-06-18 09:15 | 2024-06-18 11:30 | 0.16433 | 0.0012173 | 26 | 3510 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 71 | 46882 | Rakaia Barrhill Methven Rd | OX03 Hatfield_22 | 2024-06-18 09:02 | 2024-06-18 15:20 | 0.38934 | 0.00103 | 22 | 8316 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 72 | 46885 | Longbeach & Bells Rds. | YX03 Lynnford_22 | 2024-06-19 09:20 | 2024-06-19 14:21 | 0.28185 | 0.00093637 | 20 | 6020 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 73 | 46886 | Company Rd. | FU06 Company Rd_11 | 2024-06-20 09:01 | 2024-06-20 12:39 | 0.53074 | 0.0024346 | 52 | 11336 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 74 | 46887 | Barkers Rd. | BI20 Montalto_11 | 2024-06-20 09:27 | 2024-06-20 11:18 | 0.42095 | 0.0037923 | 81 | 8991 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 75 | 46900 | Robinson St 4 | TQ13 Industrial Estate_11 | 2024-06-23 09:09 | 2024-06-23 14:09 | 0.014046 | 4.6819e-05 | 1 | 300 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 76 | 46902 | Ealing Montalto Rd. | SX03 Ashburton Gorge_22 | 2024-06-24 09:01 | 2024-06-24 14:52 | 1.6269 | 0.004635 | 99 | 34749 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 77 | 46908 | Cliffords Rd. | SX03 Ashburton Gorge_22 | 2024-06-25 09:03 | 2024-06-25 16:09 | 0.13961 | 0.00032773 | 7 | 2982 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 78 | 46909 | Methven Hwy 3012-A | VZ01 Springfield_22 | 2024-06-25 09:39 | 2024-06-25 13:16 | 0.11176 | 0.00051501 | 11 | 2387 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 79 | 46912 | Acton Rd. | OV05 Acton_22 | 2024-06-26 09:07 | 2024-06-26 14:48 | 0.75036 | 0.0022005 | 47 | 16027 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 80 | 46913 | Gartartan Rd. | YY02 Willowby_22 | 2024-06-26 09:09 | 2024-06-26 16:09 | 0.57025 | 0.0013577 | 29 | 12180 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 81 | 46921 | 648 Fords rd | YY02 Willowby_22 | 2024-06-27 09:16 | 2024-06-27 14:19 | 0.085116 | 0.00028091 | 6 | 1818 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 82 | 46928 | Cliffords rd | SX03 Ashburton Gorge_22 | 2024-07-02 09:09 | 2024-07-02 13:55 | 0.33475 | 0.0011705 | 25 | 7150 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 83 | 46930 | Gartartans Rd | YY02 Willowby_22 | 2024-07-03 09:05 | 2024-07-03 17:15 | 0.71118 | 0.0014514 | 31 | 15190 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 84 | 46931 | Mainwarings Rd | RZ01 Dorie West_22 | 2024-07-03 09:03 | 2024-07-03 15:23 | 1.3877 | 0.0036519 | 78 | 29640 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 85 | 46936 | McLennons Bush Rd | VU06 Mt Hutt_11 | 2024-07-04 09:09 | 2024-07-04 13:57 | 0.25619 | 0.00088955 | 19 | 5472 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 86 | 46937 | Hendersons Rd | GW04 Winslow_22 | 2024-07-04 10:34 | 2024-07-04 14:48 | 0.76108 | 0.0029964 | 64 | 16256 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 87 | 46943 | Watson st 14 | TQ13 Industrial Estate_11 | 2024-07-07 09:27 | 2024-07-07 10:37 | 0.0032773 | 4.6819e-05 | 1 | 70 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 88 | 46945 | Lauriston Barrhill rd | UY02 Barrhill_22 | 2024-07-08 09:07 | 2024-07-08 16:07 | 0.29496 | 0.00070228 | 15 | 6300 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 89 | 46951 | Lauriston | UV05 Urrall_22 | 2024-07-09 09:23 | 2024-07-09 15:36 | 1.4495 | 0.0038859 | 83 | 30959 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 90 | 46954 | Dobsons rd | JV05 Poplar Rd_22 | 2024-07-10 09:30 | 2024-07-10 12:44 | 0.081745 | 0.00042137 | 9 | 1746 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 91 | 46955 | Davidsons rd Trig pole rd | JV05 Poplar Rd_22 | 2024-07-10 09:08 | 2024-07-10 11:58 | 0.22286 | 0.0013109 | 28 | 4760 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 92 | 46956 | Coskeries rd | SY02 Anama_22 | 2024-07-10 09:23 | 2024-07-10 15:14 | 1.9556 | 0.0055714 | 119 | 41769 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 93 | 46957 | Dobsons rd Drain rd | JV05 Poplar Rd_22 | 2024-07-10 13:02 | 2024-07-10 15:29 | 0.13076 | 0.00088955 | 19 | 2793 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 94 | 46958 | Boundary rd | YY02 Willowby_22 | 2024-07-11 12:36 | 2024-07-11 14:19 | 0.13985 | 0.0013577 | 29 | 2987 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 95 | 46966 | Brogdens Rd/ Adams Rd | JW04 Coldstream_22 | 2024-07-12 09:05 | 2024-07-12 11:37 | 0.17791 | 0.0011705 | 25 | 3800 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 96 | 46969 | Highbank Cairnbrae Rd. | VY02 Line Rd_22 | 2024-07-15 09:01 | 2024-07-15 11:47 | 0.29533 | 0.0017791 | 38 | 6308 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 97 | 46970 | Acton Rd. | RY02 Rakaia Huts_22 | 2024-07-15 09:11 | 2024-07-15 10:43 | 0.06461 | 0.00070228 | 15 | 1380 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 98 | 46973 | Wakanui Rd | QY03 Cochranes Rd_22 | 2024-07-16 08:01 | 2024-07-16 10:03 | 0.26846 | 0.0022005 | 47 | 5734 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 99 | 46974 | Sheates Rd | GY02 Ferrimans Rd_22 | 2024-07-16 09:06 | 2024-07-16 16:01 | 0.40802 | 0.00098319 | 21 | 8715 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 100 | 46976 | Wakanui Rd | QV08 Stanley Rd_22 | 2024-07-16 11:01 | 2024-07-16 13:29 | 0.27024 | 0.0018259 | 39 | 5772 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 101 | 46977 | Denshires Rd South | WV04 Seaview_22 | 2024-07-17 08:28 | 2024-07-17 13:29 | 0.40868 | 0.0013577 | 29 | 8729 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 102 | 46980 | Wrights Rd. | WV04 Seaview_22 | 2024-07-17 13:29 | 2024-07-17 16:41 | 0.017978 | 9.3637e-05 | 2 | 384 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 103 | 46981 | Mayfield Klondyke Rd. | BI20 Montalto_11 | 2024-07-17 09:06 | 2024-07-17 14:59 | 2.6113 | 0.0073974 | 158 | 55774 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 104 | 46992 | Wakanui Rd | ZK16 Princes St_11 | 2024-07-18 09:09 | 2024-07-18 14:43 | 0.70368 | 0.0021068 | 45 | 15030 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 105 | 46993 | Dobsons Rd | JV05 Poplar Rd_22 | 2024-07-18 12:30 | 2024-07-18 13:16 | 0.019383 | 0.00042137 | 9 | 414 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 106 | 46994 | Emersons Rd | JW04 Coldstream_22 | 2024-07-18 14:00 | 2024-07-18 16:06 | 0.10029 | 0.00079592 | 17 | 2142 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 107 | 46999 | Ealing Montalto Rd | NV05 Carew_22 | 2024-07-19 08:09 | 2024-07-19 14:03 | 0.64638 | 0.0018259 | 39 | 13806 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 108 | 47005 | Winters Rd. | PX03 Kyle_22 | 2024-07-22 09:12 | 2024-07-22 16:08 | 0.3311 | 0.00079592 | 17 | 7072 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 109 | 47006 | Ashburton Staveley Rd. | SW04 Staveley_22 | 2024-07-22 09:19 | 2024-07-22 14:15 | 1.2334 | 0.0041669 | 89 | 26344 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 110 | 47010 | Sheates Rd. | GY02 Ferrimans Rd_22 | 2024-07-23 09:03 | 2024-07-23 16:04 | 0.41392 | 0.00098319 | 21 | 8841 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 111 | 47018 | Ashburton Staveley and Olivers Rds. | KV05 Hackthorne_22 | 2024-07-24 09:04 | 2024-07-24 14:57 | 0.57844 | 0.0016387 | 35 | 12355 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 112 | 47019 | Collinsons Rd. | WV04 Seaview_22 | 2024-07-24 09:40 | 2024-07-24 12:23 | 0.068683 | 0.00042137 | 9 | 1467 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 113 | 47023 | Winchmore Laursiton Rd | UW04 Braemar_22 | 2024-07-25 11:12 | 2024-07-25 16:07 | 0.92537 | 0.0031369 | 67 | 19765 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 114 | 47025 | Mayfield Klondkye Rd | BI20 Montalto_11 | 2024-07-25 09:17 | 2024-07-25 16:00 | 3.0755 | 0.0076314 | 163 | 65689 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 115 | 47028 | Seafield Rd | QV08 Stanley Rd_22 | 2024-07-26 09:00 | 2024-07-26 16:02 | 0.55321 | 0.0013109 | 28 | 11816 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 116 | 47033 | 5 Colleridge St | UY02 Barrhill_22 | 2024-07-27 09:02 | 2024-07-27 09:13 | 0.0061801 | 0.00056182 | 12 | 132 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 117 | 47037 | Rakaia Barhill Methven Rd | OX03 Hatfield_22 | 2024-07-28 10:31 | 2024-07-28 13:36 | 0.3811 | 0.00206 | 44 | 8140 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 118 | 47040 | Lynnford Rd. | YX03 Lynnford_22 | 2024-07-29 09:32 | 2024-07-29 12:03 | 0.084835 | 0.00056182 | 12 | 1812 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 119 | 47059 | Arundel Rakaia Gorge Rd. | Forks Rd 1093-A T1 | 2024-08-02 09:23 | 2024-08-02 15:14 | 0.26293 | 0.0007491 | 16 | 5616 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 120 | 47060 | Stevens Rd. | JW04 Coldstream_22 | 2024-08-02 09:37 | 2024-08-02 12:21 | 0.04607 | 0.00028091 | 6 | 984 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 121 | 47072 | Mainwarings Rd | RZ01 Dorie West_22 | 2024-08-07 09:05 | 2024-08-07 14:59 | 0.39777 | 0.0011236 | 24 | 8496 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 122 | 47073 | Gartartons Rd | YY02 Willowby_22 | 2024-08-07 09:04 | 2024-08-07 15:36 | 0.56894 | 0.0014514 | 31 | 12152 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 123 | 47074 | Rangiatat Terrace Rd | NV05 Carew_22 | 2024-08-07 09:45 | 2024-08-07 11:54 | 0.054356 | 0.00042137 | 9 | 1161 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 124 | 47077 | Sheates Rd. | GY02 Ferrimans Rd_22 | 2024-08-08 09:04 | 2024-08-08 13:38 | 0.87233 | 0.0031837 | 68 | 18632 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 125 | 47078 | Lower Downs Rd. | SX03 Ashburton Gorge_22 | 2024-08-08 09:58 | 2024-08-08 13:00 | 0.12781 | 0.00070228 | 15 | 2730 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 126 | 47085 | Thomson St | TF59 Carters Terrace_11 | 2024-08-11 09:03 | 2024-08-11 12:53 | 0.053841 | 0.00023409 | 5 | 1150 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 127 | 47104 | Back Track | UV05 Urrall_22 | 2024-08-12 09:00 | 2024-08-12 10:54 | 0.29889 | 0.0026218 | 56 | 6384 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 128 | 47105 | Windermere Rd | GW04 Winslow_22 | 2024-08-12 09:36 | 2024-08-12 12:20 | 0.038391 | 0.00023409 | 5 | 820 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 129 | 47107 | Arundle Rakaia Gorge Rd | SW04 Staveley_22 | 2024-08-12 12:22 | 2024-08-12 17:39 | 0.059366 | 0.00018727 | 4 | 1268 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 130 | 47108 | South Belt 50 | VS08 Methven South_11 | 2024-08-12 12:47 | 2024-08-12 16:19 | 0.18859 | 0.00088955 | 19 | 4028 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 131 | 47109 | Lauriston Sub. | UV05 Urrall_22 | 2024-08-13 09:01 | 2024-08-13 14:51 | 1.3601 | 0.0038859 | 83 | 29050 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 132 | 47110 | Ashburton Staveley & Olivers Rds. | KV05 Hackthorne_22 | 2024-08-13 09:04 | 2024-08-13 15:06 | 0.59319 | 0.0016387 | 35 | 12670 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 133 | 47112 | Hinds River, Surveyors & Isleworth Rds. | YX03 Lynnford_22 | 2024-08-14 09:04 | 2024-08-14 15:14 | 1.3858 | 0.0037455 | 80 | 29600 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 134 | 47113 | Dip & Flemings Rds. | VZ01 Springfield_22 | 2024-08-14 09:23 | 2024-08-14 15:15 | 0.23072 | 0.00065546 | 14 | 4928 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 135 | 47116 | Seafield & Stanley Rds. | QV08 Stanley Rd_22 | 2024-08-15 09:00 | 2024-08-15 15:49 | 0.53617 | 0.0013109 | 28 | 11452 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 136 | 47120 | Springfield Rd East. | VZ01 Springfield_22 | 2024-08-16 09:15 | 2024-08-16 11:27 | 0.3399 | 0.002575 | 55 | 7260 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 137 | 47121 | Dromore Methven Rd. | UW04 Braemar_22 | 2024-08-16 09:00 | 2024-08-16 15:13 | 1.205 | 0.0032305 | 69 | 25737 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 138 | 47136 | Olivers Rd. | KV05 Hackthorne_22 | 2024-08-20 09:04 | 2024-08-20 15:08 | 0.10225 | 0.00028091 | 6 | 2184 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 139 | 47140 | Farm Rd. | TW07 Winchmore_11 | 2024-08-21 09:13 | 2024-08-21 15:08 | 0.033241 | 9.3637e-05 | 2 | 710 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 140 | 47142 | Stranges Rd. | YW04 Flemington_22 | 2024-08-22 09:00 | 2024-08-22 11:23 | 0.1406 | 0.00098319 | 21 | 3003 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 141 | 47143 | McKendrys Rd. | VY02 Line Rd_22 | 2024-08-22 09:14 | 2024-08-22 13:13 | 0.1119 | 0.00046819 | 10 | 2390 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 142 | 47144 | Valetta Westerfield Rd. | KY02 Punawai_22 | 2024-08-22 09:32 | 2024-08-22 13:50 | 0.38653 | 0.0014982 | 32 | 8256 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 143 | 47145 | Stranges Rd. | YY02 Willowby_22 | 2024-08-22 12:37 | 2024-08-22 14:33 | 0.010862 | 9.3637e-05 | 2 | 232 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 144 | 47149 | Taveners Rd. | PT07 Pendarves North_22 | 2024-08-23 09:05 | 2024-08-23 16:08 | 0.49511 | 0.0011705 | 25 | 10575 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 145 | 47162 | Stanley Rd 671 | PW04 Pendarves West_22 | 2024-08-26 13:37 | 2024-08-26 15:38 | 0.01133 | 9.3637e-05 | 2 | 242 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 146 | 47167 | Methven Hwy 3012-A | VZ01 Springfield_22 | 2024-08-27 09:48 | 2024-08-27 13:12 | 0.028653 | 0.00014046 | 3 | 612 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 147 | 47176 | Forest Dr & Mt Harding Rd. | VS08 Methven South_11 | 2024-08-28 09:23 | 2024-08-28 17:40 | 0.69807 | 0.0014046 | 30 | 14910 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 148 | 47177 | Valetta Westerfield Rd. | KV05 Hackthorne_22 | 2024-08-28 09:11 | 2024-08-28 11:53 | 0.091015 | 0.00056182 | 12 | 1944 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 149 | 47178 | Peters Rd. | SY02 Anama_22 | 2024-08-28 10:31 | 2024-08-28 14:03 | 0.28784 | 0.0013577 | 29 | 6148 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 150 | 47185 | Mayfield Klondyke Rd. | BI20 Montalto_11 | 2024-08-29 09:30 | 2024-08-29 14:33 | 2.3123 | 0.0076314 | 163 | 49389 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 151 | 47222 | Coskeries Rd. | SY02 Anama_22 | 2024-09-05 09:00 | 2024-09-05 14:32 | 0.23316 | 0.00070228 | 15 | 4980 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 152 | 47227 | Ashburton Staveley Rd | KV05 Hackthorne_22 | 2024-09-06 09:19 | 2024-09-06 14:50 | 0.61988 | 0.0018727 | 40 | 13240 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 153 | 47242 | Sheates Rd. | GY02 Ferrimans Rd_22 | 2024-09-09 09:03 | 2024-09-09 13:08 | 0.24088 | 0.00098319 | 21 | 5145 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 154 | 47249 | Rangitata Gorge Rd. | BI20 Montalto_11 | 2024-09-10 09:00 | 2024-09-10 15:40 | 0.91765 | 0.0022941 | 49 | 19600 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 155 | 47263 | Arundle Rakaia Gorge Rd | NT07 Stoneylea Rd_22 | 2024-09-12 09:55 | 2024-09-12 12:31 | 0.15338 | 0.00098319 | 21 | 3276 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 156 | 47277 | Thompsons Track | UX03 Mitcham_22 | 2024-09-16 09:00 | 2024-09-16 17:26 | 0.74254 | 0.0023409 | 50 | 15860 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 157 | 47289 | Rawles Crossing Rd. | GY02 Ferrimans Rd_22 | 2024-09-19 09:09 | 2024-09-19 15:12 | 0.28892 | 0.00079592 | 17 | 6171 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 158 | 47297 | Hackthorne Rd. | KV05 Hackthorne_22 | 2024-09-20 09:00 | 2024-09-20 12:37 | 0.32511 | 0.0014982 | 32 | 6944 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 159 | 47306 | Thompsons Track | UX03 Mitcham_22 | 2024-09-23 09:05 | 2024-09-23 16:00 | 0.1943 | 0.00046819 | 10 | 4150 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 160 | 47314 | Maronan Ealing Rd. | NU06 Lismore_22 | 2024-09-24 13:01 | 2024-09-24 14:17 | 0.11742 | 0.001545 | 33 | 2508 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 161 | 47315 | Copley Rd. | PT07 Pendarves North_22 | 2024-09-24 13:33 | 2024-09-24 16:12 | 0.23077 | 0.0014514 | 31 | 4929 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 162 | 47318 | Wilsons Rd | WY02 Hakatere_22 | 2024-09-25 11:07 | 2024-09-25 16:37 | 0.26265 | 0.00079592 | 17 | 5610 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 163 | 47319 | Seafield Rd | QV08 Stanley Rd_22 | 2024-09-25 08:59 | 2024-09-25 15:31 | 0.51388 | 0.0013109 | 28 | 10976 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 164 | 47323 | Acton Rd. | RZ01 Dorie West_22 | 2024-09-26 09:03 | 2024-09-26 14:08 | 0.58547 | 0.0019196 | 41 | 12505 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 165 | 47325 | Longbeach Rd. | YV05 Longbeach_22 | 2024-09-26 12:44 | 2024-09-26 14:40 | 0.10862 | 0.00093637 | 20 | 2320 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 166 | 47331 | Rawles Crossings Rd | GY02 Ferrimans Rd_22 | 2024-09-27 09:07 | 2024-09-27 15:43 | 0.31518 | 0.00079592 | 17 | 6732 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 167 | 47336 | Westerfield School & Fechneys Rds. | GY02 Ferrimans Rd_22 | 2024-09-30 09:15 | 2024-09-30 14:15 | 0.32305 | 0.0010768 | 23 | 6900 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 168 | 47341 | Le Bretons Rd. | WV04 Seaview_22 | 2024-10-01 09:36 | 2024-10-01 11:09 | 0.039187 | 0.00042137 | 9 | 837 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 169 | 47342 | Olivers Rd. | KV05 Hackthorne_22 | 2024-10-01 09:19 | 2024-10-01 15:12 | 0.099162 | 0.00028091 | 6 | 2118 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 170 | 47344 | Christys Rd. | WV04 Seaview_22 | 2024-10-01 13:56 | 2024-10-01 15:18 | 0.015357 | 0.00018727 | 4 | 328 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 171 | 47350 | Maronan Valetta Rd. | KW04 Maronan_22 | 2024-10-02 09:16 | 2024-10-02 11:03 | 0.29557 | 0.0027623 | 59 | 6313 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 172 | 47351 | Mayfield Klondyke Rd. | BI20 Montalto_11 | 2024-10-02 09:11 | 2024-10-02 14:56 | 2.6328 | 0.0076314 | 163 | 56235 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 173 | 47368 | Buckleys Rd | WV04 Seaview_22 | 2024-10-04 09:35 | 2024-10-04 13:18 | 0.42806 | 0.0019196 | 41 | 9143 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 174 | 47374 | Singletree Rd | PW04 Pendarves West_22 | 2024-10-07 08:41 | 2024-10-07 15:26 | 0.56885 | 0.0014046 | 30 | 12150 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 175 | 47376 | Gartartan Rd. | YY02 Willowby_22 | 2024-10-08 09:08 | 2024-10-08 13:19 | 0.3643 | 0.0014514 | 31 | 7781 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 176 | 47377 | Bebbingtons Rd. | FN13 Rakaia Hwy_22 | 2024-10-08 09:19 | 2024-10-08 14:18 | 0.72794 | 0.0024346 | 52 | 15548 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 177 | 47378 | Hamptons Rd. | PX03 Kyle_22 | 2024-10-08 09:05 | 2024-10-08 13:37 | 0.38204 | 0.0014046 | 30 | 8160 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 178 | 47379 | Braemar Lauriston Rd. | UW04 Braemar_22 | 2024-10-08 09:03 | 2024-10-08 14:43 | 0.47755 | 0.0014046 | 30 | 10200 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 179 | 47385 | Thompsons Track. | UX03 Mitcham_22 | 2024-10-09 09:03 | 2024-10-09 15:47 | 0.18915 | 0.00046819 | 10 | 4040 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 180 | 47386 | Wakanui Township & Wrights Rds. | WV04 Seaview_22 | 2024-10-09 09:06 | 2024-10-09 13:52 | 0.38831 | 0.0013577 | 29 | 8294 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 181 | 47390 | Tancred St Fergusson St | OW04 Rakaia_22 | 2024-10-10 09:00 | 2024-10-10 17:11 | 3.1494 | 0.0064142 | 137 | 67267 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 182 | 47391 | Denshires Rd South | WV04 Seaview_22 | 2024-10-10 09:15 | 2024-10-10 15:33 | 0.31855 | 0.00084274 | 18 | 6804 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 183 | 47405 | Ealing Rd | JX03 Junction Rd_22 | 2024-10-14 09:33 | 2024-10-14 15:25 | 0.69217 | 0.0019664 | 42 | 14784 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 184 | 47406 | Buttericks Rd | WV04 Seaview_22 | 2024-10-14 09:21 | 2024-10-14 12:02 | 0.060302 | 0.00037455 | 8 | 1288 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 185 | 47415 | Isleworth Rd | YX03 Lynnford_22 | 2024-10-16 10:02 | 2024-10-16 15:08 | 0.9742 | 0.0031837 | 68 | 20808 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 186 | 47416 | Moorehouse Rd | SX03 Ashburton Gorge_22 | 2024-10-16 10:17 | 2024-10-16 14:15 | 0.12257 | 0.00051501 | 11 | 2618 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 187 | 47417 | Moorhouse Rd | SX03 Ashburton Gorge_22 | 2024-10-16 10:44 | 2024-10-16 16:59 | 0.43893 | 0.0011705 | 25 | 9375 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 188 | 47418 | Moorhouse Rd | SY02 Anama_22 | 2024-10-16 16:57 | 2024-10-16 16:59 | 0.0028091 | 0.0014046 | 30 | 60 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 189 | 47419 | Grahams Rd | YW04 Flemington_22 | 2024-10-17 12:35 | 2024-10-17 14:11 | 0.10338 | 0.0010768 | 23 | 2208 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 190 | 47420 | Double Hill Run Rd | AE96 Upper Rakaia_11 | 2024-10-17 09:07 | 2024-10-17 14:49 | 0.17613 | 0.00051501 | 11 | 3762 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 191 | 47421 | 192 Stanley Rd | PT07 Pendarves North_22 | 2024-10-17 10:02 | 2024-10-17 14:39 | 0.29828 | 0.0010768 | 23 | 6371 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 192 | 47426 | Beach Rd East | WY02 Hakatere_22 | 2024-10-18 09:08 | 2024-10-18 14:32 | 0.7888 | 0.0024346 | 52 | 16848 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 193 | 47428 | Grahams Rd | YY02 Willowby_22 | 2024-10-18 09:21 | 2024-10-18 11:42 | 0.10562 | 0.0007491 | 16 | 2256 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 194 | 47429 | Olivers Rd | KV05 Hackthorne_22 | 2024-10-18 09:06 | 2024-10-18 09:50 | 0.072101 | 0.0016387 | 35 | 1540 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 195 | 47435 | Winchmore Lauriston Rd | UV05 Urrall_22 | 2024-10-21 09:00 | 2024-10-21 15:54 | 0.58149 | 0.0014046 | 30 | 12420 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 196 | 47436 | Harrisons Rd | RY02 Rakaia Huts_22 | 2024-10-21 15:00 | 2024-10-21 16:40 | 0.26218 | 0.0026218 | 56 | 5600 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 197 | 47437 | Hanrahans Rd | PT07 Pendarves North_22 | 2024-10-21 09:11 | 2024-10-21 10:34 | 0.0077719 | 9.3637e-05 | 2 | 166 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 198 | 47438 | Chatmos Rd | YX03 Lynnford_22 | 2024-10-21 09:21 | 2024-10-21 10:51 | 0.0042137 | 4.6819e-05 | 1 | 90 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 199 | 47440 | Westerfield Lismore Rd | GX03 Frasers Rd West_22 | 2024-10-21 09:34 | 2024-10-21 10:53 | 0.32178 | 0.0040732 | 87 | 6873 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 200 | 47442 | Dromore Methven Rd | OY02 Chertsey_22 | 2024-10-21 13:09 | 2024-10-21 13:43 | 0.011143 | 0.00032773 | 7 | 238 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 201 | 47444 | Cairnbrae Rd | BI20 Montalto_11 | 2024-10-21 14:17 | 2024-10-21 15:07 | 0.1545 | 0.00309 | 66 | 3300 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 202 | 47452 | Lauriston Barrhill Rd | UY02 Barrhill_22 | 2024-10-23 09:08 | 2024-10-23 15:43 | 0.70275 | 0.0017791 | 38 | 15010 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 203 | 47457 | Keenans Rd. | ZR09 Seafield Rd_11 | 2024-10-25 09:13 | 2024-10-25 15:35 | 0.19673 | 0.00051501 | 11 | 4202 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 204 | 47474 | Chatmos Rd | YX03 Lynnford_22 | 2024-10-29 12:46 | 2024-10-29 15:45 | 0.18437 | 0.00103 | 22 | 3938 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 205 | 47475 | Hewsons Rd | MayfKloRd 46-B T1 | 2024-10-29 09:44 | 2024-10-29 15:30 | 0.016199 | 4.6819e-05 | 1 | 346 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 206 | 47476 | Strangers Rd | YW04 Flemington_22 | 2024-10-29 09:08 | 2024-10-29 11:22 | 0.13175 | 0.00098319 | 21 | 2814 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 207 | 47477 | Dromore Merthven Rd | FN13 Rakaia Hwy_22 | 2024-10-29 08:59 | 2024-10-29 13:35 | 0.2326 | 0.00084274 | 18 | 4968 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 208 | 47479 | Buttericks Rd. | QV08 Stanley Rd_22 | 2024-10-30 09:22 | 2024-10-30 12:29 | 0.026265 | 0.00014046 | 3 | 561 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 209 | 47483 | Keenans Rd. | ZR09 Seafield Rd_11 | 2024-10-31 09:19 | 2024-10-31 14:00 | 0.14472 | 0.00051501 | 11 | 3091 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 210 | 47485 | Elgin Rd. | QV08 Stanley Rd_22 | 2024-10-31 09:21 | 2024-10-31 13:11 | 0.2046 | 0.00088955 | 19 | 4370 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 211 | 47486 | Christys Rd. | WY02 Hakatere_22 | 2024-10-31 14:30 | 2024-10-31 17:26 | 0.049441 | 0.00028091 | 6 | 1056 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 212 | 47488 | Maronan Ealing Rd. | NU06 Lismore_22 | 2024-11-01 09:17 | 2024-11-01 10:26 | 0.10661 | 0.001545 | 33 | 2277 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 213 | 47489 | Le Bretons Rd. | WV04 Seaview_22 | 2024-11-01 09:11 | 2024-11-01 11:41 | 0.063205 | 0.00042137 | 9 | 1350 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 214 | 47490 | Thompsons Track. | UX03 Mitcham_22 | 2024-11-01 09:30 | 2024-11-01 12:25 | 0.40966 | 0.0023409 | 50 | 8750 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 215 | 47510 | Arundle Rakaia Gorge Rd | SW04 Staveley_22 | 2024-11-05 09:24 | 2024-11-05 17:25 | 0.20268 | 0.00042137 | 9 | 4329 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 216 | 47511 | McCrorys Rd. | PY02 McCrorys Rd_22 | 2024-11-06 09:08 | 2024-11-06 12:00 | 0.30601 | 0.0017791 | 38 | 6536 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 217 | 47512 | Winters Rd. | PV05 Christys Rd_22 | 2024-11-06 09:03 | 2024-11-06 12:04 | 0.13559 | 0.0007491 | 16 | 2896 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 218 | 47513 | Chertsey Kyle Rd. | PX03 Kyle_22 | 2024-11-06 09:49 | 2024-11-06 13:13 | 0.69722 | 0.0034178 | 73 | 14892 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 219 | 47514 | Baxters Rd. | NV05 Carew_22 | 2024-11-06 12:31 | 2024-11-06 14:50 | 0.026031 | 0.00018727 | 4 | 556 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 220 | 47521 | Ashburton Staveley Rd | ST07 Buccleugh_22 | 2024-11-07 09:17 | 2024-11-07 13:21 | 0.50265 | 0.00206 | 44 | 10736 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 221 | 47522 | Holmesleee Rd | OX03 Hatfield_22 | 2024-11-07 09:14 | 2024-11-07 14:23 | 0.1302 | 0.00042137 | 9 | 2781 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 222 | 47524 | Methven Highway | UV05 Urrall_22 | 2024-11-07 12:34 | 2024-11-07 13:42 | 0.092326 | 0.0013577 | 29 | 1972 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 223 | 47525 | Ashburton Staveley Es | GY02 Ferrimans Rd_22 | 2024-11-07 12:32 | 2024-11-07 15:06 | 0.44702 | 0.0029028 | 62 | 9548 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 224 | 47533 | River Rd | WY02 Hakatere_22 | 2024-11-08 09:01 | 2024-11-08 10:55 | 0.10141 | 0.00088955 | 19 | 2166 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 225 | 47535 | Barkers Rd | BI20 Montalto_11 | 2024-11-08 09:21 | 2024-11-08 13:21 | 0.66295 | 0.0027623 | 59 | 14160 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 226 | 47536 | Buckleys Rd | PX03 Kyle_22 | 2024-11-08 10:16 | 2024-11-08 14:04 | 0.18147 | 0.00079592 | 17 | 3876 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 227 | 47558 | Winters Rd | PV05 Christys Rd_22 | 2024-11-12 14:31 | 2024-11-12 15:50 | 0.018493 | 0.00023409 | 5 | 395 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 228 | 47559 | Hinds Arundle Rd | NW04 Hinds West_22 | 2024-11-12 09:32 | 2024-11-12 13:20 | 0.23484 | 0.00103 | 22 | 5016 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 229 | 47561 | Fountains Rd | NY02 Fountaines Rd_22 | 2024-11-12 09:29 | 2024-11-12 11:15 | 0.11414 | 0.0010768 | 23 | 2438 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 230 | 47562 | Beach Rd East. | WY02 Hakatere_22 | 2024-11-13 09:02 | 2024-11-13 12:45 | 0.27145 | 0.0012173 | 26 | 5798 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 231 | 47564 | Wakanui School Rd. | WY02 Hakatere_22 | 2024-11-13 14:13 | 2024-11-13 16:10 | 0.021911 | 0.00018727 | 4 | 468 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 232 | 47581 | Hoattens Rd. | QY03 Cochranes Rd_22 | 2024-11-19 09:22 | 2024-11-19 12:25 | 0.0085678 | 4.6819e-05 | 1 | 183 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 233 | 47592 | Chertsey Kyle Rd | OU06 Overdale South_22 | 2024-11-20 09:06 | 2024-11-20 13:05 | 0.34688 | 0.0014514 | 31 | 7409 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 234 | 47593 | Rawles Crossing Rd | GY02 Ferrimans Rd_22 | 2024-11-20 10:04 | 2024-11-20 14:41 | 0.22047 | 0.00079592 | 17 | 4709 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 235 | 47597 | Seafield Rd | PV05 Christys Rd_22 | 2024-11-21 09:30 | 2024-11-21 15:32 | 0.64404 | 0.0017791 | 38 | 13756 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 236 | 47599 | Lauriston Barrhill Rd | UY02 Barrhill_22 | 2024-11-21 09:31 | 2024-11-21 13:50 | 0.46079 | 0.0017791 | 38 | 9842 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 237 | 47603 | Longbeach Rd | YV05 Longbeach_22 | 2024-11-22 09:33 | 2024-11-22 14:47 | 0.69095 | 0.0022005 | 47 | 14758 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 238 | 47604 | Pendarves Rakaia Rd | PT07 Pendarves North_22 | 2024-11-22 09:11 | 2024-11-22 15:59 | 0.19102 | 0.00046819 | 10 | 4080 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 239 | 47613 | Micheal St Rakaia | OV05 Acton_22 | 2024-11-26 09:00 | 2024-11-26 14:32 | 0.41968 | 0.0012641 | 27 | 8964 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 240 | 47615 | Hills Rd | GY02 Ferrimans Rd_22 | 2024-11-26 09:14 | 2024-11-26 15:16 | 0.15254 | 0.00042137 | 9 | 3258 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 241 | 47617 | Mitcham Rd | UW04 Braemar_22 | 2024-11-26 09:43 | 2024-11-26 13:50 | 0.27754 | 0.0011236 | 24 | 5928 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 242 | 47623 | Swamp Rd | NY02 Fountaines Rd_22 | 2024-11-27 09:47 | 2024-11-27 11:51 | 0.040639 | 0.00032773 | 7 | 868 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 243 | 47624 | Craycroft Maronan Rd | NT07 Stoneylea Rd_22 | 2024-11-27 09:13 | 2024-11-27 13:04 | 0.36771 | 0.0015918 | 34 | 7854 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 244 | 47626 | Christys Rd | PV05 Christys Rd_22 | 2024-11-27 09:30 | 2024-11-27 14:46 | 0.76932 | 0.0024346 | 52 | 16432 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 245 | 47627 | Winchmore Lauriston Rd | UW04 Braemar_22 | 2024-11-27 12:31 | 2024-11-27 14:30 | 0.37329 | 0.0031369 | 67 | 7973 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 246 | 47628 | Stanley Rd | QV08 Stanley Rd_22 | 2024-11-27 09:19 | 2024-11-27 14:34 | 0.3392 | 0.0010768 | 23 | 7245 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 247 | 47634 | Racecourse Rd | FH19 Mitcham Rd_22 | 2024-11-28 09:05 | 2024-11-28 14:32 | 1.1176 | 0.0034178 | 73 | 23871 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 248 | 47637 | Fairfield Rd | PW04 Pendarves West_22 | 2024-11-28 09:36 | 2024-11-28 11:24 | 0.10618 | 0.00098319 | 21 | 2268 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 249 | 47638 | Singletree Rd | PW04 Pendarves West_22 | 2024-11-28 13:01 | 2024-11-28 14:55 | 0.16012 | 0.0014046 | 30 | 3420 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 250 | 47641 | Surveyors Rd | YX03 Lynnford_22 | 2024-11-29 09:00 | 2024-11-29 15:42 | 0.54038 | 0.0031837 | 68 | 11542 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 251 | 47643 | Pannetts Rd 8 | OX03 Hatfield_22 | 2024-11-29 09:10 | 2024-11-29 13:00 | 0.19383 | 0.00084274 | 18 | 4140 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 252 | 47644 | Pannetts Rd 8 | OX03 Hatfield_22 | 2024-11-29 09:30 | 2024-11-29 13:27 | 0.31069 | 0.0013109 | 28 | 6636 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 253 | 47645 | Chertsey Kyle Rd | PW04 Pendarves West_22 | 2024-11-29 09:00 | 2024-11-29 15:51 | 0.88515 | 0.0021537 | 46 | 18906 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 254 | 47646 | Line Rd | UV05 Urrall_22 | 2024-11-29 10:36 | 2024-11-29 15:33 | 0.47376 | 0.0017323 | 37 | 10119 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 255 | 47667 | Fords Rd, Ashton. | YW04 Flemington_22 | 2024-12-03 09:15 | 2024-12-03 11:25 | 0.4017 | 0.00309 | 66 | 8580 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 256 | 47672 | Beach Rd Easdt 501 | QW06 Wakanui_22 | 2024-12-04 09:02 | 2024-12-04 12:08 | 0.29608 | 0.0015918 | 34 | 6324 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 257 | 47673 | Chetsey Kyle Rd | PX03 Kyle_22 | 2024-12-04 09:01 | 2024-12-04 15:10 | 1.2784 | 0.0034646 | 74 | 27306 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 258 | 47674 | Buckleys Rd. | PX03 Kyle_22 | 2024-12-05 09:02 | 2024-12-05 14:34 | 0.57512 | 0.0017323 | 37 | 12284 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 259 | 47681 | Thompsons Track. | OX03 Hatfield_22 | 2024-12-06 09:11 | 2024-12-06 15:33 | 0.17885 | 0.00046819 | 10 | 3820 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 260 | 47702 | Thomson St. | TF59 Carters Terrace_11 | 2024-12-09 09:38 | 2024-12-09 15:31 | 1.7188 | 0.0048691 | 104 | 36712 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 261 | 47717 | Arundle Rakaia Gorge Rd | SW04 Staveley_22 | 2024-12-10 09:34 | 2024-12-10 10:58 | 0.15338 | 0.0018259 | 39 | 3276 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 262 | 47719 | Back Track | BI20 Montalto_11 | 2024-12-10 09:38 | 2024-12-10 14:22 | 0.11967 | 0.00042137 | 9 | 2556 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 263 | 47728 | Lower Downs Rd. | SY02 Anama_22 | 2024-12-13 09:00 | 2024-12-13 14:32 | 0.45077 | 0.0013577 | 29 | 9628 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 264 | 47740 | Kermode St 2 | TJ20 Oak Grove_11 | 2024-12-15 08:01 | 2024-12-15 11:10 | 0.017697 | 9.3637e-05 | 2 | 378 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 265 | 47741 | Malcolm McDowell Ave 10 | BI20 Montalto_11 | 2024-12-15 12:51 | 2024-12-15 15:08 | 0.057727 | 0.00042137 | 9 | 1233 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 266 | 47746 | Inverrose Rd. | WV04 Seaview_22 | 2024-12-16 09:06 | 2024-12-16 14:06 | 0.40732 | 0.0013577 | 29 | 8700 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 267 | 47748 | Dorie School Rd. | RY02 Rakaia Huts_22 | 2024-12-16 09:19 | 2024-12-16 12:46 | 0.50396 | 0.0024346 | 52 | 10764 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 268 | 47750 | Mainwarings Rd. | RZ01 Dorie West_22 | 2024-12-16 11:04 | 2024-12-16 13:13 | 0.47109 | 0.0036519 | 78 | 10062 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 269 | 47751 | Wakanui School Rd. | WY02 Hakatere_22 | 2024-12-16 12:37 | 2024-12-16 15:55 | 0.03708 | 0.00018727 | 4 | 792 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 270 | 47758 | Gardiners Rd. | RZ01 Dorie West_22 | 2024-12-17 08:36 | 2024-12-17 14:10 | 0.64113 | 0.0019196 | 41 | 13694 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 271 | 47760 | Longbeach Rd. | GW04 Winslow_22 | 2024-12-17 09:07 | 2024-12-17 15:14 | 0.25774 | 0.00070228 | 15 | 5505 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 272 | 47765 | Methven Chertsey Rd. | BI20 Montalto_11 | 2024-12-17 11:05 | 2024-12-17 14:31 | 0.048223 | 0.00023409 | 5 | 1030 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 273 | 47766 | Methven Chertsey Rd. | UV05 Urrall_22 | 2024-12-17 12:05 | 2024-12-17 18:21 | 0.070415 | 0.00018727 | 4 | 1504 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 274 | 47774 | Robinson St 8 Sub | OW04 Rakaia_22 | 2024-12-19 09:38 | 2024-12-19 10:09 | 0.0087083 | 0.00028091 | 6 | 186 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 275 | 47819 | Siberia Rd. | GX03 Frasers Rd West_22 | 2025-01-06 09:08 | 2025-01-06 13:23 | 0.31041 | 0.0012173 | 26 | 6630 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 276 | 47844 | Barkers Rd 45-A | VR09 Methven North_11 | 2025-01-13 10:03 | 2025-01-13 14:14 | 0.55232 | 0.0022005 | 47 | 11797 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 277 | 47854 | Mayfield Klondkye Rd | BI20 Montalto_11 | 2025-01-14 09:02 | 2025-01-14 14:51 | 2.6634 | 0.0076314 | 163 | 56887 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 278 | 47856 | Wakanui School Rd | WY02 Hakatere_22 | 2025-01-15 09:01 | 2025-01-15 11:52 | 0.08006 | 0.00046819 | 10 | 1710 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 279 | 47864 | Rakaia River Rd | MW04 - Blackford rd feeder | 2025-01-16 09:24 | 2025-01-16 12:13 | 0.063299 | 0.00037455 | 8 | 1352 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 280 | 47865 | Arundle Rakaia Gorge Rd | NT07 Stoneylea Rd_22 | 2025-01-16 09:29 | 2025-01-16 13:41 | 0.24776 | 0.00098319 | 21 | 5292 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 281 | 47868 | Chertsey Kyle Rd. | PT07 Pendarves North_22 | 2025-01-17 09:33 | 2025-01-17 14:30 | 0.43106 | 0.0014514 | 31 | 9207 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 282 | 47874 | Lauriston Barrhill Rd | UY02 Barrhill_22 | 2025-01-20 09:07 | 2025-01-20 14:34 | 0.58177 | 0.0017791 | 38 | 12426 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 283 | 47875 | Buckleys Rd. | PX03 Kyle_22 | 2025-01-21 09:00 | 2025-01-21 14:07 | 0.24435 | 0.00079592 | 17 | 5219 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 284 | 47876 | Hakatere Heron Rd. | SX03 Ashburton Gorge_22 | 2025-01-21 09:40 | 2025-01-21 16:14 | 0.25825 | 0.00065546 | 14 | 5516 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 285 | 47883 | Anama Valetta Rd. | SY02 Anama_22 | 2025-01-22 09:09 | 2025-01-22 16:12 | 0.89119 | 0.0021068 | 45 | 19035 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 286 | 47894 | Upper Cavendish Rd | SY02 Anama_22 | 2025-01-23 09:11 | 2025-01-23 14:48 | 0.094667 | 0.00028091 | 6 | 2022 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 287 | 47895 | McLauchlans & Mainwarings Rds. | OV05 Acton_22 | 2025-01-24 09:06 | 2025-01-24 15:34 | 1.1081 | 0.0028559 | 61 | 23668 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 288 | 47906 | Rangitata Highway | NX03 Ealing_22 | 2025-01-27 09:20 | 2025-01-27 14:41 | 0.64624 | 0.0020132 | 43 | 13803 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 289 | 47907 | Ealing Montalto Rd | NX03 Ealing_22 | 2025-01-27 12:34 | 2025-01-27 15:00 | 0.33494 | 0.0022941 | 49 | 7154 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 290 | 47910 | Hekeao Rd. | SY02 Anama_22 | 2025-01-28 09:03 | 2025-01-28 12:58 | 0.088019 | 0.00037455 | 8 | 1880 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 291 | 47914 | Rakaia Hwy. | OY02 Chertsey_22 | 2025-01-28 09:24 | 2025-01-28 14:07 | 0.11925 | 0.00042137 | 9 | 2547 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 292 | 47919 | Corbetts Rd North | RW04 Dorie East_22 | 2025-01-29 09:19 | 2025-01-29 12:35 | 0.24776 | 0.0012641 | 27 | 5292 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 293 | 47920 | Mt Hutt Station Rd | MW04 - Blackford rd feeder | 2025-01-29 13:03 | 2025-01-29 14:47 | 0.043822 | 0.00042137 | 9 | 936 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 294 | 47926 | Lower Downs Rd | SY02 Anama_22 | 2025-01-30 09:00 | 2025-01-30 14:50 | 0.4916 | 0.0014046 | 30 | 10500 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 295 | 47930 | Anama Station Rd. | SY02 Anama_22 | 2025-01-31 09:21 | 2025-01-31 16:12 | 0.86591 | 0.0021068 | 45 | 18495 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 296 | 47941 | Farqhares Rd | UY02 Barrhill_22 | 2025-02-03 09:10 | 2025-02-03 12:26 | 0.14682 | 0.0007491 | 16 | 3136 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 297 | 47942 | McConnells Rd | JY02 Hinds South_22 | 2025-02-03 09:14 | 2025-02-03 13:07 | 0.42544 | 0.0018259 | 39 | 9087 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 298 | 47945 | Blairs Rd | MayfKloRd 46-B T1 | 2025-02-03 09:05 | 2025-02-03 15:19 | 0.03502 | 9.3637e-05 | 2 | 748 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 299 | 47947 | South Park Rd. | ZR09 Seafield Rd_11 | 2025-02-04 09:13 | 2025-02-04 14:15 | 0.056557 | 0.00018727 | 4 | 1208 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 300 | 47965 | Anama Settlement Rd. | MayfKloRd 46-B T1 | 2025-02-10 09:00 | 2025-02-10 16:13 | 0.3649 | 0.00084274 | 18 | 7794 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 301 | 47970 | Company Rd | FU06 Company Rd_11 | 2025-02-11 09:04 | 2025-02-11 16:56 | 1.1712 | 0.0024814 | 53 | 25016 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 302 | 47972 | Mayfield Klondyke Rd | MayfKloRd 46-B T1 | 2025-02-11 09:33 | 2025-02-11 14:30 | 0.2781 | 0.00093637 | 20 | 5940 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 303 | 47973 | Hakatere Huts | WY02 Hakatere_22 | 2025-02-11 09:06 | 2025-02-11 15:42 | 2.2063 | 0.0055714 | 119 | 47124 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 304 | 47976 | Mainwarings Rd | RZ01 Dorie West_22 | 2025-02-12 08:30 | 2025-02-12 13:53 | 1.1795 | 0.0036519 | 78 | 25194 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 305 | 47981 | Gardiners Rd. | RZ01 Dorie West_22 | 2025-02-13 09:06 | 2025-02-13 10:50 | 0.063299 | 0.00060864 | 13 | 1352 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 306 | 47983 | Gardiners Rd. | RZ01 Dorie West_22 | 2025-02-13 13:09 | 2025-02-13 15:38 | 0.28602 | 0.0019196 | 41 | 6109 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 307 | 47987 | Awaroa School Rd. | PY02 McCrorys Rd_22 | 2025-02-14 08:41 | 2025-02-14 12:38 | 0.022192 | 9.3637e-05 | 2 | 474 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 308 | 47992 | Allens Rd 7 Sub | TJ20 Oak Grove_11 | 2025-02-16 09:08 | 2025-02-16 12:52 | 0.40901 | 0.0018259 | 39 | 8736 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 309 | 48002 | Bruces Rd | SX03 Ashburton Gorge_22 | 2025-02-18 09:04 | 2025-02-18 14:43 | 0.063486 | 0.00018727 | 4 | 1356 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 310 | 48004 | Lower Downs Rd | SY02 Anama_22 | 2025-02-18 09:06 | 2025-02-18 14:55 | 0.14706 | 0.00042137 | 9 | 3141 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 311 | 48005 | Mayfield Klondyke & Coskeries Rds. | BI20 Montalto_11 | 2025-02-19 09:29 | 2025-02-19 15:56 | 2.9534 | 0.0076314 | 163 | 63081 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 312 | 48017 | McCorys Rd | RW04 Dorie East_22 | 2025-02-20 08:35 | 2025-02-20 13:44 | 0.043401 | 0.00014046 | 3 | 927 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 313 | 48018 | Mainwarings Rd. | RW04 Dorie East_22 | 2025-02-21 09:20 | 2025-02-21 13:02 | 0.55087 | 0.0024814 | 53 | 11766 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 314 | 48020 | Inverrose Rd. | WV04 Seaview_22 | 2025-02-21 09:21 | 2025-02-21 12:22 | 0.24575 | 0.0013577 | 29 | 5249 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 315 | 48021 | Lambies Rd. | RW04 Dorie East_22 | 2025-02-21 13:19 | 2025-02-21 16:01 | 0.21995 | 0.0013577 | 29 | 4698 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 316 | 48031 | Mayfield Klondyke Rd. | BI20 Montalto_11 | 2025-02-24 09:04 | 2025-02-24 16:04 | 2.222 | 0.0052905 | 113 | 47460 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 317 | 48038 | Methven Hwy between Rooneys & Shearers Rds. | UW04 Braemar_22 | 2025-02-25 09:08 | 2025-02-25 16:40 | 0.80416 | 0.0017791 | 38 | 17176 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 318 | 48041 | Dip Rd. | VZ01 Springfield_22 | 2025-02-25 13:07 | 2025-02-25 13:37 | 0.019664 | 0.00065546 | 14 | 420 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 319 | 48042 | Hinds Gorge Rd. | BI20 Montalto_11 | 2025-02-26 09:42 | 2025-02-26 15:56 | 0.71792 | 0.0019196 | 41 | 15334 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 320 | 48046 | Coskeries Rd. | SY02 Anama_22 | 2025-02-27 09:43 | 2025-02-27 15:36 | 0.1818 | 0.00051501 | 11 | 3883 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 321 | 48051 | Racecourse Rd. | ZS08 Racecourse Rd_11 | 2025-02-28 09:32 | 2025-02-28 10:46 | 0.020787 | 0.00028091 | 6 | 444 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 322 | 48066 | Anama Station Rd | SY02 Anama_22 | 2025-03-03 09:11 | 2025-03-03 11:39 | 0.1178 | 0.00079592 | 17 | 2516 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 323 | 48074 | Rangitata Terrace Rd | NV05 Carew_22 | 2025-03-05 09:14 | 2025-03-05 13:47 | 0.11503 | 0.00042137 | 9 | 2457 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 324 | 48078 | Woodvale Rd | BI20 Montalto_11 | 2025-03-06 09:18 | 2025-03-06 14:09 | 0.054497 | 0.00018727 | 4 | 1164 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 325 | 48079 | Methven Highway | UW04 Braemar_22 | 2025-03-06 09:21 | 2025-03-06 12:56 | 0.38251 | 0.0017791 | 38 | 8170 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 326 | 48080 | Mayfield Klondyke Rd. | BI20 Montalto_11 | 2025-03-07 09:02 | 2025-03-07 16:10 | 2.2643 | 0.0052905 | 113 | 48364 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 327 | 48087 | Rakaia Hwy | OY02 Chertsey_22 | 2025-03-11 10:36 | 2025-03-11 13:41 | 0.27717 | 0.0014982 | 32 | 5920 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 328 | 48097 | Methven Highway | UW04 Braemar_22 | 2025-03-14 09:00 | 2025-03-14 11:38 | 0.21452 | 0.0013577 | 29 | 4582 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 329 | 48098 | Winters Rd | PX03 Kyle_22 | 2025-03-14 09:37 | 2025-03-14 11:24 | 0.025048 | 0.00023409 | 5 | 535 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 330 | 48100 | Barkers Rd | BI20 Montalto_11 | 2025-03-14 09:43 | 2025-03-14 14:50 | 0.057493 | 0.00018727 | 4 | 1228 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 331 | 48105 | Melcombe St | IT07 Bryant St_11 | 2025-03-16 08:02 | 2025-03-16 17:53 | 0.47039 | 0.00079592 | 17 | 10047 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 332 | 48107 | Dorrie School, Griggs & Harrisons Rds. | RY02 Rakaia Huts_22 | 2025-03-17 10:00 | 2025-03-17 13:51 | 0.56239 | 0.0024346 | 52 | 12012 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 333 | 48122 | Hinds Gorge Rd | BI20 Montalto_11 | 2025-03-19 10:00 | 2025-03-19 16:02 | 0.69488 | 0.0019196 | 41 | 14842 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 334 | 48130 | Longbeach Rd. | YV05 Longbeach_22 | 2025-03-21 09:01 | 2025-03-21 13:18 | 0.60162 | 0.0023409 | 50 | 12850 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 335 | 48131 | Acton Rd. | OV05 Acton_22 | 2025-03-21 13:05 | 2025-03-21 13:55 | 0.10768 | 0.0021537 | 46 | 2300 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 336 | 48136 | Rangitata Hwy | NX03 Ealing_22 | 2025-03-24 09:06 | 2025-03-24 14:07 | 0.60597 | 0.0020132 | 43 | 12943 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 337 | 48140 | Mainwarings Rd. | OV05 Acton_22 | 2025-03-25 09:00 | 2025-03-25 10:46 | 0.064516 | 0.00060864 | 13 | 1378 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 338 | 48152 | Hinds Gorge Rd | BI20 Montalto_11 | 2025-03-26 09:10 | 2025-03-26 13:43 | 0.12781 | 0.00046819 | 10 | 2730 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 339 | 48155 | Hakatere Huts | WY02 Hakatere_22 | 2025-03-27 09:00 | 2025-03-27 11:08 | 0.71314 | 0.0055714 | 119 | 15232 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 340 | 48161 | Upper Downs Rd | BI20 Montalto_11 | 2025-03-28 09:04 | 2025-03-28 14:32 | 0.29177 | 0.00088955 | 19 | 6232 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 341 | 48167 | Montalto Hydro Station and Montalto Substation. | BI20 Montalto_11 | 2025-03-31 08:59 | 2025-04-01 13:31 | 0.080154 | 4.6819e-05 | 1 | 1712 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 342 | 48168 | Line Rd 1470 | UV05 Urrall_22 | 2025-03-31 09:18 | 2025-03-31 11:55 | 0.022052 | 0.00014046 | 3 | 471 | Planned | Planned |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 343 | 46606 | Scarness Rd | VU06 Mt Hutt_11 | 2024-04-10 11:52 | 2024-04-10 12:31 | 0.016433 | 0.00042137 | 9 | 351 | Unplanned | Foreign Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 344 | 46611 | Muckles Rd | RY02 Rakaia Huts_22 | 2024-04-11 13:52 | 2024-04-11 14:59 | 0.0062737 | 9.3637e-05 | 2 | 134 | Unplanned | Foreign Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 345 | 46612 | Rakaia Hwy 451 | FN13 Rakaia Hwy_22 | 2024-04-11 17:05 | 2024-04-11 20:33 | 0.19051 | 0.0013109 | 28 | 4069 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 346 | 46614 | Withells Rd | NV05 Carew_22 | 2024-04-11 18:56 | 2024-04-11 20:31 | 0.20947 | 0.0027155 | 58 | 4474 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 347 | 46616 | Rakaia Huts Feeder | RY02 Rakaia Huts_22 | 2024-04-12 02:00 | 2024-04-12 04:45 | 0.37909 | 0.0090828 | 194 | 8097 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 348 | 46625 | Valetta Westerfield Rd | KV05 Hackthorne_22 | 2024-04-16 15:06 | 2024-04-16 15:34 | 0.015731 | 0.00056182 | 12 | 336 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 349 | 46631 | Tinwald East | TF59 Carters Terrace_11 | 2024-04-17 09:21 | 2024-04-17 09:26 | 0.22613 | 0.045227 | 966 | 4830 | Unplanned | Human Element |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 350 | 46636 | Winterslow area | SW04 Staveley_22 | 2024-04-17 07:01 | 2024-04-17 08:44 | 0.11574 | 0.0011236 | 24 | 2472 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 351 | 46654 | Lowes Rd. | GX03 Frasers Rd West_22 | 2024-04-24 19:05 | 2024-04-24 19:58 | 0.037221 | 0.00070228 | 15 | 795 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 352 | 46656 | Mt Peel & Shepherds Bush. | BI20 Montalto_11 | 2024-04-25 11:00 | 2024-04-25 13:45 | 0.11588 | 0.00070228 | 15 | 2475 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 353 | 46657 | Ruapuna area. | NT07 Stoneylea Rd_22 | 2024-04-25 12:12 | 2024-04-25 12:54 | 0.16518 | 0.0039328 | 84 | 3528 | Unplanned | Trees |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 354 | 46660 | South Rakaia Huts. | RY02 Rakaia Huts_22 | 2024-04-25 14:20 | 2024-04-25 15:50 | 0.29917 | 0.0033241 | 71 | 6390 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 355 | 46672 | Griggs Rd | RY02 Rakaia Huts_22 | 2024-04-29 09:10 | 2024-04-29 10:10 | 0.0309 | 0.00051501 | 11 | 660 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 356 | 46685 | 1319 Grahams rd | YW04 Flemington_22 | 2024-05-04 08:35 | 2024-05-04 10:02 | 0.020366 | 0.00023409 | 5 | 435 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 357 | 46686 | Ashton rd | YW04 Flemington_22 | 2024-05-04 09:52 | 2024-05-04 10:30 | 0.012454 | 0.00032773 | 7 | 266 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 358 | 46702 | Pole Rd. | UW04 Braemar_22 | 2024-05-07 14:40 | 2024-05-07 15:34 | 0.023737 | 0.00060864 | 13 | 507 | Unplanned | Foreign Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 359 | 46709 | Bryants Rd. | JV05 Poplar Rd_22 | 2024-05-08 19:02 | 2024-05-08 20:02 | 0.0309 | 0.00051501 | 11 | 660 | Unplanned | Trees |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 360 | 46714 | Shephards Bush Rd | NT07 Stoneylea Rd_22 | 2024-05-10 14:00 | 2024-05-10 16:07 | 0.08919 | 0.00070228 | 15 | 1905 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 361 | 46719 | Hoattens Rd | QY03 Cochranes Rd_22 | 2024-05-11 09:27 | 2024-05-11 10:10 | 0.014092 | 0.00032773 | 7 | 301 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 362 | 46720 | Longbeach Rd | YV05 Longbeach_22 | 2024-05-12 06:31 | 2024-05-12 08:55 | 0.13484 | 0.00093637 | 20 | 2880 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 363 | 46722 | Acton Rd. | OV05 Acton_22 | 2024-05-13 18:03 | 2024-05-13 20:06 | 0.057587 | 0.00046819 | 10 | 1230 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 364 | 46730 | Christys Rd | PV05 Christys Rd_22 | 2024-05-15 07:12 | 2024-05-15 12:51 | 0.92958 | 0.0044478 | 95 | 19855 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 365 | 46733 | Corbetts Rd North | RW04 Dorie East_22 | 2024-05-16 07:53 | 2024-05-16 11:40 | 0.28695 | 0.0012641 | 27 | 6129 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 366 | 46735 | Dromore Hatfield Rd | OY02 Chertsey_22 | 2024-05-16 12:12 | 2024-05-16 13:09 | 0.037642 | 0.00093637 | 20 | 804 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 367 | 46736 | Lakes Rd | NT07 Stoneylea Rd_22 | 2024-05-16 12:25 | 2024-05-16 14:08 | 0.019289 | 0.00018727 | 4 | 412 | Unplanned | Trees |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 368 | 46742 | Junction Rd feeder. | JX03 Junction Rd_22 | 2024-05-18 09:12 | 2024-05-18 09:15 | 0.0089892 | 0.0029964 | 64 | 192 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 369 | 46743 | Junction Rd. | JX03 Junction Rd_22 | 2024-05-18 11:28 | 2024-05-18 13:18 | 0.1133 | 0.00103 | 22 | 2420 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 370 | 46794 | Thompsons Track, Mitcham feeder. | UX03 Mitcham_22 | 2024-05-31 00:47 | 2024-05-31 03:31 | 0.38391 | 0.0023409 | 50 | 8200 | Unplanned | Foreign Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 371 | 46802 | 113 McKays Rd | OX03 Hatfield_22 | 2024-06-01 17:29 | 2024-06-01 18:38 | 0.032305 | 0.00046819 | 10 | 690 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 372 | 46808 | Haylors Rd. | PX03 Kyle_22 | 2024-06-04 07:51 | 2024-06-04 09:15 | 0.023597 | 0.00028091 | 6 | 504 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 373 | 46824 | Jaines rd | NV05 Carew_22 | 2024-06-06 19:41 | 2024-06-06 20:41 | 0.033709 | 0.00056182 | 12 | 720 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 374 | 46833 | Dromore Hatfield Rd. | OX03 Hatfield_22 | 2024-06-10 07:20 | 2024-06-10 09:59 | 0.041154 | 0.00032773 | 7 | 879 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 375 | 46850 | 1315 Frasers Rd, Westerfield area. | GX03 Frasers Rd West_22 | 2024-06-12 13:17 | 2024-06-12 23:05 | 0.27642 | 0.0023409 | 50 | 5904 | Unplanned | Foreign Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 376 | 46851 | Coplands & Somerton Rds. | OY02 Chertsey_22 | 2024-06-12 20:19 | 2024-06-12 20:55 | 0.033709 | 0.00093637 | 20 | 720 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 377 | 46876 | Wrens Rd | JW04 Coldstream_22 | 2024-06-16 19:30 | 2024-06-16 20:26 | 0.29889 | 0.0053373 | 114 | 6384 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 378 | 46877 | 247 Wrights Rd | WV04 Seaview_22 | 2024-06-18 08:58 | 2024-06-18 09:48 | 0.0023409 | 4.6819e-05 | 1 | 50 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 379 | 46883 | West St 441-A, West St feeder. | ZM14 West St_11 | 2024-06-19 02:02 | 2024-06-19 09:00 | 0.6769 | 0.01222 | 261 | 14458 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 380 | 46884 | Beach Rd East. | WY02 Hakatere_22 | 2024-06-19 13:38 | 2024-06-19 23:32 | 0.98549 | 0.0094106 | 201 | 21049 | Unplanned | Foreign Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 381 | 46891 | Boyds Rd | SW04 Staveley_22 | 2024-06-21 09:36 | 2024-06-21 13:18 | 0.14551 | 0.00065546 | 14 | 3108 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 382 | 46892 | Thompsons Track | UW04 Braemar_22 | 2024-06-21 14:23 | 2024-06-21 16:05 | 0.21012 | 0.00206 | 44 | 4488 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 383 | 46896 | 168 Westerfield School Rd | GX03 Frasers Rd West_22 | 2024-06-22 18:00 | 2024-06-22 19:25 | 0.09551 | 0.0011236 | 24 | 2040 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 384 | 46907 | Chertsey Rd. | OY02 Chertsey_22 | 2024-06-25 06:00 | 2024-06-25 06:50 | 0.039796 | 0.00079592 | 17 | 850 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 385 | 46910 | Surveyors Rd. | YX03 Lynnford_22 | 2024-06-25 22:58 | 2024-06-26 13:56 | 1.6514 | 0.0031837 | 68 | 35272 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 386 | 46916 | 413 Pole Rd | VZ01 Springfield_22 | 2024-06-30 17:34 | 2024-06-30 20:13 | 0.074442 | 0.00046819 | 10 | 1590 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 387 | 46920 | 53 Flemings rd | VZ01 Springfield_22 | 2024-06-27 13:20 | 2024-06-27 14:25 | 0.042605 | 0.00065546 | 14 | 910 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 388 | 46925 | 223 Hoattens rd | QY03 Cochranes Rd_22 | 2024-07-01 19:20 | 2024-07-01 20:08 | 0.015731 | 0.00032773 | 7 | 336 | Unplanned | Trees |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 389 | 46938 | Allan Smith rd | BE43 - Tramway rd feeder | 2024-07-05 12:31 | 2024-07-05 12:53 | 0.04532 | 0.00206 | 44 | 968 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 390 | 46939 | 168 Westerfield School rd | GX03 Frasers Rd West_22 | 2024-07-05 18:26 | 2024-07-05 19:21 | 0.061801 | 0.0011236 | 24 | 1320 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 391 | 46942 | 1458 Chertsey Kyle rd | PX03 Kyle_22 | 2024-07-07 19:11 | 2024-07-07 20:37 | 0.29393 | 0.0034178 | 73 | 6278 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 392 | 46949 | Surveyors rd | YX03 Lynnford_22 | 2024-07-09 15:40 | 2024-07-09 17:53 | 0.26345 | 0.0031837 | 68 | 5627 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 393 | 46962 | Acton Rd | OV05 Acton_22 | 2024-07-12 05:50 | 2024-07-12 09:31 | 0.10347 | 0.00046819 | 10 | 2210 | Unplanned | Foreign Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 394 | 46985 | Poplar Rd | YV05 Longbeach_22 | 2024-07-18 03:28 | 2024-07-18 06:16 | 0.73014 | 0.010066 | 215 | 15595 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 395 | 46997 | 659 Heburns Rd | FN13 Rakaia Hwy_22 | 2024-07-19 20:44 | 2024-07-19 21:25 | 0.0076783 | 0.00018727 | 4 | 164 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 396 | 46998 | Ashton Rd | YW04 Flemington_22 | 2024-07-19 22:44 | 2024-07-19 23:38 | 0.017697 | 0.00032773 | 7 | 378 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 397 | 47032 | 15 Muckles Rd | RY02 Rakaia Huts_22 | 2024-07-27 15:01 | 2024-07-27 16:53 | 0.010487 | 9.3637e-05 | 2 | 224 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 398 | 47038 | Rakaia Barrhill Methven Rd | OX03 Hatfield_22 | 2024-07-28 14:11 | 2024-07-28 14:13 | 0.00412 | 0.00206 | 44 | 88 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 399 | 47043 | Wilsons Rd | WY02 Hakatere_22 | 2024-07-30 01:54 | 2024-07-30 08:02 | 0.25844 | 0.00070228 | 15 | 5520 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 400 | 47050 | Hepburns Rd | FH19 Mitcham Rd_22 | 2024-08-01 09:06 | 2024-08-01 14:46 | 0.85978 | 0.022426 | 479 | 18364 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 401 | 47051 | Hepburns Rd | FH19 Mitcham Rd_22 | 2024-08-01 09:27 | 2024-08-01 09:29 | 0.0073974 | 0.0036987 | 79 | 158 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 402 | 47052 | Hoattens Rd | QY03 Cochranes Rd_22 | 2024-08-01 11:37 | 2024-08-01 12:31 | 0.017697 | 0.00032773 | 7 | 378 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 403 | 47061 | Windermere Rd. | YV05 Longbeach_22 | 2024-08-03 08:25 | 2024-08-03 09:25 | 0.0084274 | 0.00014046 | 3 | 180 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 404 | 47063 | Copley Rd | PT07 Pendarves North_22 | 2024-08-05 18:29 | 2024-08-05 23:26 | 0.25516 | 0.0022005 | 47 | 5450 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 405 | 47065 | Rakaia Barrhill Methven Rd. | UY02 Barrhill_22 | 2024-08-06 00:55 | 2024-08-06 08:03 | 0.60115 | 0.0014046 | 30 | 12840 | Unplanned | Foreign Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 406 | 47079 | Maronan Rd. | KW04 Maronan_22 | 2024-08-08 10:12 | 2024-08-08 14:57 | 0.41364 | 0.0014514 | 31 | 8835 | Unplanned | Foreign Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 407 | 47087 | Trevors Rd | NV05 Carew_22 | 2024-08-12 11:27 | 2024-08-12 13:46 | 0.18222 | 0.0013109 | 28 | 3892 | Unplanned | Trees |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 408 | 47088 | Wilkins Rd | QX05 Huntingdon_22 | 2024-08-12 11:45 | 2024-08-12 15:00 | 0.20998 | 0.0010768 | 23 | 4485 | Unplanned | Trees |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 409 | 47090 | Valletta Mayfield Rd | KY02 Punawai_22 | 2024-08-12 11:46 | 2024-08-12 13:12 | 0.44651 | 0.0067419 | 144 | 9537 | Unplanned | Trees |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 410 | 47091 | Thomsons Track | OX03 Hatfield_22 | 2024-08-12 11:56 | 2024-08-12 13:50 | 0.86123 | 0.025844 | 552 | 18395 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 411 | 47097 | 122 Lakes Rd | NT07 Stoneylea Rd_22 | 2024-08-12 13:07 | 2024-08-12 14:14 | 0.012547 | 0.00018727 | 4 | 268 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 412 | 47099 | Valetta Westerfield Rd | KV05 Hackthorne_22 | 2024-08-12 16:05 | 2024-08-12 18:54 | 0.094948 | 0.00056182 | 12 | 2028 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 413 | 47102 | Upper Downs Rd | BI20 Montalto_11 | 2024-08-12 18:54 | 2024-08-12 19:38 | 0.03914 | 0.00088955 | 19 | 836 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 414 | 47147 | Ashburton Gorge Rd. | SX03 Ashburton Gorge_22 | 2024-08-23 04:44 | 2024-08-23 06:50 | 0.3238 | 0.0038859 | 83 | 6916 | Unplanned | Trees |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 415 | 47157 | Line Rd, Mitcham feeder. | UX03 Mitcham_22 | 2024-08-26 15:46 | 2024-08-26 19:02 | 0.24992 | 0.0023409 | 50 | 5338 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 416 | 47179 | Emersons Rd, Coldstream feeder. | JW04 Coldstream_22 | 2024-08-29 06:16 | 2024-08-29 11:10 | 0.71169 | 0.013812 | 295 | 15201 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 417 | 47181 | Emersons Rd 5 RMU | JW04 Coldstream_22 | 2024-08-29 13:09 | 2024-08-29 13:11 | 0.015076 | 0.0075378 | 161 | 322 | Unplanned | Human Element |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 418 | 47182 | Wrens Rd. | JW04 Coldstream_22 | 2024-08-29 16:21 | 2024-08-29 17:06 | 0.22965 | 0.0051032 | 109 | 4905 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 419 | 47187 | Somerton Rd | OY02 Chertsey_22 | 2024-08-30 08:15 | 2024-08-30 08:54 | 0.0018259 | 4.6819e-05 | 1 | 39 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 420 | 47189 | Craycroft Maronan Rd | NV05 Carew_22 | 2024-08-30 17:02 | 2024-08-30 18:18 | 0.071164 | 0.00093637 | 20 | 1520 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 421 | 47194 | Seafield Rd. | PV05 Christys Rd_22 | 2024-09-01 14:02 | 2024-09-01 15:31 | 0.15834 | 0.0017791 | 38 | 3382 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 422 | 47196 | Maronan Ealing Rd. | NU06 Lismore_22 | 2024-09-01 20:02 | 2024-09-01 21:08 | 0.10197 | 0.001545 | 33 | 2178 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 423 | 47197 | Shepherds Bush & Ealing Montalto Rds. | NT07 Stoneylea Rd_22 | 2024-09-01 19:52 | 2024-09-02 03:38 | 0.45386 | 0.002575 | 55 | 9694 | Unplanned | Trees |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 424 | 47199 | Shepherds Bush Rd. | NT07 Stoneylea Rd_22 | 2024-09-02 09:31 | 2024-09-02 11:27 | 0.038017 | 0.00032773 | 7 | 812 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 425 | 47202 | Sheates Rd. | GY02 Ferrimans Rd_22 | 2024-09-02 11:32 | 2024-09-02 13:39 | 0.12487 | 0.00098319 | 21 | 2667 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 426 | 47207 | 51 Withells Rd | NX03 Ealing_22 | 2024-09-03 02:02 | 2024-09-03 03:26 | 0.015731 | 0.00018727 | 4 | 336 | Unplanned | Trees |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 427 | 47211 | Upper Rakaia Gorge | AE96 Upper Rakaia_11 | 2024-09-03 06:56 | 2024-09-03 10:13 | 0.12913 | 0.00065546 | 14 | 2758 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 428 | 47218 | Hackthore Sub | KX03 Hackthorne South_22 | 2024-09-03 18:39 | 2024-09-03 18:59 | 0.073927 | 0.0047287 | 101 | 1579 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 429 | 47218 | Hackthore Sub | KU06 Mayfield_22 | 2024-09-03 18:39 | 2024-09-03 18:59 | 0.14856 | 0.0095042 | 203 | 3173 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 430 | 47218 | Hackthore Sub | KT07 Westerfield_22 | 2024-09-03 18:39 | 2024-09-03 18:59 | 0.024908 | 0.0015918 | 34 | 532 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 431 | 47218 | Hackthore Sub | KY02 Punawai_22 | 2024-09-03 18:39 | 2024-09-03 18:59 | 0.10614 | 0.0067887 | 145 | 2267 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 432 | 47218 | Hackthore Sub | KW04 Maronan_22 | 2024-09-03 18:39 | 2024-09-03 18:59 | 0.10904 | 0.006976 | 149 | 2329 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 433 | 47218 | Hackthore Sub | KV05 Hackthorne_22 | 2024-09-03 18:39 | 2024-09-03 18:59 | 0.131 | 0.0083805 | 179 | 2798 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 434 | 47234 | Upper Rakaia Gorge Rd. | AE96 Upper Rakaia_11 | 2024-09-07 14:30 | 2024-09-07 14:36 | 0.0039328 | 0.00065546 | 14 | 84 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 435 | 47235 | South Rakaia Huts. | RY02 Rakaia Huts_22 | 2024-09-07 15:50 | 2024-09-07 16:16 | 0.08521 | 0.0032773 | 70 | 1820 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 436 | 47237 | Fountaines Rd. | NY02 Fountaines Rd_22 | 2024-09-07 18:42 | 2024-09-07 19:43 | 0.037127 | 0.00060864 | 13 | 793 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 437 | 47253 | Rawles Crossing Rd, Ferrimans Rd feeder. | GY02 Ferrimans Rd_22 | 2024-09-10 21:46 | 2024-09-10 22:18 | 0.19486 | 0.012688 | 271 | 4162 | Unplanned | Trees |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 438 | 47254 | Rawles Crossing Rd, Ferrimans Rd feeder | GY02 Ferrimans Rd_22 | 2024-09-10 22:14 | 2024-09-10 22:40 | 0.04429 | 0.0097851 | 209 | 946 | Unplanned | Trees |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 439 | 47255 | 177 Wakanui Township Rd. | WV04 Seaview_22 | 2024-09-11 00:08 | 2024-09-11 06:38 | 0.073037 | 0.00018727 | 4 | 1560 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 440 | 47264 | 62 Mill Rd | GY02 Ferrimans Rd_22 | 2024-09-13 13:01 | 2024-09-13 14:02 | 0.025703 | 0.00042137 | 9 | 549 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 441 | 47267 | Methven Highway | VZ01 Springfield_22 | 2024-09-14 06:59 | 2024-09-14 10:17 | 0.04635 | 0.00023409 | 5 | 990 | Unplanned | Foreign Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 442 | 47270 | Corbetts Rd North | RW04 Dorie East_22 | 2024-09-14 16:19 | 2024-09-14 17:17 | 0.016293 | 0.00028091 | 6 | 348 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 443 | 47280 | Lowes Rd | GX03 Frasers Rd West_22 | 2024-09-17 16:59 | 2024-09-17 18:24 | 0.059694 | 0.00070228 | 15 | 1275 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 444 | 47283 | 250 Baxters Rd | NV05 Carew_22 | 2024-09-18 04:27 | 2024-09-18 05:22 | 0.0206 | 0.00037455 | 8 | 440 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 445 | 47286 | Wrights Rd | WV04 Seaview_22 | 2024-09-18 13:40 | 2024-09-18 14:48 | 0.0063673 | 9.3637e-05 | 2 | 136 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 446 | 47294 | Winchmore Lauriston Rd. | UW04 Braemar_22 | 2024-09-20 20:20 | 2024-09-21 03:10 | 0.57587 | 0.0014046 | 30 | 12300 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 447 | 47299 | Wallaces Rd. | KY02 Punawai_22 | 2024-09-21 07:49 | 2024-09-21 08:27 | 0.016012 | 0.00042137 | 9 | 342 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 448 | 47304 | Pole Rd | UW04 Braemar_22 | 2024-09-23 08:41 | 2024-09-23 10:22 | 0.0047287 | 4.6819e-05 | 1 | 101 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 449 | 47324 | Wrights Rd. | WV04 Seaview_22 | 2024-09-26 13:28 | 2024-09-26 15:38 | 0.17651 | 0.0013577 | 29 | 3770 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 450 | 47326 | Maronan Valetta Rd, Punawai feeder. | KY02 Punawai_22 | 2024-09-26 12:55 | 2024-09-26 13:47 | 0.34571 | 0.0066483 | 142 | 7384 | Unplanned | Trees |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 451 | 47335 | Marrs Rd | VU06 Mt Hutt_11 | 2024-09-29 12:40 | 2024-09-29 13:20 | 0.0056182 | 0.00014046 | 3 | 120 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 452 | 47337 | Haylors Rd. | PX03 Kyle_22 | 2024-09-30 07:33 | 2024-09-30 09:08 | 0.026687 | 0.00028091 | 6 | 570 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 453 | 47346 | Winchmore Lauriston Rd, Braemar feeder. | UW04 Braemar_22 | 2024-10-01 19:04 | 2024-10-02 00:08 | 1.11 | 0.018119 | 387 | 23709 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 454 | 47360 | 533 Heburns Rd | FH19 Mitcham Rd_22 | 2024-10-05 19:45 | 2024-10-05 20:35 | 0.0023409 | 4.6819e-05 | 1 | 50 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 455 | 47362 | Tindalls Rd | GX03 Frasers Rd West_22 | 2024-10-06 16:58 | 2024-10-06 18:32 | 0.052811 | 0.00056182 | 12 | 1128 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 456 | 47366 | Ashburton River Rd | VZ01 Springfield_22 | 2024-10-04 08:55 | 2024-10-04 08:56 | 0.0096915 | 0.0096915 | 207 | 207 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 457 | 47370 | Ashburton River Rd | VZ01 Springfield_22 | 2024-10-04 11:07 | 2024-10-04 12:17 | 0.058992 | 0.00084274 | 18 | 1260 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 458 | 47375 | Isleworth Settlement Rd. | JV05 Poplar Rd_22 | 2024-10-08 06:28 | 2024-10-08 07:54 | 0.017697 | 0.00023409 | 5 | 378 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 459 | 47393 | Mainwarings Rd, Dorie East feeder. | RW04 Dorie East_22 | 2024-10-11 11:44 | 2024-10-11 15:21 | 0.71628 | 0.0051969 | 111 | 15299 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 460 | 47395 | Corbetts Rd North | RW04 Dorie East_22 | 2024-10-12 17:02 | 2024-10-12 18:06 | 0.080903 | 0.0012641 | 27 | 1728 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 461 | 47396 | Blacks Rd. | GY02 Ferrimans Rd_22 | 2024-10-13 08:45 | 2024-10-13 10:04 | 0.014795 | 0.00018727 | 4 | 316 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 462 | 47398 | Barford Rd | KX03 Hackthorne South_22 | 2024-10-14 05:18 | 2024-10-14 06:05 | 0.13072 | 0.0027155 | 58 | 2792 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 463 | 47399 | 561 Lauriston Braemar Rd | UW04 Braemar_22 | 2024-10-14 06:45 | 2024-10-14 07:57 | 0.053935 | 0.0007491 | 16 | 1152 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 464 | 47402 | Bryants Rd | JV05 Poplar Rd_22 | 2024-10-14 21:58 | 2024-10-15 00:32 | 0.079311 | 0.00051501 | 11 | 1694 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 465 | 47403 | Bryants Rd | JV05 Poplar Rd_22 | 2024-10-15 01:05 | 2024-10-15 01:51 | 0.02369 | 0.00051501 | 11 | 506 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 466 | 47410 | 102 Coplands Rd | OY02 Chertsey_22 | 2024-10-16 06:46 | 2024-10-16 07:37 | 0.047755 | 0.00093637 | 20 | 1020 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 467 | 47430 | Allens Rd 7 | TJ20 Oak Grove_11 | 2024-10-20 12:22 | 2024-10-20 21:36 | 1.4717 | 0.0027155 | 58 | 31435 | Unplanned | Foreign Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 468 | 47461 | Jacksons Rd. | GY02 Ferrimans Rd_22 | 2024-10-26 09:48 | 2024-10-26 10:51 | 0.044244 | 0.00070228 | 15 | 945 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 469 | 47462 | 1397 Ashburton Gorge Rd. | SX03 Ashburton Gorge_22 | 2024-10-26 12:10 | 2024-10-27 10:49 | 0.25085 | 0.0016387 | 35 | 5358 | Unplanned | Trees |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 470 | 47466 | 2410 Double Hill Run Rd. | AE96 Upper Rakaia_11 | 2024-10-27 10:00 | 2024-10-27 13:32 | 0.019851 | 9.3637e-05 | 2 | 424 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 471 | 47469 | Watts Rd | KU06 Mayfield_22 | 2024-10-29 08:15 | 2024-10-29 09:50 | 0.057821 | 0.00060864 | 13 | 1235 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 472 | 47491 | Boltons & Cracroft Maronan Rds. | NT07 Stoneylea Rd_22 | 2024-11-01 20:00 | 2024-11-01 20:55 | 0.064891 | 0.0015918 | 34 | 1386 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 473 | 47498 | Jaines Rd | NV05 Carew_22 | 2024-11-04 06:45 | 2024-11-04 07:48 | 0.035395 | 0.00056182 | 12 | 756 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 474 | 47515 | Griggs Rd. | RZ01 Dorie West_22 | 2024-11-06 09:49 | 2024-11-06 13:30 | 0.048504 | 0.00051501 | 11 | 1036 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 475 | 47526 | Hoatens Rd | QY03 Cochranes Rd_22 | 2024-11-08 05:25 | 2024-11-08 06:51 | 0.012079 | 0.00014046 | 3 | 258 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 476 | 47549 | McKenzies Rd. | KY02 Punawai_22 | 2024-11-11 06:04 | 2024-11-11 07:39 | 0.04003 | 0.00042137 | 9 | 855 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 477 | 47553 | Lethams Rd. | UX03 Mitcham_22 | 2024-11-11 20:18 | 2024-11-11 21:10 | 0.034084 | 0.00065546 | 14 | 728 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 478 | 47567 | Arundel Rakaia Gorge & Watts Rds. | KU06 Mayfield_22 | 2024-11-13 20:44 | 2024-11-13 21:59 | 0.045648 | 0.00060864 | 13 | 975 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 479 | 47571 | Hoattens Rd | QY03 Cochranes Rd_22 | 2024-11-14 16:04 | 2024-11-14 16:30 | 0.015825 | 0.00060864 | 13 | 338 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 480 | 47574 | Ealing Montalto Rd | NT07 Stoneylea Rd_22 | 2024-11-17 11:46 | 2024-11-17 16:08 | 1.0537 | 0.004635 | 99 | 22506 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 481 | 47578 | McKays, Somerton & Rakaia Barrhill Methven Rds. | OX03 Hatfield_22 | 2024-11-18 11:57 | 2024-11-18 13:25 | 0.094761 | 0.0010768 | 23 | 2024 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 482 | 47587 | Trig Pole Rd | JV05 Poplar Rd_22 | 2024-11-20 05:18 | 2024-11-20 06:53 | 0.084508 | 0.00088955 | 19 | 1805 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 483 | 47606 | Elgin Sub | QV08 Stanley Rd_22 | 2024-11-24 02:29 | 2024-11-24 04:06 | 0.43598 | 0.0044946 | 96 | 9312 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 484 | 47606 | Elgin Sub | QW06 Wakanui_22 | 2024-11-24 02:29 | 2024-11-24 03:54 | 0.17112 | 0.0020132 | 43 | 3655 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 485 | 47606 | Elgin Sub | QY03 Cochranes Rd_22 | 2024-11-24 02:29 | 2024-11-24 03:54 | 0.32244 | 0.0033241 | 71 | 6887 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 486 | 47606 | Elgin Sub | QX05 Huntingdon_22 | 2024-11-24 02:29 | 2024-11-24 04:06 | 0.4326 | 0.004916 | 105 | 9240 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 487 | 47606 | Elgin Sub | OY02 Chertsey_22 | 2024-11-24 02:29 | 2024-11-24 03:46 | 0.70298 | 0.0091296 | 195 | 15015 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 488 | 47606 | Elgin Sub | OX03 Hatfield_22 | 2024-11-24 02:29 | 2024-11-24 03:46 | 0.92649 | 0.012032 | 257 | 19789 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 489 | 47606 | Elgin Sub | OW04 Rakaia_22 | 2024-11-24 02:29 | 2024-11-24 03:46 | 2.3649 | 0.030713 | 656 | 50512 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 490 | 47606 | Elgin Sub | OV05 Acton_22 | 2024-11-24 02:29 | 2024-11-24 03:46 | 0.31724 | 0.00412 | 88 | 6776 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 491 | 47606 | Elgin Sub | OU06 Overdale South_22 | 2024-11-24 02:29 | 2024-11-24 03:46 | 0.26317 | 0.0034178 | 73 | 5621 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 492 | 47633 | Grahams Rd | YW04 Flemington_22 | 2024-11-28 20:56 | 2024-11-28 22:33 | 0.061473 | 0.0010768 | 23 | 1313 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 493 | 47658 | Mt Somers | SX03 Ashburton Gorge_22 | 2024-12-01 14:49 | 2024-12-01 15:37 | 0.26293 | 0.0054778 | 117 | 5616 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 494 | 47665 | Siberia & Simpsons Rds. | GX03 Frasers Rd West_22 | 2024-12-03 08:05 | 2024-12-03 10:01 | 0.26069 | 0.0022473 | 48 | 5568 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 495 | 47692 | Ruapuna & Mt Peel. | NT07 Stoneylea Rd_22 | 2024-12-08 16:13 | 2024-12-08 18:51 | 0.25142 | 0.002575 | 55 | 5370 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 496 | 47695 | Farquhars Rd. | UY02 Barrhill_22 | 2024-12-08 18:40 | 2024-12-08 19:30 | 0.037455 | 0.0007491 | 16 | 800 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 497 | 47698 | Lauriston Barrhill Rd 3, Barrhill feeder. | UY02 Barrhill_22 | 2024-12-08 21:52 | 2024-12-08 23:02 | 0.52765 | 0.0075378 | 161 | 11270 | Unplanned | Trees |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 498 | 47699 | Franks Rd. | UV05 Urrall_22 | 2024-12-08 23:52 | 2024-12-09 03:46 | 0.12051 | 0.00051501 | 11 | 2574 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 499 | 47700 | Thompsons Track | UW04 Braemar_22 | 2024-12-09 00:40 | 2024-12-09 02:20 | 0.206 | 0.00206 | 44 | 4400 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 500 | 47701 | Tinwald East | TF59 Carters Terrace_11 | 2024-12-09 08:37 | 2024-12-09 08:43 | 0.20619 | 0.034365 | 734 | 4404 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 501 | 47709 | Hakatere Station, Ashburton Gorge | SX03 Ashburton Gorge_22 | 2024-12-09 13:55 | 2024-12-09 19:38 | 0.76839 | 0.0039328 | 84 | 16412 | Unplanned | Trees |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 502 | 47710 | Buccleugh feeder. | ST07 Buccleugh_22 | 2024-12-09 22:07 | 2024-12-10 01:59 | 0.85575 | 0.0068823 | 147 | 18278 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 503 | 47712 | Copley Rd | PT07 Pendarves North_22 | 2024-12-10 06:26 | 2024-12-10 07:20 | 0.020226 | 0.00037455 | 8 | 432 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 504 | 47713 | Withells Rd | NV05 Carew_22 | 2024-12-10 07:12 | 2024-12-10 09:11 | 0.30203 | 0.0027623 | 59 | 6451 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 505 | 47723 | Boltons Rd | NT07 Stoneylea Rd_22 | 2024-12-11 10:13 | 2024-12-11 11:37 | 0.019664 | 0.00023409 | 5 | 420 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 506 | 47724 | Mainwarings Rd | RZ01 Dorie West_22 | 2024-12-12 14:12 | 2024-12-12 14:42 | 0.2163 | 0.0072101 | 154 | 4620 | Unplanned | Foreign Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 507 | 47725 | Mainwarings Rd | RZ01 Dorie West_22 | 2024-12-12 15:14 | 2024-12-12 15:42 | 0.20188 | 0.0072101 | 154 | 4312 | Unplanned | Foreign Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 508 | 47727 | Rangitata Gorge | BI20 Montalto_11 | 2024-12-12 16:50 | 2024-12-12 19:39 | 0.27693 | 0.0016387 | 35 | 5915 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 509 | 47736 | Ruapuna School Rd 291. | NT07 Stoneylea Rd_22 | 2024-12-14 12:07 | 2024-12-14 14:14 | 0.02973 | 0.00023409 | 5 | 635 | Unplanned | Trees |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 510 | 47744 | Windermere Rd. | YV05 Longbeach_22 | 2024-12-15 17:53 | 2024-12-15 21:55 | 0.16209 | 0.00098319 | 21 | 3462 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 511 | 47745 | Mitcham & Winchmore Dromore Rds. | FH19 Mitcham Rd_22 | 2024-12-15 21:43 | 2024-12-15 23:05 | 0.080715 | 0.0019196 | 41 | 1724 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 512 | 47753 | Fairfield Rd, Stanley Rd feeder. | QV08 Stanley Rd_22 | 2024-12-16 15:53 | 2024-12-16 18:36 | 0.25446 | 0.0044946 | 96 | 5435 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 513 | 47756 | Fairfield Rd. | QV08 Stanley Rd_22 | 2024-12-17 05:57 | 2024-12-17 07:58 | 0.085116 | 0.00079592 | 17 | 1818 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 514 | 47757 | Lower Beach & Grahams Rds, Longbeach feeder. | YV05 Longbeach_22 | 2024-12-17 07:47 | 2024-12-17 12:28 | 0.84597 | 0.010206 | 218 | 18069 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 515 | 47770 | Braemar Lauriston Rd. | UW04 Braemar_22 | 2024-12-18 09:21 | 2024-12-18 11:13 | 0.010487 | 9.3637e-05 | 2 | 224 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 516 | 47782 | 411 Kyle rd | OU06 Overdale South_22 | 2024-12-22 09:39 | 2024-12-22 12:07 | 0.031509 | 0.00037455 | 8 | 673 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 517 | 47785 | Double Hill Run rd | AE96 Upper Rakaia_11 | 2024-12-23 05:26 | 2024-12-23 08:01 | 0.1016 | 0.00065546 | 14 | 2170 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 518 | 47795 | 306 Mill rd | GY02 Ferrimans Rd_22 | 2024-12-27 15:55 | 2024-12-27 16:43 | 0.017978 | 0.00037455 | 8 | 384 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 519 | 47798 | Racecourse Rd. | ZN13 Allenton_11 | 2024-12-22 17:26 | 2024-12-22 17:28 | 0.0079592 | 0.0039796 | 85 | 170 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 520 | 47800 | Ealing/Giddings rd | NX03 Ealing_22 | 2024-12-31 08:02 | 2024-12-31 09:52 | 0.36809 | 0.0068355 | 146 | 7862 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 521 | 47802 | Ealing/Giddings rd | NX03 Ealing_22 | 2024-12-31 09:11 | 2024-12-31 09:12 | 0.0048223 | 0.0048223 | 103 | 103 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 522 | 47806 | 1235 Arundel Rakaia Gorge rd | NT07 Stoneylea Rd_22 | 2024-12-31 08:37 | 2024-12-31 13:43 | 0.04298 | 0.00014046 | 3 | 918 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 523 | 47807 | Chertsey Rd. | OY02 Chertsey_22 | 2025-01-02 09:05 | 2025-01-02 10:07 | 0.049347 | 0.00079592 | 17 | 1054 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 524 | 47816 | Scarness Rd, Mt Hutt 11kV Feeder. | VU06 Mt Hutt_11 | 2025-01-05 16:00 | 2025-01-05 17:20 | 0.34276 | 0.0079592 | 170 | 7321 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 525 | 47817 | Giddings Rd. | NX03 Ealing_22 | 2025-01-05 17:15 | 2025-01-05 19:20 | 0.064376 | 0.00051501 | 11 | 1375 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 526 | 47820 | Trevors & Withells Rds. | NV05 Carew_22 | 2025-01-06 05:40 | 2025-01-06 07:23 | 0.20614 | 0.0027623 | 59 | 4403 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 527 | 47827 | Blackford Rd West feeder | MT07 Blackford Rd West_11 | 2025-01-08 00:33 | 2025-01-08 04:54 | 0.23217 | 0.00088955 | 19 | 4959 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 528 | 47828 | Mt Hutt Station Rd, Blackford Rd East feeder. | MU06 Blackford Rd East_11 | 2025-01-08 00:55 | 2025-01-08 05:35 | 1.1656 | 0.0049628 | 106 | 24897 | Unplanned | Foreign Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 529 | 47829 | Mt Hutt 11kV feeder | VU06 Mt Hutt_11 | 2025-01-08 02:53 | 2025-01-08 02:59 | 0.047755 | 0.0079592 | 170 | 1020 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 530 | 47830 | Mt Hutt Station Rd, Blackford Rd East feeder. | MU06 Blackford Rd East_11 | 2025-01-08 05:05 | 2025-01-08 07:17 | 0.089658 | 0.0038391 | 82 | 1915 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 531 | 47831 | Braemar Lauriston Rd | UW04 Braemar_22 | 2025-01-09 08:42 | 2025-01-09 09:46 | 0.0059928 | 9.3637e-05 | 2 | 128 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 532 | 47839 | Ashton area | YW04 Flemington_22 | 2025-01-12 01:13 | 2025-01-12 06:34 | 0.32553 | 0.0010768 | 23 | 6953 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 533 | 47843 | Wakanui School Rd, Hakatere feeder. | WY02 Hakatere_22 | 2025-01-13 01:18 | 2025-01-13 05:44 | 0.96634 | 0.011611 | 248 | 20640 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 534 | 47848 | Forks Rd | SW04 Staveley_22 | 2025-01-14 05:35 | 2025-01-14 07:21 | 0.34824 | 0.0044478 | 95 | 7438 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 535 | 47858 | McDougalls Rd | NY02 Fountaines Rd_22 | 2025-01-15 13:14 | 2025-01-15 14:37 | 0.18653 | 0.0022473 | 48 | 3984 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 536 | 47871 | Jones Rd, Carew feeder. | NV05 Carew_22 | 2025-01-18 14:16 | 2025-01-18 17:42 | 1.1863 | 0.013531 | 289 | 25338 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 537 | 47881 | Coldstream Rd. | JY02 Hinds South_22 | 2025-01-22 05:00 | 2025-01-22 06:23 | 0.11269 | 0.0013577 | 29 | 2407 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 538 | 47890 | 381 Westerfield Lismore Rd | GX03 Frasers Rd West_22 | 2025-01-23 05:17 | 2025-01-23 05:52 | 0.021302 | 0.00060864 | 13 | 455 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 539 | 47891 | Windermere Rd | YV05 Longbeach_22 | 2025-01-23 09:15 | 2025-01-23 11:00 | 0.014748 | 0.00014046 | 3 | 315 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 540 | 47896 | Mainwarings Rd. | RY02 Rakaia Huts_22 | 2025-01-24 09:06 | 2025-01-24 15:34 | 0.43598 | 0.0011236 | 24 | 9312 | Unplanned | Human Element |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 541 | 47901 | Tinwald East | TF59 Carters Terrace_11 | 2025-01-26 00:16 | 2025-01-26 01:36 | 3.0264 | 0.037829 | 808 | 64640 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 542 | 47902 | Barford Rd. | GW04 Winslow_22 | 2025-01-26 08:05 | 2025-01-26 09:16 | 0.0033241 | 4.6819e-05 | 1 | 71 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 543 | 47904 | Hinds Arundel Rd, Coldstream - Carew 66kV Circuit. | NY02 Fountaines Rd_22 | 2025-01-26 16:47 | 2025-01-26 17:27 | 0.043073 | 0.0010768 | 23 | 920 | Unplanned | Trees |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 544 | 47908 | Withells, Trevors rd area. | NV05 Carew_22 | 2025-01-28 08:41 | 2025-01-28 10:57 | 0.33794 | 0.0027623 | 59 | 7218 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 545 | 47915 | Ashburton Staveley Rd. | SW04 Staveley_22 | 2025-01-28 11:27 | 2025-01-28 12:00 | 0.17613 | 0.0053373 | 114 | 3762 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 546 | 47932 | Winchmore Dromore & Mitcham Rds. | FH19 Mitcham Rd_22 | 2025-01-31 21:55 | 2025-01-31 23:03 | 0.13053 | 0.0019196 | 41 | 2788 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 547 | 47937 | Arundle Rakaia Gorge Rd | SW04 Staveley_22 | 2025-02-03 15:38 | 2025-02-03 16:11 | 0.0092701 | 0.00028091 | 6 | 198 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 548 | 47939 | Rakaia | OW04 Rakaia_22 | 2025-02-03 23:54 | 2025-02-04 01:26 | 0.84746 | 0.031743 | 678 | 18101 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 549 | 47949 | Somerton Rd. | OX03 Hatfield_22 | 2025-02-04 14:23 | 2025-02-04 15:18 | 0.0088955 | 0.00018727 | 4 | 190 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 550 | 47954 | Hakatere Heron & Ashburton Gorge Rds. | SX03 Ashburton Gorge_22 | 2025-02-05 19:51 | 2025-02-06 00:07 | 0.36121 | 0.0039328 | 84 | 7715 | Unplanned | Foreign Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 551 | 47955 | Windermere Rd. | YV05 Longbeach_22 | 2025-02-06 06:33 | 2025-02-06 08:28 | 0.016152 | 0.00014046 | 3 | 345 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 552 | 47956 | Trevors & Withells Rds. | NV05 Carew_22 | 2025-02-06 21:24 | 2025-02-06 23:38 | 0.29589 | 0.0027623 | 59 | 6320 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 553 | 47961 | Blackford Rd East feeder. | MU06 Blackford Rd East_11 | 2025-02-09 23:38 | 2025-02-10 02:48 | 0.94293 | 0.0049628 | 106 | 20140 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 554 | 47994 | Old Main South Rd. | JY02 Hinds South_22 | 2025-02-16 16:18 | 2025-02-16 17:08 | 0.046819 | 0.00093637 | 20 | 1000 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 555 | 47998 | Vaughans Rd. | VY02 Line Rd_22 | 2025-02-17 08:02 | 2025-02-17 12:31 | 0.062971 | 0.00023409 | 5 | 1345 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 556 | 47999 | Wallaces Rd | KY02 Punawai_22 | 2025-02-18 14:13 | 2025-02-18 15:05 | 0.021911 | 0.00042137 | 9 | 468 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 557 | 48009 | Rakaia Hwy 1052 | OY02 Chertsey_22 | 2025-02-19 16:45 | 2025-02-19 19:27 | 0.083431 | 0.00051501 | 11 | 1782 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 558 | 48010 | Tindalls & Westerfield School Rds. | GX03 Frasers Rd West_22 | 2025-02-19 20:28 | 2025-02-19 22:27 | 0.195 | 0.0016387 | 35 | 4165 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 559 | 48016 | Montgomerys Rd | YY02 Willowby_22 | 2025-02-20 16:14 | 2025-02-20 18:26 | 0.0309 | 0.00023409 | 5 | 660 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 560 | 48022 | Cracroft Maronan Rd. | NT07 Stoneylea Rd_22 | 2025-02-21 05:50 | 2025-02-21 06:55 | 0.027389 | 0.00042137 | 9 | 585 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 561 | 48024 | Robertsons Rd. | UW04 Braemar_22 | 2025-02-21 21:41 | 2025-02-21 22:34 | 0.034739 | 0.00065546 | 14 | 742 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 562 | 48037 | Robertsons Rd. | UW04 Braemar_22 | 2025-02-24 21:22 | 2025-02-24 22:20 | 0.038017 | 0.00065546 | 14 | 812 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 563 | 48039 | Boltons Rd, Carew feeder. | NV05 Carew_22 | 2025-02-25 09:11 | 2025-02-25 12:03 | 1.4689 | 0.013531 | 289 | 31374 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 564 | 48043 | Windermere Rd. | JV05 Poplar Rd_22 | 2025-02-26 10:10 | 2025-02-26 11:15 | 0.0091296 | 0.00014046 | 3 | 195 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 565 | 48053 | Ashburton Gorge feeder. | SX03 Ashburton Gorge_22 | 2025-02-28 23:31 | 2025-03-01 01:22 | 0.58949 | 0.0054778 | 117 | 12591 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 566 | 48057 | McConnells Rd North. | JY02 Hinds South_22 | 2025-03-02 01:03 | 2025-03-02 02:06 | 0.21532 | 0.0034178 | 73 | 4599 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 567 | 48058 | Wallaces Rd. | KY02 Punawai_22 | 2025-03-02 15:42 | 2025-03-02 16:41 | 0.024861 | 0.00042137 | 9 | 531 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 568 | 48065 | 418 Pyes Rd | JV05 Poplar Rd_22 | 2025-03-03 20:31 | 2025-03-03 23:25 | 0.14664 | 0.00084274 | 18 | 3132 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 569 | 48067 | Trevors Rd. | NV05 Carew_22 | 2025-03-04 12:07 | 2025-03-04 12:52 | 0.058992 | 0.0013109 | 28 | 1260 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 570 | 48069 | Stanley Rd, FTN-LSN 66kV Circuit. | PT07 Pendarves North_22 | 2025-03-04 23:30 | 2025-03-04 23:44 | 0.015076 | 0.0010768 | 23 | 322 | Unplanned | Trees |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 571 | 48071 | Hinds River Rd | YV05 Longbeach_22 | 2025-03-05 09:03 | 2025-03-05 10:45 | 0.24355 | 0.0023878 | 51 | 5202 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 572 | 48073 | Wightmans Rd | MT07 Blackford Rd West_11 | 2025-03-05 10:52 | 2025-03-05 17:12 | 0.072803 | 0.00088955 | 19 | 1555 | Unplanned | Foreign Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 573 | 48073 | Wightmans Rd | MU06 Blackford Rd East_11 | 2025-03-05 10:52 | 2025-03-05 17:12 | 0.40601 | 0.0049628 | 106 | 8672 | Unplanned | Foreign Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 574 | 48091 | Windermere Rd | YV05 Longbeach_22 | 2025-03-12 16:43 | 2025-03-12 20:34 | 0.52203 | 0.010206 | 218 | 11150 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 575 | 48101 | Mill Rd | GY02 Ferrimans Rd_22 | 2025-03-15 17:00 | 2025-03-15 17:56 | 0.055059 | 0.00098319 | 21 | 1176 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 576 | 48102 | Jaines Rd | NV05 Carew_22 | 2025-03-16 06:00 | 2025-03-16 07:18 | 0.043822 | 0.00056182 | 12 | 936 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 577 | 48117 | Dobsons Ferry Rd, Rakaia Huts feeder. | RY02 Rakaia Huts_22 | 2025-03-18 09:39 | 2025-03-18 10:13 | 0.26865 | 0.0090828 | 194 | 5738 | Unplanned | Trees |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 578 | 48120 | Farquhars Rd, Mitcham feeder. | UY02 Barrhill_22 | 2025-03-18 17:40 | 2025-03-18 21:41 | 0.53355 | 0.0075378 | 161 | 11396 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 579 | 48127 | Upper Rakaia Gorge. | AE96 Upper Rakaia_11 | 2025-03-21 00:43 | 2025-03-21 07:47 | 0.27792 | 0.00065546 | 14 | 5936 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 580 | 48133 | Wheatstone Rd, Flemington feeder. JE25030125 & 0126 | YW04 Flemington_22 | 2025-03-23 02:22 | 2025-03-23 11:36 | 1.9381 | 0.020038 | 428 | 41396 | Unplanned | Foreign Interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 581 | 48159 | Winchmore Dromore Rd | FN13 Rakaia Hwy_22 | 2025-03-28 02:27 | 2025-03-28 03:37 | 0.055714 | 0.00079592 | 17 | 1190 | Unplanned | Trees |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
EA Networks | 2025 |  | 582 | 48166 | 97 Beggs Rd | WV04 Seaview_22 | 2025-03-30 11:44 | 2025-03-30 12:16 | 0.0059928 | 0.00018727 | 4 | 128 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 9 | 2024-05-20-0286 | Paekakariki - 96 Tilley Rd | Z165 | 2024-05-01 08:05 | 2024-05-01 15:24 | 0.76724 | 0.0017477 | 82 | 35998 | Planned | Planned interruption | Ames St Paekakariki - 11KV Reconductoring and pole changes Stage 1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 10 | 2024-07-01-0017 | Otaki - 15 Riverbank Rd | L350 | 2024-07-01 09:00 | 2024-07-01 14:26 | 0.097274 | 0.00029839 | 14 | 4564 | Planned | Planned interruption | Atkinson Ave Otaki Beach 400V Reconductoring Stage 1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 11 | 2024-07-01-0016 | Levin West - 270 Kawiu Rd | E156 | 2024-07-01 14:17 | 2024-07-01 15:58 | 0.002174 | 2.1313e-05 | 1 | 102 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 12 | 2024-07-01-0026 | Paraparaumu West - 11 Arko Pl | 402 | 2024-07-01 23:24 | 2024-07-02 02:55 | 2.7021 | 0.012767 | 599 | 126778 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 13 | 2024-08-01-0006 | Otaki - 15 Riverbank Rd | L348 | 2024-08-01 08:41 | 2024-08-01 16:08 | 0.038108 | 8.5253e-05 | 4 | 1788 | Planned | Planned interruption | Miro St, Otaki - Pole & arm replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 14 | 2024-09-01-0001 | Levin West - 270 Kawiu Rd | E153 | 2024-09-01 00:46 | 2024-09-01 01:00 | 0.2174 | 0.014941 | 701 | 10200 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 15 | 2024-09-02-0039 | Waikanae - 18 Parata St | 652 | 2024-09-01 13:20 | 2024-09-01 15:40 | 0.14323 | 0.001023 | 48 | 6720 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 16 | 2024-09-03-0071 | Levin West - 270 Kawiu Rd | E148 | 2024-09-01 01:54 | 2024-09-01 06:34 | 0.041774 | 0.00014919 | 7 | 1960 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 17 | 2024-09-03-0072 | Levin West - 270 Kawiu Rd | E148 | 2024-09-01 03:53 | 2024-09-01 05:45 | 0.050044 | 0.00049021 | 23 | 2348 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 18 | 2024-09-04-0080 | Levin West - 270 Kawiu Rd | E148 | 2024-09-01 04:16 | 2024-09-01 06:05 | 0.0023232 | 2.1313e-05 | 1 | 109 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 19 | 2024-09-04-0082 | Levin West - 270 Kawiu Rd | E150 | 2024-09-01 07:07 | 2024-09-01 10:35 | 0.0044332 | 2.1313e-05 | 1 | 208 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 20 | 2024-09-04-0084 | Levin West - 270 Kawiu Rd | E150 | 2024-09-01 07:49 | 2024-09-01 10:35 | 0.20167 | 0.0012149 | 57 | 9462 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 21 | 2024-09-04-0085 | Waikanae - 18 Parata St | 652 | 2024-09-01 13:20 | 2024-09-01 15:40 | 0.14024 | 0.0010017 | 47 | 6580 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 22 | 2024-10-01-0005 | Raumati - 133 Matai Rd | Z212 | 2024-10-01 08:55 | 2024-10-01 15:33 | 0.050896 | 0.00012788 | 6 | 2388 | Planned | Planned interruption | Cnr Poplar Ave & Matai Rd - Replace 11Kv Pole 23610N & Replace ABS Z31 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 23 | 2024-10-01-0008 | Foxton - 13 Union St | C2 | 2024-10-01 10:10 | 2024-10-01 13:35 | 0.026215 | 0.00012788 | 6 | 1230 | Planned | Planned interruption | 250 Hickford Rd, Foxton - Install lightning arrestors at Tx B249 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 24 | 2024-11-19-0240 | Foxton - 13 Union St | C1 | 2024-11-01 17:09 | 2024-11-01 20:32 | 0.0043266 | 2.1313e-05 | 1 | 203 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 25 | 2025-01-02-0013 | Otaki - 15 Riverbank Rd | L348 | 2025-01-02 13:20 | 2025-01-02 18:08 | 0.0061382 | 2.1313e-05 | 1 | 288 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 26 | 2025-02-02-0005 | Paraparaumu East - 42 Tongariro St | V311 | 2025-02-02 15:49 | 2025-02-02 16:30 | 0.0017477 | 4.2627e-05 | 2 | 82 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 27 | 2024-05-02-0038 | Levin West - 270 Kawiu Rd | E148 | 2024-05-02 09:37 | 2024-05-02 14:44 | 0.15704 | 0.00051152 | 24 | 7368 | Planned | Planned interruption | Commenced Schedule for team to install new 11kV prop pole in Sorensons Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 28 | 2024-05-02-0029 | Otaki - 15 Riverbank Rd | L352 | 2024-05-02 08:44 | 2024-05-02 09:24 | 0.0025576 | 6.394e-05 | 3 | 120 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 29 | 2024-05-02-0047 | Shannon - 22 Stafford St | 119 | 2024-05-02 15:27 | 2024-05-02 18:00 | 0.0032609 | 2.1313e-05 | 1 | 153 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 30 | 2024-07-02-0032 | Otaki - 15 Riverbank Rd | L350 | 2024-07-02 09:22 | 2024-07-02 13:45 | 0.078476 | 0.00029839 | 14 | 3682 | Planned | Planned interruption | Atkinson Ave - 400V reconducting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 31 | 2024-09-02-0047 | Otaki - 15 Riverbank Rd | L350 | 2024-09-02 13:38 | 2024-09-02 14:57 | 0.021974 | 0.00027707 | 13 | 1031 | Planned | Planned interruption | 130 Rangiuru Rd, Otaki - Replace 11Kv xarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 32 | 2024-09-02-0032 | Paraparaumu East - 42 Tongariro St | V318 | 2024-09-02 07:34 | 2024-09-02 08:39 | 0.0013854 | 2.1313e-05 | 1 | 65 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 33 | 2024-10-02-0015 | Levin West - 270 Kawiu Rd | E153 | 2024-10-02 09:03 | 2024-10-02 13:30 | 0.23901 | 0.00089516 | 42 | 11214 | Planned | Planned interruption | Replace ABS H298 & 11Kv Pole 33923Y | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 34 | 2025-02-03-0012 | Otaki - 15 Riverbank Rd | L348 | 2025-02-03 09:25 | 2025-02-03 15:44 | 0.12924 | 0.00034101 | 16 | 6064 | Planned | Planned interruption | Convent Rd otaki Replace TX structure M27 and 400V reconductoring Stage 1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 35 | 2025-02-03-0009 | Shannon - 22 Stafford St | 119 | 2025-02-03 06:16 | 2025-02-03 08:00 | 0.0088663 | 8.5253e-05 | 4 | 416 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 36 | 2025-03-13-0136 | Raumati - 133 Matai Rd | Z210 | 2025-03-03 08:11 | 2025-03-03 17:30 | 0.55997 | 0.0010017 | 47 | 26273 | Planned | Planned interruption | Raumati Rd 400V reconductoring and HV pole changes Stage 1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 37 | 2024-04-03-0025 | Waikanae - 18 Parata St | 652 | 2024-04-03 14:14 | 2024-04-03 15:15 | 0.0039217 | 6.394e-05 | 3 | 184 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 38 | 2024-04-03-0030 | Shannon - 22 Stafford St | 129 | 2024-04-03 05:36 | 2024-04-03 09:00 | 0.052175 | 0.00025576 | 12 | 2448 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 39 | 2024-05-03-0052 | Paraparaumu East - 42 Tongariro St | V311 | 2024-05-03 08:00 | 2024-05-03 15:00 | 0.46548 | 0.0011083 | 52 | 21840 | Planned | Planned interruption | 11kV pole and X-arm changes in Makora Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 40 | 2024-05-03-0057 | Levin East - 69 Tararua Rd | G309 | 2024-05-03 10:07 | 2024-05-03 12:54 | 0.021356 | 0.00012788 | 6 | 1002 | Planned | Planned interruption | Commenced Schedule for team to upgrade LV bushing on TX D42 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 41 | 2024-06-04-0037 | Shannon - 22 Stafford St | 149 | 2024-06-03 06:51 | 2024-06-03 09:00 | 0.0054988 | 4.2627e-05 | 2 | 258 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 42 | 2024-07-03-0051 | Otaki - 15 Riverbank Rd | L351 | 2024-07-03 08:32 | 2024-07-03 18:09 | 0.39353 | 0.00068203 | 32 | 18464 | Planned | Planned interruption | 106 Waerenga Rd - Replace 11KV ABS with new ENTEC Setup | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 43 | 2024-07-03-0054 | Levin West - 270 Kawiu Rd | E151 | 2024-07-03 09:12 | 2024-07-03 15:19 | 0.57883 | 0.0015772 | 74 | 27158 | Planned | Planned interruption | Kings Dr - Replace TX E265, change arm & replace solid links E266 with DDO's | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 44 | 2024-09-03-0059 | Levin West - 270 Kawiu Rd | E153 | 2024-09-03 09:01 | 2024-09-03 13:20 | 0.0055202 | 2.1313e-05 | 1 | 259 | Planned | Planned interruption | CD Farm Rd - 400V Reconducting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 45 | 2024-10-03-0033 | Foxton - 13 Union St | C4 | 2024-10-03 03:42 | 2024-10-03 08:17 | 0.98555 | 0.028794 | 1351 | 46241 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 46 | 2024-10-03-0045 | Paekakariki - 96 Tilley Rd | Z167 | 2024-10-03 20:30 | 2024-10-03 21:34 | 0.008163 | 0.00012788 | 6 | 383 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 47 | 2024-11-03-0028 | Otaki - 15 Riverbank Rd | L349 | 2024-11-03 04:39 | 2024-11-03 08:09 | 0.031331 | 0.00014919 | 7 | 1470 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 48 | 2024-12-03-0020 | Paekakariki - 96 Tilley Rd | Z165 | 2024-12-03 08:10 | 2024-12-03 14:23 | 0.59624 | 0.0015985 | 75 | 27975 | Planned | Planned interruption | Wellington Rd - 11Kv pole change & reconducting (Stage 3) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 49 | 2025-02-04-0028 | Foxton - 13 Union St | C4 | 2025-02-04 01:36 | 2025-02-04 05:15 | 0.5268 | 0.0024084 | 113 | 24717 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 50 | 2025-03-04-0027 | Shannon - 22 Stafford St | 139 | 2025-03-04 10:00 | 2025-03-04 14:45 | 0.25512 | 0.00089516 | 42 | 11970 | Planned | Planned interruption | Manhahao Road, Shannon - Rework @ various sites | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 51 | 2024-04-04-0036 | Paraparaumu East - 42 Tongariro St | V311 | 2024-04-04 08:14 | 2024-04-04 13:53 | 0.028901 | 8.5253e-05 | 4 | 1356 | Planned | Planned interruption | 11KV reconducting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 52 | 2024-04-04-0048 | Shannon - 22 Stafford St | 119 | 2024-04-04 18:18 | 2024-04-04 21:35 | 0.20491 | 0.0010444 | 49 | 9614 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 53 | 2024-05-04-0076 | Paraparaumu East - 42 Tongariro St | V317 | 2024-05-04 07:32 | 2024-05-04 13:45 | 0.063599 | 0.00017051 | 8 | 2984 | Planned | Planned interruption | Replace Tx W701 due to an oil leak & install new switchgear | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 54 | 2024-05-04-0074 | Foxton - 13 Union St | C4 | 2024-05-04 03:19 | 2024-05-04 06:58 | 0.37038 | 0.0056907 | 267 | 17378 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 55 | 2024-07-04-0089 | Levin East - 69 Tararua Rd | G310 | 2024-07-04 09:06 | 2024-07-04 09:15 | 0.24399 | 0.028539 | 1339 | 11448 | Unplanned | Human error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 56 | 2024-09-04-0081 | Shannon - 22 Stafford St | 149 | 2024-09-04 10:12 | 2024-09-04 12:15 | 0.0078646 | 6.394e-05 | 3 | 369 | Planned | Planned interruption | 654 Opiki Rd - Install lightning arrestors at Tx B271 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 57 | 2024-09-04-0083 | Foxton - 13 Union St | C1 | 2024-09-04 10:09 | 2024-09-04 12:58 | 0.010806 | 6.394e-05 | 3 | 507 | Planned | Planned interruption | 1563 Levin Rd, Foxton - Install lightning arrestors at Tx C171 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 58 | 2024-09-04-0077 | Waikanae - 18 Parata St | 652 | 2024-09-04 07:31 | 2024-09-04 09:14 | 0.0043692 | 4.2627e-05 | 2 | 205 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 59 | 2024-09-04-0079 | Waikanae - 18 Parata St | 652 | 2024-09-04 09:39 | 2024-09-04 10:07 | 0.00059677 | 2.1313e-05 | 1 | 28 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 60 | 2024-10-04-0048 | Otaki - 15 Riverbank Rd | L351 | 2024-10-04 08:09 | 2024-10-04 15:46 | 0.69362 | 0.0017903 | 84 | 32544 | Planned | Planned interruption | Rahui Rd - Replace 11Kv xarms & DDO's at multiple sites | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 61 | 2024-11-04-0042 | Levin West - 270 Kawiu Rd | E148 | 2024-11-04 08:56 | 2024-11-04 14:18 | 0.2402 | 0.00074597 | 35 | 11270 | Planned | Planned interruption | Te Whanga Rd - Replace 11Kv Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 62 | 2024-11-04-0037 | Otaki - 15 Riverbank Rd | L352 | 2024-11-04 02:46 | 2024-11-04 05:45 | 0.098212 | 0.00068203 | 32 | 4608 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 63 | 2024-12-04-0025 | Waikanae - 18 Parata St | 662 | 2024-12-04 08:40 | 2024-12-04 15:55 | 0.055628 | 0.00012788 | 6 | 2610 | Planned | Planned interruption | 11kV Pole replacement and new transformer installation - 14 Ngarara Road Waikanae | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 64 | 2025-02-05-0052 | Otaki - 15 Riverbank Rd | L352 | 2025-02-05 12:27 | 2025-02-05 12:36 | 0.025064 | 0.0029199 | 137 | 1176 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 65 | 2025-03-05-0037 | Otaki - 15 Riverbank Rd | L349 | 2025-03-05 02:36 | 2025-03-05 03:54 | 0.79465 | 0.013236 | 621 | 37284 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 66 | 2024-06-05-0046 | Waikanae - 18 Parata St | 652 | 2024-06-05 08:02 | 2024-06-05 16:10 | 2.0282 | 0.0041561 | 195 | 95160 | Planned | Planned interruption | Reikorangi Rd, Waikanae - Replace CB200 & ABS S195, install new 11Kv pole & drop 11Kv lines for tree removal | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 67 | 2024-07-05-0113 | Paraparaumu East - 42 Tongariro St | V311 | 2024-07-05 09:43 | 2024-07-05 11:07 | 0.005371 | 6.394e-05 | 3 | 252 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 68 | 2024-07-05-0129 | Shannon - 22 Stafford St | 129 | 2024-07-05 19:56 | 2024-07-05 21:51 | 0.002451 | 2.1313e-05 | 1 | 115 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 69 | 2024-09-05-0099 | Shannon - 22 Stafford St | 119 | 2024-09-05 10:00 | 2024-09-05 12:06 | 0.0080564 | 6.394e-05 | 3 | 378 | Planned | Planned interruption | 278 Okuku Rd, Opiki - Install lightning arrestors @ Tx B192 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 70 | 2024-09-05-0100 | Foxton - 13 Union St | C2 | 2024-09-05 10:10 | 2024-09-05 12:50 | 0.020461 | 0.00012788 | 6 | 960 | Planned | Planned interruption | 125 Cummerfield Rd - Install lightning arrestors at Tx B58 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 71 | 2024-09-05-0102 | Shannon - 22 Stafford St | 149 | 2024-09-05 10:49 | 2024-09-05 13:10 | 0.015026 | 0.00010657 | 5 | 705 | Planned | Planned interruption | 177 Tane Rd, Opiki - Install lightning arrestors at Tx B308 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 72 | 2024-09-05-0119 | Levin West - 270 Kawiu Rd | E156 | 2024-09-05 18:12 | 2024-09-06 00:19 | 0.046932 | 0.00012788 | 6 | 2202 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 73 | 2024-10-05-0062 | Foxton - 13 Union St | C1 | 2024-10-05 04:57 | 2024-10-05 06:09 | 0.0030691 | 4.2627e-05 | 2 | 144 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 74 | 2024-12-05-0037 | Shannon - 22 Stafford St | 119 | 2024-12-05 08:30 | 2024-12-05 14:24 | 0.2188 | 0.00061809 | 29 | 10266 | Planned | Planned interruption | Albert Rd Tokomaru - 11KV Arm changes and 11KV recondctoring Stage 3 & 4 Switching 92144 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 75 | 2024-12-05-0038 | Paraparaumu West - 11 Arko Pl | 402 | 2024-12-05 08:38 | 2024-12-05 16:01 | 0.56651 | 0.0012788 | 60 | 26580 | Planned | Planned interruption | 62 Woodleigh Gr Pram Upgrade TX W294 from a 100KVA to 200KVA & HV fuses to 20Amp | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 76 | 2024-12-05-0040 | Paraparaumu East - 42 Tongariro St | V313 | 2024-12-05 10:09 | 2024-12-05 11:46 | 0.0041348 | 4.2627e-05 | 2 | 194 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 77 | 2025-03-06-0055 | Levin East - 69 Tararua Rd | G309 | 2025-03-06 08:03 | 2025-03-06 16:44 | 0.088855 | 0.00017051 | 8 | 4169 | Planned | Planned interruption | Intersection Arapaepae Rd & Tararua Rd's - Replace 2 x 33Kv Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 78 | 2025-03-06-0057 | Paraparaumu East - 42 Tongariro St | V313 | 2025-03-06 09:03 | 2025-03-06 15:40 | 0.42324 | 0.0010657 | 50 | 19858 | Planned | Planned interruption | Valley Rd - Replace Bypass ABS Y14 & 11Kv links Y32 / Y33 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 79 | 2025-03-06-0054 | Otaki - 15 Riverbank Rd | L352 | 2025-03-06 08:00 | 2025-03-06 09:25 | 0.1395 | 0.0016411 | 77 | 6545 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 80 | 2025-03-06-0068 | Foxton - 13 Union St | C2 | 2025-03-06 21:37 | 2025-03-06 23:45 | 0.021846 | 0.00017051 | 8 | 1025 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 81 | 2024-04-06-0076 | Otaki - 15 Riverbank Rd | L349 | 2024-04-06 11:51 | 2024-04-06 13:45 | 0.0064153 | 8.5253e-05 | 4 | 301 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 82 | 2024-05-06-0095 | Levin East - 69 Tararua Rd | G313 | 2024-05-06 09:50 | 2024-05-06 12:14 | 0.015346 | 0.00010657 | 5 | 720 | Planned | Planned interruption | Ugrade pole mount Tx G106 from 30KVa to 50Kva | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 83 | 2024-05-06-0105 | Levin West - 270 Kawiu Rd | E148 | 2024-05-06 13:37 | 2024-05-06 17:20 | 0.0098041 | 6.394e-05 | 3 | 460 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 84 | 2024-06-06-0059 | Shannon - 22 Stafford St | 149 | 2024-06-06 10:19 | 2024-06-06 15:13 | 0.04382 | 0.00014919 | 7 | 2056 | Planned | Planned interruption | Opiki Rd - Replace 11Kv Poles & xarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 85 | 2024-07-06-0136 | Paraparaumu East - 42 Tongariro St | V311 | 2024-07-06 07:05 | 2024-07-06 07:51 | 0.0029412 | 6.394e-05 | 3 | 138 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 86 | 2024-08-06-0060 | Otaki - 15 Riverbank Rd | L352 | 2024-08-06 08:45 | 2024-08-06 10:18 | 0.0019821 | 4.2627e-05 | 2 | 93 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 87 | 2024-09-06-0129 | Foxton - 13 Union St | C2 | 2024-09-06 10:05 | 2024-09-06 12:45 | 0.017051 | 0.00010657 | 5 | 800 | Planned | Planned interruption | 50 Hickford Rd, Foxton - Install lightning arrestors at Tx B345 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 88 | 2024-09-06-0130 | Shannon - 22 Stafford St | 149 | 2024-09-06 10:15 | 2024-09-06 11:50 | 0.010124 | 0.00010657 | 5 | 475 | Planned | Planned interruption | 64 Ashlea Rd, Tokomaru - Install lightning arrestors at Tx B131 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 89 | 2024-09-06-0121 | Otaki - 15 Riverbank Rd | L349 | 2024-09-06 06:35 | 2024-09-06 07:46 | 0.060722 | 0.001087 | 51 | 2849 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 90 | 2024-10-06-0067 | Otaki - 15 Riverbank Rd | L349 | 2024-10-06 05:30 | 2024-10-06 08:09 | 0.081438 | 0.00051152 | 24 | 3821 | Unplanned | Adverse environment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 91 | 2025-02-07-0066 | Otaki - 15 Riverbank Rd | L349 | 2025-02-07 09:14 | 2025-02-07 15:56 | 0.017136 | 4.2627e-05 | 2 | 804 | Planned | Planned interruption | 296 Old main Rd North Otaki Replace 33KV Pole 25597Y and TX structure L385 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 92 | 2025-03-07-0072 | Waikanae - 18 Parata St | 652 | 2025-03-07 09:00 | 2025-03-07 11:42 | 0.16573 | 0.001023 | 48 | 7776 | Planned | Planned interruption | Terrace Rd Rikiorangi -Install new 11KV Pole across river | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 93 | 2024-06-07-0077 | Otaki - 15 Riverbank Rd | L351 | 2024-06-07 09:44 | 2024-06-07 11:00 | 0.0032183 | 4.2627e-05 | 2 | 151 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 94 | 2024-07-07-0152 | Otaki - 15 Riverbank Rd | L352 | 2024-07-07 09:30 | 2024-07-07 13:26 | 0.03521 | 0.00014919 | 7 | 1652 | Planned | Planned interruption | Switching 89546A - Otaki oxidation ponds Replace 11KV Cross arms Multiple sites | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 95 | 2024-09-07-0142 | Levin West - 270 Kawiu Rd | E153 | 2024-09-07 05:02 | 2024-09-07 06:58 | 0.86091 | 0.014919 | 700 | 40393 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 96 | 2024-11-20-0262 | Waikanae - 18 Parata St | 682 | 2024-11-07 20:48 | 2024-11-08 03:28 | 2.5376 | 0.020503 | 962 | 119062 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 97 | 2025-02-08-0073 | Otaki - 15 Riverbank Rd | L349 | 2025-02-08 06:47 | 2025-02-08 10:43 | 0.020141 | 8.5253e-05 | 4 | 945 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 98 | 2025-02-08-0082 | Levin East - 69 Tararua Rd | G308 | 2025-02-08 21:12 | 2025-02-08 23:29 | 0.011701 | 8.5253e-05 | 4 | 549 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 99 | 2024-05-08-0121 | Levin East - 69 Tararua Rd | G308 | 2024-05-08 07:59 | 2024-05-09 02:19 | 0.84066 | 0.0018543 | 87 | 39443 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 100 | 2024-06-08-0098 | Otaki - 15 Riverbank Rd | L349 | 2024-06-08 17:26 | 2024-06-08 18:47 | 0.023189 | 0.00036233 | 17 | 1088 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 101 | 2024-09-08-0156 | Levin West - 270 Kawiu Rd | E156 | 2024-09-08 11:25 | 2024-09-10 16:57 | 0.41073 | 0.00012788 | 6 | 19271 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 102 | 2024-10-09-0113 | Shannon - 22 Stafford St | 149 | 2024-10-08 09:07 | 2024-10-08 15:08 | 0.015388 | 4.2627e-05 | 2 | 722 | Planned | Planned interruption | Karaka St, Tokomaru - Replace ABS A146 & arm changes | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 103 | 2025-02-09-0084 | Foxton - 13 Union St | C3 | 2025-02-09 01:10 | 2025-02-09 06:50 | 1.6487 | 0.038876 | 1824 | 77355 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 104 | 2025-02-09-0091 | Shannon - 22 Stafford St | 149 | 2025-02-09 21:15 | 2025-02-09 22:35 | 0.0034101 | 4.2627e-05 | 2 | 160 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 105 | 2024-05-07-0117 | Levin East - 69 Tararua Rd | G311 | 2024-04-09 06:30 | 2024-04-10 13:07 | 0.039153 | 2.1313e-05 | 1 | 1837 | Planned | Planned interruption | Switching 87920A - Install 11KV Transformer H245 and Install new 11KV RMU | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 106 | 2024-05-09-0137 | Paekakariki - 96 Tilley Rd | Z165 | 2024-05-09 08:04 | 2024-05-09 15:46 | 0.6105 | 0.0013214 | 62 | 28644 | Planned | Planned interruption | Ames St - 11Kv Reconducting & Pole changes - Stage 2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 107 | 2024-05-09-0132 | Waikanae - 18 Parata St | 652 | 2024-05-09 02:21 | 2024-05-09 04:22 | 0.056928 | 0.00046889 | 22 | 2671 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 108 | 2024-06-11-0143 | Otaki - 15 Riverbank Rd | L351 | 2024-06-09 09:05 | 2024-06-09 12:25 | 0.36233 | 0.0018116 | 85 | 17000 | Planned | Planned interruption | River bank rd - Replace 11KV Cross arms at multiple Sites (Switching-88840A) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 109 | 2024-06-09-0109 | Shannon - 22 Stafford St | 149 | 2024-06-09 18:16 | 2024-06-09 19:58 | 0.0043479 | 4.2627e-05 | 2 | 204 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 110 | 2024-07-09-0182 | Paraparaumu East - 42 Tongariro St | V311 | 2024-07-09 07:50 | 2024-07-09 15:50 | 0.47895 | 0.0011296 | 53 | 22472 | Planned | Planned interruption | 19 Makorae Gr, Otihanger - Install new HV cable, upgrade W504 to 300KVA | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 111 | 2024-09-09-0166 | Levin East - 69 Tararua Rd | G308 | 2024-09-09 09:42 | 2024-09-09 14:42 | 0.03197 | 0.00010657 | 5 | 1500 | Planned | Planned interruption | 3 Kuku Beach Rd, Ohau - Upgrade conductor & upgrade Tx H78 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 112 | 2024-09-09-0162 | Levin East - 69 Tararua Rd | G308 | 2024-09-09 05:55 | 2024-09-09 07:00 | 0.0027707 | 4.2627e-05 | 2 | 130 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 113 | 2024-12-09-0080 | Shannon - 22 Stafford St | 119 | 2024-12-09 08:30 | 2024-12-09 15:30 | 0.2596 | 0.00061809 | 29 | 12180 | Planned | Planned interruption | Albert Rd - 11Kv arm/pole change & reconducting - Stage 5 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 114 | 2024-08-10-0116 | Otaki - 15 Riverbank Rd | L351 | 2024-08-10 20:53 | 2024-08-10 22:32 | 0.0063301 | 6.394e-05 | 3 | 297 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 115 | 2024-09-10-0187 | Otaki - 15 Riverbank Rd | L349 | 2024-09-10 10:20 | 2024-09-10 14:20 | 0.26088 | 0.001087 | 51 | 12240 | Planned | Planned interruption | Taylors Rd - Replace 11Kv Xarms & Do Fuses L466 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 116 | 2024-10-11-0138 | Paraparaumu East - 42 Tongariro St | V318 | 2024-10-10 19:39 | 2024-10-10 22:30 | 1.9187 | 0.035124 | 1648 | 90022 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 117 | 2025-02-11-0109 | Otaki - 15 Riverbank Rd | L352 | 2025-02-11 19:02 | 2025-02-11 20:03 | 0.0039003 | 6.394e-05 | 3 | 183 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 118 | 2024-04-16-0199 | Levin East - 69 Tararua Rd | G308 | 2024-04-11 08:33 | 2024-04-11 16:26 | 0.1613 | 0.00034101 | 16 | 7568 | Planned | Planned interruption | Upgrade 11KV Pole & Hardware. Remove old 11KV Cable & Terminate new 11KV Cable and install new ground mount switch gear | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 119 | 2024-07-11-0223 | Foxton - 13 Union St | C3 | 2024-07-11 10:10 | 2024-07-11 14:03 | 0.004966 | 2.1313e-05 | 1 | 233 | Planned | Planned interruption | Foxton Beach Rd - Replace Tx Structure at Tx C195 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 120 | 2024-07-11-0235 | Foxton - 13 Union St | C1 | 2024-07-11 10:00 | 2024-07-11 15:10 | 0.14536 | 0.00046889 | 22 | 6820 | Planned | Planned interruption | Hickford Rd - Replace ABS B50 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 121 | 2024-07-11-0228 | Foxton - 13 Union St | C1 | 2024-07-11 11:11 | 2024-07-11 11:29 | 0.00038364 | 2.1313e-05 | 1 | 18 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 122 | 2024-09-12-0223 | Shannon - 22 Stafford St | 149 | 2024-09-11 08:37 | 2024-09-11 16:30 | 0.060487 | 0.00012788 | 6 | 2838 | Planned | Planned interruption | Foxton Shannon Rd flood Gates. Replace 33KV Poles and relocate Entec B137 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 123 | 2024-09-11-0204 | Otaki - 15 Riverbank Rd | L352 | 2024-09-11 06:22 | 2024-09-11 07:29 | 0.001428 | 2.1313e-05 | 1 | 67 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 124 | 2024-09-11-0212 | Levin East - 69 Tararua Rd | G313 | 2024-09-11 13:39 | 2024-09-11 17:00 | 0.078689 | 0.00042627 | 20 | 3692 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 125 | 2024-10-22-0297 | Levin West - 270 Kawiu Rd | E153 | 2024-10-11 08:30 | 2024-10-11 13:53 | 0.020653 | 6.394e-05 | 3 | 969 | Planned | Planned interruption | Tiro Tiro Rd Levin Replace 11KV ABS H131 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 126 | 2024-12-11-0105 | Levin East - 69 Tararua Rd | G308 | 2024-12-11 09:00 | 2024-12-11 16:10 | 0.50406 | 0.0011722 | 55 | 23650 | Planned | Planned interruption | Muhunoa West Rd - 11KV Poles & cross arm changes Stage 1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 127 | 2024-12-11-0106 | Waikanae - 18 Parata St | 632 | 2024-12-11 08:02 | 2024-12-11 16:27 | 0.13992 | 0.00027707 | 13 | 6565 | Planned | Planned interruption | 32 Peka Peka Rd Replace ABS P382 install New Entec / Links and tree removel | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 128 | 2024-12-11-0109 | Otaki - 15 Riverbank Rd | L351 | 2024-12-11 13:32 | 2024-12-11 17:43 | 0.02142 | 8.5253e-05 | 4 | 1005 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 129 | 2025-03-12-0120 | Levin West - 270 Kawiu Rd | E153 | 2025-03-12 09:12 | 2025-03-12 15:42 | 0.24105 | 0.00061809 | 29 | 11310 | Planned | Planned interruption | Mako Mako & Hamaria Rd's - Replace 11Kv xarms at multiple sites | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 130 | 2025-03-12-0124 | Levin East - 69 Tararua Rd | G308 | 2025-03-12 12:12 | 2025-03-12 13:47 | 0.057546 | 0.00061809 | 29 | 2700 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 131 | 2024-04-16-0203 | Shannon - 22 Stafford St | 139 | 2024-04-12 14:36 | 2024-04-12 17:01 | 0.012362 | 8.5253e-05 | 4 | 580 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 132 | 2024-05-12-0187 | Foxton - 13 Union St | C1 | 2024-05-12 06:16 | 2024-05-12 07:28 | 0.038407 | 0.00053283 | 25 | 1802 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 133 | 2024-07-12-0247 | Shannon - 22 Stafford St | 119 | 2024-07-12 10:08 | 2024-07-12 13:58 | 0.014706 | 6.394e-05 | 3 | 690 | Planned | Planned interruption | Opiki Rd - Install lightning arrestors at Tx B265 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 134 | 2024-07-12-0248 | Foxton - 13 Union St | C1 | 2024-07-12 10:08 | 2024-07-12 11:28 | 0.0051152 | 6.394e-05 | 3 | 240 | Planned | Planned interruption | 342 Springs Rd, Foxton - Install lightning arrestors at Tx B241 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 135 | 2024-07-12-0256 | Foxton - 13 Union St | C1 | 2024-07-12 12:39 | 2024-07-12 13:30 | 0.0032609 | 6.394e-05 | 3 | 153 | Planned | Planned interruption | 278 Springs Rd, Foxton - Install lightning arrestors at Tx B240 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 136 | 2024-08-12-0129 | Otaki - 15 Riverbank Rd | L350 | 2024-08-12 00:06 | 2024-08-12 01:46 | 0.005371 | 8.5253e-05 | 4 | 252 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 137 | 2024-08-12-0147 | Otaki - 15 Riverbank Rd | L352 | 2024-08-12 17:26 | 2024-08-12 23:58 | 0.0083335 | 2.1313e-05 | 1 | 391 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 138 | 2024-08-12-0152 | Paraparaumu East - 42 Tongariro St | V311 | 2024-08-12 18:19 | 2024-08-12 22:47 | 0.017136 | 6.394e-05 | 3 | 804 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 139 | 2024-08-13-0168 | Otaki - 15 Riverbank Rd | L352 | 2024-08-12 17:56 | 2024-08-12 23:10 | 0.033462 | 0.00010657 | 5 | 1570 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 140 | 2024-11-12-0135 | Otaki - 15 Riverbank Rd | L348 | 2024-11-12 08:30 | 2024-11-12 15:37 | 0.27068 | 0.0006394 | 30 | 12700 | Planned | Planned interruption | 11KV Reconductoring and pole changes and tree trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 141 | 2024-11-12-0149 | Paraparaumu East - 42 Tongariro St | V311 | 2024-11-12 20:05 | 2024-11-12 21:02 | 0.21989 | 0.0038577 | 181 | 10317 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 142 | 2024-11-22-0281 | Paraparaumu East - 42 Tongariro St | V311 | 2024-11-12 17:44 | 2024-11-12 19:38 | 1.0801 | 0.014898 | 699 | 50678 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 143 | 2024-12-12-0122 | Waikanae - 18 Parata St | 652 | 2024-12-12 09:00 | 2024-12-12 14:45 | 0.35295 | 0.001023 | 48 | 16560 | Planned | Planned interruption | Terrace Rd, Reikoangi - Isolation for tree removal | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 144 | 2024-12-12-0127 | Levin West - 270 Kawiu Rd | E148 | 2024-12-12 14:09 | 2024-12-12 16:33 | 0.024532 | 0.00017051 | 8 | 1151 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 145 | 2024-12-12-0139 | Raumati - 133 Matai Rd | Z210 | 2024-12-12 19:25 | 2024-12-12 19:44 | 0.37573 | 0.019672 | 923 | 17629 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 146 | 2025-02-13-0122 | Shannon - 22 Stafford St | 119 | 2025-02-13 09:16 | 2025-02-13 14:50 | 0.085339 | 0.00025576 | 12 | 4004 | Planned | Planned interruption | Tane Rd, Opiki - Replace ABS B103 & lightning arrestors at Tx B115 & B155 & xarm changes | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 147 | 2025-03-13-0144 | Otaki - 15 Riverbank Rd | L352 | 2025-03-13 17:10 | 2025-03-13 18:08 | 0.002515 | 4.2627e-05 | 2 | 118 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 148 | 2024-04-13-0167 | Otaki - 15 Riverbank Rd | L349 | 2024-04-13 08:04 | 2024-04-13 10:25 | 0.0030052 | 2.1313e-05 | 1 | 141 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 149 | 2024-06-13-0166 | Raumati - 133 Matai Rd | Z212 | 2024-06-13 09:05 | 2024-06-13 14:45 | 0.18841 | 0.00055415 | 26 | 8840 | Planned | Planned interruption | 46 Clunie Ave, Raumati - Replace 11kv Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 150 | 2024-07-13-0275 | Paraparaumu East - 42 Tongariro St | V311 | 2024-07-13 13:25 | 2024-07-13 14:10 | 0.024809 | 0.00057546 | 27 | 1164 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 151 | 2024-09-13-0241 | Shannon - 22 Stafford St | 149 | 2024-09-13 09:08 | 2024-09-13 15:33 | 0.19694 | 0.00051152 | 24 | 9240 | Planned | Planned interruption | Foxton Shannon Rd - Replace 33Kv Pole, Straighten 33Kv poles, install lightning arrestors at Tx B25 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 152 | 2024-09-13-0247 | Waikanae - 18 Parata St | 652 | 2024-09-13 18:57 | 2024-09-14 12:57 | 0.55037 | 0.0014493 | 68 | 25823 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 153 | 2024-11-13-0164 | Levin West - 270 Kawiu Rd | E154 | 2024-11-13 08:57 | 2024-11-13 18:29 | 1.4629 | 0.0025576 | 120 | 68640 | Planned | Planned interruption | Weraroa Rd - 11Kv Pole change & upgrade PMTX E64 to GMTX | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 154 | 2024-11-13-0166 | Paraparaumu East - 42 Tongariro St | V311 | 2024-11-13 10:18 | 2024-11-13 13:06 | 0.48697 | 0.0028986 | 136 | 22848 | Planned | Planned interruption | instal new DDO's to repair cable fault later on today | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 155 | 2024-11-13-0169 | Otaki - 15 Riverbank Rd | L348 | 2024-11-13 01:05 | 2024-11-13 01:30 | 0.0047955 | 0.00019182 | 9 | 225 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 156 | 2024-12-13-0174 | Paraparaumu East - 42 Tongariro St | V317 | 2024-12-13 08:13 | 2024-12-13 16:07 | 0.010103 | 2.1313e-05 | 1 | 474 | Planned | Planned interruption | 33 Tongariro St - Replace defective ABS V10 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 157 | 2024-12-13-0175 | Levin East - 69 Tararua Rd | G308 | 2024-12-13 09:00 | 2024-12-13 14:36 | 0.042968 | 0.00012788 | 6 | 2016 | Planned | Planned interruption | Nuhunoa West Rd 400V Recondutiring & Arm changes | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 158 | 2024-12-13-0182 | Waikanae - 18 Parata St | 632 | 2024-12-13 12:43 | 2024-12-13 14:43 | 0.011147 | 0.00010657 | 5 | 523 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 159 | 2025-01-15-0135 | Shannon - 22 Stafford St | 119 | 2024-12-13 04:26 | 2024-12-13 06:55 | 0.0095271 | 6.394e-05 | 3 | 447 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 160 | 2025-01-14-0113 | Foxton - 13 Union St | C1 | 2025-01-14 13:04 | 2025-01-14 15:05 | 0.42226 | 0.0055841 | 262 | 19812 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 161 | 2025-01-14-0115 | Levin East - 69 Tararua Rd | G308 | 2025-01-14 15:00 | 2025-01-14 17:50 | 0.018138 | 0.00010657 | 5 | 851 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 162 | 2025-02-14-0126 | Shannon - 22 Stafford St | 119 | 2025-02-14 06:00 | 2025-02-14 07:35 | 0.0080991 | 8.5253e-05 | 4 | 380 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 163 | 2025-03-14-0147 | Foxton - 13 Union St | C4 | 2025-03-14 09:56 | 2025-03-14 10:45 | 0.10056 | 0.00211 | 99 | 4718 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 164 | 2024-06-14-0176 | Paraparaumu East - 42 Tongariro St | V319 | 2024-06-14 09:00 | 2024-06-14 13:00 | 0.081843 | 0.00034101 | 16 | 3840 | Planned | Planned interruption | Old SH 1 South of Pram Replace 11KV Cross arms and Links and Straighten Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 165 | 2024-06-14-0188 | Shannon - 22 Stafford St | 119 | 2024-06-14 18:19 | 2024-06-14 19:36 | 0.036467 | 0.00046889 | 22 | 1711 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 166 | 2024-07-14-0281 | Otaki - 15 Riverbank Rd | L352 | 2024-07-14 12:02 | 2024-07-14 13:40 | 0.0020887 | 2.1313e-05 | 1 | 98 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 167 | 2024-08-14-0188 | Otaki - 15 Riverbank Rd | L352 | 2024-08-14 09:21 | 2024-08-14 23:25 | 0.089942 | 0.00010657 | 5 | 4220 | Planned | Planned interruption | Te Hapia Rd, Te Horo - Replace LV Poles, straighten & restrain 11Kv Line (Priority 0) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 168 | 2024-08-14-0196 | Otaki - 15 Riverbank Rd | L349 | 2024-08-14 13:00 | 2024-08-14 18:20 | 0.14141 | 0.00049021 | 23 | 6635 | Planned | Planned interruption | 14 waikawa beach street, manauka transformer replacemet | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 169 | 2024-09-14-0265 | Waikanae - 18 Parata St | 652 | 2024-09-14 12:57 | 2024-09-14 14:49 | 0.063855 | 0.00074597 | 35 | 2996 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 170 | 2024-10-14-0161 | Otaki - 15 Riverbank Rd | L352 | 2024-10-14 07:55 | 2024-10-14 13:36 | 0.021782 | 6.394e-05 | 3 | 1022 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 171 | 2024-11-14-0185 | Otaki - 15 Riverbank Rd | L348 | 2024-11-14 08:30 | 2024-11-14 15:14 | 0.19804 | 0.00049021 | 23 | 9292 | Planned | Planned interruption | Wairongamai Rd, Otaki - 11Kv Reconducting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 172 | 2024-12-18-0396 | Foxton - 13 Union St | C4 | 2024-12-14 20:17 | 2024-12-15 03:19 | 1.9782 | 0.017051 | 800 | 92813 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 173 | 2024-05-15-0232 | Foxton - 13 Union St | C2 | 2024-05-15 10:02 | 2024-05-15 11:30 | 0.018756 | 0.00021313 | 10 | 880 | Planned | Planned interruption | Commenced shcedule for team to install lightening arrestors at TX C135 in 60A Purcell street, Foxton | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 174 | 2024-05-15-0233 | Foxton - 13 Union St | C1 | 2024-05-15 10:12 | 2024-05-15 13:07 | 0.018649 | 0.00010657 | 5 | 875 | Planned | Planned interruption | Commenced shcedule for team to install lightening arrestors at TX C107 in 64 Stewart Road, Foxton | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 175 | 2024-07-15-0284 | Levin West - 270 Kawiu Rd | E150 | 2024-07-15 05:27 | 2024-07-15 11:50 | 8.1699 | 0.022571 | 1059 | 383325 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 176 | 2024-07-15-0292 | Levin West - 270 Kawiu Rd | E150 | 2024-07-15 12:20 | 2024-07-15 14:51 | 0.37011 | 0.002451 | 115 | 17365 | Unplanned | Human error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 177 | 2024-10-15-0189 | Foxton - 13 Union St | C2 | 2024-10-15 21:15 | 2024-10-15 23:50 | 0.0033036 | 2.1313e-05 | 1 | 155 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 178 | 2024-11-15-0193 | Levin East - 69 Tararua Rd | G309 | 2024-11-15 09:11 | 2024-11-15 13:40 | 0.2408 | 0.00089516 | 42 | 11298 | Planned | Planned interruption | Kawiu Rd, Levin - Replace defective ABS E143 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 179 | 2024-12-15-0283 | Otaki - 15 Riverbank Rd | L349 | 2024-12-15 17:40 | 2024-12-15 20:20 | 0.04073 | 0.00025576 | 12 | 1911 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 180 | 2025-01-16-0142 | Raumati - 133 Matai Rd | Z211 | 2025-01-16 09:42 | 2025-01-16 16:11 | 0.082909 | 0.00021313 | 10 | 3890 | Planned | Planned interruption | Poplar Ave Raumati Replace 11KV Pole & Starighten 11KV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 181 | 2025-02-16-0148 | Levin West - 270 Kawiu Rd | E153 | 2025-02-16 19:38 | 2025-02-16 19:53 | 0.2213 | 0.01477 | 693 | 10383 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 182 | 2025-03-16-0167 | Foxton - 13 Union St | C4 | 2025-03-16 02:46 | 2025-03-16 05:47 | 3.0464 | 0.029689 | 1393 | 142933 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 183 | 2025-03-16-0171 | Foxton - 13 Union St | C4 | 2025-03-16 17:34 | 2025-03-16 19:00 | 0.18048 | 0.00211 | 99 | 8468 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 184 | 2024-05-16-0248 | Levin East - 69 Tararua Rd | G308 | 2024-05-16 09:15 | 2024-05-16 13:57 | 0.012021 | 4.2627e-05 | 2 | 564 | Planned | Planned interruption | Commenced Schedule for team to upgrade TX L3 from 200kVA to 300kVA at Tatum Park, Levin | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 185 | 2024-06-16-0200 | Levin West - 270 Kawiu Rd | E150 | 2024-06-16 14:46 | 2024-06-16 15:56 | 0.0014919 | 2.1313e-05 | 1 | 70 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 186 | 2024-07-16-0307 | Otaki - 15 Riverbank Rd | L348 | 2024-07-16 09:55 | 2024-07-16 15:11 | 0.020205 | 6.394e-05 | 3 | 948 | Planned | Planned interruption | Old Coach Rd - Replace 30KV Tx M117 & Structure | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 187 | 2024-07-16-0319 | Otaki - 15 Riverbank Rd | L349 | 2024-07-16 17:54 | 2024-07-16 19:09 | 0.67919 | 0.013236 | 621 | 31867 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 188 | 2024-09-16-0271 | Otaki - 15 Riverbank Rd | L349 | 2024-09-16 06:51 | 2024-09-16 08:14 | 0.030052 | 0.00036233 | 17 | 1410 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 189 | 2024-09-16-0272 | Otaki - 15 Riverbank Rd | L352 | 2024-09-16 08:10 | 2024-09-16 10:10 | 0.013214 | 0.00014919 | 7 | 620 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 190 | 2024-10-16-0202 | Waikanae - 18 Parata St | 632 | 2024-10-16 20:45 | 2024-10-16 21:35 | 0.022251 | 0.00044758 | 21 | 1044 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 191 | 2024-11-16-0200 | Paekakariki - 96 Tilley Rd | Z165 | 2024-11-16 09:22 | 2024-11-16 11:05 | 0.18404 | 0.0017903 | 84 | 8635 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 192 | 2025-01-17-0154 | Levin East - 69 Tararua Rd | G308 | 2025-01-17 09:06 | 2025-01-17 14:31 | 0.027707 | 8.5253e-05 | 4 | 1300 | Planned | Planned interruption | Transformer structure/Crossarm changes @ J15 Stage 6 : Muhunoa West Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 193 | 2025-03-17-0185 | Levin East - 69 Tararua Rd | G313 | 2025-03-17 09:00 | 2025-03-17 16:06 | 0.2633 | 0.00061809 | 29 | 12354 | Planned | Planned interruption | Muhunoa West Rd, Ohau - Resag 11Kv line & Replace 11Kv xarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 194 | 2025-03-17-0179 | Foxton - 13 Union St | C4 | 2025-03-17 05:13 | 2025-03-17 05:53 | 0.29242 | 0.0073105 | 343 | 13720 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 195 | 2024-04-18-0228 | Foxton - 13 Union St | C4 | 2024-04-17 09:37 | 2024-04-17 20:04 | 0.18709 | 0.00029839 | 14 | 8778 | Planned | Planned interruption | Replace 11KV Pole & Hardware Install new ABS & DOF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 196 | 2024-05-17-0260 | Foxton - 13 Union St | C2 | 2024-05-17 09:53 | 2024-05-17 11:52 | 0.071528 | 0.00061809 | 29 | 3356 | Planned | Planned interruption | Commenced schedule for team to install lightening arrestors on TX C8 in Foxton | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 197 | 2024-06-17-0214 | Foxton - 13 Union St | C1 | 2024-06-17 09:43 | 2024-06-17 14:31 | 0.024553 | 8.5253e-05 | 4 | 1152 | Planned | Planned interruption | 624 Kere Kere Rd, Foxton - Replace ABS E231 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 198 | 2024-06-17-0206 | Otaki - 15 Riverbank Rd | L352 | 2024-06-17 06:27 | 2024-06-17 08:02 | 0.0080991 | 8.5253e-05 | 4 | 380 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 199 | 2024-06-17-0217 | Levin West - 270 Kawiu Rd | E154 | 2024-06-17 09:42 | 2024-06-17 13:17 | 0.50406 | 0.0023445 | 110 | 23650 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 200 | 2024-07-17-0333 | Otaki - 15 Riverbank Rd | L349 | 2024-07-17 00:30 | 2024-07-17 05:08 | 0.0059251 | 2.1313e-05 | 1 | 278 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 201 | 2024-08-17-0235 | Levin West - 270 Kawiu Rd | E153 | 2024-08-17 13:41 | 2024-08-17 15:05 | 0.0015772 | 2.1313e-05 | 1 | 74 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 202 | 2024-08-21-0326 | Shannon - 22 Stafford St | 119 | 2024-08-17 16:11 | 2024-08-17 18:15 | 0.010571 | 8.5253e-05 | 4 | 496 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 203 | 2024-10-17-0212 | Foxton - 13 Union St | C4 | 2024-10-17 10:45 | 2024-10-17 15:18 | 0.017456 | 6.394e-05 | 3 | 819 | Planned | Planned interruption | Switching 90479A - 312 Motuiti Rd Foxton Replace transfomer structure B172 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 204 | 2024-10-17-0235 | Paraparaumu West - 11 Arko Pl | 402 | 2024-10-17 08:10 | 2024-10-17 16:06 | 0.42162 | 0.00089516 | 42 | 19782 | Planned | Planned interruption | Fredrick St - Instal new ENTEC W162 wiith isolating links | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 205 | 2024-10-22-0291 | Waikanae - 18 Parata St | 622 | 2024-10-17 23:52 | 2024-10-18 00:50 | 0.08406 | 0.0014493 | 68 | 3944 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 206 | 2024-10-29-0397 | Levin West - 270 Kawiu Rd | E153 | 2024-10-17 11:45 | 2024-10-17 12:04 | 0.14578 | 0.0076728 | 360 | 6840 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 207 | 2024-11-17-0208 | Levin West - 270 Kawiu Rd | E150 | 2024-11-17 08:41 | 2024-11-17 15:37 | 0.12413 | 0.00029839 | 14 | 5824 | Planned | Planned interruption | CNR Koputaroa Rd & SH1, Levin - Remove ABS F208 & Section of line, poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 208 | 2024-12-17-0361 | Levin East - 69 Tararua Rd | G308 | 2024-12-17 09:00 | 2024-12-17 15:33 | 0.46069 | 0.0011722 | 55 | 21615 | Planned | Planned interruption | Muhunoa West Rd - 11Kv xarm chnages & 400V reconducting - Stage 3 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 209 | 2025-01-16-0148 | Waikanae - 18 Parata St | 622 | 2024-12-17 15:44 | 2024-12-17 17:50 | 1.2263 | 0.024809 | 1164 | 57537 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 210 | 2025-01-18-0170 | Paraparaumu East - 42 Tongariro St | V311 | 2025-01-18 14:22 | 2025-01-18 15:35 | 0.0055841 | 8.5253e-05 | 4 | 262 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 211 | 2025-03-24-0281 | Waikanae - 18 Parata St | 632 | 2025-03-18 08:40 | 2025-03-18 17:12 | 0.29464 | 0.00057546 | 27 | 13824 | Planned | Planned interruption | Ngarara Rd Waikanae 11KV Reconductoring and pole changers Stage 1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 212 | 2024-05-18-0270 | Otaki - 15 Riverbank Rd | L351 | 2024-05-18 09:21 | 2024-05-18 11:00 | 0.0085253 | 8.5253e-05 | 4 | 400 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 213 | 2024-07-18-0349 | Levin West - 270 Kawiu Rd | E150 | 2024-07-18 10:30 | 2024-07-18 15:18 | 0.049106 | 0.00017051 | 8 | 2304 | Planned | Planned interruption | 800SH1 Poroutawhao - 400V Xarm change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 214 | 2024-08-18-0242 | Waikanae - 18 Parata St | 652 | 2024-08-18 13:54 | 2024-08-18 15:28 | 0.0040069 | 4.2627e-05 | 2 | 188 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 215 | 2024-09-23-0416 | Shannon - 22 Stafford St | 139 | 2024-09-18 02:18 | 2024-09-18 07:03 | 0.66534 | 0.005648 | 265 | 31217 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 216 | 2024-10-18-0251 | Otaki - 15 Riverbank Rd | L352 | 2024-10-18 07:38 | 2024-10-18 14:44 | 0.18291 | 0.00049021 | 23 | 8582 | Planned | Planned interruption | Hautere Cross Rd - Replace HV Pole & 400V Reconducting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 217 | 2024-10-22-0294 | Waikanae - 18 Parata St | 622 | 2024-10-18 04:18 | 2024-10-18 05:45 | 0.076025 | 0.00087385 | 41 | 3567 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 218 | 2024-11-18-0214 | Shannon - 22 Stafford St | 119 | 2024-11-18 08:45 | 2024-11-18 14:39 | 0.2188 | 0.00061809 | 29 | 10266 | Planned | Planned interruption | Albert Rd, Tokomaru - 11Kv arm change & reconducting at various sites | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 219 | 2024-11-18-0216 | Raumati - 133 Matai Rd | Z210 | 2024-11-18 09:49 | 2024-11-18 10:24 | 0.68876 | 0.019651 | 922 | 32316 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 220 | 2024-11-18-0224 | Otaki - 15 Riverbank Rd | L351 | 2024-11-18 10:29 | 2024-11-18 13:50 | 0.004284 | 2.1313e-05 | 1 | 201 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 221 | 2025-01-17-0158 | Paraparaumu East - 42 Tongariro St | V313 | 2024-12-18 08:07 | 2024-12-18 14:51 | 0.49941 | 0.0012362 | 58 | 23432 | Planned | Planned interruption | Ruapehu St Pram Replace 33KV & 11KV Cross arms Multiple sites | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 222 | 2024-12-18-0397 | Waikanae - 18 Parata St | 672 | 2024-12-18 19:33 | 2024-12-18 21:15 | 0.14003 | 0.0014919 | 70 | 6570 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 223 | 2025-01-19-0175 | Paraparaumu East - 42 Tongariro St | V311 | 2025-01-19 23:01 | 2025-01-19 23:39 | 0.0017051 | 8.5253e-05 | 4 | 80 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 224 | 2025-02-19-0191 | Foxton - 13 Union St | C1 | 2025-02-19 22:36 | 2025-02-20 00:15 | 0.010571 | 0.00010657 | 5 | 496 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 225 | 2025-03-19-0214 | Waikanae - 18 Parata St | 632 | 2025-03-19 08:03 | 2025-03-19 14:10 | 0.20337 | 0.00055415 | 26 | 9542 | Planned | Planned interruption | Ngarara Rd, Waikanae - 11Kv reconducting, HV Pole changes (Stage 2) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 226 | 2024-04-19-0235 | Otaki - 15 Riverbank Rd | L352 | 2024-04-19 09:25 | 2024-04-19 14:25 | 0.012788 | 4.2627e-05 | 2 | 600 | Planned | Planned interruption | Commenced Switching Schedule for team to replace TX Q15 Structure at Te Horo, sims Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 227 | 2024-08-19-0267 | Foxton - 13 Union St | C4 | 2024-08-19 15:47 | 2024-08-19 19:28 | 0.0047102 | 2.1313e-05 | 1 | 221 | Unplanned | Human error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 228 | 2024-09-19-0344 | Otaki - 15 Riverbank Rd | L349 | 2024-09-19 08:52 | 2024-09-19 11:25 | 0.0065219 | 4.2627e-05 | 2 | 306 | Planned | Planned interruption | Switching 90368 Main Rd North Otaki Replace 11KV Cross arms & TX L385 Structure | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 229 | 2024-09-19-0347 | Shannon - 22 Stafford St | 119 | 2024-09-19 10:40 | 2024-09-19 15:40 | 0.019182 | 6.394e-05 | 3 | 900 | Planned | Planned interruption | Switching 91392A 432 Makaru Rd Tokomaru Replace TX Structure at TX A142 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 230 | 2024-11-19-0234 | Shannon - 22 Stafford St | 119 | 2024-11-19 09:17 | 2024-11-19 14:35 | 0.122 | 0.00038364 | 18 | 5724 | Planned | Planned interruption | Puketea St - Replace 11Kv xarms at various sites | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 231 | 2024-11-19-0235 | Otaki - 15 Riverbank Rd | L350 | 2024-11-19 09:30 | 2024-11-19 15:25 | 0.030265 | 8.5253e-05 | 4 | 1420 | Planned | Planned interruption | 50 Rangiuru Rd - Tree work | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 232 | 2024-11-19-0228 | Paraparaumu East - 42 Tongariro St | V313 | 2024-11-19 05:29 | 2024-11-19 07:20 | 0.11531 | 0.0010444 | 49 | 5410 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 233 | 2024-11-19-0246 | Paraparaumu East - 42 Tongariro St | V319 | 2024-11-19 18:56 | 2024-11-19 20:01 | 0.60634 | 0.0092926 | 436 | 28449 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 234 | 2024-12-19-0406 | Levin East - 69 Tararua Rd | G311 | 2024-12-19 09:15 | 2024-12-19 13:42 | 0.39298 | 0.0014706 | 69 | 18438 | Planned | Planned interruption | Weraroa Rd - Replace defective 112Kv ABS H141 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 235 | 2025-02-20-0201 | Paekakariki - 96 Tilley Rd | Z167 | 2025-02-20 15:31 | 2025-02-20 17:16 | 0.0066924 | 6.394e-05 | 3 | 314 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 236 | 2025-03-24-0280 | Raumati - 133 Matai Rd | Z211 | 2025-03-20 09:00 | 2025-03-20 16:00 | 0.089516 | 0.00021313 | 10 | 4200 | Planned | Planned interruption | Switching 94489 - 120 Matai Rd Raumati Replace 11KV Pole: 35446D | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 237 | 2024-05-21-0313 | Levin East - 69 Tararua Rd | G309 | 2024-05-20 17:30 | 2024-05-20 18:30 | 0.0012788 | 2.1313e-05 | 1 | 60 | Planned | Planned interruption | Arapaepae Rd Isolated TX D184 to safely Replace 400V Fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 238 | 2024-06-20-0257 | Levin West - 270 Kawiu Rd | E153 | 2024-06-20 09:22 | 2024-06-20 11:47 | 0.012362 | 8.5253e-05 | 4 | 580 | Planned | Planned interruption | Hokio Sands Rd - Replace Tx J95 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 239 | 2024-06-20-0259 | Otaki - 15 Riverbank Rd | L348 | 2024-06-20 09:20 | 2024-06-20 14:20 | 0.03197 | 0.00010657 | 5 | 1500 | Planned | Planned interruption | Waiorongomai Rd, Otaki | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 240 | 2024-06-20-0263 | Levin West - 270 Kawiu Rd | E153 | 2024-06-20 12:59 | 2024-06-20 14:59 | 0.0076728 | 6.394e-05 | 3 | 360 | Planned | Planned interruption | 398 Hokio Sand Road Levin - Upgrade transformer J83 to 30 kVa | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 241 | 2024-06-20-0256 | Shannon - 22 Stafford St | 119 | 2024-06-20 09:17 | 2024-06-20 16:07 | 0.19261 | 0.00046889 | 22 | 9037 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 242 | 2024-09-20-0365 | Shannon - 22 Stafford St | 149 | 2024-09-20 09:21 | 2024-09-20 15:23 | 0.24689 | 0.00068203 | 32 | 11584 | Planned | Planned interruption | Union St, Foxton - Replace 11Kv & 400V arms at Various sites | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 243 | 2024-11-20-0259 | Levin East - 69 Tararua Rd | G308 | 2024-11-20 09:30 | 2024-11-20 14:53 | 0.95409 | 0.0031757 | 149 | 44765 | Planned | Planned interruption | Kuku West Rd - Replace defective ABS H73 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 244 | 2024-11-20-0268 | Raumati - 133 Matai Rd | Z211 | 2024-11-20 10:46 | 2024-11-20 16:38 | 0.007417 | 2.1313e-05 | 1 | 348 | Planned | Planned interruption | Paddock outside Paekakariki Sub - Replace defective ABS Z185 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 245 | 2024-11-22-0282 | Otaki - 15 Riverbank Rd | L349 | 2024-11-20 09:21 | 2024-11-20 09:25 | 0.056182 | 0.014045 | 659 | 2636 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 246 | 2024-12-20-0413 | Waikanae - 18 Parata St | 652 | 2024-12-20 07:44 | 2024-12-20 08:55 | 0.0060317 | 8.5253e-05 | 4 | 283 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 247 | 2025-01-21-0180 | Foxton - 13 Union St | C1 | 2025-01-21 07:00 | 2025-01-21 08:06 | 0.00422 | 6.394e-05 | 3 | 198 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 248 | 2025-02-21-0211 | Levin West - 270 Kawiu Rd | E151 | 2025-02-21 09:56 | 2025-02-21 13:37 | 0.080074 | 0.00036233 | 17 | 3757 | Planned | Planned interruption | 40 Gordan Pl - Replace Tx E269 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 249 | 2025-02-21-0212 | Otaki - 15 Riverbank Rd | L351 | 2025-02-21 10:00 | 2025-02-21 14:12 | 0.032226 | 0.00012788 | 6 | 1512 | Planned | Planned interruption | Rahui Rd - 400V xarms & replace Lv conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 250 | 2025-02-21-0220 | Levin West - 270 Kawiu Rd | E153 | 2025-02-21 17:45 | 2025-02-21 19:19 | 0.0060104 | 6.394e-05 | 3 | 282 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 251 | 2025-03-21-0252 | Foxton - 13 Union St | C4 | 2025-03-21 09:00 | 2025-03-21 14:30 | 0.091434 | 0.00027707 | 13 | 4290 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 252 | 2025-03-21-0265 | Paraparaumu East - 42 Tongariro St | V313 | 2025-03-21 23:31 | 2025-03-22 01:30 | 0.13694 | 0.0013641 | 64 | 6425 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 253 | 2024-05-21-0304 | Otaki - 15 Riverbank Rd | L351 | 2024-05-21 09:19 | 2024-05-21 14:33 | 0.013385 | 4.2627e-05 | 2 | 628 | Planned | Planned interruption | 413 Rahui Rd - Replace 11Kv Tx & structure L189 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 254 | 2024-05-21-0306 | Foxton - 13 Union St | C2 | 2024-05-21 10:02 | 2024-05-21 10:58 | 0.0083548 | 0.00014919 | 7 | 392 | Planned | Planned interruption | 211 Avenue Rd - Install lightning arrestors @ Tx C183 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 255 | 2024-05-21-0314 | Shannon - 22 Stafford St | 139 | 2024-05-21 09:48 | 2024-05-22 14:37 | 0.073723 | 4.2627e-05 | 2 | 3459 | Unplanned | Adverse weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 256 | 2024-05-21-0319 | Otaki - 15 Riverbank Rd | L352 | 2024-05-21 19:00 | 2024-05-21 20:20 | 0.056267 | 0.00070334 | 33 | 2640 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 257 | 2024-05-30-0487 | Shannon - 22 Stafford St | 119 | 2024-05-21 07:41 | 2024-05-21 13:43 | 0.36233 | 0.0023445 | 110 | 17000 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 258 | 2024-06-21-0280 | Otaki - 15 Riverbank Rd | L350 | 2024-06-21 11:10 | 2024-06-21 13:32 | 0.11198 | 0.00078859 | 37 | 5254 | Planned | Planned interruption | Switching 89376A - 10 Moana St Otaki - Replace 11KV Cross arms and DOF M25 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 259 | 2024-06-21-0269 | Levin West - 270 Kawiu Rd | E153 | 2024-06-21 04:27 | 2024-06-21 04:43 | 0.2466 | 0.014855 | 697 | 11570 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 260 | 2024-06-21-0271 | Levin West - 270 Kawiu Rd | E148 | 2024-06-21 07:13 | 2024-06-21 08:54 | 0.012937 | 0.00012788 | 6 | 607 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 261 | 2024-08-21-0309 | Shannon - 22 Stafford St | 119 | 2024-08-21 10:10 | 2024-08-21 12:09 | 0.0025363 | 2.1313e-05 | 1 | 119 | Planned | Planned interruption | Install lightning arrestors at Tx B268 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 262 | 2024-08-21-0319 | Waikanae - 18 Parata St | 662 | 2024-08-21 11:37 | 2024-08-21 15:48 | 0.2139 | 0.00085253 | 40 | 10036 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 263 | 2024-11-21-0269 | Shannon - 22 Stafford St | 119 | 2024-11-21 09:42 | 2024-11-21 15:26 | 0.21262 | 0.00061809 | 29 | 9976 | Planned | Planned interruption | Albert Rd, Tokomaru - 11Kv Arm, pole changes & Reconducting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 264 | 2024-12-21-0424 | Foxton - 13 Union St | C1 | 2024-12-21 11:12 | 2024-12-21 12:29 | 0.0049234 | 6.394e-05 | 3 | 231 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 265 | 2025-01-22-0199 | Levin East - 69 Tararua Rd | G311 | 2025-01-22 18:49 | 2025-01-22 20:51 | 0.05599 | 0.00057546 | 27 | 2627 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 266 | 2024-06-22-0313 | Levin West - 270 Kawiu Rd | E148 | 2024-06-22 09:05 | 2024-06-22 13:38 | 0.017477 | 6.394e-05 | 3 | 820 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 267 | 2024-06-27-0388 | Paraparaumu West - 11 Arko Pl | 402 | 2024-06-22 09:11 | 2024-06-22 10:51 | 5.5093 | 0.07157 | 3358 | 258493 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 268 | 2024-08-22-0332 | Foxton - 13 Union St | C1 | 2024-08-22 10:14 | 2024-08-22 11:11 | 0.0060743 | 0.00010657 | 5 | 285 | Planned | Planned interruption | 498 Whirokino Rd Foxton Install Lightnig arrestors at TX E247 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 269 | 2024-08-22-0335 | Foxton - 13 Union St | C2 | 2024-08-22 13:25 | 2024-08-22 14:25 | 0.0012788 | 2.1313e-05 | 1 | 60 | Planned | Planned interruption | 45 Himatangi block rd foxton Install 11KV Lightning arrestors at TX B323 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 270 | 2024-08-23-0352 | Otaki - 15 Riverbank Rd | L351 | 2024-08-22 09:22 | 2024-08-22 14:22 | 0.33249 | 0.0011083 | 52 | 15600 | Planned | Planned interruption | 346 Rahui Rd Otaki Replace 11KV Cross arms Multiple Sites | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 271 | 2024-08-22-0333 | Shannon - 22 Stafford St | 119 | 2024-08-22 12:52 | 2024-08-23 15:12 | 0.09883 | 6.394e-05 | 3 | 4637 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 272 | 2024-09-22-0403 | Shannon - 22 Stafford St | 149 | 2024-09-22 05:39 | 2024-09-22 07:30 | 0.0047316 | 4.2627e-05 | 2 | 222 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 273 | 2024-10-22-0293 | Shannon - 22 Stafford St | 119 | 2024-10-22 10:11 | 2024-10-22 13:28 | 0.016795 | 8.5253e-05 | 4 | 788 | Planned | Planned interruption | 478 Okuku Rd, Opiki - Install lightning arrestors at Tx B256 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 274 | 2024-10-22-0287 | Paraparaumu East - 42 Tongariro St | V311 | 2024-10-22 06:02 | 2024-10-22 06:40 | 0.57416 | 0.014855 | 697 | 26939 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 275 | 2024-11-22-0283 | Shannon - 22 Stafford St | 119 | 2024-11-22 10:22 | 2024-11-22 11:54 | 0.0058825 | 6.394e-05 | 3 | 276 | Planned | Planned interruption | 277 Ngui Rd - Install lightning arrestors at Tx B83 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 276 | 2024-11-26-0350 | Paraparaumu East - 42 Tongariro St | V319 | 2024-11-22 22:30 | 2024-11-22 22:44 | 0.055798 | 0.0039856 | 187 | 2618 | Planned | Planned interruption | Old raumati Rd Reinstate 11KV underground cable to main line after testring. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 277 | 2025-01-23-0209 | Levin West - 270 Kawiu Rd | E150 | 2025-01-23 09:41 | 2025-01-23 14:01 | 0.0055415 | 2.1313e-05 | 1 | 260 | Planned | Planned interruption | 1116 SH1 North - Replace 400v xarm on TX F158 - Madison | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 278 | 2024-05-23-0342 | Foxton - 13 Union St | C2 | 2024-05-23 09:42 | 2024-05-23 11:00 | 0.019949 | 0.00025576 | 12 | 936 | Planned | Planned interruption | 118 Avenue Rd, Foxton - Install lightning arrestors at Tx C15 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 279 | 2024-05-23-0346 | Foxton - 13 Union St | C2 | 2024-05-23 12:50 | 2024-05-23 13:53 | 0.010742 | 0.00017051 | 8 | 504 | Planned | Planned interruption | 167 Avenue Rd, Foxton Replace lightning arrestors at Tx C17 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 280 | 2024-05-23-0344 | Levin West - 270 Kawiu Rd | E148 | 2024-05-23 11:07 | 2024-05-23 12:30 | 0.0052857 | 6.394e-05 | 3 | 248 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 281 | 2024-07-23-0412 | Otaki - 15 Riverbank Rd | L348 | 2024-07-23 09:20 | 2024-07-23 15:19 | 0.068863 | 0.00019182 | 9 | 3231 | Planned | Planned interruption | Bennetts Rd, Otaki - 400V Reconducting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 282 | 2024-07-23-0413 | Otaki - 15 Riverbank Rd | L349 | 2024-07-23 09:39 | 2024-07-23 15:03 | 0.15883 | 0.00049021 | 23 | 7452 | Planned | Planned interruption | Waikawa Beach Rd - 400V Reconducting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 283 | 2024-08-23-0349 | Levin East - 69 Tararua Rd | G313 | 2024-08-23 15:29 | 2024-08-23 15:34 | 0.00010657 | 2.1313e-05 | 1 | 5 | Planned | Planned interruption | tap change Tx G91 due to high voltage | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 284 | 2024-09-24-0437 | Paraparaumu West - 11 Arko Pl | 402 | 2024-09-23 19:49 | 2024-09-23 20:29 | 0.055415 | 0.0013854 | 65 | 2600 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 285 | 2024-10-23-0313 | Paraparaumu West - 11 Arko Pl | 402 | 2024-10-23 09:00 | 2024-10-23 15:42 | 0.32558 | 0.00080991 | 38 | 15276 | Planned | Planned interruption | Martin Rd - Straighten 11Kv Poles & replace Lv/Hv arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 286 | 2024-10-23-0319 | Foxton - 13 Union St | C1 | 2024-10-23 10:00 | 2024-10-23 17:50 | 0.010017 | 2.1313e-05 | 1 | 470 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 287 | 2024-12-05-0044 | Otaki - 15 Riverbank Rd | L352 | 2024-11-23 07:37 | 2024-11-23 08:20 | 0.0036659 | 8.5253e-05 | 4 | 172 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 288 | 2025-01-24-0218 | Paraparaumu East - 42 Tongariro St | V311 | 2025-01-24 09:08 | 2025-01-24 10:05 | 0.0048594 | 8.5253e-05 | 4 | 228 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 289 | 2025-01-24-0220 | Foxton - 13 Union St | C1 | 2025-01-24 10:11 | 2025-01-24 11:06 | 0.0035167 | 6.394e-05 | 3 | 165 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 290 | 2025-02-24-0239 | Waikanae - 18 Parata St | 632 | 2025-02-24 09:30 | 2025-02-24 14:57 | 0.041817 | 0.00012788 | 6 | 1962 | Planned | Planned interruption | 24/02/2025 10:48:46 am #HWN4821 - Hadfield Rd, Te Horo | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 291 | 2025-03-24-0289 | Shannon - 22 Stafford St | 119 | 2025-03-24 18:31 | 2025-03-24 22:05 | 0.0091221 | 4.2627e-05 | 2 | 428 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 292 | 2024-06-24-0330 | Shannon - 22 Stafford St | 149 | 2024-06-24 08:42 | 2024-06-24 15:00 | 0.16919 | 0.00044758 | 21 | 7938 | Planned | Planned interruption | Cambells Rd - Replac ABS B117 & 11Kv arm changes | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 293 | 2024-07-25-0463 | Levin East - 69 Tararua Rd | G309 | 2024-07-24 08:05 | 2024-07-24 15:18 | 0.61301 | 0.0015559 | 73 | 28762 | Planned | Planned interruption | Replace GMTX G129 & solid links G128 with DDO's | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 294 | 2024-09-24-0443 | Levin East - 69 Tararua Rd | G310 | 2024-09-24 22:06 | 2024-09-24 22:10 | 0.006394 | 0.0012788 | 60 | 300 | Planned | Planned interruption | Lower taps at transformer G459 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 295 | 2024-10-24-0326 | Shannon - 22 Stafford St | 149 | 2024-10-24 10:04 | 2024-10-24 11:17 | 0.0077794 | 0.00010657 | 5 | 365 | Planned | Planned interruption | 228 Temukanui Rd, Opiki - Install lightning arrestors at Tx B214 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 296 | 2024-10-24-0323 | Otaki - 15 Riverbank Rd | L352 | 2024-10-24 07:48 | 2024-10-24 09:35 | 0.0045397 | 4.2627e-05 | 2 | 213 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 297 | 2024-10-24-0331 | Shannon - 22 Stafford St | 119 | 2024-10-24 13:18 | 2024-10-24 15:17 | 0.0025363 | 2.1313e-05 | 1 | 119 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 298 | 2025-01-25-0234 | Levin West - 270 Kawiu Rd | E148 | 2025-01-25 11:40 | 2025-01-25 12:45 | 0.0041561 | 6.394e-05 | 3 | 195 | Planned | Planned interruption | Repair broken 11kv stay wire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 299 | 2025-01-25-0235 | Shannon - 22 Stafford St | 129 | 2025-01-25 13:34 | 2025-01-25 17:40 | 0.094674 | 0.00042627 | 20 | 4442 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 300 | 2025-02-26-0278 | Otaki - 15 Riverbank Rd | L350 | 2025-02-25 08:42 | 2025-02-25 16:12 | 1.468 | 0.0032609 | 153 | 68875 | Planned | Planned interruption | Ngaio St Otaki Beach 11KV Cross arm changes and pole changes (Multiple sites) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 301 | 2025-03-25-0290 | Foxton - 13 Union St | CB102 | 2025-03-25 00:03 | 2025-03-25 00:20 | 0.21735 | 0.012468 | 585 | 10198 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 302 | 2025-03-25-0305 | Otaki - 15 Riverbank Rd | L352 | 2025-03-25 20:27 | 2025-03-25 22:40 | 0.093821 | 0.00070334 | 33 | 4402 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 303 | 2024-05-25-0411 | Paraparaumu East - 42 Tongariro St | V318 | 2024-05-25 12:32 | 2024-05-25 14:05 | 0.0019821 | 2.1313e-05 | 1 | 93 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 304 | 2024-05-25-0415 | Otaki - 15 Riverbank Rd | L349 | 2024-05-25 16:13 | 2024-05-25 17:30 | 0.037916 | 0.00049021 | 23 | 1779 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 305 | 2024-06-25-0338 | Foxton - 13 Union St | C2 | 2024-06-25 09:57 | 2024-06-25 11:27 | 0.023018 | 0.00025576 | 12 | 1080 | Planned | Planned interruption | 422 Foxton Shannon Rd - Install lightning arrestors at Tx B48 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 306 | 2024-06-25-0339 | Foxton - 13 Union St | C2 | 2024-06-25 09:53 | 2024-06-25 11:03 | 0.0059677 | 8.5253e-05 | 4 | 280 | Planned | Planned interruption | 217 Foxton Shannon Rd - Install lightning arrestors at Tx B59 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 307 | 2024-06-25-0348 | Foxton - 13 Union St | C2 | 2024-06-25 12:48 | 2024-06-25 13:42 | 0.0069055 | 0.00012788 | 6 | 324 | Planned | Planned interruption | 256 Foxton Shannon Road - Install lightning arrestors at transformer B212 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 308 | 2024-06-25-0349 | Foxton - 13 Union St | C2 | 2024-06-25 12:53 | 2024-06-25 13:54 | 0.010401 | 0.00017051 | 8 | 488 | Planned | Planned interruption | 592 Foxton Shannon Road - Install lightning arrestors at transformer B34 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 309 | 2024-06-25-0335 | Levin West - 270 Kawiu Rd | E153 | 2024-06-25 05:24 | 2024-06-25 06:53 | 0.013278 | 0.00014919 | 7 | 623 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 310 | 2024-06-25-0358 | Foxton - 13 Union St | C2 | 2024-06-25 18:57 | 2024-06-25 20:21 | 0.044204 | 0.0012575 | 59 | 2074 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 311 | 2024-07-25-0454 | Otaki - 15 Riverbank Rd | L348 | 2024-07-25 09:28 | 2024-07-25 15:54 | 0.074042 | 0.00019182 | 9 | 3474 | Planned | Planned interruption | Bennetts Rd - 400V Reconducting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 312 | 2024-07-25-0464 | Shannon - 22 Stafford St | 119 | 2024-07-25 10:02 | 2024-07-25 11:10 | 0.0028986 | 4.2627e-05 | 2 | 136 | Planned | Planned interruption | 70 Opiki Rd - Install lightning arrestors at Tx B93 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 313 | 2024-09-25-0445 | Levin West - 270 Kawiu Rd | E150 | 2024-09-25 09:33 | 2024-09-25 15:26 | 0.052665 | 0.00014919 | 7 | 2471 | Planned | Planned interruption | SH1 - Replace 11Kv Pole 27869T | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 314 | 2024-09-25-0446 | Shannon - 22 Stafford St | 129 | 2024-09-25 10:00 | 2024-09-25 10:19 | 0.0048594 | 0.00025576 | 12 | 228 | Planned | Planned interruption | Bryce St, Shannon - Re-install trip savers at B435 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 315 | 2024-09-25-0448 | Shannon - 22 Stafford St | 129 | 2024-09-25 10:04 | 2024-09-25 11:47 | 0.0043905 | 4.2627e-05 | 2 | 206 | Planned | Planned interruption | 125 Old Foxton Rd, Shannon - Install lightning arrestors at Tx B352 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 316 | 2024-12-25-0450 | Foxton - 13 Union St | C2 | 2024-12-25 13:55 | 2024-12-25 16:17 | 0.11207 | 0.00078859 | 37 | 5258 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 317 | 2025-01-26-0251 | Otaki - 15 Riverbank Rd | L352 | 2025-01-26 20:36 | 2025-01-26 21:47 | 0.11501 | 0.0016198 | 76 | 5396 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 318 | 2025-02-26-0286 | Levin West - 270 Kawiu Rd | E150 | 2025-02-26 20:06 | 2025-02-26 21:41 | 0.0020248 | 2.1313e-05 | 1 | 95 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 319 | 2025-02-26-0287 | Otaki - 15 Riverbank Rd | L349 | 2025-02-26 21:27 | 2025-02-26 23:57 | 0.037469 | 0.00025576 | 12 | 1758 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 320 | 2025-02-27-0295 | Otaki - 15 Riverbank Rd | L349 | 2025-02-26 18:11 | 2025-02-26 19:15 | 0.0013641 | 2.1313e-05 | 1 | 64 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 321 | 2025-03-26-0323 | Waikanae - 18 Parata St | 662 | 2025-03-26 08:05 | 2025-03-26 16:52 | 0.39312 | 0.00074597 | 35 | 18445 | Planned | Planned interruption | Ngarara Rd, Waikanae - Replace ABS T90, Links T89 & T124, Replace HV Poles 22132G, 103495A & 21664Y | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 322 | 2025-03-26-0309 | Foxton - 13 Union St | CB102 | 2025-03-26 00:02 | 2025-03-26 00:10 | 0.11972 | 0.015218 | 714 | 5617 | Unplanned | Human error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 323 | 2025-03-26-0310 | Foxton - 13 Union St | CB106 | 2025-03-26 00:02 | 2025-03-26 00:10 | 0.24553 | 0.029114 | 1366 | 11520 | Unplanned | Human error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 324 | 2025-03-26-0311 | Foxton - 13 Union St | CB104 | 2025-03-26 00:03 | 2025-03-26 00:10 | 0.10603 | 0.014493 | 680 | 4975 | Unplanned | Human error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 325 | 2025-03-26-0324 | Otaki - 15 Riverbank Rd | L352 | 2025-03-26 10:37 | 2025-03-26 21:31 | 0.041476 | 6.394e-05 | 3 | 1946 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 326 | 2025-03-26-0332 | Levin West - 270 Kawiu Rd | E153 | 2025-03-26 12:34 | 2025-03-26 13:44 | 0.0014919 | 2.1313e-05 | 1 | 70 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 327 | 2025-03-26-0333 | Otaki - 15 Riverbank Rd | L352 | 2025-03-26 14:24 | 2025-03-26 21:17 | 0.17537 | 0.00042627 | 20 | 8228 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 328 | 2024-04-26-0324 | Raumati - 133 Matai Rd | Z211 | 2024-04-26 09:15 | 2024-04-26 15:00 | 0.0073531 | 2.1313e-05 | 1 | 345 | Planned | Planned interruption | Commenced Switching Schedule 87914 for team to replace 11kV pole on old SH1, Raumati | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 329 | 2024-04-26-0330 | Waikanae - 18 Parata St | 632 | 2024-04-26 13:52 | 2024-04-26 18:45 | 0.05307 | 0.0014493 | 68 | 2490 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 330 | 2024-06-26-0360 | Paekakariki - 96 Tilley Rd | Z167 | 2024-06-26 08:05 | 2024-06-26 09:35 | 0.0076941 | 8.5253e-05 | 4 | 361 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 331 | 2024-06-26-0368 | Foxton - 13 Union St | C2 | 2024-06-26 13:27 | 2024-06-26 15:35 | 0.0027281 | 2.1313e-05 | 1 | 128 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 332 | 2024-07-26-0478 | Foxton - 13 Union St | C4 | 2024-07-26 00:57 | 2024-07-26 02:16 | 0.0033675 | 4.2627e-05 | 2 | 158 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 333 | 2024-07-26-0485 | Otaki - 15 Riverbank Rd | L352 | 2024-07-26 14:19 | 2024-07-26 15:01 | 0.00089516 | 2.1313e-05 | 1 | 42 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 334 | 2024-08-26-0373 | Waikanae - 18 Parata St | 632 | 2024-08-26 10:26 | 2024-08-26 12:23 | 0.26827 | 0.0023018 | 108 | 12587 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 335 | 2024-08-26-0380 | Otaki - 15 Riverbank Rd | L351 | 2024-08-26 19:42 | 2024-08-27 11:20 | 0.039984 | 4.2627e-05 | 2 | 1876 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 336 | 2024-09-26-0461 | Foxton - 13 Union St | C2 | 2024-09-26 09:24 | 2024-09-26 13:51 | 0.079669 | 0.00029839 | 14 | 3738 | Planned | Planned interruption | Switching 90125A - Newth Rd Foxton Replace 11KV Poles:42607M & 40445M | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 337 | 2024-09-26-0462 | Paraparaumu West - 11 Arko Pl | 405 | 2024-09-26 08:14 | 2024-09-26 16:28 | 0.20005 | 0.00040495 | 19 | 9386 | Planned | Planned interruption | Switching 91186A 132 Seaview Rd Pram Replacing ABS W41with new 11kv Entec | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 338 | 2024-10-26-0355 | Levin East - 69 Tararua Rd | G313 | 2024-10-26 01:57 | 2024-10-26 02:45 | 0.0071613 | 0.00014919 | 7 | 336 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 339 | 2024-10-26-0359 | Shannon - 22 Stafford St | 149 | 2024-10-26 21:26 | 2024-10-26 22:50 | 0.010699 | 0.00012788 | 6 | 502 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 340 | 2024-11-27-0362 | Paekakariki - 96 Tilley Rd | Z165 | 2024-11-26 08:20 | 2024-11-26 16:22 | 2.4347 | 0.0050513 | 237 | 114234 | Planned | Planned interruption | Switching Schedule 92425 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 341 | 2025-03-28-0367 | Waikanae - 18 Parata St | 662 | 2025-03-27 08:11 | 2025-03-27 14:41 | 0.29093 | 0.00074597 | 35 | 13650 | Planned | Planned interruption | Ngarara Rd Waikanae 11KV Reconductoring and pole changes Stage 2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 342 | 2024-04-27-0345 | Waikanae - 18 Parata St | 622 | 2024-04-27 11:28 | 2024-04-27 12:17 | 0.041689 | 0.00087385 | 41 | 1956 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 343 | 2024-06-27-0377 | Foxton - 13 Union St | C2 | 2024-06-27 10:34 | 2024-06-27 13:16 | 0.031075 | 0.00019182 | 9 | 1458 | Planned | Planned interruption | Foxton Shannon Rd - Install lightning arrestors at Tx B171 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 344 | 2024-06-27-0373 | Levin East - 69 Tararua Rd | G308 | 2024-06-27 07:10 | 2024-06-27 08:30 | 0.0099746 | 0.00017051 | 8 | 468 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 345 | 2024-07-27-0493 | Waikanae - 18 Parata St | 672 | 2024-07-27 06:12 | 2024-07-27 07:50 | 0.14621 | 0.0014919 | 70 | 6860 | Planned | Planned interruption | Switching 90351 - 1 Island View Tce Waikanae beach - Re terminate HV cable in TX T220 due to PD and cables touching in 11KV Transformer bay. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 346 | 2024-07-27-0492 | Otaki - 15 Riverbank Rd | L351 | 2024-07-27 07:23 | 2024-07-27 13:03 | 0.021761 | 6.394e-05 | 3 | 1021 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 347 | 2024-09-27-0477 | Waikanae - 18 Parata St | 632 | 2024-09-27 08:48 | 2024-09-27 09:46 | 0.0037511 | 2.1313e-05 | 1 | 176 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 348 | 2024-09-27-0483 | Shannon - 22 Stafford St | 119 | 2024-09-27 11:40 | 2024-09-27 12:40 | 0.01023 | 0.00017051 | 8 | 480 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 349 | 2024-11-27-0358 | Levin West - 270 Kawiu Rd | E153 | 2024-11-27 08:49 | 2024-11-27 15:50 | 0.29611 | 0.00070334 | 33 | 13893 | Planned | Planned interruption | Replace defective N/O ABS E376 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 350 | 2024-12-05-0042 | Paekakariki - 96 Tilley Rd | Z167 | 2024-11-27 07:00 | 2024-11-27 08:32 | 0.0039217 | 4.2627e-05 | 2 | 184 | Unplanned | Other cause | Faulty Lightning arrestor on Private transformer Z418P | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 351 | 2024-12-27-0458 | Levin West - 270 Kawiu Rd | E148 | 2024-12-27 05:32 | 2024-12-27 06:34 | 0.046335 | 0.00074597 | 35 | 2174 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 352 | 2024-12-27-0465 | Levin West - 270 Kawiu Rd | E153 | 2024-12-27 12:24 | 2024-12-27 18:01 | 0.84375 | 0.01428 | 670 | 39588 | Unplanned | Adverse weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 353 | 2024-12-27-0466 | Otaki - 15 Riverbank Rd | L349 | 2024-12-27 12:50 | 2024-12-27 17:37 | 0.030542 | 0.00010657 | 5 | 1433 | Unplanned | Adverse weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 354 | 2024-12-27-0471 | Levin East - 69 Tararua Rd | G313 | 2024-12-27 14:05 | 2024-12-27 14:20 | 0.21914 | 0.015324 | 719 | 10282 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 355 | 2024-12-27-0474 | Levin East - 69 Tararua Rd | G313 | 2024-12-27 14:26 | 2024-12-27 17:13 | 1.0142 | 0.033846 | 1588 | 47584 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 356 | 2024-12-27-0475 | Paekakariki - 96 Tilley Rd | Z167 | 2024-12-27 14:42 | 2024-12-27 16:19 | 0.0041135 | 4.2627e-05 | 2 | 193 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 357 | 2025-01-28-0273 | Levin West - 270 Kawiu Rd | E150 | 2025-01-28 08:20 | 2025-01-28 12:11 | 0.039387 | 0.00017051 | 8 | 1848 | Planned | Planned interruption | Poroutawhao School Replace 11KV Pole:29594T & Remove 3 X LV Poles 37022R & 29571T & 35872R | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 358 | 2025-01-28-0274 | Paraparaumu West - 11 Arko Pl | 402 | 2025-01-28 08:31 | 2025-01-28 13:14 | 0.82634 | 0.0029199 | 137 | 38771 | Planned | Planned interruption | 2 Murray court Paraparumu Upgrade TX W117 from a 200KVA to a 300KVA | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 359 | 2025-03-28-0370 | Levin East - 69 Tararua Rd | G313 | 2025-03-28 09:00 | 2025-03-28 14:56 | 0.18969 | 0.00053283 | 25 | 8900 | Planned | Planned interruption | Gladstone Rd, Levin - Upgrade N/O ABS G117 to ENTEC & tree work | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 360 | 2024-05-28-0447 | Foxton - 13 Union St | C2 | 2024-05-28 08:56 | 2024-05-28 15:55 | 0.053582 | 0.00012788 | 6 | 2514 | Planned | Planned interruption | Switching schedule 88441 commeneced for team to replace 33kV pole changes and crossarms on various sites - Foxton Shannon Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 361 | 2024-05-28-0439 | Levin East - 69 Tararua Rd | G308 | 2024-05-28 01:41 | 2024-05-28 03:11 | 0.0076728 | 8.5253e-05 | 4 | 360 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 362 | 2024-08-28-0401 | Levin West - 270 Kawiu Rd | E153 | 2024-08-28 12:24 | 2024-08-28 14:06 | 0.01087 | 0.00010657 | 5 | 510 | Planned | Planned interruption | Transformer upgrade H351 From pole top to U/G | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 363 | 2024-09-10-0197 | Levin East - 69 Tararua Rd | G306 | 2024-08-28 08:30 | 2024-08-28 16:16 | 0.70517 | 0.0015132 | 71 | 33086 | Planned | Planned interruption | Winchester St Levin Replace 11KV Poles at Various sites | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 364 | 2024-10-28-0365 | Otaki - 15 Riverbank Rd | L351 | 2024-10-28 03:30 | 2024-10-28 08:24 | 0.018798 | 6.394e-05 | 3 | 882 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 365 | 2024-10-28-0371 | Foxton - 13 Union St | C4 | 2024-10-28 09:55 | 2024-10-28 12:09 | 0.008568 | 6.394e-05 | 3 | 402 | Unplanned | Adverse weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 366 | 2024-10-28-0375 | Waikanae - 18 Parata St | 622 | 2024-10-28 13:24 | 2024-10-28 14:02 | 0.00080991 | 2.1313e-05 | 1 | 38 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 367 | 2024-10-28-0377 | Waikanae - 18 Parata St | 622 | 2024-10-28 13:18 | 2024-10-28 13:37 | 0.00040495 | 2.1313e-05 | 1 | 19 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 368 | 2024-11-28-0371 | Paekakariki - 96 Tilley Rd | Z165 | 2024-11-28 08:15 | 2024-11-28 16:30 | 0.81042 | 0.0015985 | 75 | 38024 | Planned | Planned interruption | Wellington Rd - 11Kv Pole changes & reconducting (Stage 2) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 369 | 2024-11-28-0379 | Shannon - 22 Stafford St | 119 | 2024-11-28 19:07 | 2024-11-28 22:30 | 0.025917 | 0.00012788 | 6 | 1216 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 370 | 2024-11-28-0380 | Shannon - 22 Stafford St | 149 | 2024-11-28 19:16 | 2024-11-28 19:37 | 0.051621 | 0.0024723 | 116 | 2422 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 371 | 2024-12-28-0488 | Foxton - 13 Union St | C1 | 2024-12-28 12:28 | 2024-12-28 13:29 | 0.0039003 | 6.394e-05 | 3 | 183 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 372 | 2024-12-28-0492 | Levin West - 270 Kawiu Rd | E153 | 2024-12-28 18:07 | 2024-12-28 19:01 | 0.0034314 | 6.394e-05 | 3 | 161 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 373 | 2025-01-29-0287 | Paraparaumu East - 42 Tongariro St | V313 | 2025-01-29 10:27 | 2025-01-29 11:36 | 0.013236 | 0.00019182 | 9 | 621 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 374 | 2025-03-29-0388 | Foxton - 13 Union St | C3 | 2025-03-29 16:37 | 2025-03-29 18:34 | 0.014855 | 0.00019182 | 9 | 697 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 375 | 2024-05-02-0035 | Levin East - 69 Tararua Rd | G306 | 2024-04-29 08:49 | 2024-04-29 10:00 | 0.0015132 | 2.1313e-05 | 1 | 71 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 376 | 2024-05-29-0464 | Shannon - 22 Stafford St | 129 | 2024-05-29 10:11 | 2024-05-29 12:12 | 0.0077367 | 6.394e-05 | 3 | 363 | Planned | Planned interruption | Commenced Switching Schedule for team to install lightening arrestors on TX E240 in 158 Vickerman's Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 377 | 2024-06-29-0401 | Otaki - 15 Riverbank Rd | L348 | 2024-06-29 09:00 | 2024-06-29 10:33 | 0.059464 | 0.0006394 | 30 | 2790 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 378 | 2024-07-29-0520 | Otaki - 15 Riverbank Rd | L349 | 2024-07-29 10:38 | 2024-07-29 13:52 | 0.045483 | 0.00023445 | 11 | 2134 | Planned | Planned interruption | 938 Main Rd north, Manakau - Replace PMT L218 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 379 | 2024-08-29-0410 | Levin West - 270 Kawiu Rd | E150 | 2024-08-29 09:23 | 2024-08-29 11:20 | 0.0049873 | 4.2627e-05 | 2 | 234 | Planned | Planned interruption | Lewis Farms - Install 11M Pole & 50KVA PMTX & DDO's | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 380 | 2024-08-29-0411 | Otaki - 15 Riverbank Rd | L348 | 2024-08-29 09:15 | 2024-08-29 14:20 | 0.078007 | 0.00025576 | 12 | 3660 | Planned | Planned interruption | 2Old Coach Rd, Otaki - 11Kv reconducting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 381 | 2024-08-29-0426 | Otaki - 15 Riverbank Rd | L349 | 2024-08-29 17:12 | 2024-08-29 18:18 | 0.033355 | 0.00051152 | 24 | 1565 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 382 | 2024-08-29-0428 | Otaki - 15 Riverbank Rd | L352 | 2024-08-29 18:54 | 2024-08-29 20:39 | 0.01347 | 0.00012788 | 6 | 632 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 383 | 2024-09-04-0086 | Foxton - 13 Union St | C4 | 2024-08-29 16:45 | 2024-08-29 17:58 | 0.051557 | 0.0024084 | 113 | 2419 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 384 | 2024-10-02-0016 | Levin East - 69 Tararua Rd | G306 | 2024-09-29 14:29 | 2024-09-29 15:57 | 1.3359 | 0.03067 | 1439 | 62678 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 385 | 2024-10-29-0393 | Waikanae - 18 Parata St | 652 | 2024-10-29 10:22 | 2024-10-29 11:41 | 0.039813 | 0.00051152 | 24 | 1868 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 386 | 2025-01-30-0298 | Shannon - 22 Stafford St | 149 | 2025-01-30 10:55 | 2025-01-30 13:06 | 0.002792 | 2.1313e-05 | 1 | 131 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 387 | 2024-04-30-0381 | Levin East - 69 Tararua Rd | G308 | 2024-04-30 09:05 | 2024-04-30 13:50 | 0.2369 | 0.00083122 | 39 | 11115 | Planned | Planned interruption | Commenced Schedule for team to replace 11kV crossarms on Kuku East Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 388 | 2024-04-30-0380 | Waikanae - 18 Parata St | 652 | 2024-04-30 08:49 | 2024-04-30 11:16 | 0.0062661 | 4.2627e-05 | 2 | 294 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 389 | 2024-08-30-0441 | Levin East - 69 Tararua Rd | G308 | 2024-08-30 09:35 | 2024-08-30 15:26 | 0.044886 | 0.00012788 | 6 | 2106 | Planned | Planned interruption | 30Parakawau Rd, Ohau - Remove tx H68 & 11Kv Poles & 11Kv conductor & Replace 11Kv Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 390 | 2024-09-30-0519 | Paekakariki - 96 Tilley Rd | Z167 | 2024-09-30 09:43 | 2024-09-30 15:35 | 0.10145 | 0.00029839 | 14 | 4760 | Planned | Planned interruption | QE Park - Replace ABS Z222 & 11Kv links Z171 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 391 | 2024-10-30-0406 | Otaki - 15 Riverbank Rd | L349 | 2024-10-30 08:30 | 2024-10-30 13:34 | 0.44221 | 0.0016198 | 76 | 20748 | Planned | Planned interruption | Waikawa Beach Rd - Replace 11Kv arms at various sites | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 392 | 2024-10-30-0408 | Otaki - 15 Riverbank Rd | L352 | 2024-10-30 10:04 | 2024-10-30 10:52 | 0.0051578 | 0.00010657 | 5 | 242 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 393 | 2024-12-30-0499 | Otaki - 15 Riverbank Rd | L349 | 2024-12-30 06:51 | 2024-12-30 10:05 | 0.014664 | 0.00010657 | 5 | 688 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 394 | 2024-12-30-0506 | Levin West - 270 Kawiu Rd | E148 | 2024-12-30 13:41 | 2024-12-30 15:37 | 0.0064366 | 6.394e-05 | 3 | 302 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 395 | 2024-12-30-0510 | Levin West - 270 Kawiu Rd | E148 | 2024-12-30 20:38 | 2024-12-30 22:15 | 0.072103 | 0.00074597 | 35 | 3383 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 396 | 2024-12-30-0514 | Levin West - 270 Kawiu Rd | E150 | 2024-12-30 21:20 | 2024-12-30 23:02 | 0.016838 | 0.00019182 | 9 | 790 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 397 | 2024-12-30-0520 | Levin West - 270 Kawiu Rd | E148 | 2024-12-30 22:50 | 2024-12-31 00:01 | 0.0072465 | 0.00027707 | 13 | 340 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 398 | 2025-02-05-0056 | Shannon - 22 Stafford St | 119 | 2025-01-31 20:17 | 2025-01-31 23:32 | 0.20137 | 0.0023232 | 109 | 9448 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 399 | 2025-03-31-0406 | Shannon - 22 Stafford St | 119 | 2025-03-31 10:08 | 2025-03-31 14:20 | 0.05371 | 0.00021313 | 10 | 2520 | Planned | Planned interruption | 37 Nikau St Tokomaru - Replace 11KV Cross arms at pole:48207Y | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 400 | 2024-05-31-0498 | Levin West - 270 Kawiu Rd | E153 | 2024-05-31 09:08 | 2024-05-31 15:10 | 0.0077154 | 2.1313e-05 | 1 | 362 | Planned | Planned interruption | Commenced Schedule for team to change 11kV crossarm and LV tidy up in Hokio Beach Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 401 | 2024-05-31-0506 | Foxton - 13 Union St | C4 | 2024-05-31 08:58 | 2024-05-31 12:15 | 0.025512 | 0.00049021 | 23 | 1197 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 402 | 2024-06-01-0003 | Shannon - 22 Stafford St | 149 | 2024-05-31 18:17 | 2024-05-31 18:41 | 0.001023 | 4.2627e-05 | 2 | 48 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 403 | 2024-07-31-0549 | Raumati - 133 Matai Rd | Z210 | 2024-07-31 09:02 | 2024-07-31 15:19 | 0.26516 | 0.00070334 | 33 | 12441 | Planned | Planned interruption | Switching 90075 - Old SH1 Raumati Replace 11KV ABS Z16 & Remove old 11KV Line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 404 | 2024-07-31-0551 | Shannon - 22 Stafford St | 149 | 2024-07-31 10:10 | 2024-07-31 12:22 | 0.0084401 | 6.394e-05 | 3 | 396 | Planned | Planned interruption | 788 Opiki Rd - Install lightning arrestors at Tx B154 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 405 | 2024-10-31-0417 | Shannon - 22 Stafford St | 119 | 2024-10-31 09:01 | 2024-10-31 14:21 | 0.21486 | 0.00070334 | 33 | 10081 | Planned | Planned interruption | Swiching 91675A - Kaihinua Rd Shannon Replace 11KV Bypass ABS A50 and 11KV Cross arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 406 | 2024-12-31-0521 | Levin West - 270 Kawiu Rd | E148 | 2024-12-31 04:18 | 2024-12-31 04:59 | 0.0026002 | 6.394e-05 | 3 | 122 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 407 | 2024-12-31-0522 | Levin West - 270 Kawiu Rd | E148 | 2024-12-31 05:04 | 2024-12-31 05:12 | 0.0015346 | 0.00019182 | 9 | 72 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 408 | 2024-12-31-0523 | Levin West - 270 Kawiu Rd | E150 | 2024-12-31 08:29 | 2024-12-31 09:34 | 0.0013854 | 2.1313e-05 | 1 | 65 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 409 | 2024-12-31-0524 | Levin West - 270 Kawiu Rd | E148 | 2024-12-31 08:47 | 2024-12-31 15:03 | 0.024041 | 6.394e-05 | 3 | 1128 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 410 | 2024-12-31-0526 | Foxton - 13 Union St | C3 | 2024-12-31 09:52 | 2024-12-31 15:21 | 0.0070334 | 2.1313e-05 | 1 | 330 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electra | 2025 |  | 411 | 2024-12-31-0527 | Foxton - 13 Union St | C3 | 2024-12-31 09:51 | 2024-12-31 11:04 | 0.0015559 | 2.1313e-05 | 1 | 73 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 9 | 94236-94236 | 113/2 Lewis E Of Dee (2) | Leven St 12 LEV 12 | 2024-04-08 23:04 | 2024-04-08 23:10 | 0.014897 | 0.0024828 | 44 | 6 | Planned | Planned interruption | Upgrade - Cable testing | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 10 | 94083-94083 | 371/3 Tay W Of Stuart (3) | Racecourse Rd 8 RRD 8 | 2024-04-09 09:32 | 2024-04-09 13:22 | 0.012978 | 5.6427e-05 | 1 | 230 | Unplanned | Other cause | Upgrade - Safety isolation - LV Board alterations & New LV fuse installation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 11 | 94139-94139 | Spey St 8 | Spey St 8 SPY 8 | 2024-04-16 08:00 | 2024-04-16 14:51 | 2.4583 | 0.0059813 | 106 | 411 | Planned | Planned interruption | Ring main unit maintenance - Service Ring main unit | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 12 | 94300-94300 | 869/1 Forfar Cres Reserve | Racecourse Rd 6 RRD 6 | 2024-05-07 08:31 | 2024-05-07 14:00 | 1.0025 | 0.0030471 | 54 | 329 | Planned | Planned interruption | Upgrade - Replace Transformer LV board | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 13 | 94303-94303 | 358/2 Inglewood N Of Otepuni (2) | Southern 8 SOU 8 | 2024-05-07 08:54 | 2024-05-07 11:09 | 1.2874 | 0.0095362 | 169 | 135 | Planned | Planned interruption | Upgrade - Ring main unit maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 14 | 94317-94317 | 357/4 Otepuni At Lindisfarne (4) | Southern 9 SOU 9 | 2024-05-08 19:31 | 2024-05-09 03:01 | 0.50784 | 0.0011285 | 20 | 450 | Planned | Planned interruption | Upgrade - Ring main unit maintnenace | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 15 | 94317-94318 | 835/2 Prospect W Of Inglewood | Southern 8 SOU 8 | 2024-05-08 19:32 | 2024-05-09 03:04 | 0.58662 | 0.0012978 | 23 | 452 | Planned | Planned interruption | Upgrade - Replace poles & wires | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 16 | 94334-94334 | 533/2 Tay E Of Jed | Spey St 14 SPY 14 | 2024-05-12 23:00 | 2024-05-13 03:16 | 0.30335 | 0.001185 | 21 | 256 | Planned | Planned interruption | Upgrade - Ring main unit maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 17 | 94469-94469 | Leven St 11 | Leven St 11 LEV 11 | 2024-05-22 09:21 | 2024-05-22 11:52 | 0.0085205 | 5.6427e-05 | 1 | 151 | Unplanned | Other cause | Upgrade - Remove transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 18 | 94567-94567 | 305/3 Yarrow W Of Adamson Cres East | Spey St 11 SPY 11 | 2024-06-05 08:02 | 2024-06-05 13:45 | 1.4129 | 0.0041192 | 73 | 343 | Planned | Planned interruption | Service ring main unit - Ring main unit maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 19 | 94567-94567 | 305/4 Yarrow W Of Adamson Cres East | Spey St 11 SPY 11 | 2024-06-05 08:02 | 2024-06-05 13:50 | 1.9833 | 0.0056991 | 101 | 348 | Planned | Planned interruption | Service ring main unit - Ring main unit maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 20 | 94602-94602 | 320/3 Yarrow Opp Lithgow St (3) | Racecourse Rd 8 RRD 8 | 2024-06-09 07:00 | 2024-06-09 09:46 | 0.51518 | 0.0031035 | 55 | 166 | Planned | Planned interruption | Service ring main unit - Ring main unit maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 21 | 94631-94631 | 445/2 Bute St (2) | Leven St 13 LEV 13 | 2024-06-12 20:00 | 2024-06-13 00:36 | 0.59181 | 0.0021442 | 38 | 276 | Planned | Planned interruption | Upgrade - Remove redundant transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 22 | 94689-94689 | 358/2 Inglewood N Of Otepuni (2) | Southern 8 SOU 8 | 2024-06-18 08:23 | 2024-06-18 14:53 | 3.7411 | 0.0095926 | 170 | 390 | Planned | Planned interruption | Serive ring main unit - Ring main unit maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 23 | 94704-94704 | Do 123951 | Ocean Beach BFE 2 | 2024-06-19 08:09 | 2024-06-19 15:30 | 0.84607 | 0.0019185 | 34 | 441 | Planned | Planned interruption | New connection - New transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 24 | 94706-94706 | Leven St 7 | Leven St 7 LEV 7 | 2024-06-19 17:53 | 2024-06-19 21:37 | 0.050559 | 0.00022571 | 4 | 224 | Planned | Planned interruption | Service ring main unit - Ring main unit maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 25 | 94731-94731 | 501/2 Kmart Forth St (2) | Spey St 9 SPY 9 | 2024-06-23 07:32 | 2024-06-23 10:53 | 0.056709 | 0.00028214 | 5 | 201 | Planned | Planned interruption | Service ring main unit - Ring main unit mainteance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 26 | 94742-94742 | 250/2 Earn East Of Conon(2) | Leven St 11 LEV 11 | 2024-06-25 08:17 | 2024-06-25 11:32 | 0.92427 | 0.0047399 | 84 | 195 | Planned | Planned interruption | Service ring main unit - Ring main unit maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 27 | 94750-94750 | 967 Liffey S. Of Bann | Bluff Borough BFE 1 | 2024-06-26 09:45 | 2024-06-26 11:16 | 0.35944 | 0.0039499 | 70 | 91 | Unplanned | Unknown | Unknown - CB Tripped | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 28 | 94750-94750 | Shannon St S Of Gore St | Bluff Borough BFE 1 | 2024-06-26 09:45 | 2024-06-26 11:00 | 0.84641 | 0.011285 | 200 | 75 | Unplanned | Unknown | Unknown - CB Tripped | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 29 | 94750-94750 | Bann St Cb Bann St Cb | Bluff Borough BFE 1 | 2024-06-26 09:45 | 2024-06-26 09:53 | 0.16522 | 0.020652 | 366 | 8 | Unplanned | Unknown | Unknown - CB Tripped | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 30 | 94750-94750 | 962 Bann E Of Liffey 962 | Bluff Borough BFE 1 | 2024-06-26 09:45 | 2024-06-26 11:27 | 0.65613 | 0.0064327 | 114 | 102 | Unplanned | Unknown | Unknown - CB Tripped | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 31 | 94750-94750 | Bluff Borough | Bluff Borough BFE 1 | 2024-06-26 09:45 | 2024-06-26 10:45 | 0.074484 | 0.0012414 | 22 | 60 | Unplanned | Unknown | Unknown - CB Tripped | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 32 | 94750-94750 | 961 Bann W Of Liffey | Bluff Borough BFE 1 | 2024-06-26 09:45 | 2024-06-26 11:14 | 0.14564 | 0.0016364 | 29 | 89 | Unplanned | Unknown | Unknown - CB Tripped | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 33 | 94750-94750 | 929/1 Suir N Of Ocean Beach Rd (1) | Bluff Borough BFE 1 | 2024-06-26 09:45 | 2024-06-26 09:55 | 0.030471 | 0.0030471 | 54 | 10 | Unplanned | Unknown | Unknown - CB Tripped | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 34 | 94768-94768 | 929/1 Suir N Of Ocean Beach Rd (1) | Bluff Borough BFE 1 | 2024-06-27 18:32 | 2024-06-27 18:47 | 0.046552 | 0.0031035 | 55 | 15 | Unplanned | Defective equipment | Deterioration - Failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 35 | 94768-94768 | Bluff Borough | Bluff Borough BFE 1 | 2024-06-27 18:32 | 2024-06-27 22:13 | 0.28682 | 0.0012978 | 23 | 221 | Unplanned | Defective equipment | Deterioration - Failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 36 | 94768-94768 | Bluff Borough | Bluff Borough BFE 1 | 2024-06-27 18:32 | 2024-06-27 19:52 | 0.099312 | 0.0012414 | 22 | 80 | Unplanned | Defective equipment | Deterioration - Failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 37 | 94768-94768 | 961 Bann W Of Liffey | Bluff Borough BFE 1 | 2024-06-27 18:32 | 2024-06-27 20:20 | 1.2798 | 0.01185 | 210 | 108 | Unplanned | Defective equipment | Deterioration - Failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 38 | 94768-94768 | Shannon St S Of Gore St | Bluff Borough BFE 1 | 2024-06-27 18:32 | 2024-06-27 20:54 | 1.3942 | 0.0098183 | 174 | 142 | Unplanned | Defective equipment | Deterioration - Failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 39 | 94768-94768 | Bluff Borough | Bluff Borough BFE 1 | 2024-06-27 20:17 | 2024-06-27 20:19 | 0.0024828 | 0.0012414 | 22 | 2 | Unplanned | Defective equipment | Deterioration - Failed insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 40 | 94805-94805 | 490/2 Pumping Stn, Stead St (2) | Leven St 13 LEV 13 | 2024-07-01 08:15 | 2024-07-04 09:40 | 0.74568 | 0.00016928 | 3 | 4405 | Unplanned | Other cause | New connection - Relocate RMU & transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 41 | 94805-94805 | 490/2 Pumping Stn, Stead St (2) | Leven St 13 LEV 13 | 2024-07-04 07:43 | 2024-07-04 09:40 | 0.019806 | 0.00016928 | 3 | 117 | Unplanned | Other cause | New connection - Relocate RMU & transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 42 | 94810-94810 | 266/4 Eye W Of Nith (4) | Spey St 9 SPY 9 | 2024-07-04 09:20 | 2024-07-04 13:22 | 0.040966 | 0.00016928 | 3 | 242 | Unplanned | Defective equipment | Deterioration - Failed transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 43 | 94810-94810 | 266/3 Eye W Of Nith (3) | Spey St 9 SPY 9 | 2024-07-04 12:39 | 2024-07-04 12:48 | 0.026916 | 0.0029906 | 53 | 9 | Unplanned | Defective equipment | Deterioration - Failed transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 44 | 94838-94838 | 163/3 Ramrig N Of Lewis (3) | Spey St 10 SPY 10 | 2024-07-09 08:12 | 2024-07-09 11:10 | 0.5022 | 0.0028214 | 50 | 178 | Planned | Planned interruption | Upgrade - RMU maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 45 | 94843-94843 | 642/3 Salford S Of Lamond | Racecourse Rd 12 RRD 12 | 2024-07-09 08:22 | 2024-07-09 14:51 | 2.4145 | 0.006207 | 110 | 389 | Planned | Planned interruption | Upgrade - RMU maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 46 | 94838-94838 | 163/4 Ramrig N Of Lewis (4) | Spey St 10 SPY 10 | 2024-07-09 08:28 | 2024-07-09 11:15 | 0.0094233 | 5.6427e-05 | 1 | 167 | Planned | Planned interruption | Upgrade - RMU maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 47 | 95197-95197 | Leven St 13 | Leven St 13 LEV 13 | 2024-08-20 10:27 | 2024-08-20 11:02 | 0.38511 | 0.011003 | 195 | 35 | Unplanned | Third party interference | Third party vehicle - Broken pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 48 | 95197-95197 | 405 Mersey N. Of Bond Pl. | Leven St 13 LEV 13 | 2024-08-20 10:27 | 2024-08-20 15:19 | 0.2142 | 0.00073355 | 13 | 292 | Unplanned | Third party interference | Third party vehicle - Broken pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 49 | 95248-95248 | Do 16025 | Ocean Beach BFE 2 | 2024-08-26 20:34 | 2024-08-27 05:05 | 0.086503 | 0.00016928 | 3 | 511 | Planned | Planned interruption | Upgrade - Install earthing points | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 50 | 95248-95248 | 973 Foreshore Rd | Ocean Beach BFE 2 | 2024-08-26 20:34 | 2024-08-26 22:34 | 0.27085 | 0.0022571 | 40 | 120 | Planned | Planned interruption | Upgrade - Install earthing points | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 51 | 95292-95292 | 404 Bond Pl. W. Of Mersey (404). | Leven St 13 LEV 13 | 2024-09-01 08:31 | 2024-09-01 10:09 | 0.094007 | 0.00095926 | 17 | 98 | Planned | Planned interruption | Upgrade - Repair switch | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 52 | 95292-95292 | 436 Mersey At Spey | Leven St 13 LEV 13 | 2024-09-01 08:35 | 2024-09-01 10:14 | 0.055863 | 0.00056427 | 10 | 99 | Planned | Planned interruption | Upgrade - Repair switch | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 53 | 95344-95344 | Leven St 9 | Leven St 9 LEV 9 | 2024-09-03 15:00 | 2024-09-03 18:57 | 0.013373 | 5.6427e-05 | 1 | 237 | Planned | Planned interruption | Fleet plan - Transformer maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 54 | 95344-95344 | 431/1 Sth Construction Co Bond St | Leven St 9 LEV 9 | 2024-09-03 15:03 | 2024-09-03 18:57 | 0.026408 | 0.00011285 | 2 | 234 | Planned | Planned interruption | Fleet plan - Transformer maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 55 | 95409-95409 | Do 14529 | Bluff Borough BFE 1 | 2024-09-07 11:31 | 2024-09-07 12:09 | 0.038596 | 0.0010157 | 18 | 38 | Unplanned | Defective equipment | Deterioration - Failed lead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 56 | 95481-95481 | 685/1 Bourke E Of Windsor | Spey St 11 SPY 11 | 2024-09-10 22:33 | 2024-09-11 01:35 | 0.80104 | 0.0044013 | 78 | 182 | Planned | Planned interruption | Fleet plan - RMU 680 maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 57 | 95496-95496 | 995 Gore E Of Shannon | Ocean Beach BFE 2 | 2024-09-13 13:36 | 2024-09-13 13:53 | 0.10552 | 0.006207 | 110 | 17 | Unplanned | Other cause | Allow high load to pass - High load | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 58 | 95505-95505 | Leven St 11 | Leven St 11 LEV 11 | 2024-09-14 08:00 | 2024-09-14 12:44 | 0.016025 | 5.6427e-05 | 1 | 284 | Unplanned | Other cause | 5 Yearly maintenance - Service transformer & testing | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 59 | 95509-95509 | Do 15854 | Leven St 9 LEV 9 | 2024-09-15 08:14 | 2024-09-15 12:04 | 0.10383 | 0.00045142 | 8 | 230 | Planned | Planned interruption | Fleet plan - Transformer maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 60 | 95624-95624 | Southern 8 | Southern 8 SOU 8 | 2024-09-25 18:00 | 2024-09-25 19:36 | 0.027085 | 0.00028214 | 5 | 96 | Unplanned | Other cause | Upgrade - To replace LV fuseway | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 61 | 95642-95642 | 174/2 Liffey S Of Thames(2) | Leven St 12 LEV 12 | 2024-09-29 06:00 | 2024-09-29 08:28 | 0.016702 | 0.00011285 | 2 | 148 | Planned | Planned interruption | Upgrade - RMU Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 62 | 95667-95667 | 995 Gore E Of Shannon | Ocean Beach BFE 2 | 2024-10-02 09:05 | 2024-10-02 15:24 | 2.3524 | 0.006207 | 110 | 379 | Planned | Planned interruption | Upgrade - Replace poles, crossarms & insulators | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 63 | 95715-95715 | 824/3 Rockdale Rd North Of Tweed | Racecourse Rd 6 RRD 6 | 2024-10-08 08:09 | 2024-10-08 15:30 | 0.024884 | 5.6427e-05 | 1 | 441 | Planned | Planned interruption | Upgrade - Transformer maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 64 | 95718-95718 | 507/5 Conon S Of Tay | Spey St 9 SPY 9 | 2024-10-08 08:15 | 2024-10-08 10:43 | 0.0083512 | 5.6427e-05 | 1 | 148 | Planned | Planned interruption | Upgrade - Transformer maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 65 | 95721-95721 | 995 Gore E Of Shannon | Ocean Beach BFE 2 | 2024-10-08 19:10 | 2024-10-08 21:14 | 0.76966 | 0.006207 | 110 | 124 | Unplanned | Defective equipment | Deterioration - Damaged wires | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 66 | 95746-95746 | 398/2 Anglem At Museum | Southern 8 SOU 8 | 2024-10-10 17:37 | 2024-10-10 19:43 | 0.01422 | 0.00011285 | 2 | 126 | Planned | Planned interruption | Upgrade - RMU maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 67 | 95895-95895 | 974 Barrow E. Of Palmer (974) | Ocean Beach BFE 2 | 2024-10-26 17:46 | 2024-10-27 03:01 | 0.78293 | 0.0014107 | 25 | 555 | Unplanned | Defective equipment | Deterioration - Broken pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 68 | 95895-95895 | Gore St Cb | Ocean Beach BFE 2 | 2024-10-26 17:46 | 2024-10-26 19:08 | 0.27299 | 0.0033292 | 59 | 82 | Unplanned | Defective equipment | Deterioration - Broken pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 69 | 96134-96134 | Spey St 9 | Spey St 9 SPY 9 | 2024-11-21 09:28 | 2024-11-21 12:20 | 0.019411 | 0.00011285 | 2 | 172 | Unplanned | Unknown | Unknown - Blown fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 70 | 96239-96239 | Spey St 9 | Spey St 9 SPY 9 | 2024-11-30 06:58 | 2024-11-30 14:02 | 0.04785 | 0.00011285 | 2 | 424 | Unplanned | Other cause | Upgrade - New RMU | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 71 | 96381-96381 | Leven St 13 | Leven St 13 LEV 13 | 2024-12-08 07:00 | 2024-12-08 11:33 | 0.30809 | 0.0011285 | 20 | 273 | Planned | Planned interruption | Upgrade - RMU maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 72 | 96361-96361 | Bluff Borough | Bluff Borough BFE 1 | 2024-12-09 01:05 | 2024-12-09 01:29 | 0.0040627 | 0.00016928 | 3 | 24 | Unplanned | Adverse weather | High winds - Failed lead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 73 | 96383-96383 | Spey St 11 | Spey St 11 SPY 11 | 2024-12-09 09:33 | 2024-12-09 10:08 | 2.3522 | 0.067205 | 1191 | 35 | Unplanned | Defective equipment | Deterioration - Failed cable "GV" | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 74 | 96383-96383 | 685/2 Bourke E Of Windsor | Spey St 11 SPY 11 | 2024-12-09 09:33 | 2024-12-09 10:18 | 0.42151 | 0.0093669 | 166 | 45 | Unplanned | Defective equipment | Deterioration - Failed cable "GV" | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 75 | 96606-96606 | Shannon St S Of Gore St | Bluff Borough BFE 1 | 2024-12-20 15:56 | 2024-12-20 18:37 | 1.8079 | 0.011229 | 199 | 161 | Unplanned | Defective equipment | Deterioration - Broken wire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 76 | 96606-96606 | 961 Bann W Of Liffey | Bluff Borough BFE 1 | 2024-12-20 15:56 | 2024-12-20 17:08 | 0.86537 | 0.012019 | 213 | 72 | Unplanned | Defective equipment | Deterioration - Broken wire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 77 | 96606-96606 | Bluff Borough | Bluff Borough BFE 1 | 2024-12-20 15:56 | 2024-12-20 17:00 | 0.27807 | 0.0043449 | 77 | 64 | Unplanned | Defective equipment | Deterioration - Broken wire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 78 | 96606-96606 | Bann St Cb Bann St Cb | Bluff Borough BFE 1 | 2024-12-20 15:56 | 2024-12-20 16:00 | 0.082158 | 0.020539 | 364 | 4 | Unplanned | Defective equipment | Deterioration - Broken wire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 79 | 96658-96658 | 397/1 Surry Park (1) | Spey St 11 SPY 11 | 2025-01-12 07:00 | 2025-01-12 09:51 | 0.09649 | 0.00056427 | 10 | 171 | Planned | Planned interruption | Upgrade - RMU 397 maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 80 | 96715-96715 | Do 37376 | Leven St 9 LEV 9 | 2025-01-19 07:00 | 2025-01-19 10:04 | 0.010383 | 5.6427e-05 | 1 | 184 | Unplanned | Other cause | Upgrade - Replace transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 81 | 96765-96765 | 585/2 Deveron N Of Don | Spey St 12 SPY 12 | 2025-01-23 09:50 | 2025-01-23 10:02 | 0.050784 | 0.004232 | 75 | 12 | Unplanned | Defective equipment | Deterioration - Failed Halo RMU | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 82 | 96765-96766 | Leven St 6 | Leven St 6 LEV 6 | 2025-01-23 09:50 | 2025-01-23 10:02 | 0.03521 | 0.0029342 | 52 | 12 | Unplanned | Defective equipment | Deterioration - Failed Halo RMU | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 83 | 96782-96782 | Southern 9 | Southern 9 SOU 9 | 2025-01-24 17:31 | 2025-01-24 18:16 | 1.6987 | 0.03775 | 669 | 45 | Unplanned | Third party interference | Third party vehicle - Broken poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 84 | 96782-96782 | Southern 9 | Southern 9 SOU 9 | 2025-01-24 17:31 | 2025-01-25 08:34 | 0.20381 | 0.00022571 | 4 | 903 | Unplanned | Third party interference | Third party vehicle - Broken poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 85 | 96782-96782 | 357/4 Otepuni At Lindisfarne (4) | Southern 9 SOU 9 | 2025-01-24 17:31 | 2025-01-25 02:33 | 0.48934 | 0.00090283 | 16 | 542 | Unplanned | Third party interference | Third party vehicle - Broken poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 86 | 96917-96917 | Bluff Borough | Bluff Borough BFE 1 | 2025-02-10 16:01 | 2025-02-10 16:30 | 0.0049092 | 0.00016928 | 3 | 29 | Unplanned | Defective equipment | Deterioration - Failed lead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 87 | 96945-96945 | Bann St Cb Bann St Cb | Bluff Borough BFE 1 | 2025-02-12 17:28 | 2025-02-12 17:59 | 0.63672 | 0.020539 | 364 | 31 | Unplanned | Third party interference | Safety isolation - Broken wires (telecom) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 88 | 96981-96981 | 712/4 Janet W Of Elles Road | Southern 10 SOU 10 | 2025-02-16 23:00 | 2025-02-17 02:53 | 1.0649 | 0.0045706 | 81 | 233 | Planned | Planned interruption | Upgrade - RMU & transformer maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 89 | 96998-96998 | 995 Gore E Of Shannon | Ocean Beach BFE 2 | 2025-02-18 11:18 | 2025-02-18 11:34 | 0.099312 | 0.006207 | 110 | 16 | Unplanned | Other cause | Safety isolation - Allow high load to pass | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 90 | 97138-97138 | 170/1 Victoria Av Opp Thomson | Spey St 6 SPY 6 | 2025-03-02 07:00 | 2025-03-02 11:03 | 1.2066 | 0.0049656 | 88 | 243 | Planned | Planned interruption | Upgrade - RMU maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 91 | 97287-97287 | Leven St 11 | Leven St 11 LEV 11 | 2025-03-17 21:12 | 2025-03-17 22:08 | 1.8865 | 0.033687 | 597 | 56 | Unplanned | Third party interference | Third party vehicle - Car hit RMU/transformer 225 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Electricity Invercargill | 2025 | ELIN | 92 | 97287-97287 | Leven St 11 | Leven St 11 LEV 11 | 2025-03-17 21:12 | 2025-03-18 01:15 | 1.1518 | 0.0047399 | 84 | 243 | Unplanned | Third party interference | Third party vehicle - Car hit RMU/transformer 225 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 10 | 7774 | 1400 Wharerata Road | Muriwai 0905 | 2024-04-01 08:48 | 2024-04-01 10:00 | 0.0027647 | 3.8398e-05 | 1 | 72 | Unplanned | Wildlife | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 11 | N/A 9 | Tuai | Tuai Sub | 2024-04-02 11:16 | 2024-04-02 12:07 | 0.0019583 | 3.8398e-05 | 1 | 51 | Unplanned | Human Error | Whilst switching for Transpower shutdowns on the 8th Lost comms, got Genesis to switch manual (Neil) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 12 | N/A 9 | Tuai | Lake | 2024-04-02 11:16 | 2024-04-02 12:07 | 0.019583 | 0.00038398 | 10 | 510 | Unplanned | Human Error | Whilst switching for Transpower shutdowns on the 8th Lost comms, got Genesis to switch manual (Neil) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 13 | N/A 9 | Tuai | Village 2002 | 2024-04-02 11:16 | 2024-04-02 12:07 | 0.34858 | 0.0068349 | 178 | 9078 | Unplanned | Human Error | Whilst switching for Transpower shutdowns on the 8th Lost comms, got Genesis to switch manual (Neil) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 14 | N/A 9 | Tuai | Ruakituri 2003 | 2024-04-02 11:16 | 2024-04-02 12:07 | 0.31724 | 0.0062205 | 162 | 8262 | Unplanned | Human Error | Whilst switching for Transpower shutdowns on the 8th Lost comms, got Genesis to switch manual (Neil) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 15 | 28690 | Matawai / Te Karaka | Hexton-Puha 50 | 2024-04-03 07:43 | 2024-04-03 08:36 | 1.2614 | 0.038091 | 992 | 32850 | Unplanned | Defective Equipment | Broken dead end (rust) Dropped conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 16 | 3942 | Tauwhaparae Rd Tutamoe Rd | Tauwhareparae 0404 | 2024-04-03 08:33 | 2024-04-03 13:50 | 0.48689 | 0.0015359 | 40 | 6351.0586 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 17 | 3946 | Mahurangi Tiniroto Rd | Ruakituri 2003 | 2024-04-03 09:04 | 2024-04-03 15:11 | 0.14092 | 0.00038398 | 10 | 1835.7046 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 18 | 3944 | Tauwhaparae Rd Tutamoe Rd | Tauwhareparae 0404 | 2024-04-05 08:31 | 2024-04-05 14:11 | 0.52221 | 0.0015359 | 40 | 6811.0586 | Planned | Planned | Replace 11kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 19 | 6297 | 7078 Waiapu road | Makarika 0204 | 2024-04-06 08:31 | 2024-04-06 09:35 | 0.0024575 | 3.8398e-05 | 1 | 64 | Unplanned | Unknown cause | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 20 | 6657 | 836 Rangitukia Road | Tiki Tiki 0206 | 2024-04-08 08:28 | 2024-04-08 10:00 | 0.0070652 | 7.6796e-05 | 2 | 184 | Unplanned | Unknown cause | Replace TX fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 21 | 7501 | 138 Rakankaka Road | Te Arai 0906 | 2024-04-08 19:10 | 2024-04-08 20:30 | 0.021503 | 0.00026879 | 7 | 560 | Unplanned | Unknown cause | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 22 | 3951 | Morere Hill | Nuhaka 3203 | 2024-04-09 09:00 | 2024-04-09 14:59 | 0.13785 | 0.00038398 | 10 | 1795.6892 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 23 | 3945 | Matawai Rd Te Wera Rd Koranga Valley Rd Moanui Rd Tahora Rd | Matawai 1204 | 2024-04-09 09:32 | 2024-04-09 14:23 | 0.8486 | 0.0029183 | 76 | 11085.9181 | Planned | Planned | Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 24 | 6985 | 646 Tiniroto Road | Lavenham 0902 | 2024-04-10 07:37 | 2024-04-10 09:00 | 0.0095611 | 0.00011519 | 3 | 249 | Unplanned | Wildlife | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 25 | 3896A | Waimata Valley Rd Mander Rd Riverside Rd | Waimata 0903 | 2024-04-10 09:00 | 2024-04-10 15:48 | 0.50132 | 0.0012287 | 32 | 13056 | Planned | Planned | Tree removal works | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 26 | 6984 | 264 Ruakaka Road | Tiniroto 1003 | 2024-04-10 17:53 | 2024-04-11 11:00 | 0.07887 | 7.6796e-05 | 2 | 2054 | Unplanned | Wildlife | Replace HV fuse - Tiriroto road closed had to go long way round why attended day after | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 27 | 6658 | 846 Kopuapounamu Road | Awatere 0101 | 2024-04-11 07:50 | 2024-04-11 12:45 | 0.18124 | 0.00061437 | 16 | 4720 | Unplanned | Defective Equipment | Repair broken conductor J2148-J2149 & replace HV fuse links J330 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 28 | 3948 | Matawai | Matawai 1204 | 2024-04-11 08:30 | 2024-04-11 14:33 | 1.0449 | 0.0028799 | 75 | 13641.7425 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 29 | 3950 | Makaretu Rd Main Rd Te Karaka Fitzgerald Rd | Matawai 1204 | 2024-04-11 08:48 | 2024-04-11 16:38 | 0.79407 | 0.0016895 | 44 | 9520.0571 | Planned | Planned | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 30 | 28761 | Kopuapounamu Road | Awatere 0101 | 2024-04-11 11:00 | 2024-04-11 12:20 | 0.049149 | 0.00061437 | 16 | 1280 | Unplanned | Defective Equipment | Conductor rusted through | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 31 | 8012 | 395 Spooners Road | Raupunga 3101 | 2024-04-12 09:00 | 2024-04-12 13:00 | 0.027647 | 0.00011519 | 3 | 720 | Unplanned | Unknown cause | Replace Pole & TX fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 32 | 3959 | Tereparataki Waihi Rd | Frasertown 3103 | 2024-04-12 11:08 | 2024-04-12 12:55 | 0.032869 | 0.00030718 | 8 | 428.1315 | Planned | Planned | Replace Insulators | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 33 | 6983 | E77 Ngakorara Road | Waimata 0903 | 2024-04-12 14:05 | 2024-04-12 15:11 | 0.060822 | 0.00092155 | 24 | 1584 | Unplanned | Vegetation | Tree on line - removed branch replace HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 34 | N/A 7 | Ngakaroa Road | Waimata 0903 | 2024-04-12 14:05 | 2024-04-12 15:07 | 0.062666 | 0.0013823 | 36 | 1632 | Unplanned | Vegetation | Fire dept report branch on lines on fire. Isolated, removed with hot stick | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 35 | 28763 | Walsh Street | Gladstone 0607 | 2024-04-14 08:30 | 2024-04-15 17:20 | 0.21726 | 0.0035326 | 92 | 5658 | Unplanned | Defective Equipment | Cable failure up pole B425 at crutch joint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 36 | 3956 | Matawai Rd Pitcher Rd Te Karaka Poynter Rd | Te Karaka 1203 | 2024-04-14 09:01 | 2024-04-14 10:29 | 0.15206 | 0.0017279 | 45 | 1984.6654 | Planned | Planned | Install and Connect TX E1529 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 37 | 5776 | Opotoma Road, Nuhaka | Mahia 3301 | 2024-04-14 17:10 | 2024-04-14 18:30 | 0.046078 | 0.00057597 | 15 | 1200 | Unplanned | Defective Equipment | Replace DDO fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 38 | 3952 | Matawai Rd Te Wera Rd Koranga Valley Rd Moanui Rd Tahora Rd | Matawai 1204 | 2024-04-16 08:32 | 2024-04-16 15:37 | 1.0771 | 0.0025343 | 66 | 14060.5431 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 39 | 3952A | Matawai Rd Motu Rd Kerei St Raumati St Neill Rd | Matawai 1204 | 2024-04-16 08:34 | 2024-04-16 11:30 | 0.23653 | 0.0013439 | 35 | 3084.1393 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 40 | 3949 | Matawai Rd Te Wera Rd Koranga Valley Rd Moanui Rd Tahora Rd | Matawai 1204 | 2024-04-18 08:30 | 2024-04-18 15:15 | 0.93445 | 0.0027647 | 72 | 12196.4898 | Planned | Planned | Replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 41 | 7778 | 4008 Te Araroa Rd | Awatere 0101 | 2024-04-19 08:03 | 2024-04-19 08:38 | 0.0013439 | 3.8398e-05 | 1 | 35 | Unplanned | Unknown cause | Replace TX fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 42 | 3953 | Matawai Rd Te Wera Rd Koranga Valley Rd Moanui Rd Tahora Rd | Matawai 1204 | 2024-04-19 08:33 | 2024-04-19 13:12 | 0.6444 | 0.0027647 | 72 | 8416.3796 | Planned | Planned | Replace 11kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 43 | N/A 8 | SH 2 Whakaki | Nuhaka 3203 | 2024-04-19 22:35 | 2024-04-20 00:09 | 0.33433 | 0.0047998 | 125 | 8707 | Unplanned | Unknown cause | 2 fuses down @ W8167. Patrolled beyond. Nothing identified. Reloaded fuses and relivened | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 44 | 7502 | 6339 Matawai Road | Matawai 1204 | 2024-04-20 13:33 | 2024-04-20 15:30 | 0.026955 | 0.00023039 | 6 | 702 | Unplanned | Unknown cause | Replace TX fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 45 | 28777 | Waikura | Hicks Bay 0102 | 2024-04-21 07:19 | 2024-04-24 17:30 | 0.56802 | 0.00011519 | 3 | 14793 | Unplanned | Lightning | Lightning strike blew TX plus 3 jumpers. Access limited (river in flood) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 46 | 28701 | Walker Road | Ruatoria 0201 | 2024-04-21 08:00 | 2024-04-21 10:47 | 0.089775 | 0.00053757 | 14 | 2338 | Unplanned | Defective Equipment | Replaced 11kV x-arm at TX Pole J122 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 47 | 8403 | 1743 Waikura Road | Hicks Bay 0102 | 2024-04-21 17:49 | 2024-04-21 20:00 | 0.025151 | 0.00019199 | 5 | 655 | Unplanned | Lightning | Replace TX fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 48 | 84041 | 558 Te Kumi Road | Hicks Bay 0102 | 2024-04-21 20:32 | 2024-04-21 22:00 | 0.010137 | 0.00011519 | 3 | 264 | Unplanned | Unknown cause | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 49 | 7503 | 96 Baillie Road, Waimata | Waimata 0903 | 2024-04-21 20:46 | 2024-04-21 22:30 | 0.0039934 | 3.8398e-05 | 1 | 104 | Unplanned | Unknown cause | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 50 | 3960 | Ormond Valley Road | Waimata 0903 | 2024-04-22 09:03 | 2024-04-22 16:22 | 0.57313 | 0.0013055 | 34 | 7098.2549 | Planned | Planned | Tree Clearing for Eastland Treecare | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 51 | 3969 | Whakarau Rd | Matawai 1204 | 2024-04-22 09:04 | 2024-04-22 16:03 | 0.17698 | 0.00042238 | 11 | 2288.9664 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 52 | 3966 | Waihi Road | Frasertown 3103 | 2024-04-22 09:45 | 2024-04-22 16:06 | 0.27796 | 0.00072956 | 19 | 3565.0991 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 53 | 3971 | Rockhill Rd Tiniroto Rd | W O Kuri 1001 | 2024-04-22 10:56 | 2024-04-22 13:44 | 0.012902 | 7.6796e-05 | 2 | 168.0129 | Planned | Planned | Install Line markers | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 54 | 5778 | 67 Rotoparu Road | Frasertown 3103 | 2024-04-22 12:25 | 2024-04-22 12:36 | 0.0025343 | 0.00023039 | 6 | 66 | Unplanned | Unknown cause | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 55 | 28688 | Riverpoint Road | Bell 1406 | 2024-04-22 15:53 | 2024-04-22 17:01 | 0.10444 | 0.0015359 | 40 | 2720 | Unplanned | Defective Equipment | Broken x-arm @TX C205 Replaced. Crossarm identified when responding to an LV contact by excavator - 11kV was not a result of LV contact | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 56 | 28775 | Maromaaku Road | Frasertown 3103 | 2024-04-22 20:37 | 2024-04-23 10:40 | 0.16185 | 0.00019199 | 5 | 4215 | Unplanned | Adverse Weather | Repair conductor 2 wires down. Windy raining | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 57 | 3975 | Hicks Bay Te Araroa Rd Waikura | Hicks Bay 0102 | 2024-04-23 08:31 | 2024-04-23 16:57 | 3.8245 | 0.0086396 | 225 | 47504.6153 | Planned | Planned | Replace 11kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 58 | 3965 | Mangone Valley Rd Wai Station Rd | Morere 3401 | 2024-04-23 09:05 | 2024-04-23 12:58 | 0.66206 | 0.0028415 | 74 | 8652.5401 | Planned | Planned | Relocate Pole W8043 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 59 | 28776 | SH2 Iwtea | Nuhaka 3203 | 2024-04-23 13:49 | 2024-04-23 14:18 | 0.016703 | 0.00057597 | 15 | 435 | Unplanned | Defective Equipment | Replaced broken binder at Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 60 | 3955 | Riverside Road | Whangara 0506 | 2024-04-24 08:43 | 2024-04-24 14:34 | 0.17406 | 0.00049917 | 13 | 4533 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 61 | 3957 | Waiapu Rd SH 35 Kopuaroa Rd Kiekie Rd | Makarika 0204 | 2024-04-24 09:02 | 2024-04-24 14:41 | 0.19998 | 0.00061437 | 16 | 2604.6629 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 62 | 3970 | Whakarau Rd | Matawai 1204 | 2024-04-24 09:03 | 2024-04-24 15:54 | 0.1736 | 0.00042238 | 11 | 2261.4548 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 63 | 3974 | Mahurangi Rd Tiniroto Rd | Ruakituri 2003 | 2024-04-24 09:05 | 2024-04-24 14:20 | 0.12095 | 0.00038398 | 10 | 1575.6048 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 64 | 28779 | Waimata Valley Road | Waimata 0903 | 2024-04-24 20:09 | 2024-04-25 11:40 | 0.21449 | 0.00023039 | 6 | 5586 | Unplanned | Wildlife | Repairs to broken conductor between Poles G539 - G538. Conductor broke mid-span. Potential for turkey strike - Pole condition (blue tag) 11kV x-arm deteriorated badly. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 65 | 5780 | Kaiwaitau Road, Mahia | Mahia 3301 | 2024-04-25 07:47 | 2024-04-25 08:35 | 0.064509 | 0.0013439 | 35 | 1680 | Unplanned | Unknown cause | Replace HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 66 | 28801 | Aberdeen Rd / Albert St - MVA | Campion 0802 | 2024-04-26 00:21 | 2024-04-26 13:29 | 3.8671 | 0.031026 | 808 | 100712 | Unplanned | Third Party Interference | Car V's Pole B4038 - Install 300kVA Generator @ TX B440 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 67 | 3977 | Whakarau Road | Matawai 1204 | 2024-04-26 09:03 | 2024-04-26 15:30 | 0.16346 | 0.00042238 | 11 | 2129.399 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 68 | 28780 | Tiniroto Road | Tiniroto 1003 | 2024-04-26 09:25 | 2024-04-26 14:00 | 0.6328 | 0.0032638 | 85 | 16480 | Unplanned | Wildlife | Duck flew into line, clashed and burnt down. Sample brought back 7/16 Cu installed 1954 conductor 600D could see splatter marks | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 69 | 28781 | 660 Mahia Coast Road | Mahia 3301 | 2024-04-26 12:21 | 2024-04-27 12:45 | 3.8387 | 0.0096763 | 252 | 99971 | Unplanned | Third Party Interference | Person at 660 Felled tree thru line W160-W7626. W160 red tagged, sent bucket from Gisborne. Couldn't fix that night, fixed next day | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 70 | N/A 6 | Tuai Substation | Tuai Sub | 2024-04-29 06:36 | 2024-04-29 10:09 | 0.0081788 | 3.8398e-05 | 1 | 213 | Unplanned | Defective Equipment | Due to faults @ Wairoa T2 (CB112) - Opened 110kV CB172 - Intertripped 110kV CB 302 (Tuai) - Lost comms @ Tuai. Wentia (ex Napier) restored switching & supplied returned. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 71 | N/A 6 | Tuai Substation | Lake | 2024-04-29 06:36 | 2024-04-29 10:09 | 0.081788 | 0.00038398 | 10 | 2130 | Unplanned | Defective Equipment | Due to faults @ Wairoa T2 (CB112) - Opened 110kV CB172 - Intertripped 110kV CB 302 (Tuai) - Lost comms @ Tuai. Wentia (ex Napier) restored switching & supplied returned. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 72 | N/A 6 | Tuai Substation | Village 2002 | 2024-04-29 06:36 | 2024-04-29 10:09 | 1.4558 | 0.0068349 | 178 | 37914 | Unplanned | Defective Equipment | Due to faults @ Wairoa T2 (CB112) - Opened 110kV CB172 - Intertripped 110kV CB 302 (Tuai) - Lost comms @ Tuai. Wentia (ex Napier) restored switching & supplied returned. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 73 | N/A 6 | Tuai Substation | Ruakituri 2003 | 2024-04-29 06:36 | 2024-04-29 10:09 | 1.325 | 0.0062205 | 162 | 34506 | Unplanned | Defective Equipment | Due to faults @ Wairoa T2 (CB112) - Opened 110kV CB172 - Intertripped 110kV CB 302 (Tuai) - Lost comms @ Tuai. Wentia (ex Napier) restored switching & supplied returned. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 74 | 8501 | Kanakanaia Road | Kanakanaia 1202 | 2024-04-29 08:23 | 2024-04-29 10:00 | 0.026072 | 0.00026879 | 7 | 679 | Unplanned | Wildlife | Replaced HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 75 | 3972 | Whakarau Rd | Matawai 1204 | 2024-04-29 09:05 | 2024-04-29 15:13 | 0.15544 | 0.00042238 | 11 | 2024.8549 | Planned | Planned | Replace Poles, install HV fuses F2298 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 76 | 3967 | Wheatstone Road | Dalton 0502 | 2024-04-29 09:24 | 2024-04-29 11:31 | 0.029259 | 0.00023039 | 6 | 762 | Planned | Planned | Upgrade TX A1702P | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 77 | 3973 | Waiapu Rd SH35 Tokomaru Bay | Mata 0304 | 2024-04-29 09:37 | 2024-04-29 15:19 | 0.052529 | 0.00015359 | 4 | 684.1051 | Planned | Planned | Relocate Pole away from slip | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 78 | 3981 | Nuhaka Opoutama Rd | Mahia 3301 | 2024-04-29 10:00 | 2024-04-29 14:42 | 0.032485 | 0.00011519 | 3 | 180.0207 | Planned | Planned | Replace 33kV fuse base | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 79 | 5777 | 3 Raukituri Valley | Ruakituri 2003 | 2024-04-29 20:00 | 2024-04-29 21:00 | 0.023039 | 0.00038398 | 10 | 600 | Unplanned | Unknown cause | Replace TX fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 80 | 3968 | Arakihi Rd | Tauwhareparae 0404 | 2024-04-30 08:35 | 2024-04-30 14:02 | 0.025112 | 7.6796e-05 | 2 | 302.0232 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 81 | 3978 | Matawai Rd | Matawai 1204 | 2024-04-30 08:56 | 2024-04-30 13:04 | 0.047614 | 0.00019199 | 5 | 620.1728 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 82 | 3976 | Utting Rd | Waimata 0903 | 2024-04-30 09:05 | 2024-04-30 14:54 | 0.17421 | 0.00049917 | 13 | 2269.6324 | Planned | Planned | Tree Clearing | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 83 | N/A2 | Tiniroto Road, Wairoa | Frasertown 3103 | 2024-05-01 14:01 | 2024-05-01 18:34 | 0.41266 | 0.0052221 | 136 | 10747 | Unplanned | Wildlife | B&C phase wrapped at Pole W6494 - W6495. No wind. Suspect bird strike. Line next to river. (untangle with hot stick) Access difficult | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 84 | 28811 | Manuka - Totara St | Elgin 0703 | 2024-05-01 22:08 | 2024-05-02 15:15 | 2.1243 | 0.093 | 2422 | 55324 | Unplanned | Defective Equipment | Fault in cable crutch | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 85 | 3979 | Tauwhareparae Rd | Tauwhareparae 0404 | 2024-05-02 08:32 | 2024-05-02 14:21 | 0.37523 | 0.0010751 | 28 | 4891.4187 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 86 | 7780 | Kora Rd, Tikitiki | Tiki Tiki 0206 | 2024-05-02 12:33 | 2024-05-02 13:25 | 0.013977 | 0.00026879 | 7 | 364 | Unplanned | Unknown cause | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 87 | 8503 | Ngakaroa Road | Waimata 0903 | 2024-05-02 15:44 | 2024-05-02 16:30 | 0.0088315 | 0.00019199 | 5 | 230 | Unplanned | Wildlife | Replaced fuses DDO | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 88 | 3980 | Te Aroara Rd Te Hue Rd Haig Rd | Awatere 0101 | 2024-05-03 10:01 | 2024-05-03 13:49 | 0.15759 | 0.00069116 | 18 | 2053.4183 | Planned | Planned | Replace TX J214 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 89 | 8504 | Brown Beach Road | Muriwai 0905 | 2024-05-03 18:07 | 2024-05-03 19:55 | 0.024882 | 0.00023039 | 6 | 648 | Unplanned | Wildlife | Replaced DDO fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 90 | 28796 | Kanakanaia | Kanakanaia 1202 | 2024-05-04 11:38 | 2024-05-04 14:16 | 0.60235 | 0.0068732 | 179 | 15687 | Unplanned | Wildlife | Broken conductor at pole E593 after bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 91 | 5670 | Papatu Rd | Te Arai 0906 | 2024-05-05 09:25 | 2024-05-05 10:13 | 0.060822 | 0.0012671 | 33 | 1584 | Unplanned | Unknown cause | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 92 | 3984 | Matokitoki Valley Rd Cave Rd | Whangara 0506 | 2024-05-06 11:00 | 2024-05-06 12:26 | 0.13539 | 0.0015743 | 41 | 1765.7755 | Planned | Planned | Install new TX B1831 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 93 | 3989 | Haisman Rd Hansen Rd Nelson Rd Newstead Rd | Haisman 0804 | 2024-05-06 15:00 | 2024-05-06 16:00 | 0.18178 | 0.0030718 | 80 | 2372.16 | Planned | Planned | Replace 50kV / 11kV poles at Makaraka | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 94 | 3989 | Makaraka | Haisman 0804 | 2024-05-06 15:25 | 2024-05-06 15:57 | 0.08724 | 0.0027263 | 71 | 2272 | Unplanned | Defective Equipment | Low oil level in RMU C712 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 95 | 1553 | Bell Road | Bell 1406 | 2024-05-06 16:33 | 2024-05-06 16:57 | 0.0046078 | 0.00019199 | 5 | 120 | Unplanned | Defective Equipment | Low voltage on TX C5157. Tap change carried out | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 96 | 3985 | Tiniroto Rd Main Highway Gisborne | W O Kuri 1001 | 2024-05-07 08:31 | 2024-05-07 15:54 | 0.23814 | 0.00053757 | 14 | 3102.667 | Planned | Planned | Replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 97 | 8317 | Tiniroto Road | Tiniroto 1003 | 2024-05-07 16:00 | 2024-05-07 18:00 | 0.0046078 | 3.8398e-05 | 1 | 120 | Unplanned | Wildlife | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 98 | 8316 | Wharerata Road | Bell 1406 | 2024-05-07 17:13 | 2024-05-08 14:00 | 0.19153 | 0.00015359 | 4 | 4988 | Unplanned | Wildlife | Birds nest on LV Bushings Replace TX fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 99 | 28828 | Bell Road | Bell 1406 | 2024-05-08 08:28 | 2024-05-08 09:29 | 0.011711 | 0.00019199 | 5 | 305 | Unplanned | Defective Equipment | Replaced TX C5157 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 100 | 3958A | Taumata Rd | Tahora 1103 | 2024-05-08 09:00 | 2024-05-08 13:15 | 0.21349 | 0.00084476 | 22 | 2781.5325 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 101 | 28797 | 3833 Lake Road | Frasertown 3103 | 2024-05-08 09:40 | 2024-05-08 11:12 | 0.024728 | 0.00026879 | 7 | 644 | Unplanned | Defective Equipment | Replace TX W1686 - Move HV fuses from W1686 to W4493 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 102 | 3986 | Tiniroto Rd Main Highway Gisborne | W O Kuri 1001 | 2024-05-09 08:32 | 2024-05-09 15:55 | 0.23814 | 0.00053757 | 14 | 3102.667 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 103 | 3990 | Valley Rd | Haisman 0804 | 2024-05-09 09:03 | 2024-05-09 09:57 | 0.029029 | 0.00053757 | 14 | 378.2032 | Planned | Planned | Upgrade TX B3127 to 50kVA | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 104 | N/A1 | Brickworks | Brickworks 3201 | 2024-05-09 12:07 | 2024-05-09 14:08 | 2.2512 | 0.02373 | 618 | 58629 | Unplanned | Unknown cause | Weather - Wet/Windy. Patrol unable to identify potential cause | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 105 | 3991 | Kaiti Substn - Tyndall Rd, Halley St, Herchell Rd | Herschell 0501 | 2024-05-09 13:00 | 2024-05-09 13:26 | 0.11681 | 0.0044926 | 117 | 1639.2669 | Planned | Planned | AUFLS protection upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 106 | 8319 | Grant Rd | Harris 1502 | 2024-05-10 01:19 | 2024-05-10 03:00 | 0.22494 | 0.0022271 | 58 | 5858 | Unplanned | Defective Equipment | Replaced DDO - TX needs replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 107 | 28838 | Mata Rd - Fernside spur | Mata 0304 | 2024-05-10 05:19 | 2024-05-13 16:08 | 0.34777 | 0.0024575 | 64 | 9057 | Unplanned | Defective Equipment | Broken Pole H4439 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 108 | 3987 | Tiniroto Road | W O Kuri 1001 | 2024-05-10 08:37 | 2024-05-10 14:30 | 0.054218 | 0.00015359 | 4 | 706.1084 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 109 | 3989B | Haisman Rd Hansen Rd Nelson Rd Newstead Rd | Haisman 0804 | 2024-05-10 09:01 | 2024-05-10 09:57 | 0.15904 | 0.0030718 | 80 | 2075.6055 | Planned | Planned | Restoration of 11kV & 50kV poles at Makaraka | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 110 | 8322 | Browns Beach Road | Muriwai 0905 | 2024-05-11 18:18 | 2024-05-11 19:30 | 0.016588 | 0.00023039 | 6 | 432 | Unplanned | Wildlife | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 111 | 8323 | Waihua Road | Rototahi 0403 | 2024-05-12 14:56 | 2024-05-12 17:00 | 0.014284 | 0.00011519 | 3 | 372 | Unplanned | Wildlife | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 112 | 8015 | Kaiwaitau Road, Mahia | Mahia 3301 | 2024-05-12 17:00 | 2024-05-12 18:00 | 0.080636 | 0.0013439 | 35 | 2100 | Unplanned | Wildlife | Replace HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 113 | 3982 | Whakarau Road | Matawai 1204 | 2024-05-13 09:07 | 2024-05-13 15:28 | 0.029259 | 7.6796e-05 | 2 | 381.0293 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 114 | 8406 | 82 Jabson Rd | Te Arai 0906 | 2024-05-13 13:09 | 2024-05-13 15:00 | 0.012787 | 0.00011519 | 3 | 333 | Unplanned | Wildlife | Replace Isolation C2172 & TX fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 115 | 28851 | CBD | City 0602 | 2024-05-14 00:54 | 2024-05-15 19:16 | 0.38433 | 0.0051069 | 133 | 10009 | Unplanned | Defective Equipment | Cable Crutch at RMU B460 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 116 | 3988 | Tiniroto Road | W O Kuri 1001 | 2024-05-14 08:35 | 2024-05-14 15:27 | 0.22148 | 0.00053757 | 14 | 2885.5504 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 117 | 3999 | Cricklewood Road | Raupunga 3101 | 2024-05-14 09:05 | 2024-05-14 12:09 | 0.042391 | 0.00023039 | 6 | 552.2073 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 118 | 3983 | Whakarau Rd Pukekiwi Rd | Matawai 1204 | 2024-05-14 09:06 | 2024-05-14 16:19 | 0.033253 | 7.6796e-05 | 2 | 414.0318 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 119 | 28859 | Waima Street | Seaside 0302 | 2024-05-15 10:45 | 2024-05-15 11:56 | 0.19902 | 0.0028031 | 73 | 5183 | Unplanned | Vegetation | Trees in contact to 11kV OH lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 120 | 8410 | Jabson Rd | Te Arai 0906 | 2024-05-15 11:34 | 2024-05-15 13:30 | 0.013363 | 0.00011519 | 3 | 348 | Unplanned | Wildlife | Replace Isolation C2172 & TX fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 121 | 5787 | 8 Otoi Road | Raupunga 3101 | 2024-05-15 17:52 | 2024-05-15 23:30 | 0.025957 | 7.6796e-05 | 2 | 676 | Unplanned | Unknown cause | Replace TX fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 122 | 5786 | 2280 Ruapapa Road | Raupunga 3101 | 2024-05-15 18:15 | 2024-05-16 14:00 | 0.045502 | 3.8398e-05 | 1 | 1185 | Unplanned | Defective Equipment | Replaced HV fuses and replaced TX 16/5/24 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 123 | 5785 | 1151 SH2 Wairoa | Raupunga 3101 | 2024-05-15 18:36 | 2024-05-15 19:30 | 0.0020735 | 3.8398e-05 | 1 | 54 | Unplanned | Lightning | Replaced HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 124 | 5784 | Ngamotu Road | Affco 3202 | 2024-05-15 18:55 | 2024-05-15 20:00 | 0.0049917 | 7.6796e-05 | 2 | 130 | Unplanned | Lightning | Replace TX fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 125 | 5789 | 160A Tawhara Road | Borough One 3204 | 2024-05-16 07:29 | 2024-05-16 08:30 | 0.0070268 | 0.00011519 | 3 | 183 | Unplanned | Lightning | Replace HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 126 | 5792 | 546 Waireka Road | Raupunga 3101 | 2024-05-16 07:40 | 2024-05-16 13:30 | 0.013439 | 3.8398e-05 | 1 | 350 | Unplanned | Unknown cause | Replace HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 127 | 5791 | 202 Otoi Road | Raupunga 3101 | 2024-05-16 08:25 | 2024-05-16 12:30 | 0.0094075 | 3.8398e-05 | 1 | 245 | Unplanned | Unknown cause | Replace TX fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 128 | 3992 | Tiniroto Rd Main Highway | W O Kuri 1001 | 2024-05-16 08:38 | 2024-05-16 16:12 | 0.24406 | 0.00053757 | 14 | 3095.6632 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 129 | N/A3 | Whatatutu Rd | Whatatutu 1201 | 2024-05-16 10:11 | 2024-05-16 11:16 | 0.50474 | 0.0093691 | 244 | 13145 | Unplanned | Unknown cause | Line patrolled from substation to E863. No identifable fault. Pole E1928 - Insulator damaged, potential source. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 130 | 28863 | Otoi Road | Frasertown 3103 | 2024-05-16 10:39 | 2024-05-16 14:59 | 0.1198 | 0.00046078 | 12 | 3120 | Unplanned | Lightning | Transformer W446 damaged by Lightnight. Pole W446 red tagged and replaced | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 131 | 8411 | 396 Stafford Rd, Pehiri | Tahunga 1004 | 2024-05-16 11:50 | 2024-05-16 15:00 | 0.021887 | 0.00011519 | 3 | 570 | Unplanned | Unknown cause | Replace DDO fuse @ isolation pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 132 | 5790 | 5 Otoi Road | Raupunga 3101 | 2024-05-16 13:04 | 2024-05-16 14:10 | 0.0050685 | 7.6796e-05 | 2 | 132 | Unplanned | Lightning | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 133 | 28902 | Tiniroto Road | Tiniroto 1003 | 2024-05-17 00:46 | 2024-05-17 10:43 | 0.81427 | 0.0032638 | 85 | 21206 | Unplanned | Vegetation | Tree thru line D3290 - D3291 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 134 | 3993 | Tiniroto Rd Main Highway | W O Kuri 1001 | 2024-05-17 08:37 | 2024-05-17 13:19 | 0.1516 | 0.00053757 | 14 | 1975.2418 | Planned | Planned | Replace 11kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 135 | 3000 | Wainui Rd Wheatstone Rd | Tamarau 0503 | 2024-05-17 09:03 | 2024-05-17 10:14 | 0.10905 | 0.0015359 | 40 | 2840 | Planned | Planned | Straighten Pole A2335 & Re-sag line A2335-A2922 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 136 | 28869 | Valley Road | Haisman 0804 | 2024-05-17 12:39 | 2024-05-17 16:36 | 2.5622 | 0.03978 | 1036 | 66728 | Unplanned | Defective Equipment | Fuse Switch B761 faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 137 | 7782 | Anaura Bay Road, Tolaga Bay | Mata 0304 | 2024-05-17 12:39 | 2024-05-17 15:25 | 0.019122 | 0.00011519 | 3 | 498 | Unplanned | Unknown cause | Replace HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 138 | 8016 | 370 SH2 Wairoa | Nuhaka 3203 | 2024-05-18 18:00 | 2024-05-18 19:30 | 0.010367 | 0.00011519 | 3 | 270 | Unplanned | Wildlife | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 139 | 8413 | 137a Moanui Road, Matawai | Matawai 1204 | 2024-05-19 14:39 | 2024-05-19 17:30 | 0.085359 | 0.00049917 | 13 | 2223 | Unplanned | Wildlife | Remove possum and replace DDO fuse @ F292 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 140 | 6664 | Thatcher Rd, Ruatoria | Tiki Tiki 0206 | 2024-05-20 01:12 | 2024-05-20 14:35 | 0.030834 | 3.8398e-05 | 1 | 803 | Unplanned | Wildlife | Ducks/Geese in paddocks - Replace HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 141 | 3004 | State Highway 2 Haliburton Rd Kakariki Rd | Raupunga 3101 | 2024-05-20 10:00 | 2024-05-20 10:08 | 0.017202 | 0.0021503 | 56 | 224.4817 | Planned | Planned | Replace Poles - Shutdown Cancelled due to Helicopter was unable to fly. Ground team notified @ 10:07 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 142 | 28872 | Solander Street | Solander 0706 | 2024-05-20 15:16 | 2024-05-21 16:52 | 0.0072572 | 0.00023039 | 6 | 189 | Unplanned | Defective Equipment | 11kV bushing on B422 cracked. Faultman cleaned bushing. Switch soaked for 80min | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 143 | 5796 | 3 Ruakituri Road | Ruakituri 2003 | 2024-05-20 17:21 | 2024-05-20 18:30 | 0.026495 | 0.00038398 | 10 | 690 | Unplanned | Unknown cause | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 144 | 6990 | Whatatutu Rd | Whatatutu 1201 | 2024-05-20 17:45 | 2024-05-20 18:45 | 0.023039 | 0.00038398 | 10 | 600 | Unplanned | Defective Equipment | Burning DDO holder | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 145 | N/A4 | Tapuihikitia Road | Whatatutu 1201 | 2024-05-20 18:40 | 2024-05-20 19:35 | 0.018431 | 0.00038398 | 10 | 480 | Unplanned | Defective Equipment | HV Fuse link at F35 burnt out. Line patrolled no apparent cause. WO generated for replacement of HV Fuses @ F35 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 146 | 7789 | 264 Ruakaka Rd | Tiniroto 1003 | 2024-05-20 18:42 | 2024-05-20 21:45 | 0.014054 | 7.6796e-05 | 2 | 366 | Unplanned | Wildlife | Replace HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 147 | 6665 | Beach Road, Tokomaru Bay | Seaside 0302 | 2024-05-21 06:08 | 2024-05-21 17:07 | 1.2146 | 0.0018431 | 48 | 31632 | Unplanned | Vegetation | Multiple fuses blew, SD to cut trees - Replaced fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 148 | 3005 | Titarangi Rd Jackson Rd | Frasertown 3103 | 2024-05-21 09:15 | 2024-05-21 13:22 | 0.15175 | 0.00061437 | 16 | 1977.7694 | Planned | Planned | Replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 149 | 28907 | Makarika Road | Makarika 0204 | 2024-05-21 10:33 | 2024-05-21 10:53 | 0.00076796 | 3.8398e-05 | 1 | 20 | Unplanned | Defective Equipment | 11kV conductor hanging low. Possibly due to pole twisting over time | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 150 | 28908 | 4109 SH35 Whangara | Rototahi 0403 | 2024-05-21 10:43 | 2024-05-21 14:33 | 0.51204 | 0.008294 | 216 | 13335 | Unplanned | Defective Equipment | 11kV road xing brough down at Pole G2993. Deadend gave out on kidney termination | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 151 | 28909 | Beach Rd, Waima | Seaside 0302 | 2024-05-21 12:19 | 2024-05-21 17:06 | 0.52897 | 0.0018431 | 48 | 13776 | Unplanned | Vegetation | Trees in 400V tripping HV fuses on TX H80 plus other sites. ATS engaged to clear under shutdown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 152 | 7787 | 1255 Panikau Road, Whangara | Dalton 0502 | 2024-05-21 15:02 | 2024-05-21 15:24 | 0.0076028 | 0.00034558 | 9 | 198 | Unplanned | Vegetation | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 153 | 7786 | 770 Tutamoe Road, Tolaga Bay | Tauwhareparae 0404 | 2024-05-21 16:14 | 2024-05-21 22:38 | 0.16219 | 0.00042238 | 11 | 4224 | Unplanned | Vegetation | Replace HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 154 | N/A5 | SH2 Nuhaka / Morere | Morere 3401 | 2024-05-21 20:12 | 2024-05-22 10:40 | 0.87348 | 0.013746 | 358 | 22748 | Unplanned | Unknown cause | Isolated fault between CB W790 & RMU W1457. Fault not found see later switching | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 155 | 6667 | 146 Matanui Road, Tolaga Bay | Tauwhareparae 0404 | 2024-05-22 04:30 | 2024-05-22 08:15 | 0.0086396 | 3.8398e-05 | 1 | 225 | Unplanned | Lightning | Lightning night before - Replaced HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 156 | 8601 | Paparatu Road | Te Arai 0906 | 2024-05-22 07:33 | 2024-05-22 09:00 | 0.036747 | 0.00042238 | 11 | 957 | Unplanned | Adverse Weather | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 157 | 3995 | Waikura Valley Rd Te Kumi Rd | Hicks Bay 0102 | 2024-05-22 08:33 | 2024-05-22 16:18 | 0.69635 | 0.0014975 | 39 | 18135 | Planned | Planned | Replace 11kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 158 | 28910 | Raupunga | Raupunga 3101 | 2024-05-22 10:31 | 2024-05-29 12:40 | 1.2255 | 0.013862 | 361 | 31915 | Unplanned | Defective Equipment | Faulty TX | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 159 | 5795 | Cnr of Clyde Bank Road | Nuhaka 3203 | 2024-05-22 16:20 | 2024-05-22 18:30 | 0.054909 | 0.00042238 | 11 | 1430 | Unplanned | Unknown cause | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 160 | 7792 | 76 Whakatere Road, Manutuke | Te Arai 0906 | 2024-05-23 07:02 | 2024-05-23 11:43 | 0.064739 | 0.00023039 | 6 | 1686 | Unplanned | Defective Equipment | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 161 | 7791 | 17 Arero Road, Tolaga Bay | Mata 0304 | 2024-05-23 08:10 | 2024-05-23 09:58 | 0.004147 | 3.8398e-05 | 1 | 108 | Unplanned | Lightning | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 162 | 7790 | 599 Arakihi Road, Tolaga Bay | Tauwhareparae 0404 | 2024-05-23 17:33 | 2024-05-24 08:29 | 0.10321 | 0.00011519 | 3 | 2688 | Unplanned | Lightning | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 163 | 5797 | Cnr Omana Rd & SH2 | Morere 3401 | 2024-05-24 07:22 | 2024-05-24 08:30 | 0.031333 | 0.00046078 | 12 | 816 | Unplanned | Unknown cause | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 164 | 3006 | Titirangi Rd Jackson Rd | Frasertown 3103 | 2024-05-24 08:04 | 2024-05-24 15:50 | 0.2863 | 0.00061437 | 16 | 3730.2904 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 165 | 6668 | 157 Matakaoa Road | Hicks Bay 0102 | 2024-05-24 08:10 | 2024-05-24 10:45 | 0.027455 | 0.00030718 | 8 | 715 | Unplanned | Lightning | Lightning replaced fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 166 | 3997 | Waikura Valley Rd Te Kumi Rd | Hicks Bay 0102 | 2024-05-24 08:32 | 2024-05-24 12:31 | 0.35791 | 0.0014975 | 39 | 4671.0126 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 167 | 28882 | Solander Street | Solander 0706 | 2024-05-24 08:51 | 2024-05-24 16:46 | 0.0044926 | 0.00023039 | 6 | 117 | Unplanned | Defective Equipment | Low voltage fault reserfaced from earlier in week. Switchgear replaced, Tracking on Bushings All 3 Fuses NOT Tripping. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 168 | 7793 | Lake Road, Waituhi | Lavenham 0902 | 2024-05-26 06:59 | 2024-05-26 08:45 | 0.024421 | 0.00023039 | 6 | 636 | Unplanned | Wildlife | Replace HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 169 | 7794 | 209 Browns Beach Road | Muriwai 0905 | 2024-05-26 21:00 | 2024-05-26 21:40 | 0.0092155 | 0.00023039 | 6 | 240 | Unplanned | Wildlife | Replace HV Fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 170 | 6666 | 846 Kopuapounamu Road | Awatere 0101 | 2024-05-27 07:03 | 2024-05-27 07:45 | 0.025803 | 0.00061437 | 16 | 672 | Unplanned | Wildlife | Replaced HD fuse link | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 171 | 3998 | Whakarau road | Matawai 1204 | 2024-05-27 09:05 | 2024-05-27 16:06 | 0.17782 | 0.00042238 | 11 | 2283.4641 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 172 | 7795 | 2798 Ihungia Road | Mata 0304 | 2024-05-28 07:38 | 2024-05-28 10:32 | 0.066813 | 0.00038398 | 10 | 1740 | Unplanned | Unknown cause | Replace HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 173 | 3032 | Utting Rd Waimata Valley Rd | Waimata 0903 | 2024-05-28 08:55 | 2024-05-28 12:29 | 0.22417 | 0.0011135 | 29 | 5838 | Planned | Planned | Tree Cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 174 | 3008 | Cricklewood Road | Raupunga 3101 | 2024-05-28 09:38 | 2024-05-28 13:40 | 0.046462 | 0.00019199 | 5 | 605.144 | Planned | Planned | Replace Poles W3938 & W3934 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 175 | 3012 | Kowhai Pl Black St Clyde Rd | Borough One 3204 | 2024-05-28 10:04 | 2024-05-28 13:37 | 0.33533 | 0.0015743 | 41 | 4373.3743 | Planned | Planned | Replace ring main unit | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 176 | 7505 | 61 Pakowhai Road | Muriwai 0905 | 2024-05-28 14:21 | 2024-05-28 18:50 | 0.16527 | 0.00061437 | 16 | 4304 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 177 | 7506 | 200 Campbells Road, Ngatapa | Lavenham 0902 | 2024-05-29 07:30 | 2024-05-29 08:45 | 0.023039 | 0.00030718 | 8 | 600 | Unplanned | Unknown cause | Replaced fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 178 | 3009 | Lavenham Road | Waimata 0903 | 2024-05-29 08:31 | 2024-05-29 16:05 | 1.3946 | 0.0030718 | 80 | 18215.7847 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 179 | 3001 | Whakarau Rd | Matawai 1204 | 2024-05-29 09:01 | 2024-05-29 16:07 | 0.17993 | 0.00042238 | 11 | 2305.4734 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 180 | 7507 | 69 Saleyards Road | Bell 1406 | 2024-05-29 10:40 | 2024-05-29 11:30 | 0.021119 | 0.00042238 | 11 | 550 | Unplanned | Unknown cause | Replaced TX fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 181 | 7796 | 2780 Waiapu Road | Mata 0304 | 2024-05-30 07:46 | 2024-05-30 09:38 | 0.021503 | 0.00019199 | 5 | 560 | Unplanned | Unknown cause | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 182 | 3010 | Lavenham Rd Lake Rd Renner Rd Judd Rd | Lavenham 0902 | 2024-05-30 08:35 | 2024-05-30 15:09 | 0.84721 | 0.0021503 | 56 | 11055.722 | Planned | Planned | Replace 11kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 183 | 3013 | Mclean St Lahore St Sydney St Black St | Borough Two 3205 | 2024-05-30 09:01 | 2024-05-30 16:37 | 0.928 | 0.0020351 | 53 | 11922.7146 | Planned | Planned | Replace GMTX W1570 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 184 | 7509 | 1180 Arahini Road, Tolaga Bay | Tauwhareparae 0404 | 2024-05-30 14:48 | 2024-05-30 21:00 | 0.028568 | 7.6796e-05 | 2 | 744 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 185 | 28918 | Awapuni Road | Willows 0702 | 2024-05-30 15:11 | 2024-05-30 15:56 | 0.012095 | 0.00026879 | 7 | 315 | Unplanned | Defective Equipment | To replace broken dead-ends on pole B6313 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 186 | 28893 | Lake Road | Lavenham 0902 | 2024-05-30 15:18 | 2024-05-30 16:04 | 0.098913 | 0.0021503 | 56 | 2576 | Unplanned | Defective Equipment | Post insulator on ABS D322 failed during operation and broke off. Repairs made to ensure ABS D322 closed until permanent reapirs made. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 187 | 3002 | Whakarau Rd | Matawai 1204 | 2024-05-31 09:03 | 2024-05-31 15:04 | 0.15248 | 0.00042238 | 11 | 1986.3386 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 188 | 3020 | Cricklewood Road | Raupunga 3101 | 2024-05-31 09:06 | 2024-05-31 13:57 | 0.044695 | 0.00015359 | 4 | 582.0922 | Planned | Planned | Replace Pole W536 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 189 | 28926 | Tiniroto Road | Frasertown 3103 | 2024-05-31 17:19 | 2024-06-01 14:16 | 1.4202 | 0.0052221 | 136 | 36987 | Unplanned | Wildlife | Bindstrike caused side of aged x-arm to brake off and line down at pole W6476. The softwood pole has aged and needs to be replaced. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 190 | 28927 | All Patutahi Sub | Lavenham 0902 | 2024-05-31 23:00 | 2024-06-01 01:18 | 1.5694 | 0.020466 | 533 | 40872 | Unplanned | Defective Equipment | Protection fault - updated relay more sensitive to previous model | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 191 | 28927 | All Patutahi Sub | Muriwai 0905 | 2024-05-31 23:00 | 2024-05-31 23:48 | 0.72906 | 0.015858 | 413 | 18987 | Unplanned | Defective Equipment | Protection fault - updated relay more sensitive to previous model | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 192 | 28927 | All Patutahi Sub | Te Arai 0906 | 2024-05-31 23:00 | 2024-05-31 23:51 | 0.45824 | 0.0089851 | 234 | 11934 | Unplanned | Defective Equipment | Protection fault - updated relay more sensitive to previous model | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 193 | 28927 | All Patutahi Sub | Waimata 0903 | 2024-05-31 23:00 | 2024-06-01 00:37 | 1.9818 | 0.021695 | 565 | 51612 | Unplanned | Defective Equipment | Protection fault - updated relay more sensitive to previous model | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 194 | 28927 | All Patutahi Sub | Patutahi Sub 09 | 2024-05-31 23:00 | 2024-05-31 23:50 | 0.0019199 | 3.8398e-05 | 1 | 50 | Unplanned | Defective Equipment | Protection fault - updated relay more sensitive to previous model | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 195 | 7510 | 369 Kirkpatrick Rd | Waimata 0903 | 2024-06-01 08:05 | 2024-06-01 09:30 | 0.026111 | 0.00030718 | 8 | 680 | Unplanned | Unknown cause | Replaced fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 196 | 7511 | 1012 Waimata Rd | Waimata 0903 | 2024-06-01 15:26 | 2024-06-01 21:00 | 0.02565 | 7.6796e-05 | 2 | 668 | Unplanned | Unknown cause | Replaced TX fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 197 | 28931 | Ruakituri Road, Tiniroto Rd | Ruakituri 2003 | 2024-06-02 11:32 | 2024-06-04 17:06 | 0.7187 | 0.0039166 | 102 | 18717 | Unplanned | Defective Equipment | Repair/Replace broken pole @ W7509 W7510 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 198 | 8019 | 614 Waihua Valley Rd | Raupunga 3101 | 2024-06-04 09:50 | 2024-06-04 10:30 | 0.0015359 | 3.8398e-05 | 1 | 40 | Unplanned | Unknown cause | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 199 | 3014 | Hill Rd Balance St Stanford Crescent | Aberdeen 0609 | 2024-06-04 10:01 | 2024-06-04 11:08 | 0.23669 | 0.0035326 | 92 | 3092.8875 | Planned | Planned | Replace 11kV cable termination & Surge arrestors @ B5014 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 200 | 3019 | Tiniroto Rd Bushy Knoll Rd | Tiniroto 1003 | 2024-06-04 10:01 | 2024-06-04 16:29 | 0.64063 | 0.0016511 | 43 | 7731.2796 | Planned | Planned | Isolate 11kV for tree clearing | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 201 | 8018 | Mangatoto Stn | Morere 3401 | 2024-06-04 13:13 | 2024-06-04 14:00 | 0.0072188 | 0.00015359 | 4 | 188 | Unplanned | Unknown cause | Replaced HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 202 | 3962C | Waiapu Rd | Toko Tie 0401 | 2024-06-05 08:30 | 2024-06-05 14:34 | 0.041931 | 0.00011519 | 3 | 546.0674 | Planned | Planned | Relocate existing poles for new roadway | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 203 | 3003A | SH 2 Iwitea | Nuhaka 3203 | 2024-06-05 09:08 | 2024-06-05 16:20 | 0.24882 | 0.00057597 | 15 | 3091.7797 | Planned | Planned | Replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 204 | 3022 | Ohuka Rd Ebbett Rd | Ruakituri 2003 | 2024-06-06 08:32 | 2024-06-06 15:20 | 0.43866 | 0.0010751 | 28 | 5718.1412 | Planned | Planned | Tree Cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 205 | 3044 | Seddon St Park Rd Lavenham Rd Cemetery Rd Onslow Rd Atkins St Bilham St | Lavenham 0902 | 2024-06-06 09:01 | 2024-06-06 13:21 | 0.55908 | 0.0021503 | 56 | 14560 | Planned | Planned | Replace ABS D338 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 206 | 3963C | Waiapu Road | Mata 0304 | 2024-06-06 09:02 | 2024-06-06 10:15 | 0.0084092 | 0.00011519 | 3 | 109.5674 | Planned | Planned | Run fibre under power. Problem with fibre drum - Shutdown returned early | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 207 | N/A 10 | Patutahi Road | Lavenham 0902 | 2024-06-06 14:35 | 2024-06-06 15:41 | 0.41792 | 0.017241 | 449 | 10884 | Unplanned | Defective Equipment | Fault on ABS not closed propably after shutdown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 208 | 7512 | 57 Pitcher Road, Te Karaka | Te Karaka 1203 | 2024-06-07 06:31 | 2024-06-07 08:00 | 0.023922 | 0.00026879 | 7 | 623 | Unplanned | Unknown cause | Replaced isolation fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 209 | 3024 | SH 2 Iwetea | Nuhaka 3203 | 2024-06-07 09:04 | 2024-06-07 14:35 | 0.19065 | 0.00057597 | 15 | 2483.9298 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 210 | 28946 | Waihi Rd | Frasertown 3103 | 2024-06-10 03:46 | 2024-06-10 07:55 | 0.16404 | 0.00791 | 206 | 4272 | Unplanned | Defective Equipment | Conductor came off the insulator at Pole # W4591 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 211 | 28947 | Port Sub | Crawford 1504 | 2024-06-10 06:12 | 2024-06-10 06:37 | 0.90907 | 0.036363 | 947 | 23675 | Unplanned | Defective Equipment | Relay failed CB A614 tripped | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 212 | 28947 | Port Sub | Esplanade 1503 | 2024-06-10 06:12 | 2024-06-10 07:13 | 1.7052 | 0.027954 | 728 | 44408 | Unplanned | Defective Equipment | Relay failed CB A614 tripped | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 213 | 28947 | Port Sub | Port A 1501 | 2024-06-10 06:12 | 2024-06-10 06:38 | 0.19568 | 0.007526 | 196 | 5096 | Unplanned | Defective Equipment | Relay failed CB A614 tripped | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 214 | 28947 | Port Sub | Harris 1502 | 2024-06-10 06:12 | 2024-06-10 06:49 | 1.2105 | 0.032715 | 852 | 31524 | Unplanned | Defective Equipment | Relay failed CB A614 tripped | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 215 | 28950 | Tuporoa Road | Ruatoria 0201 | 2024-06-10 12:05 | 2024-06-11 14:02 | 0.28065 | 0.0014975 | 39 | 7309 | Unplanned | Defective Equipment | Replace Pole J1629. Repair broken conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 216 | N/A 11 | Tolaga Bay Sub | Rototahi 0403 | 2024-06-10 12:06 | 2024-06-10 12:18 | 0.099528 | 0.008294 | 216 | 2592 | Unplanned | Wildlife | Seagull (bird) came in contact with 50kV conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 217 | N/A 11 | Tolaga Bay Sub | Town 0402 | 2024-06-10 12:06 | 2024-06-10 12:19 | 0.10233 | 0.0078716 | 205 | 2665 | Unplanned | Wildlife | Seagull (bird) came in contact with 50kV conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 218 | N/A 11 | Tolaga Bay Sub | Toko Tie 0401 | 2024-06-10 12:06 | 2024-06-10 12:21 | 0.048382 | 0.0032254 | 84 | 1260 | Unplanned | Wildlife | Seagull (bird) came in contact with 50kV conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 219 | N/A 11 | Tolaga Bay Sub | Tauwhareparae 0404 | 2024-06-10 12:06 | 2024-06-10 12:23 | 0.095304 | 0.0056061 | 146 | 2482 | Unplanned | Wildlife | Seagull (bird) came in contact with 50kV conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 220 | 3007 | Browns Beach Rd State Highway 2 | Muriwai 0905 | 2024-06-10 12:35 | 2024-06-10 16:39 | 0.056215 | 0.00023039 | 6 | 705.1624 | Planned | Planned | Replace TX Pole C394 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 221 | 3041 | Lavenham Road | Lavenham 0902 | 2024-06-11 08:32 | 2024-06-11 16:27 | 1.0579 | 0.0022271 | 58 | 27550 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 222 | 3021 | Bloomfield Rd Riverpoint Rd | Bell 1406 | 2024-06-11 09:04 | 2024-06-11 14:28 | 0.68425 | 0.0021119 | 55 | 8928.817 | Planned | Planned | Change TX & HV fuses @ C198, C207, C490 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 223 | 3040 | State Highway 2 Haliburton Rd | Raupunga 3101 | 2024-06-11 10:00 | 2024-06-11 12:05 | 0.26879 | 0.0021503 | 56 | 7000 | Planned | Planned | Replace 11kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 224 | 3025 | Wharerata Rd | Bell 1406 | 2024-06-12 08:31 | 2024-06-12 11:34 | 0.1827 | 0.00099835 | 26 | 2329.3232 | Planned | Planned | Replace TX & TX Fuses C542 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 225 | 3056 | Patutahi Rd Onslow Rd Park Rd Seddon St | Lavenham 0902 | 2024-06-12 09:00 | 2024-06-12 10:33 | 0.21729 | 0.0024191 | 63 | 5659 | Planned | Planned | To remove ABS D1493 & jumper through 11kV | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 226 | 3059 | Kirkpatrick Rd Ellmers Rd | Waimata 0903 | 2024-06-12 09:03 | 2024-06-12 13:36 | 0.083861 | 0.00030718 | 8 | 2184 | Planned | Planned | Relocate Pole D4767 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 227 | 29007 | Kirkpatrick Rd | Waimata 0903 | 2024-06-12 12:40 | 2024-06-12 13:36 | 0.051607 | 0.00092155 | 24 | 1344 | Unplanned | Defective Equipment | Replace HV D630 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 228 | 3026 | Bloomfield Road | Bell 1406 | 2024-06-12 13:16 | 2024-06-12 15:04 | 0.062205 | 0.00057597 | 15 | 810.5184 | Planned | Planned | Replace TX & DDO @ C475 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 229 | 29008 | Awatere | Awatere 0101 | 2024-06-12 14:52 | 2024-06-12 17:20 | 0.022732 | 0.00015359 | 4 | 592 | Unplanned | Adverse Environment | Slip caused pole to move a conductor to sag close to ground | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 230 | 7191 | Lake Road | Lavenham 0902 | 2024-06-12 17:51 | 2024-06-12 19:00 | 0.015897 | 0.00023039 | 6 | 414 | Unplanned | Wildlife | Replaced DDO's | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 231 | 3042 | Lavenham Road | Lavenham 0902 | 2024-06-13 08:31 | 2024-06-13 16:07 | 2.1887 | 0.0047998 | 125 | 28636.793 | Planned | Planned | Replace 11kV/400V poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 232 | 3036 | Titirangi Rd Jackson Rd | Frasertown 3103 | 2024-06-13 08:59 | 2024-06-13 14:00 | 0.18492 | 0.00061437 | 16 | 2409.7694 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 233 | 3027 | Tucker Rd Matawai Rd College RD Brown RD | Waimata 0903 | 2024-06-13 09:05 | 2024-06-13 11:01 | 0.25389 | 0.0021887 | 57 | 3313.2358 | Planned | Planned | To replace TX D413 & DDO fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 234 | 3033 | Pehiri Rd Tahora Rd | Tahunga 1004 | 2024-06-13 10:00 | 2024-06-13 12:33 | 0.088123 | 0.00057597 | 15 | 1148.1609 | Planned | Planned | To replace kidney insulators | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 235 | 3028 | Snowsill Road | Waimata 0903 | 2024-06-13 13:04 | 2024-06-13 14:52 | 0.045617 | 0.00042238 | 11 | 594.2509 | Planned | Planned | Replace TX E52 & HV Fuses E52 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 236 | 28955 | Grey Street | Port A 1501 | 2024-06-14 03:30 | 2024-06-14 06:04 | 0.058211 | 0.00061437 | 16 | 1516 | Unplanned | Defective Equipment | Fault in RMU (Fust Switch) B1047 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 237 | 3043 | Lavenham Road | Lavenham 0902 | 2024-06-14 08:31 | 2024-06-14 14:13 | 0.89406 | 0.0027647 | 72 | 12198.2017 | Unplanned | Human Error | Changing Poles - P # 28923 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 238 | 3060 | Wharekopae Rd Main Rd | Ngatapa 1102 | 2024-06-14 09:01 | 2024-06-14 11:32 | 0.034789 | 0.00023039 | 6 | 906 | Planned | Planned | Replace pole D4039 - Post car V's pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 239 | 3030 | Ormond Valley Rd Whitmore Rd | Waimata 0903 | 2024-06-14 09:05 | 2024-06-14 12:11 | 0.23569 | 0.0012671 | 33 | 3074.0179 | Planned | Planned | Replace TX Pole E853 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 240 | 3035 | Tiniroto Road | Frasertown 3103 | 2024-06-14 09:05 | 2024-06-14 13:36 | 0.29136 | 0.0010751 | 28 | 3798.5156 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 241 | 3038 | Waiapu Rd | Mata 0304 | 2024-06-14 09:32 | 2024-06-14 13:44 | 0.038705 | 0.00015359 | 4 | 504.0922 | Planned | Planned | Excavations below 11kV for battering hill | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 242 | 28956 | Waimata Valley Road | Waimata 0903 | 2024-06-14 18:32 | 2024-06-14 22:50 | 0.45678 | 0.0032254 | 84 | 11896 | Unplanned | Vegetation | 2 Wires down E1198 - E1199 - Tree thru line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 243 | 7190 | 1180 Arakihi Road | Tauwhareparae 0404 | 2024-06-15 07:26 | 2024-06-15 09:30 | 0.0095227 | 7.6796e-05 | 2 | 248 | Unplanned | Adverse Weather | Replaced DDO's | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 244 | 7189 | Bond Road, Ormond | Waimata 0903 | 2024-06-15 20:01 | 2024-06-15 20:30 | 0.022271 | 0.00076796 | 20 | 580 | Unplanned | Wildlife | Replaced DDO's | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 245 | 3037 | Ford Road | Waimata 0903 | 2024-06-17 09:02 | 2024-06-17 10:23 | 0.037323 | 0.00046078 | 12 | 486.2239 | Planned | Planned | Straighten Pole E2258 - E2259. Resag 11kV & 400V conductors | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 246 | N/A 15 | Te Araroa Road | Awatere 0101 | 2024-06-17 10:00 | 2024-06-17 11:43 | 0.013977 | 0.010483 | 273 | 364 | Unplanned | Human Error | Wiring fault in AUFLS scheme caused CB to open when testing - CB J523 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 247 | 3048 | Back Ormond Rd Sterling Park Silverstone Pl | Haisman 0804 | 2024-06-17 10:02 | 2024-06-17 16:51 | 1.5291 | 0.0056445 | 147 | 19939.9662 | Planned | Planned | To connect 11kV cable, dismantle 11kV OH | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 248 | 3029 A | Te Araroa Road | Awatere 0101 | 2024-06-18 09:19 | 2024-06-18 15:43 | 0.53081 | 0.0013823 | 36 | 6921.5547 | Planned | Planned | Replace Pole J3363 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 249 | 1572 | Arapata Rd | Raupunga 3101 | 2024-06-18 10:19 | 2024-06-20 15:27 | 1.1351 | 0.016012 | 417 | 29562 | Unplanned | Vegetation | Trees through line @ W5588 where wires are down. Caused jaint failure at span W1719 & broke poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 250 | 3023A | Lake Rd Ruapapa Rd Titirangi Rd Rangiahua Rd Cricklewood Rd | Frasertown 3103 | 2024-06-18 11:42 | 2024-06-18 15:18 | 0.00061437 | 0.00015359 | 4 | 16 | Unplanned | Human Error | Replace hanging arm on pole TX W1647 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 251 | 3023A | Lake Rd Ruapapa Rd Titirangi Rd Rangiahua Rd Cricklewood Rd | Frasertown 3103 | 2024-06-18 11:44 | 2024-06-18 15:17 | 0.8097 | 0.0038014 | 99 | 10599.9509 | Planned | Planned | Replace hanging arm on TX pole W1647 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 252 | 3046 | Tiniroto Road Main Highway | W O Kuri 1001 | 2024-06-19 08:39 | 2024-06-19 15:44 | 0.22847 | 0.00053757 | 14 | 2976.5993 | Planned | Planned | Replace 11kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 253 | 6992 | 4876 Tiniroto Road | Tiniroto 1003 | 2024-06-19 09:19 | 2024-06-19 12:45 | 0.00791 | 3.8398e-05 | 1 | 206 | Unplanned | Lightning | Replace DDO's | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 254 | 1574 | Ngatapa | Ngatapa Sub 11 | 2024-06-19 23:12 | 2024-06-19 23:36 | 0.00092155 | 3.8398e-05 | 1 | 24 | Unplanned | Defective Equipment | H Structure D943 collapsed | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 255 | 1574 | Ngatapa | Totangi 1101 | 2024-06-19 23:12 | 2024-06-19 23:36 | 0.012902 | 0.00053757 | 14 | 336 | Unplanned | Defective Equipment | H Structure D943 collapsed | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 256 | 1574 | Ngatapa | Ngatapa 1102 | 2024-06-19 23:12 | 2024-06-19 23:36 | 0.064509 | 0.0026879 | 70 | 1680 | Unplanned | Defective Equipment | H Structure D943 collapsed | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 257 | 1574 | Ngatapa | Tahora 1103 | 2024-06-19 23:12 | 2024-06-19 23:36 | 0.13915 | 0.0057981 | 151 | 3624 | Unplanned | Defective Equipment | H Structure D943 collapsed | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 258 | 1574 | Ngatapa | W O Kuri 1001 | 2024-06-19 23:12 | 2024-06-20 00:50 | 0.17686 | 0.0018047 | 47 | 4606 | Unplanned | Defective Equipment | H Structure D943 collapsed | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 259 | 1574 | Ngatapa | Tiniroto 1003 | 2024-06-19 23:12 | 2024-06-20 00:52 | 0.47998 | 0.0047998 | 125 | 12500 | Unplanned | Defective Equipment | H Structure D943 collapsed | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 260 | 1574 | Ngatapa | Tahunga 1004 | 2024-06-19 23:12 | 2024-06-20 00:50 | 0.18439 | 0.0018815 | 49 | 4802 | Unplanned | Defective Equipment | H Structure D943 collapsed | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 261 | 1574 | Ngatapa | Parikanapa 1002 | 2024-06-19 23:12 | 2024-06-20 00:51 | 0.11404 | 0.0011519 | 30 | 2970 | Unplanned | Defective Equipment | H Structure D943 collapsed | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 262 | 1574 | Ngatapa | Pehiri Sub 10 | 2024-06-19 23:12 | 2024-06-20 00:50 | 0.003763 | 3.8398e-05 | 1 | 98 | Unplanned | Defective Equipment | H Structure D943 collapsed | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 263 | 29027 | Lloyd George Road | Tamarau 0503 | 2024-06-20 09:42 | 2024-06-20 10:56 | 0.1989 | 0.0026879 | 70 | 5180 | Unplanned | Defective Equipment | Repair broken strands mid span, cause unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 264 | 28967 | Port feeder being fed by Crawford at time of fault | Crawford 1504 | 2024-06-20 10:48 | 2024-06-20 15:51 | 1.8553 | 0.055447 | 1444 | 48318 | Unplanned | Defective Equipment | Jumper blown at ABS A4110 due to AFLS switching. Later found faulty lightening arrestor @ A6458 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 265 | 5672 | 1809 McMillan & Matawai Rd | Te Karaka 1203 | 2024-06-21 07:09 | 2024-06-21 09:45 | 0.02396 | 0.00015359 | 4 | 624 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 266 | 3049 | Tiniroto Rd Main Highway | Kanakanaia 1202 | 2024-06-21 08:30 | 2024-06-21 15:01 | 0.85466 | 0.0021887 | 57 | 11141.1824 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 267 | 3031 | Tyndall Road | Herschell 0501 | 2024-06-21 13:00 | 2024-06-21 14:23 | 0.56092 | 0.0067581 | 176 | 7353.3608 | Planned | Planned | AUFLS protection testing on CB A473 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 268 | 5673 | 82 Jobson Road | Te Arai 0906 | 2024-06-23 08:00 | 2024-06-23 09:30 | 0.010367 | 0.00011519 | 3 | 270 | Unplanned | Unknown cause | Fuse fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 269 | 29036 | Poroporo Road | Tiki Tiki 0206 | 2024-06-23 17:42 | 2024-07-02 16:55 | 1.6141 | 0.0032254 | 84 | 42036 | Unplanned | Defective Equipment | Broken conductor from J1004 to J1006. Poles/Conductor replaced. (River in-flood - no access to pole sites). Tree in River broke conductor ? TCL | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 270 | 29034 | 3km South of Nicks Head Stn Road / SH2 | Muriwai 0905 | 2024-06-23 21:46 | 2024-06-24 11:53 | 1.0827 | 0.0053373 | 139 | 28196 | Unplanned | Third Party Interference | Car V's Pole @ Pole C3561 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 271 | 3051 | Glenroy Road | Dalton 0502 | 2024-06-24 09:09 | 2024-06-24 14:17 | 0.24836 | 0.00080636 | 21 | 3236.6078 | Planned | Planned | Upgrade TX A222 & TX A435 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 272 | 5573 | 1400 Wharerata Road | Muriwai 0905 | 2024-06-24 14:57 | 2024-06-24 15:30 | 0.0012671 | 3.8398e-05 | 1 | 33 | Unplanned | Unknown cause | Replace Fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 273 | 3054 | Solander Street | Solander 0706 | 2024-06-24 16:07 | 2024-06-24 21:43 | 0.012902 | 3.8398e-05 | 1 | 336 | Unplanned | Defective Equipment | Planned - Replace Oil RMU with Gas Switch RMU B1043, B1044, B1045 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 274 | 3052 | Kanakanaia Rd Bruce Rd | Kanakanaia 1202 | 2024-06-25 08:31 | 2024-06-25 13:47 | 0.68828 | 0.0021887 | 57 | 8973.7314 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 275 | 3061 | Titirangi Rd Jackson Rd | Frasertown 3103 | 2024-06-25 09:24 | 2024-06-25 13:05 | 0.13578 | 0.00061437 | 16 | 1769.7694 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 276 | 28982 | 1673 Tiniroto Road | W O Kuri 1001 | 2024-06-25 11:45 | 2024-06-25 15:32 | 0.034865 | 0.00015359 | 4 | 908 | Unplanned | Defective Equipment | Replaced TX D173 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 277 | 29136 | Mata Road about Tuakau Road | Mata 0304 | 2024-06-25 12:28 | 2024-06-27 19:32 | 3.806 | 0.0011519 | 30 | 99120 | Unplanned | Vegetation | Tree through 11kV @ Pole H1206 (see fault sheet #9) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 278 | 28993 | Waihau Bay Road | Rototahi 0403 | 2024-06-25 15:42 | 2024-07-04 12:48 | 6.5799 | 0.044119 | 1149 | 171360 | Unplanned | Vegetation | Tress through line. Slip across road prevented access to site. Blown jumper, town feeding Rotutahi, Dalton feeding A140 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 279 | N/A 18 | Papuni Road | Ruakituri 2003 | 2024-06-25 15:54 | 2024-06-28 13:06 | 4.2521 | 0.0081404 | 212 | 110737 | Unplanned | Adverse Weather | o/c trip on W816. Line patrol & Heli patrol did not identify any obvious fault cause | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 280 | 28984 | Waimata | Waimata 0903 | 2024-06-25 16:03 | 2024-06-30 16:44 | 7.8681 | 0.0080252 | 209 | 204910 | Unplanned | Vegetation | Muitiple faults tree thru line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 281 | 29119 | Waiapu Road | Mata 0304 | 2024-06-25 17:53 | 2024-06-28 17:05 | 3.8246 | 0.0032638 | 85 | 99603 | Unplanned | Vegetation | Tree through line @ Pole G703 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 282 | 28992 | Kanakanaia Road | Kanakanaia 1202 | 2024-06-25 17:55 | 2024-06-26 09:27 | 1.2439 | 0.0057981 | 151 | 32396 | Unplanned | Vegetation | Tree thru line broke conductor & arm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 283 | N/A 14 | SH35 Waipiro Road | Inland 0301 | 2024-06-25 18:10 | 2024-06-26 14:20 | 1.1016 | 0.013823 | 360 | 28690 | Unplanned | Vegetation | Trees across lines between H62 - H2021 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 284 | 29108 | Waipiro Road | Inland 0301 | 2024-06-25 18:10 | 2024-07-02 19:29 | 2.8426 | 0.0028799 | 75 | 74029 | Unplanned | Vegetation | Trees brought down poles & lines between H2246 & H2209 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 285 | 29102 | Awapuni Road | Lytton 0701 | 2024-06-25 19:11 | 2024-06-25 20:25 | 0.17417 | 0.0027263 | 71 | 4536 | Unplanned | Vegetation | GDC trees thru line - wet & windy | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 286 | 29043 | Te Araroa & Ruatoria | Ruatoria 0201 | 2024-06-25 19:16 | 2024-06-25 19:26 | 0.11865 | 0.011865 | 309 | 3090 | Unplanned | Vegetation | Tree on 50kV line @ Pole - Photo attached | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 287 | 29043 | Te Araroa & Ruatoria | Tiki Tiki 0206 | 2024-06-25 19:16 | 2024-06-26 04:35 | 1.3187 | 0.012134 | 316 | 34344 | Unplanned | Vegetation | Tree on 50kV line @ Pole - Photo attached | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 288 | 29043 | Te Araroa & Ruatoria | Makarika 0204 | 2024-06-25 19:16 | 2024-06-27 10:45 | 0.32542 | 0.008678 | 226 | 8475 | Unplanned | Vegetation | Tree on 50kV line @ Pole - Photo attached | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 289 | 29043 | Te Araroa & Ruatoria | Te Araroa 0103 | 2024-06-25 19:16 | 2024-06-26 03:45 | 0.47921 | 0.0099835 | 260 | 12480 | Unplanned | Vegetation | Tree on 50kV line @ Pole - Photo attached | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 290 | 29043 | Te Araroa & Ruatoria | Hicks Bay 0102 | 2024-06-25 19:16 | 2024-06-26 04:11 | 1.1548 | 0.01966 | 512 | 30074 | Unplanned | Vegetation | Tree on 50kV line @ Pole - Photo attached | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 291 | 29043 | Te Araroa & Ruatoria | Awatere 0101 | 2024-06-25 19:16 | 2024-06-26 04:36 | 0.50989 | 0.01605 | 418 | 13279 | Unplanned | Vegetation | Tree on 50kV line @ Pole - Photo attached | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 292 | 28988 | Waihua | Raupunga 3101 | 2024-06-25 19:36 | 2024-06-26 16:40 | 11.8361 | 0.015436 | 402 | 308247 | Unplanned | Vegetation | Tree through lines - See 22, 27 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 293 | 29105 | Tapuaeroa | Tiki Tiki 0206 | 2024-06-25 19:45 | 2024-06-26 16:20 | 1.7619 | 0.0015359 | 40 | 45884 | Unplanned | Adverse Weather | Wires down - windy | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 294 | 29048 | Nuhaka - Mahia | Morere 3401 | 2024-06-25 20:18 | 2024-06-25 21:10 | 0.14115 | 0.010291 | 268 | 3676 | Unplanned | Adverse Weather | Multiply faults conductor clashing | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 295 | 29048 | Nuhaka - Mahia | Mahia 3301 | 2024-06-25 20:18 | 2024-06-28 13:00 | 8.1406 | 0.17698 | 4609 | 212006 | Unplanned | Adverse Weather | Multiply faults conductor clashing | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 296 | 29103 | Matokitoki Valley Road | Whangara 0506 | 2024-06-25 22:56 | 2024-06-26 14:48 | 4.8338 | 0.044926 | 1170 | 125886 | Unplanned | Defective Equipment | Faulty Lightning Arrestor @ TX B641 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 297 | N/A 12 | Entire Crawford Feeder | Crawford 1504 | 2024-06-26 00:20 | 2024-06-26 00:41 | 0.76362 | 0.036363 | 947 | 19887 | Unplanned | Defective Equipment | Fault Initally not found. Later found faulty Lightening arrestor @ A6458 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 298 | 29107 | Whatatutu Rd | Whatatutu 1201 | 2024-06-26 00:32 | 2024-07-01 15:07 | 2.6275 | 0.0051069 | 133 | 68429 | Unplanned | Vegetation | Tree across line between ABS E174 & HV links E739 - E773-E775 E777-E778 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 299 | 29114 | Ruakituri - Crosshills | Ruakituri 2003 | 2024-06-26 00:40 | 2024-06-28 17:16 | 7.8447 | 0.007142 | 186 | 204300 | Unplanned | Vegetation | Trees through line byd - Cut jumpers @ pole W7327 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 300 | N/A 17 | Kotemaori | Raupunga 3101 | 2024-06-26 04:13 | 2024-06-26 14:52 | 0.70656 | 0.0069116 | 180 | 18401 | Unplanned | Adverse Weather | Unknown feeding Raupunga - See 12, 27 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 301 | 29101 | Kings Road | Bushmere 0805 | 2024-06-26 04:46 | 2024-06-26 11:18 | 0.16557 | 0.00042238 | 11 | 4312 | Unplanned | Vegetation | Tree thru lines - high winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 302 | 29127 | Wai-O-Moko Road | Dalton 0502 | 2024-06-26 05:27 | 2024-06-29 11:38 | 2.7604 | 0.0044158 | 115 | 71889 | Unplanned | Adverse Environment | Fallen pole beyond HV links A4017 - in river. Wet & Windy - see 5 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 303 | 29115 | Puha | Puha Sub 12 | 2024-06-26 05:54 | 2024-06-26 06:12 | 0.00069116 | 3.8398e-05 | 1 | 18 | Unplanned | Defective Equipment | Broken pole stay gave way | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 304 | 29115 | Puha | Whatatutu 1201 | 2024-06-26 05:54 | 2024-06-26 06:12 | 0.16864 | 0.0093691 | 244 | 4392 | Unplanned | Defective Equipment | Broken pole stay gave way | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 305 | 29115 | Puha | Kanakanaia 1202 | 2024-06-26 05:54 | 2024-06-26 06:12 | 0.12372 | 0.0068732 | 179 | 3222 | Unplanned | Defective Equipment | Broken pole stay gave way | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 306 | 29115 | Puha | Te Karaka 1203 | 2024-06-26 05:54 | 2024-06-26 06:12 | 0.12579 | 0.0069884 | 182 | 3276 | Unplanned | Defective Equipment | Broken pole stay gave way | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 307 | 29115 | Puha | Matawai 1204 | 2024-06-26 05:54 | 2024-06-26 06:12 | 0.2661 | 0.014783 | 385 | 6930 | Unplanned | Defective Equipment | Broken pole stay gave way | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 308 | 29117 | Lake Road | Frasertown 3103 | 2024-06-26 07:47 | 2024-06-28 14:09 | 7.181 | 0.014054 | 366 | 187016 | Unplanned | Vegetation | Out of zone tree went through line broke 50/11kV Pole - see 12, 22 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 309 | N/A 19 | Wairoa Town | Borough One 3204 | 2024-06-26 08:09 | 2024-06-26 11:25 | 5.5348 | 0.056867 | 1481 | 144144 | Unplanned | Adverse Weather | a Park switch station under threath of flood waters - Off Loaded | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 310 | 28985 | SH35 Whangara Road | Dalton 0502 | 2024-06-26 09:36 | 2024-06-26 11:51 | 0.73302 | 0.0056829 | 148 | 19090 | Unplanned | Adverse Weather | Broken conductor High winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 311 | 28986 | Tansley Road | Lavenham 0902 | 2024-06-26 09:54 | 2024-06-26 12:46 | 0.066045 | 0.00038398 | 10 | 1720 | Unplanned | Adverse Weather | Broke conductor - high winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 312 | 29045 | Mata Road | Mata 0304 | 2024-06-26 10:35 | 2024-06-27 18:42 | 1.2771 | 0.00076796 | 20 | 33260 | Unplanned | Vegetation | High winds blew conductor into trees. Cleared from tree using liveline stick | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 313 | N/A 16 | All feeders | Te Araroa Sub 01 | 2024-06-26 11:06 | 2024-06-26 11:37 | 0.76339 | 0.027339 | 712 | 19881 | Unplanned | Unknown cause | Generator CB1 tripped on O/C | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 314 | 29049 | Wharerata Road | Muriwai 0905 | 2024-06-26 12:49 | 2024-06-28 17:54 | 1.9154 | 0.010214 | 266 | 49884 | Unplanned | Vegetation | Tree cleared from line @ Pole C3768 & C5992 (2 faults). Feeder stayed in for 6 min, tree found on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 315 | 29113 | Marumaru | Frasertown 3103 | 2024-06-26 12:52 | 2024-06-27 15:23 | 4.4258 | 0.002995 | 78 | 115261 | Unplanned | Vegetation | Tree through line W6021 - W6022 & W5866 - W5867 - 2 x faults | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 316 | 5571 | Hororoa Rd | Tauwhareparae 0404 | 2024-06-26 13:57 | 2024-06-29 16:00 | 0.68241 | 0.00015359 | 4 | 17772 | Unplanned | Unknown cause | Fuse fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 317 | 29110 | Mangaopono Road | Tiki Tiki 0206 | 2024-06-26 16:30 | 2024-06-30 14:57 | 0.30081 | 0.00088315 | 23 | 7834 | Unplanned | Vegetation | Tree thru line - Remove tree & repair 11kV conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 318 | 29111 | Lake Road | Frasertown 3103 | 2024-06-26 21:00 | 2024-06-28 11:36 | 2.177 | 0.016818 | 438 | 56695 | Unplanned | Vegetation | Tree through line beyond W4297 & W4300 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 319 | 29106 | Waingake | Te Arai 0906 | 2024-06-26 21:07 | 2024-06-27 17:25 | 2.6224 | 0.0038398 | 100 | 68296 | Unplanned | Adverse Weather | Broken Conductor high winds C793 - C100 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 320 | 29046 | Tauhara Valley | Brickworks 3201 | 2024-06-27 13:45 | 2024-06-27 14:46 | 0.0070268 | 0.00011519 | 3 | 183 | Unplanned | Defective Equipment | Open jumper @ TX W1591 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 321 | 29051 | Kopupounama Road | Awatere 0101 | 2024-06-27 16:14 | 2024-06-27 18:20 | 0.07741 | 0.00061437 | 16 | 2016 | Unplanned | Vegetation | Conductor brought down by tree | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 322 | 6993 | 168 Wharf road | Rototahi 0403 | 2024-06-28 11:59 | 2024-06-29 08:00 | 0.092232 | 7.6796e-05 | 2 | 2402 | Unplanned | Adverse Weather | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 323 | 29129 | Berry Road | Tiniroto 1003 | 2024-06-28 13:24 | 2024-06-29 15:14 | 0.47614 | 0.00030718 | 8 | 12400 | Unplanned | Vegetation | Tree thru line broke pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 324 | 28990 | Panikau Road | Dalton 0502 | 2024-06-28 15:17 | 2024-06-29 16:08 | 0.057251 | 3.8398e-05 | 1 | 1491 | Unplanned | Vegetation | Clear trees and repair conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 325 | 28991 | Tiniroto Road | Lavenham 0902 | 2024-06-29 09:53 | 2024-06-29 11:12 | 0.091003 | 0.0011519 | 30 | 2370 | Unplanned | Vegetation | Trees damage conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 326 | 29130 | Parikanapa Road | Parikanapa 1002 | 2024-06-29 12:22 | 2024-06-29 15:00 | 0.05921 | 0.00046078 | 12 | 1542 | Unplanned | Defective Equipment | No apparent cause for fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 327 | 28994 | Whakapunake line | Ruakituri 2003 | 2024-06-29 15:59 | 2024-06-30 12:26 | 0.047114 | 3.8398e-05 | 1 | 1227 | Unplanned | Defective Equipment | Repair broken jumper | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 328 | 5574 | 1118 Wharerata Road | Muriwai 0905 | 2024-06-30 08:36 | 2024-06-30 09:00 | 0.0055293 | 0.00023039 | 6 | 144 | Unplanned | Unknown cause | Fuse fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 329 | 5572 | 187 Berry Road | Tiniroto 1003 | 2024-06-30 09:30 | 2024-06-30 11:30 | 0.023039 | 0.00019199 | 5 | 600 | Unplanned | Unknown cause | Fuse fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 330 | 28996 | Hillside Road | Ngatapa 1102 | 2024-06-30 14:13 | 2024-06-30 15:57 | 0.0079868 | 7.6796e-05 | 2 | 208 | Unplanned | Defective Equipment | Repair broken conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 331 | 29126 | Arikihi road | Tauwhareparae 0404 | 2024-06-30 15:00 | 2024-06-30 18:06 | 0.014284 | 7.6796e-05 | 2 | 372 | Unplanned | Vegetation | Wires down G1645 - G1643 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 332 | N/A 13 | Feeder fault - Crawford | Crawford 1504 | 2024-06-30 15:24 | 2024-06-30 16:10 | 1.4317 | 0.036363 | 947 | 37286 | Unplanned | Wildlife | Fault Initally not found. Patrol would indicate potential bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 333 | 6994 | Goodwin Road | Whangara 0506 | 2024-07-01 08:50 | 2024-07-01 13:00 | 0.028799 | 0.00011519 | 3 | 750 | Unplanned | Adverse Weather | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 334 | 29054 | 20km Waimata Valely Road | Waimata 0903 | 2024-07-01 13:44 | 2024-07-01 14:39 | 0.0042238 | 7.6796e-05 | 2 | 110 | Unplanned | Defective Equipment | Replaced TX G188 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 335 | 29055 | Cave Road | Whangara 0506 | 2024-07-01 14:21 | 2024-07-01 14:49 | 0.0010751 | 3.8398e-05 | 1 | 28 | Unplanned | Defective Equipment | Broken insulator + conductor down @ Pole A2795 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 336 | 29056 | Waihua Valley Road | Raupunga 3101 | 2024-07-01 14:41 | 2024-07-02 16:30 | 1.3255 | 0.013708 | 357 | 34521 | Unplanned | Defective Equipment | Pole W3892 failed | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 337 | 3065 | Onepoto Rd Waimoko Rd Lake Rd | Village 2002 | 2024-07-02 10:13 | 2024-07-02 14:12 | 0.94524 | 0.003955 | 103 | 11736.7359 | Planned | Planned | Tree clearing | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 338 | 6996 | 187 Berry Road | Tiniroto 1003 | 2024-07-02 10:18 | 2024-07-02 14:15 | 0.1274 | 0.00053757 | 14 | 3318 | Unplanned | Adverse Weather | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 339 | 6671 | 4934 Waiapu Road | Inland 0301 | 2024-07-02 11:51 | 2024-07-03 07:15 | 0.044695 | 3.8398e-05 | 1 | 1164 | Unplanned | Unknown cause | Fuse fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 340 | 29135 | Marumoko Road | Matawai 1204 | 2024-07-02 13:11 | 2024-07-03 12:50 | 0.49756 | 0.0036094 | 94 | 12958 | Unplanned | Vegetation | Trees brought down 6 span HV conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 341 | 29058 | Te Araroa | Hicks Bay 0102 | 2024-07-02 13:25 | 2024-07-02 13:34 | 0.088469 | 0.0098299 | 256 | 2304 | Unplanned | Vegetation | Tree fell on 50kV line @ Pole J1877 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 342 | 29058 | Te Araroa | Te Araroa 0103 | 2024-07-02 13:25 | 2024-07-02 13:35 | 0.049533 | 0.0049533 | 129 | 1290 | Unplanned | Vegetation | Tree fell on 50kV line @ Pole J1877 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 343 | 29058 | Te Araroa | Awatere 0101 | 2024-07-02 13:25 | 2024-07-02 13:36 | 0.038436 | 0.0034942 | 91 | 1001 | Unplanned | Vegetation | Tree fell on 50kV line @ Pole J1877 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 344 | 29058 | Te Araroa | Te Araroa Sub 01 | 2024-07-02 13:25 | 2024-07-02 13:33 | 0.00030718 | 3.8398e-05 | 1 | 8 | Unplanned | Vegetation | Tree fell on 50kV line @ Pole J1877 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 345 | 6995 | 1400 Wharerata Road | Muriwai 0905 | 2024-07-02 14:06 | 2024-07-02 18:00 | 0.0089851 | 3.8398e-05 | 1 | 234 | Unplanned | Wildlife | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 346 | 7402 | 187 Berry Road | Tiniroto 1003 | 2024-07-03 19:20 | 2024-07-04 09:30 | 0.26111 | 0.00030718 | 8 | 6800 | Unplanned | Wildlife | Replaced fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 347 | 6999 | 209 Brown Beach Road | Muriwai 0905 | 2024-07-04 07:26 | 2024-07-04 09:00 | 0.021656 | 0.00023039 | 6 | 564 | Unplanned | Wildlife | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 348 | 3066 | Anaura Bay Rd Lockwood Rd | Mata 0304 | 2024-07-04 09:00 | 2024-07-04 16:00 | 0.9515 | 0.0022655 | 59 | 12418.0693 | Planned | Planned | Replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 349 | N/A 21 | Hokoroa Road, Waimata Valley Road | Waimata 0903 | 2024-07-04 09:19 | 2024-07-04 09:35 | 0.0036862 | 0.00023039 | 6 | 96 | Unplanned | Human Error | HV Links G527 Open/Close to ensure closed fully | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 350 | 29069 | Crawford Rd & De Latour Rd | Crawford 1504 | 2024-07-04 17:54 | 2024-07-04 19:55 | 2.63 | 0.036363 | 947 | 68492 | Unplanned | Defective Equipment | Faulty lightening arrestor @ A6458 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 351 | 3074 | Lavenham Road | Lavenham 0902 | 2024-07-05 08:59 | 2024-07-05 10:25 | 0.013209 | 0.00015359 | 4 | 172.0264 | Planned | Planned | Upgrade TX D366 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 352 | 3073 | Maki Street | Esplanade 1503 | 2024-07-05 09:00 | 2024-07-05 09:27 | 0.0020735 | 7.6796e-05 | 2 | 54 | Planned | Planned | Change SW/GR | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 353 | 3072 | Anaura Rd Lockwood Rd | Mata 0304 | 2024-07-05 09:05 | 2024-07-05 12:07 | 0.062896 | 0.00034558 | 9 | 819.4665 | Planned | Planned | Replace LV Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 354 | 3039 | Erepeti Rd | Ruakituri 2003 | 2024-07-05 09:12 | 2024-07-05 13:42 | 0.072572 | 0.00026879 | 7 | 945.2822 | Planned | Planned | Cut Trees | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 355 | 29070 | Anaura Bay Road | Mata 0304 | 2024-07-05 09:16 | 2024-07-05 11:12 | 0.26199 | 0.0022655 | 59 | 6823 | Unplanned | Defective Equipment | Conductor break in binder @ G1471 (part power response) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 356 | 3075 | Lavenham Road | Lavenham 0902 | 2024-07-05 12:47 | 2024-07-05 14:45 | 0.004531 | 3.8398e-05 | 1 | 59.0023 | Planned | Planned | Upgrade TX | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 357 | 7404 | 418 Waiatai Valley Rd | Nuhaka 3203 | 2024-07-05 13:02 | 2024-07-05 14:00 | 0.031179 | 0.00053757 | 14 | 812 | Unplanned | Third Party Interference | Replaced fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 358 | 3073A | Maki Street | Esplanade 1503 | 2024-07-05 16:02 | 2024-07-05 16:08 | 0.00046078 | 7.6796e-05 | 2 | 12 | Planned | Planned | Change SW/GR | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 359 | 6674 | Puhanga Road | Makarika 0204 | 2024-07-06 07:26 | 2024-07-06 10:00 | 0.088699 | 0.00057597 | 15 | 2310 | Unplanned | Defective Equipment | conductor badly pitted (clashing?) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 360 | 3063 | Lavenham Road | Lavenham 0902 | 2024-07-07 09:01 | 2024-07-07 10:15 | 0.20458 | 0.0027647 | 72 | 2672.9575 | Planned | Planned | Upgrade TX | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 361 | 3067 | Anarua Bay Road | Mata 0304 | 2024-07-08 09:00 | 2024-07-08 16:16 | 0.98775 | 0.0022655 | 59 | 12418.0693 | Planned | Planned | Pole Replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 362 | 3089 | Glenroy Rd Waiomoko Rd Andrews Rd Pa Rd | Dalton 0502 | 2024-07-08 10:03 | 2024-07-08 14:20 | 0.83842 | 0.0033022 | 86 | 21835 | Planned | Planned | To restore 11kV Conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 363 | 3076 A | Motu Road | Matawai 1204 | 2024-07-09 08:30 | 2024-07-09 09:00 | 0.10613 | 0.0044158 | 115 | 1386.4074 | Planned | Planned | Replace poles & ABS F228 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 364 | 3076 | Motu Road | Matawai 1204 | 2024-07-09 09:00 | 2024-07-09 16:28 | 0.28276 | 0.00065277 | 17 | 3571.1692 | Planned | Planned | Replace poles & ABS F228 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 365 | 3078 | Valley Rd Duncan St Justin St Campbell St | Haisman 0804 | 2024-07-09 09:02 | 2024-07-09 15:58 | 2.2578 | 0.0056061 | 146 | 29467.441 | Planned | Planned | Replaced RMU (Oil) with RMU (Gas) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 366 | 3077 | Mohaka Coach Rd | Raupunga 3101 | 2024-07-09 09:08 | 2024-07-09 13:10 | 0.032523 | 0.00023039 | 6 | 418.5625 | Planned | Planned | Install HV Fuses W5846. Repair 11kV damage | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 367 | 3076 B | Motu Road | Matawai 1204 | 2024-07-09 16:00 | 2024-07-09 17:46 | 0.30864 | 0.004339 | 113 | 3173.9323 | Planned | Planned | Replace poles & ABS F228 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 368 | 3076 | Motu Road | Matawai 1204 | 2024-07-09 16:36 | 2024-07-09 17:46 | 0.0026879 | 3.8398e-05 | 1 | 70 | Unplanned | Human Error | Replacing poles & ABS F228 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 369 | N/A 20 | Wairoa Town | Borough Two 3205 | 2024-07-09 17:22 | 2024-07-09 19:55 | 2.1555 | 0.03882 | 1011 | 56136 | Unplanned | Unknown cause | Cause not found. Report of a bang in Ruthford St | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 370 | 3068 | Anaura Bay Rd Lockwood Rd | Mata 0304 | 2024-07-10 09:00 | 2024-07-10 15:53 | 0.93564 | 0.0022655 | 59 | 12211.1015 | Planned | Planned | Pole replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 371 | 7407 | 412 Waiaka Road | Nuhaka 3203 | 2024-07-10 11:49 | 2024-07-10 13:00 | 0.038168 | 0.00053757 | 14 | 994 | Unplanned | Unknown cause | Replaced fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 372 | 3071 A | Waiapu road | Seaside 0302 | 2024-07-11 08:32 | 2024-07-11 09:02 | 0.12902 | 0.0043006 | 112 | 1574.7433 | Planned | Planned | To install new TX H4009. To replace ABSD H246 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 373 | 3071 | Waiapu road | Seaside 0302 | 2024-07-11 09:10 | 2024-07-11 13:11 | 0.99942 | 0.004147 | 108 | 13081.1812 | Planned | Planned | To install new TX H4009. To replace ABSD H246 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 374 | 3079 | Crawford Rd De Lautour Rutene Rd Shaw St Wainui Rd | Esplanade 1503 | 2024-07-11 09:32 | 2024-07-11 16:41 | 1.8944 | 0.0044158 | 115 | 22408.5159 | Planned | Planned | Replace TX A345 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 375 | 3071 B | Waiapu road | Seaside 0302 | 2024-07-11 16:01 | 2024-07-11 16:27 | 0.11182 | 0.0043006 | 112 | 1462.2616 | Planned | Planned | To install new TX H4009. To replace ABSD H246 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 376 | 6679 | 84 Koia Road | Tiki Tiki 0206 | 2024-07-11 18:45 | 2024-07-11 19:40 | 0.014783 | 0.00026879 | 7 | 385 | Unplanned | Lightning | Bad Lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 377 | 3069 | Anaura Bay Rd Lockwood Rd | Mata 0304 | 2024-07-12 09:00 | 2024-07-12 14:32 | 0.75214 | 0.0022655 | 59 | 9816.1882 | Planned | Planned | Replace HV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 378 | 3070 | Matokitoki Valley Road | Whangara 0506 | 2024-07-12 09:03 | 2024-07-12 13:00 | 0.00061437 | 7.6796e-05 | 2 | 16 | Unplanned | Human Error | Install ABS B1834. Replace ABS B78 with HV Links B78 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 379 | 3070 | Matokitoki Valley Rd Howarth St Justin St | Whangara 0506 | 2024-07-12 09:03 | 2024-07-12 13:02 | 0.96106 | 0.0041086 | 107 | 12541.5512 | Planned | Planned | Install ABS B1834. Replace ABS B78 with HV Links B78 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 380 | 29092 | Matawai Road | Matawai 1204 | 2024-07-12 12:47 | 2024-07-12 14:33 | 0.0040702 | 3.8398e-05 | 1 | 106 | Unplanned | Defective Equipment | Replaced faulty transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 381 | 7409 | 764 Awamate Road | Frasertown 3103 | 2024-07-14 23:44 | 2024-07-15 13:00 | 0.15282 | 0.00019199 | 5 | 3980 | Unplanned | Unknown cause | Replaced fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 382 | 8414 | 1706 Parikanapa Road | Parikanapa 1002 | 2024-07-15 11:44 | 2024-07-15 13:00 | 0.0058365 | 7.6796e-05 | 2 | 152 | Unplanned | Unknown cause | Replaced ddo fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 383 | 8415 | 210 Pa Road | Dalton 0502 | 2024-07-16 06:28 | 2024-07-16 09:28 | 0.19353 | 0.0010751 | 28 | 5040 | Unplanned | Defective Equipment | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 384 | 29146 | Pa Road, Whangara | Dalton 0502 | 2024-07-16 08:10 | 2024-07-16 09:28 | 0.083861 | 0.0010751 | 28 | 2184 | Unplanned | Defective Equipment | Repaired broken binder pole A1246 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 385 | 6678 | 84 Koia Road | Tiki Tiki 0206 | 2024-07-16 08:16 | 2024-07-16 12:30 | 0.068272 | 0.00026879 | 7 | 1778 | Unplanned | Lightning | Lightning overnight | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 386 | 3088 | Matawai & Otoko Areas | Matawai 1204 | 2024-07-16 09:00 | 2024-07-16 17:37 | 4.9254 | 0.018124 | 472 | 57626.7278 | Planned | Planned | Pole, Switchgear, TX Replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 387 | 3088a | Matawai & Otoko Areas | Matawai 1204 | 2024-07-16 09:00 | 2024-07-16 10:15 | 0.087356 | 0.0026879 | 70 | 525.7056 | Planned | Planned | Pole, Switchgear, TX Replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 388 | 3088b | Matawai & Otoko Areas | Matawai 1204 | 2024-07-16 17:09 | 2024-07-16 17:33 | 0.032254 | 0.0013439 | 35 | 0 | Planned | Planned | Pole, Switchgear, TX Replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 389 | 3096 | Whatatutu Rd Mangamaia Rd Armstrong Rd Tarndale Rd | Whatatutu 1201 | 2024-07-17 09:33 | 2024-07-17 13:55 | 1.8572 | 0.0071036 | 185 | 48366 | Planned | Planned | Replace ABS F362 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 390 | 8417 | 542 Waitangi Road | Kanakanaia 1202 | 2024-07-18 07:45 | 2024-07-18 09:00 | 0.037438 | 0.00049917 | 13 | 975 | Unplanned | Unknown cause | Replace ddo fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 391 | 3087 | Caesar Road | Waimata 0903 | 2024-07-18 08:07 | 2024-07-18 08:23 | 0.0036862 | 0.00023039 | 6 | 48.0111 | Planned | Planned | Shelterbelt Trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 392 | 3086 | Brown Road | Waimata 0903 | 2024-07-18 09:02 | 2024-07-18 10:05 | 0.036286 | 0.00057597 | 15 | 435.2505 | Planned | Planned | Shelterbelt Trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 393 | 3083 | Waiomoko Rd Andrews Rd | Dalton 0502 | 2024-07-18 09:03 | 2024-07-18 15:44 | 0.32335 | 0.00080636 | 21 | 4213.8952 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 394 | 3090 | Muriwai Beach Road | Muriwai 0905 | 2024-07-18 09:04 | 2024-07-18 13:40 | 0.64647 | 0.0023423 | 61 | 8437.7173 | Planned | Planned | Install TX C4704 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 395 | 29151 | Frasertown Road | Nuhaka 3203 | 2024-07-18 12:03 | 2024-07-18 14:32 | 0.32039 | 0.0021503 | 56 | 8344 | Unplanned | Third Party Interference | Car versus pole W6681 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 396 | 3111 | De Latour Rd Seymour Rd Martin Rd Turenne St Owen St Kelvin St Vivian St Huxley St Tui St Kara St | Crawford 1504 | 2024-07-19 09:01 | 2024-07-19 10:43 | 1.0222 | 0.010022 | 261 | 26622 | Planned | Planned | To remove faulty LA and Rejoin 11kV jumpers | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 397 | 29210 | Ngatapa | Ngatapa Sub 11 | 2024-07-20 18:57 | 2024-07-20 21:58 | 1.1723 | 0.033598 | 875 | 30529 | Unplanned | Unknown cause | High fault current on Totangi (2k+ amps) cause trip on D13 (incomer) & 50kV CB D31. During initial restoration switching the circuilativy current in VR resulted in tripping CB D640 (Lavenham) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 398 | 9301 | 209 Browns Beach Road | Muriwai 0905 | 2024-07-22 07:59 | 2024-07-22 09:23 | 0.019353 | 0.00023039 | 6 | 504 | Unplanned | Wildlife | Replaced fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 399 | 7798 | 1473 Waikura Road | Hicks Bay 0102 | 2024-07-22 08:32 | 2024-07-22 13:29 | 0.057021 | 0.00019199 | 5 | 1485 | Unplanned | Unknown cause | Replaced fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 400 | 3084 | Waiomoko Rd Andrews Rd | Dalton 0502 | 2024-07-22 09:03 | 2024-07-22 14:15 | 0.25158 | 0.00080636 | 21 | 3278.6416 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 401 | 9302 | 209 Browns Beach Road | Muriwai 0905 | 2024-07-22 10:30 | 2024-07-22 11:15 | 0.010367 | 0.00023039 | 6 | 270 | Unplanned | Wildlife | Replaced fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 402 | 9303 | 209 Browns Beach Road | Muriwai 0905 | 2024-07-22 17:33 | 2024-07-22 18:16 | 0.0099067 | 0.00023039 | 6 | 258 | Unplanned | Wildlife | Replaced fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 403 | 7410 | 764 Awamate Road | Frasertown 3103 | 2024-07-22 18:14 | 2024-07-22 20:30 | 0.026111 | 0.00019199 | 5 | 680 | Unplanned | Unknown cause | Replaced fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 404 | 3053A | Kanakanaia Rd Bruce Rd | Kanakanaia 1202 | 2024-07-23 08:30 | 2024-07-23 14:41 | 0.80866 | 0.0021887 | 57 | 10541.5262 | Planned | Planned | Remove ABS E318. Replace HV Links E135 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 405 | 7800 | 7078 Waiapu Road | Makarika 0204 | 2024-07-24 06:10 | 2024-07-24 08:05 | 0.0044158 | 3.8398e-05 | 1 | 115 | Unplanned | Unknown cause | Replaced fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 406 | 3092 | Motu Road | Matawai 1204 | 2024-07-24 08:30 | 2024-07-24 14:59 | 0.11949 | 0.00030718 | 8 | 1556.478 | Planned | Planned | Replace 11kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 407 | 3085 | Waiomoko Rd Andrews Rd | Dalton 0502 | 2024-07-24 09:02 | 2024-07-24 15:52 | 0.33061 | 0.00080636 | 21 | 4308.4714 | Planned | Planned | Replace 11kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 408 | 29218 | Te Hue Road | Awatere 0101 | 2024-07-25 09:01 | 2024-07-25 12:17 | 0.015052 | 7.6796e-05 | 2 | 392 | Unplanned | Defective Equipment | Replace pole J787 - Faulty x-arm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 409 | 7401 | 2225 SH2 Whakaki | Nuhaka 3203 | 2024-07-25 18:29 | 2024-07-25 19:30 | 0.11946 | 0.0019583 | 51 | 3111 | Unplanned | Unknown cause | Replaced fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 410 | N/A 22 | SH35 Whangara Road | Rototahi 0403 | 2024-07-26 00:49 | 2024-07-26 01:55 | 0.5474 | 0.008294 | 216 | 14256 | Unplanned | Unknown cause | Daylight patrol Goodwin Rd - Tolaga Bay - Tokomaru Bay. Unable to identify obvious fault cause at accessible points. Restore supply to 50kV cct | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 411 | N/A 22 | SH35 Whangara Road | Town 0402 | 2024-07-26 00:49 | 2024-07-26 02:05 | 0.59824 | 0.0078716 | 205 | 15580 | Unplanned | Unknown cause | Daylight patrol Goodwin Rd - Tolaga Bay - Tokomaru Bay. Unable to identify obvious fault cause at accessible points. Restore supply to 50kV cct | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 412 | N/A 22 | SH35 Whangara Road | Toko Tie 0401 | 2024-07-26 00:49 | 2024-07-26 02:07 | 0.25158 | 0.0032254 | 84 | 6552 | Unplanned | Unknown cause | Daylight patrol Goodwin Rd - Tolaga Bay - Tokomaru Bay. Unable to identify obvious fault cause at accessible points. Restore supply to 50kV cct | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 413 | N/A 22 | SH35 Whangara Road | Tauwhareparae 0404 | 2024-07-26 00:49 | 2024-07-26 02:11 | 0.4597 | 0.0056061 | 146 | 11972 | Unplanned | Unknown cause | Daylight patrol Goodwin Rd - Tolaga Bay - Tokomaru Bay. Unable to identify obvious fault cause at accessible points. Restore supply to 50kV cct | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 414 | N/A 22 | SH35 Whangara Road | Tolaga Bay Sub | 2024-07-26 00:49 | 2024-07-26 02:05 | 0.0029183 | 3.8398e-05 | 1 | 76 | Unplanned | Unknown cause | Daylight patrol Goodwin Rd - Tolaga Bay - Tokomaru Bay. Unable to identify obvious fault cause at accessible points. Restore supply to 50kV cct | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 415 | 3099 | Motu Road | Matawai 1204 | 2024-07-26 08:32 | 2024-07-26 13:36 | 0.093384 | 0.00030718 | 8 | 1216.4055 | Planned | Planned | Replace 11kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 416 | 3098 | Bruce Road | Waimata 0903 | 2024-07-26 08:33 | 2024-07-26 09:33 | 0.020735 | 0.00034558 | 9 | 270.0933 | Planned | Planned | Shelterbelt clearing | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 417 | 5100B | Worsley Street | Tamarau 0503 | 2024-07-26 09:01 | 2024-07-26 14:38 | 1.3717 | 0.0040702 | 106 | 12718.5571 | Planned | Planned | Install new 11/400 Pole & TX A2475 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 418 | N/A 23 | Parkinson Sub | Solander 0706 | 2024-07-28 18:32 | 2024-07-28 19:35 | 0.099182 | 0.0015743 | 41 | 2583 | Unplanned | Unknown cause | CB31=450a Bphase ER - No fault found. No obvious sign of cause | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 419 | N/A 23 | Parkinson Sub | Cedenco A 0704 | 2024-07-28 18:32 | 2024-07-28 19:35 | 0.0072572 | 0.00011519 | 3 | 189 | Unplanned | Unknown cause | CB31=450a Bphase ER - No fault found. No obvious sign of cause | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 420 | N/A 23 | Parkinson Sub | Innes 0705 | 2024-07-28 18:32 | 2024-07-28 19:34 | 0.076182 | 0.0012287 | 32 | 1984 | Unplanned | Unknown cause | CB31=450a Bphase ER - No fault found. No obvious sign of cause | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 421 | N/A 23 | Parkinson Sub | Chalmers 0707 | 2024-07-28 18:32 | 2024-07-28 19:33 | 1.6677 | 0.027339 | 712 | 43432 | Unplanned | Unknown cause | CB31=450a Bphase ER - No fault found. No obvious sign of cause | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 422 | N/A 23 | Parkinson Sub | Lytton 0701 | 2024-07-28 18:32 | 2024-07-28 19:32 | 0.16358 | 0.0027263 | 71 | 4260 | Unplanned | Unknown cause | CB31=450a Bphase ER - No fault found. No obvious sign of cause | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 423 | N/A 23 | Parkinson Sub | Willows 0702 | 2024-07-28 18:32 | 2024-07-28 19:31 | 0.18804 | 0.003187 | 83 | 4897 | Unplanned | Unknown cause | CB31=450a Bphase ER - No fault found. No obvious sign of cause | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 424 | N/A 23 | Parkinson Sub | Elgin 0703 | 2024-07-28 18:32 | 2024-07-28 19:30 | 2.0511 | 0.035365 | 921 | 53418 | Unplanned | Unknown cause | CB31=450a Bphase ER - No fault found. No obvious sign of cause | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 425 | N/A 23 | Parkinson Sub | JNL Sub 16 | 2024-07-28 18:32 | 2024-07-28 19:26 | 0.0020735 | 3.8398e-05 | 1 | 54 | Unplanned | Unknown cause | CB31=450a Bphase ER - No fault found. No obvious sign of cause | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 426 | 7411 | 385 Awamate Road | Raupunga 3101 | 2024-07-29 06:20 | 2024-07-29 07:20 | 0.036862 | 0.00061437 | 16 | 960 | Unplanned | Unknown cause | Replaced fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 427 | 3100 | Kanakanaia Rd Waitangi Rd | Kanakanaia 1202 | 2024-07-30 08:30 | 2024-07-30 14:51 | 0.40963 | 0.0010751 | 28 | 5339.7348 | Planned | Planned | Replace 11kV poles - E1068 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 428 | 3093 | Waiomoko Road | Dalton 0502 | 2024-07-30 09:06 | 2024-07-30 15:05 | 0.12406 | 0.00034558 | 9 | 1616.0583 | Planned | Planned | Replace 11kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 429 | 3107 | Nuhaka Opoutama Rd Waikokopu Rd Whaanga St Wai Station Rd | Nuhaka 3203 | 2024-07-30 09:07 | 2024-07-30 17:02 | 0.4195 | 0.00088315 | 23 | 5098.9992 | Planned | Planned | Replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 430 | 6681 | Maraehara Road | Tiki Tiki 0206 | 2024-07-30 10:30 | 2024-07-30 14:40 | 0.27839 | 0.0011135 | 29 | 7250 | Unplanned | Defective Equipment | Floating wire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 431 | 29223 | Maraehara Road | Tiki Tiki 0206 | 2024-07-30 13:23 | 2024-07-30 14:45 | 0.091311 | 0.0011135 | 29 | 2378 | Unplanned | Defective Equipment | Insulator dislodged from x-arm on pole J2161 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 432 | 6682 | 2754 Ihungia road | Mata 0304 | 2024-07-30 13:40 | 2024-07-30 16:45 | 0.14918 | 0.00080636 | 21 | 3885 | Unplanned | Adverse Weather | Flooding/roads/traffic - bad weather | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 433 | N/A 24 | Mata Road | Mata 0304 | 2024-07-30 16:28 | 2024-07-30 16:44 | 0.018431 | 0.0011519 | 30 | 480 | Unplanned | Unknown cause | 1 HV fuse down @ H272 (Centry 0) Opened Sectionaliser to close fuses. Slosed Sectionaliser, fuses holding | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 434 | 3094 | Waiomoko Rd Wharekiri Rd | Dalton 0502 | 2024-07-31 09:06 | 2024-07-31 16:02 | 0.41531 | 0.00099835 | 26 | 5387.3731 | Planned | Planned | Replace 11kV poles - A3999, A4000, A4001, A4004 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 435 | 3106 | Lavenham Rd | Lavenham 0902 | 2024-07-31 09:15 | 2024-07-31 15:25 | 0.085244 | 0.00023039 | 6 | 1110.2557 | Planned | Planned | Replace 11kV Poles - D2001 - D390 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 436 | 3131 | Clyde Rd Brian Avenue Chamberlain Avenue | Borough One 3204 | 2024-07-31 15:34 | 2024-07-31 16:10 | 0.1175 | 0.0032638 | 85 | 3060 | Planned | Planned | Urgent Fault - To Repair neutral connections on TX W1579 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 437 | 3108 | Nuhaka - Opoutama Rd - Waikokopu Road | Morere 3401 | 2024-08-01 09:03 | 2024-08-01 15:25 | 0.33737 | 0.00088315 | 23 | 4396.8797 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 438 | 29168/29169 | Waipiro Road | Inland 0301 | 2024-08-01 13:01 | 2024-08-02 16:22 | 0.16976 | 0.0024959 | 65 | 4421 | Unplanned | Vegetation | Tree through 11kV between poles H2224 & H2226 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 439 | 29167 | 43 Omana Road, Nuhaka | Morere 3401 | 2024-08-01 13:55 | 2024-08-01 14:42 | 0.0072188 | 0.00015359 | 4 | 188 | Unplanned | Vegetation | Tree contacted LV line from TX W7975 & Pole W20544. Wrapped conductor, Isolated from TX W7975 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 440 | 7412 | 145 Nuhaka Oputama Rd | Morere 3401 | 2024-08-01 21:22 | 2024-08-01 22:30 | 0.015666 | 0.00023039 | 6 | 408 | Unplanned | Unknown cause | Replaced TX fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 441 | 7413 | 310 Kaiwaitau Road | Mahia 3301 | 2024-08-02 07:22 | 2024-08-02 09:40 | 0.18546 | 0.0013439 | 35 | 4830 | Unplanned | Unknown cause | Replaced fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 442 | 3105 | Kanakanaia Rd Waitangi Rd | Kanakanaia 1202 | 2024-08-02 08:30 | 2024-08-02 15:52 | 0.47521 | 0.0010751 | 28 | 6194.653 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 443 | 9306 | Tiniroto Road | Tiniroto 1003 | 2024-08-02 08:36 | 2024-08-02 11:00 | 0.066352 | 0.00046078 | 12 | 1728 | Unplanned | Wildlife | Replaced fuses - HV fuses next to lake | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 444 | 3109 | Oak St, Elm Street | Gladstone 0607 | 2024-08-02 09:03 | 2024-08-02 16:09 | 0.78516 | 0.0018431 | 48 | 7141.1377 | Planned | Planned | Replace SW/GR | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 445 | 29170 | Managapa | Gladstone 0607 | 2024-08-03 08:05 | 2024-08-03 13:51 | 5.518 | 0.042391 | 1104 | 143705 | Unplanned | Unknown cause | Fault indicators indicated fault past B847, (new SW/GR) Patrolled nothing found - Switching incident | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 446 | N/A 25 | Coast | Tauwhareparae 0404 | 2024-08-03 09:15 | 2024-08-03 09:52 | 0.20743 | 0.0056061 | 146 | 5402 | Unplanned | Wildlife | Duck hit line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 447 | N/A 25 | Coast | Toko Tie 0401 | 2024-08-03 09:15 | 2024-08-03 09:49 | 0.10966 | 0.0032254 | 84 | 2856 | Unplanned | Wildlife | Duck hit line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 448 | N/A 25 | Coast | Town 0402 | 2024-08-03 09:15 | 2024-08-03 09:48 | 0.25976 | 0.0078716 | 205 | 6765 | Unplanned | Wildlife | Duck hit line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 449 | N/A 25 | Coast | Rototahi 0403 | 2024-08-03 09:15 | 2024-08-03 09:42 | 0.22497 | 0.0083324 | 217 | 5859 | Unplanned | Wildlife | Duck hit line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 450 | N/A 26 | Wairoa Township | Borough Two 3205 | 2024-08-03 16:47 | 2024-08-03 18:16 | 1.4653 | 0.027339 | 712 | 38160 | Unplanned | Defective Equipment | Unknown - Later found cracked insulator & burnt x-arm - Pole W3017 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 451 | N/A 27 | Wairoa Township | Borough Two 3205 | 2024-08-04 02:33 | 2024-08-04 04:00 | 1.3882 | 0.025458 | 663 | 36153 | Unplanned | Defective Equipment | Not found, later found broken insulator/burnt x-arm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 452 | 9307 | Ruakaka Road | Tiniroto 1003 | 2024-08-04 18:30 | 2024-08-04 21:00 | 0.13247 | 0.00088315 | 23 | 3450 | Unplanned | Unknown cause | Replaced fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 453 | 3095 | Panikau Road | Dalton 0502 | 2024-08-05 09:02 | 2024-08-05 16:15 | 0.14964 | 0.00034558 | 9 | 1881.65 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 454 | 3114 | Kanakanaia Rd, Waitangi Rd | Kanakanaia 1202 | 2024-08-06 08:30 | 2024-08-06 14:23 | 0.37953 | 0.0010751 | 28 | 4947.3134 | Planned | Planned | Replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 455 | 29234 | Rutherford Street, Tawhara Valley Rd | Borough Two 3205 | 2024-08-06 10:22 | 2024-08-06 13:59 | 0.16665 | 0.00076796 | 20 | 4340 | Unplanned | Defective Equipment | Replaced pole W3017. Boro 2 had been faulting suspect this was our fault. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 456 | 3116 | Mata Road, Ihungia Rd | Mata 0304 | 2024-08-07 09:00 | 2024-08-07 16:21 | 0.55881 | 0.0012671 | 33 | 6938.7812 | Planned | Planned | Replace 11kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 457 | 3097 | Panikau Road | Dalton 0502 | 2024-08-07 09:03 | 2024-08-07 16:16 | 0.14964 | 0.00034558 | 9 | 1877.1485 | Planned | Planned | Replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 458 | 3115 | Kanakanaia Rd, Waitangi Rd | Kanakanaia 1202 | 2024-08-08 08:30 | 2024-08-08 15:57 | 0.48059 | 0.0010751 | 28 | 6264.7283 | Planned | Planned | Replace 11kV poles. Install HV fuses E1107 & E957. Remove HV fuses E142 & E148 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 459 | 3103A | Goodwin Road | Whangara 0506 | 2024-08-08 09:02 | 2024-08-08 13:53 | 0.61456 | 0.0021119 | 55 | 16005 | Planned | Planned | Replace TX pole A88 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 460 | 3091A | Pakowhai Rd | Muriwai 0905 | 2024-08-09 08:41 | 2024-08-09 11:10 | 0.091541 | 0.00061437 | 16 | 2384 | Unplanned | Human Error | Outage in place to allow for bridge installation in close proximity to OH 11kV. Note: Only had 1 day notice from bridge contractor of wanting shutdown that was deferred earlier in July | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 461 | 3102 | Panikau Road | Dalton 0502 | 2024-08-09 09:03 | 2024-08-09 16:09 | 0.49073 | 0.0011519 | 30 | 6262.2054 | Planned | Planned | Replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 462 | 3125A | 113 Whatatutu Road | Matawai 1204 | 2024-08-09 09:32 | 2024-08-09 11:15 | 0.00791 | 7.6796e-05 | 2 | 206 | Planned | Planned | Upgrade TX F273 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 463 | 3126A | 113 Whatatutu Road | Whatatutu 1201 | 2024-08-09 11:41 | 2024-08-09 14:35 | 0.033406 | 0.00019199 | 5 | 870 | Planned | Planned | Upgrade TX F447 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 464 | 29243 | Ardkeen, Ruapapa, Cricklewood | Frasertown 3103 | 2024-08-10 00:42 | 2024-08-10 14:54 | 2.4908 | 0.0067581 | 176 | 64867 | Unplanned | Vegetation | Tree across 50kV / 11kV @ Pole W4775. 11kV conductor damaged | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 465 | 3117 | Pitchers Road | Te Karaka 1203 | 2024-08-10 09:12 | 2024-08-10 11:47 | 0.041662 | 0.00026879 | 7 | 542.6458 | Planned | Planned | Cutover 11kV OH to U/ground and connect to RMU E876 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 466 | 8116 | 361 Waiapu Road | Toko Tie 0401 | 2024-08-10 10:21 | 2024-08-10 12:30 | 0.0099067 | 7.6796e-05 | 2 | 258 | Unplanned | Lightning | Lightning storm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 467 | 8117 | 838 Paroa Road | Toko Tie 0401 | 2024-08-10 11:19 | 2024-08-10 13:15 | 0.0044542 | 3.8398e-05 | 1 | 116 | Unplanned | Lightning | Lightning storm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 468 | 8118 | 601 Waiapu Rd | Toko Tie 0401 | 2024-08-10 13:35 | 2024-08-10 15:30 | 0.013247 | 0.00011519 | 3 | 345 | Unplanned | Lightning | Lightning storm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 469 | 29244 | Humphrey Road | Lavenham 0902 | 2024-08-10 14:14 | 2024-08-10 15:09 | 0.014783 | 0.00026879 | 7 | 385 | Unplanned | Defective Equipment | DDO fuse @ HV fuses D3029 required replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 470 | 8119 | 14 Ruakaka Road | Tiniroto 1003 | 2024-08-11 07:45 | 2024-08-11 09:15 | 0.048382 | 0.00053757 | 14 | 1260 | Unplanned | Unknown cause | Replaced fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 471 | 8120 | 77 Wharekaka Road | Toko Tie 0401 | 2024-08-11 17:51 | 2024-08-11 18:30 | 0.002995 | 7.6796e-05 | 2 | 78 | Unplanned | Unknown cause | Replaced glass fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 472 | 29245 | Bushy Knoll Rd | Tiniroto 1003 | 2024-08-11 19:31 | 2024-08-12 11:46 | 0.39174 | 0.00046078 | 12 | 10202 | Unplanned | Wildlife | Possum on pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 473 | 7192 | Wharekaka Road | Toko Tie 0401 | 2024-08-12 13:13 | 2024-08-12 16:30 | 0.0075644 | 3.8398e-05 | 1 | 197 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 474 | 29183 | Whakaki | Nuhaka 3203 | 2024-08-12 19:05 | 2024-08-13 19:05 | 1.6716 | 0.011942 | 311 | 43533 | Unplanned | Vegetation | Tree thru line broke x-arm. No backfeed. See Tahanui Fault #2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 475 | 29182 | Nuhaka | Morere 3401 | 2024-08-12 19:19 | 2024-08-12 22:38 | 1.8269 | 0.010291 | 268 | 47578 | Unplanned | Defective Equipment | Broken conductor - High winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 476 | 29248 | Taurau Valley Road | Te Arai 0906 | 2024-08-12 19:21 | 2024-08-15 11:55 | 1.1062 | 0.01797 | 468 | 28810 | Unplanned | Defective Equipment | Pole C2662 snapped @ ground level during high winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 477 | N/A 29 | Ohuka | Ruakituri 2003 | 2024-08-12 19:25 | 2024-08-12 20:52 | 0.38986 | 0.004723 | 123 | 10153 | Unplanned | Adverse Weather | High wind through region during this period | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 478 | 29249 | Maungataniwha | Raupunga 3101 | 2024-08-12 19:35 | 2024-08-13 15:38 | 1.2339 | 0.0059517 | 155 | 32135 | Unplanned | Vegetation | Tree through line W5127 - W5128 - See Fault 6 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 479 | 3120 | Motu Road | Matawai 1204 | 2024-08-13 08:30 | 2024-08-13 14:08 | 0.10383 | 0.00030718 | 8 | 1352.4153 | Planned | Planned | Replace 11kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 480 | 29247 | Manuka & Tutara Street | Elgin 0703 | 2024-08-13 08:41 | 2024-08-14 16:46 | 3.0445 | 0.039051 | 1017 | 79287 | Unplanned | Defective Equipment | Cable term at B1430, then cable fault Manuka St (Jnt) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 481 | 29187 | Mahanga Rd | Mahia 3301 | 2024-08-13 11:00 | 2024-08-14 14:03 | 1.9611 | 0.0056061 | 146 | 51072 | Unplanned | Vegetation | Replace 11kV pole W9196 & remove tree from 11kV. Broke x-arm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 482 | N/A 28 | Tahaenui, Mahia | Mahia 3301 | 2024-08-13 14:07 | 2024-08-13 16:03 | 4.0249 | 0.063434 | 1652 | 104820 | Unplanned | Adverse Weather | High winds through region during this day. Potential line clash - High. Generator failed. Fault at Iwetea, No back feed. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 483 | N/A 28 | Tahaenui, Mahia | Nuhaka 3203 | 2024-08-13 14:07 | 2024-08-13 15:34 | 0.24387 | 0.0028031 | 73 | 6351 | Unplanned | Adverse Weather | High winds through region during this day. Potential line clash - High. Generator failed. Fault at Iwetea, No back feed. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 484 | N/A 28 | Tahaenui, Mahia | Morere 3401 | 2024-08-13 14:07 | 2024-08-13 15:34 | 0.88527 | 0.010175 | 265 | 23055 | Unplanned | Adverse Weather | High winds through region during this day. Potential line clash - High. Generator failed. Fault at Iwetea, No back feed. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 485 | 7414 | 217 Preston Rd | Morere 3401 | 2024-08-13 15:49 | 2024-08-14 13:00 | 0.58565 | 0.00046078 | 12 | 15252 | Unplanned | Adverse Weather | Replaced fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 486 | 3123 | Waimata Valley Rd | Waimata 0903 | 2024-08-14 08:33 | 2024-08-14 15:30 | 0.20816 | 0.00049917 | 13 | 2711.853 | Planned | Planned | Relocate TX E281 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 487 | 7193 | 3321 Wharerata Road | Muriwai 0905 | 2024-08-14 16:37 | 2024-08-14 20:30 | 0.017893 | 7.6796e-05 | 2 | 466 | Unplanned | Adverse Weather | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 488 | 6684 | 4988 Te Araroa Road | Hicks Bay 0102 | 2024-08-15 08:14 | 2024-08-15 11:45 | 0.024306 | 0.00011519 | 3 | 633 | Unplanned | Adverse Weather | High Winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 489 | 3121 | Motu Road | Matawai 1204 | 2024-08-15 08:30 | 2024-08-15 13:14 | 0.08724 | 0.00030718 | 8 | 1136.4055 | Planned | Planned | Replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 490 | 29192 | Rangiahuia Road | Frasertown 3103 | 2024-08-15 09:33 | 2024-08-15 11:22 | 0.31817 | 0.0039166 | 102 | 8286 | Unplanned | Defective Equipment | Blown lightning Arrestor TX W1651 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 491 | 6685 | 40 Puia Street | Inland 0301 | 2024-08-15 10:00 | 2024-08-15 14:15 | 0.029374 | 0.00011519 | 3 | 765 | Unplanned | Adverse Weather | High Winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 492 | 29193 | Tuai | Village 2002 | 2024-08-15 12:56 | 2024-08-15 14:38 | 0.40341 | 0.003955 | 103 | 10506 | Unplanned | Vegetation | Conductor damaged with tree through line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 493 | 29188 | 4185 SH 2 Raupunga | Raupunga 3101 | 2024-08-15 15:47 | 2024-08-15 16:47 | 0.13132 | 0.0021887 | 57 | 3420 | Unplanned | Vegetation | High Winds brought down tree throu lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 494 | 6686 | 535 Matahiia Road | Makarika 0204 | 2024-08-15 16:28 | 2024-08-15 18:20 | 0.051607 | 0.00046078 | 12 | 1344 | Unplanned | Defective Equipment | Live wire against x-arm broken - replaced 16/8/24 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 495 | 29261 | Matahiia Road | Makarika 0204 | 2024-08-15 17:16 | 2024-08-16 16:03 | 0.35295 | 0.00069116 | 18 | 9192 | Unplanned | Defective Equipment | Replace Pole H1644 and rejoin 11kV line break | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 496 | 7415 | 35 Aranui Road | Raupunga 3101 | 2024-08-15 19:50 | 2024-08-15 21:00 | 0.043006 | 0.00061437 | 16 | 1120 | Unplanned | Unknown cause | Replaced fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 497 | 29264 | Matawai Road | Waimata 0903 | 2024-08-16 02:16 | 2024-08-16 14:13 | 0.80225 | 0.0049917 | 130 | 20893 | Unplanned | Third Party Interference | MVA @ Pole E2052. Isolated to allow crane to raise 11kV conductor/pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 498 | 3112 | Titarangi Rd Jackson Rd | Frasertown 3103 | 2024-08-16 09:05 | 2024-08-16 12:48 | 0.137 | 0.00061437 | 16 | 3568 | Planned | Planned | Replace 11kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 499 | 29267 | Paroa Road | Toko Tie 0401 | 2024-08-16 11:03 | 2024-08-16 12:23 | 0.0061437 | 7.6796e-05 | 2 | 160 | Unplanned | Defective Equipment | Repair LV fault, high winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 500 | 3127 | Frasertown Road | Nuhaka 3203 | 2024-08-16 11:05 | 2024-08-16 12:56 | 0.18327 | 0.0016511 | 43 | 1830.5174 | Planned | Planned | Replace Stub Pole damaged in MVA earlier | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 501 | 7195 | 14 Ruakaka Road | Tiniroto 1003 | 2024-08-17 14:05 | 2024-08-17 16:00 | 0.061821 | 0.00053757 | 14 | 1610 | Unplanned | Wildlife | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 502 | 29302 | Wharerata / Bartletts | Muriwai 0905 | 2024-08-18 00:29 | 2024-08-18 02:42 | 0.68433 | 0.0051453 | 134 | 17822 | Unplanned | Defective Equipment | Broken polymer strain - conductor crossed over BC phases. C3514 - C659 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 503 | 29310 | Tikitiki | Tiki Tiki 0206 | 2024-08-18 02:01 | 2024-08-19 17:12 | 10.8318 | 0.020044 | 522 | 282093 | Unplanned | Vegetation | Trees thru lines J2320 - J2319 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 504 | 29327 | Poroporo Valley Road | Tiki Tiki 0206 | 2024-08-18 05:39 | 2024-08-21 14:22 | 2.4175 | 0.00049917 | 13 | 62959 | Unplanned | Vegetation | Tree thru line J1003 - J1004 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 505 | 29334 | Eastcape Lighthouse | Tiki Tiki 0206 | 2024-08-18 05:39 | 2024-08-21 14:17 | 1.3004 | 0.00026879 | 7 | 33866 | Unplanned | Vegetation | Tree thru line. Hi winds. J2508 - J248 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 506 | 29303 | Tahora | Tahora 1103 | 2024-08-18 06:47 | 2024-08-18 11:25 | 1.1301 | 0.0057597 | 150 | 29432 | Unplanned | Vegetation | Tree through 11kV lind @ pole D2921 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 507 | 29332 | Tuakau / Ihungia | Mata 0304 | 2024-08-18 07:17 | 2024-08-21 15:23 | 1.8645 | 0.00061437 | 16 | 48557 | Unplanned | Vegetation | Tree thru line x 3. See #12 & #15 No Backfeed | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 508 | N/A 30 | Awatere | Awatere 0101 | 2024-08-18 07:47 | 2024-08-18 08:08 | 0.057251 | 0.0027263 | 71 | 1491 | Unplanned | Adverse Weather | Highwind in area. J2756 in open position see #3 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 509 | 7421 | Ohuka Road | Ruakituri 2003 | 2024-08-18 08:13 | 2024-08-18 11:00 | 0.17955 | 0.0010751 | 28 | 4676 | Unplanned | Adverse Weather | Replaced fuses - wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 510 | 29305 | Ruatoria | Ruatoria 0201 | 2024-08-18 08:22 | 2024-08-20 14:03 | 1.1007 | 0.015052 | 392 | 28666 | Unplanned | Vegetation | Trees thru conductor, High wind - J1386 - J1385 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 511 | 9310 | Kanakania Road | Kanakanaia 1202 | 2024-08-18 08:24 | 2024-08-19 16:30 | 0.51768 | 0.00026879 | 7 | 13482 | Unplanned | Vegetation | Replaced HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 512 | 29272 | Panikau | Dalton 0502 | 2024-08-18 08:40 | 2024-08-20 14:33 | 2.3386 | 0.0028799 | 75 | 60904 | Unplanned | Vegetation | Tree thru line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 513 | N/A 34 | Coast | Te Araroa Sub 01 | 2024-08-18 09:18 | 2024-08-18 10:01 | 0.0016511 | 3.8398e-05 | 1 | 43 | Unplanned | Vegetation | Tree thru line - High winds. See #11 & #15 & #22 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 514 | N/A 34 | Coast | Awatere 0101 | 2024-08-18 09:18 | 2024-08-18 10:01 | 0.15025 | 0.0034942 | 91 | 3913 | Unplanned | Vegetation | Tree thru line - High winds. See #11 & #15 & #22 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 515 | N/A 34 | Coast | Hicks Bay 0102 | 2024-08-18 09:18 | 2024-08-18 10:01 | 0.42269 | 0.0098299 | 256 | 11008 | Unplanned | Vegetation | Tree thru line - High winds. See #11 & #15 & #22 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 516 | N/A 34 | Coast | Te Araroa 0103 | 2024-08-18 09:18 | 2024-08-18 10:01 | 0.21299 | 0.0049533 | 129 | 5547 | Unplanned | Vegetation | Tree thru line - High winds. See #11 & #15 & #22 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 517 | N/A 34 | Coast | Ruatoria Sub 02 | 2024-08-18 09:18 | 2024-08-18 10:04 | 0.0017663 | 3.8398e-05 | 1 | 46 | Unplanned | Vegetation | Tree thru line - High winds. See #11 & #15 & #22 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 518 | N/A 34 | Coast | Ruatoria 0201 | 2024-08-18 09:18 | 2024-08-18 13:52 | 1.1354 | 0.023653 | 616 | 29568 | Unplanned | Vegetation | Tree thru line - High winds. See #11 & #15 & #22 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 519 | N/A 34 | Coast | Makarika 0204 | 2024-08-18 09:18 | 2024-08-18 10:04 | 0.19959 | 0.004339 | 113 | 5198 | Unplanned | Vegetation | Tree thru line - High winds. See #11 & #15 & #22 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 520 | N/A 34 | Coast | Tiki Tiki 0206 | 2024-08-18 09:18 | 2024-08-18 18:41 | 4.65 | 0.024268 | 632 | 121100 | Unplanned | Vegetation | Tree thru line - High winds. See #11 & #15 & #22 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 521 | 7416 | 2026 Waihi Road | Frasertown 3103 | 2024-08-18 10:15 | 2024-08-18 14:30 | 0.029374 | 0.00011519 | 3 | 765 | Unplanned | Adverse Weather | Replace isolation fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 522 | 29309 | Waiapu Rd / Mangatuna Road | Toko Tie 0401 | 2024-08-18 11:34 | 2024-08-18 20:50 | 0.78121 | 0.0032254 | 84 | 20345 | Unplanned | Defective Equipment | Centre bolt failed, tripped x-arm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 523 | 29311 | Turihau | Dalton 0502 | 2024-08-18 11:44 | 2024-08-19 17:23 | 3.4483 | 0.0091387 | 238 | 89804 | Unplanned | Adverse Weather | Wind broke conductor A4441 - A4441. No Backfeed, see #10 & #17. See #10 Wharikiri Rd off | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 524 | 29307 | Waimata Valley Road | Waimata 0903 | 2024-08-18 12:03 | 2024-08-20 12:06 | 0.78797 | 0.003571 | 93 | 20521 | Unplanned | Vegetation | Tree thru line. Fault #10 meant no Backfeed | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 525 | 29269 | Te Puia | Inland 0301 | 2024-08-18 12:32 | 2024-08-19 14:13 | 8.3866 | 0.0061437 | 160 | 218412 | Unplanned | Vegetation | Tree thru line - High Winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 526 | 29316 | Tauwhareparau | Tauwhareparae 0404 | 2024-08-18 12:46 | 2024-08-21 18:49 | 4.9239 | 0.011059 | 288 | 128234 | Unplanned | Defective Equipment | Broken pole due to high winds G2265 plus tree thru line G2509 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 527 | 29308 | Rototahi | Rototahi 0403 | 2024-08-18 12:48 | 2024-08-19 10:49 | 3.213 | 0.008294 | 216 | 83676 | Unplanned | Vegetation | Tree thru line, no back feed. Turihau Fault #13 & #19 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 528 | 7417 | 44 Ngamotu Road | Affco 3202 | 2024-08-18 12:52 | 2024-08-18 16:30 | 0.25949 | 0.0011903 | 31 | 6758 | Unplanned | Adverse Weather | Replaced fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 529 | 29313 | Makarika | Makarika 0204 | 2024-08-18 13:02 | 2024-08-19 18:53 | 6.7753 | 0.004339 | 113 | 176448 | Unplanned | Vegetation | Tree thru line - High winds. No back feeds. See #15 & #11 & #9 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 530 | 29315 | Mata Rd / Waiapu Road | Mata 0304 | 2024-08-18 13:24 | 2024-08-19 16:37 | 3.8273 | 0.0099067 | 258 | 99674 | Unplanned | Vegetation | Tree thru line @ H3527 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 531 | N/A 32 | Coast | Town 0402 | 2024-08-18 13:33 | 2024-08-18 14:21 | 0.37784 | 0.0078716 | 205 | 9840 | Unplanned | Adverse Weather | High Winds. Tauwharepara G327 open see #16 Toko Open #12 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 532 | 29312 | Frasertown Road / Awatere Road | Nuhaka 3203 | 2024-08-18 21:08 | 2024-08-18 21:37 | 0.014476 | 0.00049917 | 13 | 377 | Unplanned | Adverse Weather | High Winds broke Conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 533 | 9405 | Te Wera Road | Matawai 1204 | 2024-08-19 07:01 | 2024-08-19 18:00 | 0.27835 | 0.00042238 | 11 | 7249 | Unplanned | Adverse Weather | Replaced fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 534 | 9308 | Mangamaia Road | Whatatutu 1201 | 2024-08-19 07:15 | 2024-08-19 12:30 | 0.30238 | 0.00095995 | 25 | 7875 | Unplanned | Adverse Weather | Replaced HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 535 | 29295 | Te Araroa Substation, All feeders. Sub on Generator | Te Araroa Sub 01 | 2024-08-19 07:32 | 2024-08-19 16:22 | 1.5779 | 0.035595 | 927 | 41093 | Unplanned | Vegetation | 4 spans of conductor down @ pole J324 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 536 | 9404 | Waingake Road | Te Arai 0906 | 2024-08-19 10:43 | 2024-08-20 14:30 | 0.32005 | 0.00019199 | 5 | 8335 | Unplanned | Adverse Weather | Replaced fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 537 | N/A 31 | Ohuka | Ruakituri 2003 | 2024-08-19 13:03 | 2024-08-19 13:57 | 0.058058 | 0.0010751 | 28 | 1512 | Unplanned | Adverse Weather | Intial fault caused by PVT pole fault. 2nd Fault not found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 538 | 29319 | Charteris Rise | Nelson 0803 | 2024-08-19 16:26 | 2024-08-20 11:53 | 0.010598 | 0.0017663 | 46 | 276 | Unplanned | Defective Equipment | Faulty cable term up pole. Install generator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 539 | 9311 | Rakaroa Road | Whatatutu 1201 | 2024-08-19 16:30 | 2024-08-19 19:00 | 0.13823 | 0.00092155 | 24 | 3600 | Unplanned | Adverse Weather | Replaced HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 540 | 29276 | Waiapu Road | Mata 0304 | 2024-08-19 17:00 | 2024-08-19 18:51 | 0.012787 | 0.00011519 | 3 | 333 | Unplanned | Defective Equipment | Broken Pole , High Winds H621 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 541 | 29328 | Waione Road | Awatere 0101 | 2024-08-19 17:30 | 2024-08-20 18:21 | 0.85877 | 0.00057597 | 15 | 22365 | Unplanned | Vegetation | Tree in line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 542 | 29331 | Waitahia | Mata 0304 | 2024-08-19 17:30 | 2024-08-22 15:14 | 1.3165 | 0.00080636 | 21 | 34286 | Unplanned | Defective Equipment | Replace burning pole. High winds broke binder wire off insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 543 | 29325 | Ruatoria | Ruatoria 0201 | 2024-08-19 18:05 | 2024-08-20 17:24 | 0.10598 | 0.0033022 | 86 | 2760 | Unplanned | Defective Equipment | Repair Faulty ABS J622. Cracked Insulator faulm type | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 544 | 29278 | Kotemaori | Raupunga 3101 | 2024-08-19 19:34 | 2024-08-19 20:13 | 0.0059901 | 0.00015359 | 4 | 156 | Unplanned | Vegetation | Tree through LV supplied by TX W595 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 545 | 9312 | Ruakaka Road | Tiniroto 1003 | 2024-08-19 20:03 | 2024-08-20 12:30 | 0.87167 | 0.00088315 | 23 | 22701 | Unplanned | Adverse Weather | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 546 | 9403 | Paparatu | Te Arai 0906 | 2024-08-19 21:38 | 2024-08-20 14:00 | 0.60331 | 0.00061437 | 16 | 15712 | Unplanned | Adverse Weather | Replaced ddo fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 547 | 29317 | Ngatapa Sub | Tahora 1103 | 2024-08-20 05:03 | 2024-08-20 05:40 | 0.21453 | 0.0057981 | 151 | 5587 | Unplanned | Wildlife | Intertrip D31 - D13 appears due to OC trip CB D15. Bird strikes - Turkey | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 548 | 29317 | Ngatapa Sub | Ngatapa 1102 | 2024-08-20 05:03 | 2024-08-20 05:39 | 0.096763 | 0.0026879 | 70 | 2520 | Unplanned | Wildlife | Intertrip D31 - D13 appears due to OC trip CB D15. Bird strikes - Turkey | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 549 | 29317 | Ngatapa Sub | Totangi 1101 | 2024-08-20 05:03 | 2024-08-20 10:00 | 0.15966 | 0.00053757 | 14 | 4158 | Unplanned | Wildlife | Intertrip D31 - D13 appears due to OC trip CB D15. Bird strikes - Turkey | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 550 | 29317 | Ngatapa Sub | Ngatapa Sub 11 | 2024-08-20 05:03 | 2024-08-20 05:34 | 0.0011903 | 3.8398e-05 | 1 | 31 | Unplanned | Wildlife | Intertrip D31 - D13 appears due to OC trip CB D15. Bird strikes - Turkey | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 551 | 29281 | SH 35 | Tiki Tiki 0206 | 2024-08-20 10:48 | 2024-08-20 17:12 | 0.17348 | 0.00069116 | 18 | 4518 | Unplanned | Defective Equipment | Replaced 11kV Pole J2383. Repair 11kV conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 552 | 29290 | Waihi Rd | Frasertown 3103 | 2024-08-20 15:45 | 2024-08-20 16:45 | 0.025343 | 0.00042238 | 11 | 660 | Unplanned | Defective Equipment | Broken Jumper | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 553 | 29293 | Bushy Knoll Rd | Tiniroto 1003 | 2024-08-20 17:43 | 2024-08-22 15:10 | 0.8203 | 0.00046078 | 12 | 21363 | Unplanned | Vegetation | Replaced pole damaged by tree. Multiple faults on at same time | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 554 | 3118 | Andrews Rd Waiomoko Rd | Dalton 0502 | 2024-08-22 09:14 | 2024-08-22 14:09 | 0.033982 | 0.00011519 | 3 | 442.557 | Planned | Planned | Replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 555 | 9314 | Lake Road | Lavenham 0902 | 2024-08-22 10:57 | 2024-08-22 15:00 | 0.055984 | 0.00023039 | 6 | 1458 | Unplanned | Wildlife | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 556 | 7420 | 14 Spence Road, Te Ringa | Ruakituri 2003 | 2024-08-23 07:23 | 2024-08-23 09:00 | 0.037246 | 0.00038398 | 10 | 970 | Unplanned | Unknown cause | Replaced fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 557 | 3138 | Rakauroa Rd Tahora Rd Shaw Rd | Matawai 1204 | 2024-08-23 08:57 | 2024-08-23 10:59 | 0.070268 | 0.00057597 | 15 | 916.4255 | Planned | Planned | Replace TX F186 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 558 | 3119 | Andrews Rd Waiomoko Rd | Whangara 0506 | 2024-08-23 09:03 | 2024-08-23 14:40 | 0.03882 | 0.00011519 | 3 | 505.5582 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 559 | 29300 | Popoporo Valley | Tiki Tiki 0206 | 2024-08-23 11:24 | 2024-08-23 14:23 | 0.089352 | 0.00049917 | 13 | 2327 | Unplanned | Defective Equipment | High Winds blew pole on 45deg lean. Straighten | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 560 | 9315 | Te Wera Road | Matawai 1204 | 2024-08-23 12:36 | 2024-08-23 18:30 | 0.14952 | 0.00042238 | 11 | 3894 | Unplanned | Defective Equipment | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 561 | 3130 | Potae St Beach Rd Tokomaru St Waima St Hikirangi St | Seaside 0302 | 2024-08-24 09:02 | 2024-08-24 13:07 | 1.0536 | 0.0043006 | 112 | 13792.2497 | Planned | Planned | Tree Cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 562 | 29359 | Waitahia | Mata 0304 | 2024-08-25 11:09 | 2024-08-25 12:55 | 0.016281 | 0.00015359 | 4 | 424 | Unplanned | Defective Equipment | High winds broke binder | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 563 | 29360 | Goodwin Road | Whangara 0506 | 2024-08-25 19:00 | 2024-08-25 19:42 | 0.088469 | 0.0021119 | 55 | 2304 | Unplanned | Defective Equipment | Broken jumper on A87 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 564 | 29362 | Hiruharama Road | Makarika 0204 | 2024-08-25 19:08 | 2024-08-26 12:23 | 0.51204 | 0.004339 | 113 | 13335 | Unplanned | Vegetation | Tree across line @ pole H241. Tree team arranged for 26/8 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 565 | 3144 | Riverside Rd Goodwin Rd | Whangara 0506 | 2024-08-26 09:03 | 2024-08-26 13:41 | 0.58711 | 0.0021119 | 55 | 7661.1454 | Planned | Planned | To install sectionaliser controls onto A91 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 566 | 29361 | Wharf Road | Rototahi 0403 | 2024-08-26 10:51 | 2024-08-26 12:04 | 0.044849 | 0.00061437 | 16 | 1168 | Unplanned | Third Party Interference | Replace pole G2678 (car V's pole over weekend) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 567 | 29401 | Mata Road | Mata 0304 | 2024-08-26 11:17 | 2024-08-26 11:50 | 0.029144 | 0.00088315 | 23 | 759 | Unplanned | Defective Equipment | Repair blown jumper on ABS H179. High Winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 568 | 3148 | Waikura Valley Rd Te Kumi Rd | Hicks Bay 0102 | 2024-08-27 08:34 | 2024-08-27 10:44 | 0.18969 | 0.0014591 | 38 | 2479.9804 | Planned | Planned | Pole Replacements - Helicopter unable to fly due to wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 569 | 3139 | Nuhaka Opoutama Rd Waikokopu Rd Whaanga St Wai Station Rd | Nuhaka 3203 | 2024-08-27 09:04 | 2024-08-27 13:19 | 0.2252 | 0.00088315 | 23 | 2935.8516 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 570 | 3167 | Parkers Lane | Campion 0802 | 2024-08-27 09:04 | 2024-08-27 16:00 | 0.17571 | 0.00042238 | 11 | 4576 | Planned | Planned | Replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 571 | 3147 | Tyndall Rd Lawrence St Halley St | Herschell 0501 | 2024-08-27 09:05 | 2024-08-27 14:38 | 0.9462 | 0.0028415 | 74 | 12356.0096 | Planned | Planned | Replace and upgrade TX A289 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 572 | 3124 | Tapuihikitia Rd Rangatira Rd | Whatatutu 1201 | 2024-08-27 09:07 | 2024-08-27 12:34 | 0.087432 | 0.00042238 | 11 | 1138.9809 | Planned | Planned | Upgrade TX & DDO Fuses F442 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 573 | 29353 | Mahia Peninsula | Mahia 3301 | 2024-08-27 09:49 | 2024-08-27 13:09 | 3.0975 | 0.072035 | 1876 | 80668 | Unplanned | Defective Equipment | Generator not running correctly. Speed Freq mismatch. Low oil pressure claims | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 574 | 29347 | Cobden Street | City 0602 | 2024-08-27 10:41 | 2024-09-05 06:26 | 0.14061 | 0.0072956 | 190 | 3662 | Unplanned | Defective Equipment | Cable termination failure @RMU B889. Fault at Library (old) open point B608 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 575 | 6688 | 243 Tuparoa Road | Ruatoria 0201 | 2024-08-27 17:50 | 2024-08-27 18:25 | 0.026879 | 0.00076796 | 20 | 700 | Unplanned | Adverse Weather | High winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 576 | 3145 | Taumata Road | Tahora 1103 | 2024-08-28 09:00 | 2024-08-28 12:10 | 0.1605 | 0.00084476 | 22 | 2092.2302 | Planned | Planned | To install sectionaliser control @ switch D3416 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 577 | N/A 33 | Bell Road | Bell 1406 | 2024-08-29 00:15 | 2024-08-29 02:33 | 0.97999 | 0.0091003 | 237 | 25522 | Unplanned | Unknown cause | Patrol no fault found. No wind/rain | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 578 | 3141 | Nuhaka Opoutama Rd Waikokopu Rd Whaanga St Wai Station Rd | Nuhaka 3203 | 2024-08-29 09:03 | 2024-08-29 13:53 | 0.25611 | 0.00088315 | 23 | 3338.3516 | Planned | Planned | Replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 579 | 3151 | Rangitukia Rd Beach Rd East Cape Rd | Tiki Tiki 0206 | 2024-08-29 09:05 | 2024-08-29 15:32 | 0.69842 | 0.0018047 | 47 | 9110.9129 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 580 | 3152 | River Parade Bridge St Freyberg St | Borough One 3204 | 2024-08-29 09:06 | 2024-08-29 15:35 | 0.19418 | 0.00049917 | 13 | 2497.2459 | Planned | Planned | Upgrade TX W1534 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 581 | 29373 | East Cape Road | Te Araroa 0103 | 2024-08-29 11:41 | 2024-08-30 09:59 | 0.4766 | 0.0013823 | 36 | 12412 | Unplanned | Defective Equipment | Replace x-arm @ pole J3764 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 582 | 29372 | Bushmere Road | Bell 1406 | 2024-08-29 14:32 | 2024-08-29 15:07 | 0.0040318 | 0.00011519 | 3 | 105 | Unplanned | Defective Equipment | To repair HV termination dead-end @ C5365 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 583 | 3157 | Kotare Road | Frasertown 3103 | 2024-08-30 09:14 | 2024-08-30 13:18 | 0.018738 | 7.6796e-05 | 2 | 244.0253 | Planned | Planned | Replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 584 | 7423 | 740 HereHeretu Road | Nuhaka 3203 | 2024-08-30 12:56 | 2024-08-30 14:00 | 0.0024575 | 3.8398e-05 | 1 | 64 | Unplanned | Vegetation | Replaced fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 585 | 5575 | Waitangi Road | Kanakanaia 1202 | 2024-08-30 18:30 | 2024-08-30 20:30 | 0.059901 | 0.00049917 | 13 | 1560 | Unplanned | Unknown cause | Fuse fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 586 | 5577 | 1542 Panikau Road | Dalton 0502 | 2024-08-31 11:30 | 2024-08-31 12:38 | 0.0026111 | 3.8398e-05 | 1 | 68 | Unplanned | Unknown cause | Fuse fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 587 | N/A 35 | Waikura Valley Road | Hicks Bay 0102 | 2024-09-01 02:30 | 2024-09-01 11:24 | 0.77917 | 0.0038782 | 101 | 20292 | Unplanned | Adverse Weather | No obvious fault found. High wind through area at the time | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 588 | 6690 | 1904 Waikura Road | Hicks Bay 0102 | 2024-09-01 07:10 | 2024-09-01 11:15 | 0.36689 | 0.0014975 | 39 | 9555 | Unplanned | Adverse Weather | Very wndy overnight through to 10:30am | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 589 | 29381 | Matawai Rd, Te Wera Rd, Koranga Valley Road | Matawai 1204 | 2024-09-01 12:29 | 2024-09-01 18:12 | 0.93511 | 0.0027263 | 71 | 24353 | Unplanned | Vegetation | High wind caused conductor to be caught in tree by Pole F1947 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 590 | 29383 | Stanley Road | Lytton 0701 | 2024-09-01 19:43 | 2024-09-03 17:50 | 0.04865 | 0.0029566 | 77 | 1267 | Unplanned | Defective Equipment | Blown 11kV cable termination | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 591 | 29388 | Awapuni Road | Awapuni 0606 | 2024-09-02 09:30 | 2024-09-05 14:24 | 0.0055293 | 7.6796e-05 | 2 | 144 | Unplanned | Defective Equipment | Cable fault between fues switch B220 & TX B323 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 592 | 29394 | Waimata feeder, Ingram Rd | Waimata 0903 | 2024-09-02 17:52 | 2024-09-02 19:45 | 0.94778 | 0.02492 | 649 | 24683 | Unplanned | Defective Equipment | Wire down between pole D4547 & D4548. Broke Mid-span. No obvious cause | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 593 | 3179 | Cave Road | Whangara 0506 | 2024-09-03 08:32 | 2024-09-03 14:18 | 0.053143 | 0.00015359 | 4 | 1384 | Planned | Planned | Replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 594 | 3168 | Lake Road | Frasertown 3103 | 2024-09-03 09:00 | 2024-09-03 16:19 | 1.9048 | 0.004339 | 113 | 49607 | Planned | Planned | Replace 50kV/11kV poles & Switchgear | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 595 | 3158 | Waiapu Road | Toko Tie 0401 | 2024-09-03 09:09 | 2024-09-03 16:31 | 0.69585 | 0.0015743 | 41 | 9054.7326 | Planned | Planned | Replace 11kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 596 | 3159 | Lake Road | Frasertown 3103 | 2024-09-04 09:01 | 2024-09-04 15:55 | 0.22256 | 0.00053757 | 14 | 2899.5579 | Planned | Planned | Replace 11kV pole & TX W1693 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 597 | 29453 | Waimata Feeder | Waimata 0903 | 2024-09-05 07:42 | 2024-09-05 08:50 | 0.48474 | 0.02492 | 649 | 12624 | Unplanned | Third Party Interference | Bulk carrier dropped load at site and contacted OH 11kV | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 598 | 3180 | Cave Road | Whangara 0506 | 2024-09-05 08:31 | 2024-09-05 12:53 | 0.040241 | 0.00015359 | 4 | 1048 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 599 | 3160 | Waiapu Road | Toko Tie 0401 | 2024-09-05 09:00 | 2024-09-05 16:11 | 0.67853 | 0.0015743 | 41 | 8849.4099 | Planned | Planned | Replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 600 | 29455 | Royd Rd | Waimata 0903 | 2024-09-05 09:34 | 2024-09-05 10:21 | 0.070384 | 0.0014975 | 39 | 1833 | Unplanned | Defective Equipment | Broken shackle insulator at Pole C2030 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 601 | 3161 | Waiapu Road | Toko Tie 0401 | 2024-09-06 09:00 | 2024-09-06 13:17 | 0.26644 | 0.0010367 | 27 | 3474.1187 | Planned | Planned | Pole Replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 602 | 3155 | Collin Street | Brickworks 3201 | 2024-09-06 09:02 | 2024-09-06 16:09 | 1.0985 | 0.0025727 | 67 | 14341.3007 | Planned | Planned | Replace TX W1576 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 603 | 29431 | Kipling Road | Kanakanaia 1202 | 2024-09-06 14:38 | 2024-09-06 16:03 | 0.34854 | 0.0068732 | 179 | 9077 | Unplanned | Defective Equipment | Cable termination failure@ pole F3386. Jumpers removed cable isolated | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 604 | 3203 | Renner Road | Lavenham 0902 | 2024-09-09 10:02 | 2024-09-09 11:36 | 0.0072188 | 7.6796e-05 | 2 | 188 | Unplanned | Third Party Interference | Stopbank construction LV installation + LV lines removed @ TX D360 until further notice | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 605 | 3169 | Kanakania Road | Kanakanaia 1202 | 2024-09-10 08:30 | 2024-09-10 15:59 | 0.4655 | 0.0010367 | 27 | 6067.7842 | Planned | Planned | Replace poles & install new HV fuses @ E1107 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 606 | 3162a | Russell Parade, Carroll St | Frasertown 3103 | 2024-09-10 08:45 | 2024-09-10 08:59 | 0.00053757 | 3.8398e-05 | 1 | 0 | Planned | Planned | Install RMU & upgrade poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 607 | 3146 | Woodgreen / Ebbett Road | Ruakituri 2003 | 2024-09-10 09:00 | 2024-09-10 12:12 | 0.28015 | 0.0014591 | 38 | 3654.6536 | Planned | Planned | Upgrade controls sectionalizer W799 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 608 | 3162 | Russell Parade, Carroll St | Frasertown 3103 | 2024-09-10 09:04 | 2024-09-10 17:58 | 1.2905 | 0.0025727 | 67 | 14953.8356 | Planned | Planned | Install RMU & upgrade poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 609 | 3162b | Russell Parade, Carroll St | Frasertown 3103 | 2024-09-10 17:00 | 2024-09-10 17:14 | 0.00053757 | 3.8398e-05 | 1 | 7.0003 | Planned | Planned | Install RMU & upgrade poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 610 | 3162 | Russell Parade, Carroll St | Frasertown 3103 | 2024-09-10 17:31 | 2024-09-10 17:52 | 0.033061 | 0.0016895 | 44 | 861 | Unplanned | Human Error | Install RMU and Upgrade poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 611 | 29476 | Makaretu Road | Matawai 1204 | 2024-09-11 06:35 | 2024-09-11 14:23 | 0.50394 | 0.0023423 | 61 | 13124 | Unplanned | Defective Equipment | Pin off crossarm pole F761 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 612 | 3171 | Motu Road | Matawai 1204 | 2024-09-11 08:31 | 2024-09-11 16:14 | 0.088891 | 0.00019199 | 5 | 1122.7155 | Planned | Planned | Replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 613 | 3172 | Bloomfield Road | Bushmere 0805 | 2024-09-11 08:33 | 2024-09-11 10:47 | 0.010291 | 7.6796e-05 | 2 | 134.0103 | Planned | Planned | Replace LV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 614 | 3192 | Ormond Valley Road | Waimata 0903 | 2024-09-11 08:34 | 2024-09-11 11:40 | 0.23569 | 0.0012671 | 33 | 6138 | Planned | Planned | Cut trees from 11kV line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 615 | 3170 | Kanakania Road | Kanakanaia 1202 | 2024-09-12 08:30 | 2024-09-12 15:24 | 0.42921 | 0.0010367 | 27 | 5594.7944 | Planned | Planned | Replace 11kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 616 | 3204 | Russel Parade | Frasertown 3103 | 2024-09-12 09:03 | 2024-09-12 14:42 | 0.26034 | 0.00076796 | 20 | 6780 | Planned | Planned | OHUG conversion from DDO W1626 to Fuse switch W1318 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 617 | 3163 | Russell Parade Road | Frasertown 3103 | 2024-09-12 09:03 | 2024-09-12 10:04 | 0.1069 | 0.0018431 | 48 | 1345.2386 | Planned | Planned | Disconnect redundant 11kV OH Pole W1258 - W1626 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 618 | 29449 | Hereheretau Road | Nuhaka 3203 | 2024-09-12 15:41 | 2024-09-12 16:30 | 0.035749 | 0.00072956 | 19 | 931 | Unplanned | Defective Equipment | Repair broken 11kV jumper @ pole W8506 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 619 | 3174 | Kanakanaia Road | Kanakanaia 1202 | 2024-09-13 08:34 | 2024-09-13 13:07 | 0.073379 | 0.00026879 | 7 | 955.8104 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 620 | 3176 | Haisman Rd, Tuckers Road | Haisman 0804 | 2024-09-13 09:00 | 2024-09-13 18:48 | 1.4902 | 0.0025343 | 66 | 14887.6339 | Planned | Planned | Replace Pole C5729 hit by car | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 621 | 29434 | Kipling Road | Te Karaka 1203 | 2024-09-13 14:54 | 2024-09-13 15:16 | 0.021119 | 0.00095995 | 25 | 550 | Unplanned | Defective Equipment | Repair cable term fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 622 | 3177 | Goodwin Road | Whangara 0506 | 2024-09-14 09:03 | 2024-09-14 11:26 | 0.082364 | 0.00057597 | 15 | 1073.1177 | Planned | Planned | Install new TX | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 623 | 3175 | Matawai | Matawai 1204 | 2024-09-17 08:30 | 2024-09-17 09:41 | 0.6434 | 0.0090619 | 236 | 3572.0793 | Planned | Planned | To replace Pole F1559. Install Sectionalisers at F423 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 624 | 3183 | Matawai Road | Matawai 1204 | 2024-09-17 08:31 | 2024-09-17 12:40 | 0.62147 | 0.0024959 | 65 | 5864.6009 | Planned | Planned | Replace 11kV pole F1962. Early start time due to Major Matawai S/down on Otoko Hill started prior to this advertised outage time. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 625 | 3175a | Matawai | Matawai 1204 | 2024-09-17 08:32 | 2024-09-17 17:00 | 0.039012 | 7.6796e-05 | 2 | 478.0367 | Planned | Planned | To replace Pole F1559. Install Sectionalisers at F423 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 626 | 29478 | 3709 Whangara Road | Rototahi 0403 | 2024-09-17 09:34 | 2024-09-17 10:08 | 0.0013055 | 3.8398e-05 | 1 | 34 | Unplanned | Defective Equipment | Replaced 11kV termination dedend @ TX A150 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 627 | 3182 | Matawai Road | Matawai 1204 | 2024-09-17 13:07 | 2024-09-17 14:39 | 0.010598 | 0.00011519 | 3 | 138.0159 | Planned | Planned | Replaced TX F237 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 628 | 3175b | Matawai | Matawai 1204 | 2024-09-17 16:03 | 2024-09-17 17:00 | 0.51653 | 0.0090619 | 236 | 3214.8713 | Planned | Planned | To replace Pole F1559. Install Sectionalisers at F423 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 629 | 8425 | 1405 Wharekopae Road | Lavenham 0902 | 2024-09-17 16:40 | 2024-09-18 12:32 | 0.04577 | 3.8398e-05 | 1 | 1192 | Unplanned | Lightning | Replaced fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 630 | 29517 | Wairere Road | Tamarau 0503 | 2024-09-17 16:42 | 2024-09-18 16:20 | 0.28153 | 0.0036094 | 94 | 7332 | Unplanned | Lightning | Lightening blew up cable term. Install generator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 631 | 8424 | 88 Campbell Road | Lavenham 0902 | 2024-09-18 07:41 | 2024-09-18 08:30 | 0.015052 | 0.00030718 | 8 | 392 | Unplanned | Lightning | Replace DDO | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 632 | 7514 | 2762 Bushy Knoll Rd | Tiniroto 1003 | 2024-09-18 08:04 | 2024-09-18 12:30 | 0.030642 | 0.00011519 | 3 | 798 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 633 | 3184 | Bushmere Road | Bell 1406 | 2024-09-18 08:36 | 2024-09-18 16:03 | 0.08582 | 0.00019199 | 5 | 1117.7145 | Planned | Planned | Replace LV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 634 | 3156 | Morere Road | Nuhaka 3203 | 2024-09-18 09:00 | 2024-09-18 12:14 | 1.147 | 0.0062973 | 164 | 14997.9744 | Planned | Planned | Upgraded Switch W810 to Sectionaliser | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 635 | 3189 | Tolaga Bay | Toko Tie 0401 | 2024-09-18 09:00 | 2024-09-18 16:30 | 0.19007 | 0.00042238 | 11 | 1650.6969 | Planned | Planned | Replace ABS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 636 | 29481 | Wharekopae Road | Lavenham 0902 | 2024-09-18 12:21 | 2024-09-19 13:54 | 0.058864 | 3.8398e-05 | 1 | 1533 | Unplanned | Lightning | Replace TX D1914 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 637 | 29482 | Wharekopae Road | Lavenham 0902 | 2024-09-18 12:51 | 2024-09-19 11:47 | 0.052836 | 3.8398e-05 | 1 | 1376 | Unplanned | Lightning | Replace TX D52 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 638 | 7516 | 551 Parikanapa Road | Parikanapa 1002 | 2024-09-18 14:00 | 2024-09-18 15:00 | 0.0023039 | 3.8398e-05 | 1 | 60 | Unplanned | Lightning | Replaced TX fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 639 | 7419 | 3141 Mahia Eastcoast Road | Mahia 3301 | 2024-09-18 14:45 | 2024-09-19 11:00 | 0.41988 | 0.00034558 | 9 | 10935 | Unplanned | Adverse Weather | Replaced fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 640 | 8432 | 148 Campbell Rd | Lavenham 0902 | 2024-09-18 18:34 | 2024-09-18 19:40 | 0.0025343 | 3.8398e-05 | 1 | 66 | Unplanned | Lightning | Replace DDA fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 641 | 3193 | Wheatstone Road | Dalton 0502 | 2024-09-19 08:32 | 2024-09-19 15:11 | 0.4443 | 0.0011135 | 29 | 5791.9424 | Planned | Planned | Replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 642 | 3191 | Rutherford Street | Borough Two 3205 | 2024-09-19 08:34 | 2024-09-19 15:47 | 0.81469 | 0.0018815 | 49 | 10628.4599 | Planned | Planned | Upgrade TX W1548 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 643 | 3195 | Taylors bay | Mahia 3301 | 2024-09-20 08:34 | 2024-09-20 13:24 | 0.5345 | 0.0018431 | 48 | 6975.9244 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 644 | 3220 | Tuckers Road, Haisman Rd | Haisman 0804 | 2024-09-20 09:00 | 2024-09-20 15:45 | 1.0264 | 0.0025343 | 66 | 26730 | Planned | Planned | To complete installation of replacement 50kV/11kV Pole C5729 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 645 | 3194 | Parkers Lane | Campion 0802 | 2024-09-20 09:03 | 2024-09-20 13:28 | 0.11193 | 0.00042238 | 11 | 1458.2666 | Planned | Planned | Replace HV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 646 | 3223 | Whangara Road | Dalton 0502 | 2024-09-20 09:04 | 2024-09-20 13:21 | 0.35526 | 0.0013823 | 36 | 9252 | Planned | Planned | Replace Pole A784 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 647 | 3197 | Kabul Street | Borough One 3204 | 2024-09-20 09:05 | 2024-09-20 14:05 | 0.57597 | 0.0019199 | 50 | 7515.8392 | Planned | Planned | Replave TX W1577 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 648 | 8440 | 1K up Kaiaua Road | Toko Tie 0401 | 2024-09-21 07:46 | 2024-09-21 12:06 | 0.0099835 | 3.8398e-05 | 1 | 260 | Unplanned | Unknown cause | Replace DDO fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 649 | 29495 | Kaiaua Road | Toko Tie 0401 | 2024-09-21 12:22 | 2024-09-21 13:00 | 0.023346 | 0.00061437 | 16 | 608 | Unplanned | Defective Equipment | Floating wire cracked insulator at pole G727 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 650 | 9410 | 3406 Whakarau Road | Matawai 1204 | 2024-09-22 19:34 | 2024-09-22 21:00 | 0.0066045 | 7.6796e-05 | 2 | 172 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 651 | 9411 | 1542 Panikau Road | Dalton 0502 | 2024-09-23 08:00 | 2024-09-23 10:00 | 0.04147 | 0.00034558 | 9 | 1080 | Unplanned | Unknown cause | Replace fruse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 652 | 3198 | McDonalds Road | JNL_A 1405 | 2024-09-23 08:35 | 2024-09-23 14:29 | 0.081557 | 0.00023039 | 6 | 1062.2447 | Planned | Planned | Replace HV Bus | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 653 | 9412 | 1532 Whakekopae Road | Lavenham 0902 | 2024-09-23 09:30 | 2024-09-23 14:32 | 0.011596 | 3.8398e-05 | 1 | 302 | Unplanned | Unknown cause | Replaced fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 654 | 3185 | Waikura Valley Road | Hicks Bay 0102 | 2024-09-24 08:31 | 2024-09-24 15:56 | 0.64931 | 0.0014591 | 38 | 8467.3369 | Planned | Planned | Replace HV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 655 | 8706 | 3406 Whakarau Road | Matawai 1204 | 2024-09-24 08:49 | 2024-09-24 12:30 | 0.008486 | 3.8398e-05 | 1 | 221 | Unplanned | Adverse Weather | Replaced DDO's | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 656 | 3188 | Pongaroa / Onenui | Mahia 3301 | 2024-09-24 09:02 | 2024-09-24 13:29 | 1.1585 | 0.004339 | 113 | 15150.9557 | Planned | Planned | Upgrade remote switch W1221 to Sectionaliser | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 657 | 3201 | Waiapu Road | Toko Tie 0401 | 2024-09-24 09:04 | 2024-09-24 12:45 | 0.35641 | 0.0016127 | 42 | 4651.1601 | Planned | Planned | Replace ABS G42 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 658 | 7428 | 1737 Ohuka Road | Ruakituri 2003 | 2024-09-24 11:20 | 2024-09-24 14:00 | 0.061437 | 0.00038398 | 10 | 1600 | Unplanned | Unknown cause | Replace Fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 659 | 8705 | 81 Waiherere Road | Waimata 0903 | 2024-09-24 13:36 | 2024-09-24 15:30 | 0.01751 | 0.00015359 | 4 | 456 | Unplanned | Vegetation | Replaced DDO | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 660 | 8703 | 1542 Panikau Road | Dalton 0502 | 2024-09-24 16:47 | 2024-09-24 20:00 | 0.066697 | 0.00034558 | 9 | 1737 | Unplanned | Adverse Weather | Replace DDO | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 661 | 8704 | 119 Hill Side Road | Ngatapa 1102 | 2024-09-24 17:49 | 2024-09-24 18:30 | 0.0031486 | 7.6796e-05 | 2 | 82 | Unplanned | Adverse Weather | Replaced DDO's | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 662 | 3202 | Crawford Road / Wainui Rd | Crawford 1504 | 2024-09-25 08:32 | 2024-09-25 15:34 | 1.831 | 0.004339 | 113 | 23946.4542 | Planned | Planned | Replace RMU | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 663 | 3199 | McDonalds Road | JNL_A 1405 | 2024-09-25 08:34 | 2024-09-25 14:56 | 0.088008 | 0.00023039 | 6 | 1146.264 | Planned | Planned | Replace HV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 664 | 3186 | Waikura Valley Road | Hicks Bay 0102 | 2024-09-26 08:33 | 2024-09-26 12:48 | 0.37208 | 0.0014591 | 38 | 4854.9804 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 665 | 3200 | McDonalds Road | JNL_A 1405 | 2024-09-27 08:37 | 2024-09-27 12:37 | 0.055293 | 0.00023039 | 6 | 720.2281 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 666 | 3206 | Waiapu Road | Toko Tie 0401 | 2024-09-27 09:01 | 2024-09-27 13:25 | 0.41562 | 0.0015743 | 41 | 5422.6503 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 667 | 3190 | Campbell Street | Brickworks 3201 | 2024-09-27 09:04 | 2024-09-27 14:52 | 0.6414 | 0.0018431 | 48 | 8367.3936 | Planned | Planned | Replace TX | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 668 | 29538 | Bushy Knoll Rd | Tiniroto 1003 | 2024-09-27 10:43 | 2024-09-27 15:27 | 0.10559 | 0.00072956 | 19 | 2750 | Unplanned | Defective Equipment | Broken conductor at bind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 669 | 8702 | 263 Kaiaua Road | Toko Tie 0401 | 2024-09-27 15:15 | 2024-09-27 16:45 | 0.0034558 | 3.8398e-05 | 1 | 90 | Unplanned | Defective Equipment | Replace broken ddo | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 670 | 8701 | Pitcher Road | Te Karaka 1203 | 2024-09-27 16:47 | 2024-09-27 20:00 | 0.051876 | 0.00026879 | 7 | 1351 | Unplanned | Wildlife | Replaced ddo fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 671 | 7427 | 370 SH2 Wairoa | Nuhaka 3203 | 2024-09-27 19:09 | 2024-09-27 20:00 | 0.0058749 | 0.00011519 | 3 | 153 | Unplanned | Unknown cause | Replace Fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 672 | 3210 | Matawai Road | Te Karaka 1203 | 2024-09-28 09:04 | 2024-09-28 11:11 | 0.10728 | 0.00084476 | 22 | 1398.1801 | Planned | Planned | Install new TX E1841 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 673 | 3215 | Awapuni Road | Lytton 0701 | 2024-10-01 09:02 | 2024-10-01 11:26 | 0.10506 | 0.00072956 | 19 | 1368.998 | Planned | Planned | Replace ampact joints & check cable toms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 674 | 1621 | Maungataniwha | Raupunga 3101 | 2024-10-01 15:04 | 2024-10-01 16:08 | 0.02588 | 0.00042238 | 11 | 674 | Unplanned | Vegetation | Restore 11kV conductor after plantation clearance. Remove generator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 675 | 3224 | Kaimoe Road | Lavenham 0902 | 2024-10-02 08:33 | 2024-10-02 10:06 | 0.078562 | 0.00084476 | 22 | 1023.8642 | Planned | Planned | To install Line fault indicators @ D315 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 676 | 3221 | SH 2 Waihua | Raupunga 3101 | 2024-10-02 09:00 | 2024-10-02 14:16 | 1.8706 | 0.0069116 | 180 | 24432.8682 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 677 | 3213 | Makarika | Makarika 0204 | 2024-10-02 09:05 | 2024-10-02 12:31 | 0.17855 | 0.00088315 | 23 | 2326.6646 | Planned | Planned | Cut trees | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 678 | 1622 | Tolaga Bay Sub | Rototahi 0403 | 2024-10-03 04:32 | 2024-10-03 10:00 | 0.26541 | 0.016588 | 432 | 6912 | Unplanned | Defective Equipment | Centre bolt out of x-arm @pole A908. Blown jumper @ pole A1071 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 679 | 1622 | Tolaga Bay Sub | Town 0402 | 2024-10-03 04:32 | 2024-10-03 10:01 | 0.27551 | 0.015743 | 410 | 7175 | Unplanned | Defective Equipment | Centre bolt out of x-arm @pole A908. Blown jumper @ pole A1071 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 680 | 1622 | Tolaga Bay Sub | Toko Tie 0401 | 2024-10-03 04:32 | 2024-10-03 10:30 | 0.21541 | 0.0065277 | 170 | 5610 | Unplanned | Defective Equipment | Centre bolt out of x-arm @pole A908. Blown jumper @ pole A1071 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 681 | 1622 | Tolaga Bay Sub | Tauwhareparae 0404 | 2024-10-03 04:32 | 2024-10-03 11:22 | 0.4809 | 0.011212 | 292 | 12524 | Unplanned | Defective Equipment | Centre bolt out of x-arm @pole A908. Blown jumper @ pole A1071 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 682 | 8602 | 160 Hikuwai Road | Mata 0304 | 2024-10-03 09:01 | 2024-10-03 11:05 | 0.023807 | 0.00019199 | 5 | 620 | Unplanned | Unknown cause | Replace HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 683 | 8603 | 84 Koia Road | Tiki Tiki 0206 | 2024-10-03 16:42 | 2024-10-03 18:45 | 0.033061 | 0.00026879 | 7 | 861 | Unplanned | Unknown cause | Replace HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 684 | 29544 | Ihungia Road | Mata 0304 | 2024-10-03 19:38 | 2024-10-04 15:33 | 0.17375 | 0.00061437 | 16 | 4525 | Unplanned | Vegetation | 2 span down between Poles H635 - H633. Pine tree out of zone | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 685 | 8604 | 5422 Te Araroa Road | Awatere 0101 | 2024-10-04 07:41 | 2024-10-04 12:00 | 0.01989 | 7.6796e-05 | 2 | 518 | Unplanned | Unknown cause | Replace HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 686 | 7429 | 3141 Mahia Eastcoast Road | Mahia 3301 | 2024-10-04 08:00 | 2024-10-04 11:00 | 0.062205 | 0.00034558 | 9 | 1620 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 687 | 3222 | SH2 Waihua, Mohaka | Raupunga 3101 | 2024-10-04 09:03 | 2024-10-04 15:52 | 2.7312 | 0.0067197 | 175 | 35655.7821 | Planned | Planned | Pole Replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 688 | 3222 | SH2 Waihua Mohaka | Raupunga 3101 | 2024-10-04 09:04 | 2024-10-04 15:49 | 0.077756 | 0.00019199 | 5 | 2025 | Unplanned | Human Error | Pole Replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 689 | 29545 | Koia Road | Tiki Tiki 0206 | 2024-10-04 10:28 | 2024-10-04 10:56 | 0.0032254 | 0.00011519 | 3 | 84 | Unplanned | Defective Equipment | Moved centre phase connection @ TX J241 to outside phase. Was only AB connection on Koia Road, other 2 TX were AC connections. AC fuses only used @ HV fuses J2076. Centre phase left deenergised, to reduce risk of line clash during hight winds. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 690 | 1623 | Wharf Rd, Main Rd, Monkhouse Uawa Parade | Rototahi 0403 | 2024-10-04 15:13 | 2024-10-04 15:39 | 0.12679 | 0.0048766 | 127 | 3302 | Unplanned | Defective Equipment | Faulty HV DDO fuse @ TX G2909 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 691 | 29549 | Te Araroa Road | Awatere 0101 | 2024-10-04 16:28 | 2024-10-04 18:12 | 0.051722 | 0.00072956 | 19 | 1347 | Unplanned | Defective Equipment | Broken Jumper @ HV Pole J2414 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 692 | 9319 | Waihau Tap off line | Rototahi 0403 | 2024-10-05 08:07 | 2024-10-05 09:30 | 0.044619 | 0.00053757 | 14 | 1162 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 693 | 9320 | Tauwhareparae Road | Tauwhareparae 0404 | 2024-10-05 09:37 | 2024-10-05 13:45 | 0.019045 | 7.6796e-05 | 2 | 496 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 694 | 3217 | Ahimanu Road | Parikanapa 1002 | 2024-10-07 08:38 | 2024-10-07 15:38 | 0.1774 | 0.00042238 | 11 | 0 | Planned | Planned | Replace HV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 695 | N/A 41 | SH35 Waiapu Road | Inland 0301 | 2024-10-07 16:04 | 2024-10-07 19:41 | 0.17832 | 0.0061437 | 160 | 4644 | Unplanned | Vegetation | HV Conductor wrapped between poles H2036 - H2038. Caused by tree | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 696 | 8126 | Panikau Road | Dalton 0502 | 2024-10-07 20:09 | 2024-10-07 21:26 | 0.02661 | 0.00034558 | 9 | 693 | Unplanned | Unknown cause | Replaced fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 697 | 3232 | Opoutama, Mahanga | Mahia 3301 | 2024-10-08 09:01 | 2024-10-08 16:28 | 4.0687 | 0.0092923 | 242 | 53205.1034 | Planned | Planned | To replace & Upgrade s/gear - W958 & W789. Install poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 698 | 29578 | Raupunga / Kotemaori | Raupunga 3101 | 2024-10-08 09:34 | 2024-10-08 16:57 | 0.82203 | 0.013746 | 358 | 21408 | Unplanned | Vegetation | Tree through HV Line @ 745 Waihua Valley Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 699 | 3236 | Lahore Street | Borough One 3204 | 2024-10-08 12:47 | 2024-10-08 18:46 | 0.78574 | 0.0021887 | 57 | 8083.1529 | Planned | Planned | Replacing Link Box 11373 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 700 | N/A 36 | Makaraka - Parkinson Substations | Solander 0706 | 2024-10-08 21:38 | 2024-10-08 22:05 | 0.042507 | 0.0015743 | 41 | 1107 | Unplanned | Wildlife | Possum on 50kV Pole B1813 - found on ground. No Possum guards on this pole or others in proximity | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 701 | N/A 36 | Makaraka - Parkinson Substations | Cedenco A 0704 | 2024-10-08 21:38 | 2024-10-08 22:05 | 0.0031102 | 0.00011519 | 3 | 81 | Unplanned | Wildlife | Possum on 50kV Pole B1813 - found on ground. No Possum guards on this pole or others in proximity | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 702 | N/A 36 | Makaraka - Parkinson Substations | Innes 0705 | 2024-10-08 21:38 | 2024-10-08 22:05 | 0.033176 | 0.0012287 | 32 | 864 | Unplanned | Wildlife | Possum on 50kV Pole B1813 - found on ground. No Possum guards on this pole or others in proximity | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 703 | N/A 36 | Makaraka - Parkinson Substations | Chalmers 0707 | 2024-10-08 21:38 | 2024-10-08 22:06 | 0.7655 | 0.027339 | 712 | 19936 | Unplanned | Wildlife | Possum on 50kV Pole B1813 - found on ground. No Possum guards on this pole or others in proximity | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 704 | N/A 36 | Makaraka - Parkinson Substations | Lytton 0701 | 2024-10-08 21:38 | 2024-10-08 22:06 | 0.076335 | 0.0027263 | 71 | 1988 | Unplanned | Wildlife | Possum on 50kV Pole B1813 - found on ground. No Possum guards on this pole or others in proximity | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 705 | N/A 36 | Makaraka - Parkinson Substations | Willows 0702 | 2024-10-08 21:38 | 2024-10-08 22:06 | 0.089237 | 0.003187 | 83 | 2324 | Unplanned | Wildlife | Possum on 50kV Pole B1813 - found on ground. No Possum guards on this pole or others in proximity | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 706 | N/A 36 | Makaraka - Parkinson Substations | Elgin 0703 | 2024-10-08 21:38 | 2024-10-08 22:06 | 0.99021 | 0.035365 | 921 | 25788 | Unplanned | Wildlife | Possum on 50kV Pole B1813 - found on ground. No Possum guards on this pole or others in proximity | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 707 | N/A 36 | Makaraka - Parkinson Substations | Campion 0802 | 2024-10-08 21:38 | 2024-10-08 22:35 | 1.5912 | 0.027915 | 727 | 41439 | Unplanned | Wildlife | Possum on 50kV Pole B1813 - found on ground. No Possum guards on this pole or others in proximity | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 708 | N/A 36 | Makaraka - Parkinson Substations | Bushmere 0805 | 2024-10-08 21:38 | 2024-10-08 22:33 | 0.38436 | 0.0069884 | 182 | 10010 | Unplanned | Wildlife | Possum on 50kV Pole B1813 - found on ground. No Possum guards on this pole or others in proximity | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 709 | N/A 36 | Makaraka - Parkinson Substations | Nelson 0803 | 2024-10-08 21:38 | 2024-10-08 23:08 | 3.0549 | 0.033944 | 884 | 79560 | Unplanned | Wildlife | Possum on 50kV Pole B1813 - found on ground. No Possum guards on this pole or others in proximity | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 710 | N/A 36 | Makaraka - Parkinson Substations | Haisman 0804 | 2024-10-08 21:38 | 2024-10-08 23:09 | 3.3824 | 0.037169 | 968 | 88088 | Unplanned | Wildlife | Possum on 50kV Pole B1813 - found on ground. No Possum guards on this pole or others in proximity | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 711 | 3226 | Kanakanaia Road | Kanakanaia 1202 | 2024-10-09 08:30 | 2024-10-09 11:16 | 0.1721 | 0.0010367 | 27 | 2245.6187 | Planned | Planned | To replace poles - Too windy for Helicoptor operations | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 712 | 3218 | Ahimanu Road | Parikanapa 1002 | 2024-10-09 08:35 | 2024-10-09 16:04 | 0.18965 | 0.00042238 | 11 | 2470.5431 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 713 | 3233 | Waikokopu - Opoutama | Mahia 3301 | 2024-10-09 09:06 | 2024-10-09 14:25 | 0.5757 | 0.0018047 | 47 | 7510.4955 | Planned | Planned | Replace ABS & Ghoritt recloser - Recloser not working | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 714 | 8606 | 4314 Ihungia Road | Mata 0304 | 2024-10-09 14:39 | 2024-10-09 16:00 | 0.065315 | 0.00080636 | 21 | 1701 | Unplanned | Unknown cause | Replace HV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 715 | 3235 | Tarnbrane Road | Bell 1406 | 2024-10-10 09:07 | 2024-10-10 14:54 | 0.50632 | 0.0014591 | 38 | 6602.62 | Planned | Planned | Replace x-arm & connect new u/ground and TX | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 716 | 29583 | Wharerata Road | Muriwai 0905 | 2024-10-11 05:07 | 2024-10-11 11:43 | 0.8471 | 0.0099835 | 260 | 22061 | Unplanned | Vegetation | Tree through HV C3768 - C3769 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 717 | 3219 | Ahimanu Road | Parikanapa 1002 | 2024-10-11 08:32 | 2024-10-11 12:16 | 0.094613 | 0.00042238 | 11 | 1232.8363 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 718 | 3243A | Piripaua Road | Frasertown 3103 | 2024-10-11 08:33 | 2024-10-11 14:14 | 0.18331 | 0.00053757 | 14 | 4774 | Planned | Planned | Tree Cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 719 | 3225 | Waiapu Road | Makarika 0204 | 2024-10-11 09:02 | 2024-10-11 10:19 | 0.05322 | 0.00069116 | 18 | 694.8661 | Planned | Planned | To remove tree in close proximity | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 720 | 3239 | Rangiahua Road | Frasertown 3103 | 2024-10-14 08:52 | 2024-10-14 13:47 | 1.1627 | 0.0040318 | 105 | 15209.6925 | Planned | Planned | Cut Trees | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 721 | 29588 | Waimata Valley Road | Waimata 0903 | 2024-10-15 00:18 | 2024-10-15 14:58 | 0.12767 | 0.00023039 | 6 | 3325 | Unplanned | Third Party Interference | G614 Poles cut down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 722 | 3240a | Motu Road | Matawai 1204 | 2024-10-15 08:30 | 2024-10-16 14:21 | 0.031909 | 7.6796e-05 | 2 | 415.5161 | Planned | Planned | Build new HV Line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 723 | 3241 | Lahore St / Clyde Road | Borough One 3204 | 2024-10-15 08:34 | 2024-10-15 15:51 | 1.691 | 0.0043774 | 114 | 22073.7145 | Planned | Planned | Replace Link Box 11365 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 724 | 3238 | Rotoparu Road | Frasertown 3103 | 2024-10-15 08:37 | 2024-10-15 15:04 | 1.0699 | 0.0027647 | 72 | 13970.5172 | Planned | Planned | Cut trees between W6543 - W6544 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 725 | 3228 | Hikuwai Road | Mata 0304 | 2024-10-15 09:10 | 2024-10-15 16:18 | 0.082172 | 0.00019199 | 5 | 1070.2054 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 726 | 29591 | Fortesque / Weld Street | Mahia 3301 | 2024-10-15 14:31 | 2024-10-15 16:01 | 0.1486 | 0.0016511 | 43 | 3870 | Unplanned | Defective Equipment | Broken LV Conductor @ W3506 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 727 | 3240 | Motu Road | Matawai 1204 | 2024-10-15 16:30 | 2024-10-16 08:30 | 0.036862 | 3.8398e-05 | 1 | 960 | Unplanned | Human Error | Build new HV Line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 728 | 29594 | Raupunga - Mohuka | Raupunga 3101 | 2024-10-15 16:47 | 2024-10-16 15:00 | 3.8882 | 0.044158 | 1150 | 101261 | Unplanned | Adverse Environment | Slip had moved pole centre, span clashed and welded to outside. Forest harvested recently, no protection from high winds.320m SPA | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 729 | N/A 42 | Poroporo Valley Road | Tiki Tiki 0206 | 2024-10-16 09:12 | 2024-10-16 11:01 | 0.05441 | 0.00049917 | 13 | 1417 | Unplanned | Vegetation | Tree against HV conductor @ pole J1415 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 730 | 1626 | Pongoroa | Mahia 3301 | 2024-10-17 09:00 | 2024-10-17 13:32 | 1.1584 | 0.0043006 | 112 | 30168 | Planned | Planned | To replace broken d/ends. Replace larch poles. Install HV links W8995 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 731 | 3229 | Hikuwai Road | Mata 0304 | 2024-10-17 09:08 | 2024-10-17 15:05 | 0.06854 | 0.00019199 | 5 | 892.6714 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 732 | 3244 | Waiapu Road | Makarika 0204 | 2024-10-17 10:03 | 2024-10-17 12:41 | 0.27908 | 0.0017663 | 46 | 3386.0236 | Planned | Planned | Complete pipework ABS J622. Replace cable stand-offs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 733 | 3246 | Back Ormond Road | Waimata 0903 | 2024-10-18 08:31 | 2024-10-18 12:39 | 0.97132 | 0.0039166 | 102 | 12713.9164 | Planned | Planned | Replace ABS D432 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 734 | 3248 | Derby Street | Aberdeen 0609 | 2024-10-18 09:01 | 2024-10-18 10:02 | 0.24594 | 0.0040318 | 105 | 3215.4118 | Planned | Planned | Replace crucifix stand-off @B4197 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 735 | 3230 | Hikuwai Road | Mata 0304 | 2024-10-18 09:11 | 2024-10-18 14:07 | 0.056829 | 0.00019199 | 5 | 740.1584 | Planned | Planned | Replace Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 736 | 29598 | Hexton | Patutahi Sub 09 | 2024-10-18 10:30 | 2024-10-18 10:43 | 0.00049917 | 3.8398e-05 | 1 | 13 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 737 | 29598 | Hexton | Lavenham 0902 | 2024-10-18 10:30 | 2024-10-18 10:43 | 0.22413 | 0.017241 | 449 | 5837 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 738 | 29598 | Hexton | Waimata 0903 | 2024-10-18 10:30 | 2024-10-18 10:43 | 0.32396 | 0.02492 | 649 | 8437 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 739 | 29598 | Hexton | Muriwai 0905 | 2024-10-18 10:30 | 2024-10-18 10:43 | 0.20616 | 0.015858 | 413 | 5369 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 740 | 29598 | Hexton | Te Arai 0906 | 2024-10-18 10:30 | 2024-10-18 10:43 | 0.11681 | 0.0089851 | 234 | 3042 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 741 | 29598 | Hexton | Pehiri Sub 10 | 2024-10-18 10:30 | 2024-10-18 10:43 | 0.00049917 | 3.8398e-05 | 1 | 13 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 742 | 29598 | Hexton | W O Kuri 1001 | 2024-10-18 10:30 | 2024-10-18 10:43 | 0.023461 | 0.0018047 | 47 | 611 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 743 | 29598 | Hexton | Parikanapa 1002 | 2024-10-18 10:30 | 2024-10-18 10:43 | 0.014975 | 0.0011519 | 30 | 390 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 744 | 29598 | Hexton | Tiniroto 1003 | 2024-10-18 10:30 | 2024-10-18 10:43 | 0.062397 | 0.0047998 | 125 | 1625 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 745 | 29598 | Hexton | Tahunga 1004 | 2024-10-18 10:30 | 2024-10-18 10:43 | 0.02446 | 0.0018815 | 49 | 637 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 746 | 29598 | Hexton | Ngatapa Sub 11 | 2024-10-18 10:30 | 2024-10-18 10:43 | 0.00049917 | 3.8398e-05 | 1 | 13 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 747 | 29598 | Hexton | Totangi 1101 | 2024-10-18 10:30 | 2024-10-18 10:43 | 0.0069884 | 0.00053757 | 14 | 182 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 748 | 29598 | Hexton | Ngatapa 1102 | 2024-10-18 10:30 | 2024-10-18 10:43 | 0.034942 | 0.0026879 | 70 | 910 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 749 | 29598 | Hexton | Tahora 1103 | 2024-10-18 10:30 | 2024-10-18 10:43 | 0.075375 | 0.0057981 | 151 | 1963 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 750 | 29598 | Hexton | Puha Sub 12 | 2024-10-18 10:30 | 2024-10-18 10:44 | 0.00053757 | 3.8398e-05 | 1 | 14 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 751 | 29598 | Hexton | Whatatutu 1201 | 2024-10-18 10:30 | 2024-10-18 10:44 | 0.13117 | 0.0093691 | 244 | 3416 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 752 | 29598 | Hexton | Kanakanaia 1202 | 2024-10-18 10:30 | 2024-10-18 10:44 | 0.096225 | 0.0068732 | 179 | 2506 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 753 | 29598 | Hexton | Te Karaka 1203 | 2024-10-18 10:30 | 2024-10-18 10:44 | 0.097838 | 0.0069884 | 182 | 2548 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 754 | 29598 | Hexton | Matawai 1204 | 2024-10-18 10:30 | 2024-10-18 10:44 | 0.20697 | 0.014783 | 385 | 5390 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 755 | 29598 | Hexton | Dunstan 1403 | 2024-10-18 10:30 | 2024-10-18 10:45 | 0.0063357 | 0.00042238 | 11 | 165 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 756 | 29598 | Hexton | JNL_A 1405 | 2024-10-18 10:30 | 2024-10-18 10:45 | 0.011519 | 0.00076796 | 20 | 300 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 757 | 29598 | Hexton | Bell 1406 | 2024-10-18 10:30 | 2024-10-18 10:45 | 0.13651 | 0.0091003 | 237 | 3555 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 758 | 29598 | Hexton | Waipaoa 1408 | 2024-10-18 10:30 | 2024-10-18 10:45 | 0.0034558 | 0.00023039 | 6 | 90 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 759 | 3247 | Childers Road | Childers 0605 | 2024-10-18 12:01 | 2024-10-18 13:00 | 0.32623 | 0.0055293 | 144 | 4271.4885 | Planned | Planned | Replace LA's on Cruxifix | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 760 | 3249 | Stanley Road | Anzac 0604 | 2024-10-20 08:07 | 2024-10-20 16:53 | 0.30189 | 0.00057597 | 15 | 3932.3814 | Planned | Planned | Replace Oil RMU to Gas RMU | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 761 | 3251A | Sheltons Road | Rototahi 0403 | 2024-10-21 08:34 | 2024-10-21 15:59 | 0.27339 | 0.00061437 | 16 | 3562.1872 | Planned | Planned | Pole replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 762 | 3250 | Kawatiri Road | Waimata 0903 | 2024-10-21 09:02 | 2024-10-21 13:25 | 0.30296 | 0.0011519 | 30 | 3950.1837 | Planned | Planned | Replace ABS D636 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 763 | 3256 | Whakato Road | Muriwai 0905 | 2024-10-21 09:05 | 2024-10-21 09:26 | 0.030642 | 0.0014591 | 38 | 399.5822 | Planned | Planned | Tap Changer (External) in-operable | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 764 | 29631 | Pehiri Area | Tahunga 1004 | 2024-10-22 07:09 | 2024-10-22 11:03 | 0.80048 | 0.0096763 | 252 | 20847 | Unplanned | Defective Equipment | D672 CB blew-up Leading to Incomer CB D776 opening. Line Patrol from CB D672 to end of cct was undertaken - no obvious fault. Fault proved to PMR Type CB. CB D672 Isolated | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 765 | 3257 | Tiniroto Road | Lavenham 0902 | 2024-10-22 08:35 | 2024-10-22 10:03 | 0.03379 | 0.00038398 | 10 | 440.1728 | Planned | Planned | Install fault indicators @ Pole D1368 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 766 | 3255 | Clifton Lyall Road | Frasertown 3103 | 2024-10-22 08:51 | 2024-10-22 16:21 | 0.069116 | 0.00015359 | 4 | 900.1382 | Planned | Planned | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 767 | 3254 | Rangitukia Road | Tiki Tiki 0206 | 2024-10-22 09:01 | 2024-10-22 14:21 | 0.57751 | 0.0018047 | 47 | 7533.9955 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 768 | 3252 | Sheltons road | Rototahi 0403 | 2024-10-23 08:36 | 2024-10-23 15:22 | 0.24943 | 0.00061437 | 16 | 3249.9955 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 769 | 3258 | Kirkpatrick Road | Waimata 0903 | 2024-10-23 09:00 | 2024-10-23 14:37 | 0.41408 | 0.0012287 | 32 | 5398.6254 | Planned | Planned | Replace TX Structure | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 770 | 3259 | Centennial Marine Drive | JNL_A 1405 | 2024-10-24 08:33 | 2024-10-24 15:59 | 0.10275 | 0.00023039 | 6 | 1338.3083 | Planned | Planned | Replace TX C453 & 400V poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 771 | 3260 | Scott Street | Chalmers 0707 | 2024-10-24 09:02 | 2024-10-24 10:34 | 0.26141 | 0.0028415 | 74 | 3413.6723 | Planned | Planned | Replace Stand-offs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 772 | 3268 | Waihi Road | Frasertown 3103 | 2024-10-24 09:35 | 2024-10-24 12:25 | 0.16542 | 0.00099835 | 26 | 2155.8892 | Planned | Planned | Install new Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 773 | 29638 | Bruce Road | Kanakanaia 1202 | 2024-10-24 18:47 | 2024-10-24 19:21 | 0.0078332 | 0.00023039 | 6 | 204 | Unplanned | Defective Equipment | Repair blown jumper @ TX E212 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 774 | 3253 | Sheltons Road | Rototahi 0403 | 2024-10-25 08:37 | 2024-10-25 15:53 | 0.26786 | 0.00061437 | 16 | 3490.1429 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 775 | 3261 | Huxley Road | Dalton 0502 | 2024-10-26 09:01 | 2024-10-26 09:53 | 0.45924 | 0.0088315 | 230 | 6040.9377 | Planned | Planned | Install Line fault indicators @ Pole A4137 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 776 | N/A 37 | Waimata | Tahora 1103 | 2024-10-26 17:02 | 2024-10-26 20:09 | 0.22563 | 0.0017663 | 46 | 5876 | Unplanned | Vegetation | Tree branch on line, tree leaning into line D3450 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 777 | N/A 38 | Ihungia | Mata 0304 | 2024-10-28 10:00 | 2024-10-28 13:28 | 0.09684 | 0.00061437 | 16 | 2522 | Unplanned | Unknown cause | Line closed back in | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 778 | 76431 | 353 Ruakituri Road | Ruakituri 2003 | 2024-10-28 10:25 | 2024-10-28 12:30 | 0.0095995 | 7.6796e-05 | 2 | 250 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 779 | 9206 | 353 Ruakituri Road | Ruakituri 2003 | 2024-10-28 11:00 | 2024-10-28 12:15 | 0.0057597 | 7.6796e-05 | 2 | 150 | Unplanned | Wildlife | Replace HV TX fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 780 | 3245 | Wharekopae Road | Tahora 1103 | 2024-10-29 08:30 | 2024-10-29 09:28 | 0.12287 | 0.0021503 | 56 | 840.9216 | Planned | Planned | Install Generator Truck 300kVA - for work in Ngatapa Sub | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 781 | 3264 | Panikau Road | Dalton 0502 | 2024-10-29 08:30 | 2024-10-29 15:14 | 0.44987 | 0.0011135 | 29 | 5864.5231 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 782 | 3266 | Horehore Road | Makarika 0204 | 2024-10-29 09:03 | 2024-10-29 13:36 | 0.062896 | 0.00023039 | 6 | 531.1223 | Planned | Planned | To Remove Trees | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 783 | 3272 | Opoutama / Mahanga | Mahia 3301 | 2024-10-29 09:17 | 2024-10-29 16:00 | 2.9566 | 0.0073724 | 192 | 38679.4269 | Planned | Planned | To install new sectionaliser W900. Replace recloser W958. Replace defect pole W9074 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 784 | N/A 43 | Tahora | Ngatapa Sub 11 | 2024-10-29 09:46 | 2024-10-29 10:00 | 0.032216 | 0.0023423 | 61 | 839 | Unplanned | Human Error | CB D13 Closed to Bus Earth. Switching error. Generator feeding D141 - EOL Hahunga feeding D3416 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 785 | 8611 | Waione Road | Awatere 0101 | 2024-10-29 12:47 | 2024-10-29 16:55 | 0.14284 | 0.00057597 | 15 | 3720 | Unplanned | Unknown cause | Replace HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 786 | 77187 | 57 Waione Road | Awatere 0101 | 2024-10-29 12:47 | 2024-10-29 15:45 | 0.10252 | 0.00057597 | 15 | 2670 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 787 | 29643 | Kabul Streeet | Borough One 3204 | 2024-10-29 17:10 | 2024-10-29 18:02 | 0.52313 | 0.01006 | 262 | 13624 | Unplanned | Defective Equipment | Replace termination arms & DDO @ Pole W1419 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 788 | 3262 | Kanakanaia Road | Kanakanaia 1202 | 2024-10-30 08:30 | 2024-10-30 15:13 | 0.41781 | 0.0010367 | 27 | 5446.1404 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 789 | 3263 | Barkers Hill Road | Aberdeen 0609 | 2024-10-30 09:04 | 2024-10-30 14:05 | 1.0633 | 0.0035326 | 92 | 13894.9126 | Planned | Planned | Build and connect a temporary 11kV O/Head circuit and remove redundant circuit. For hill reinstatement roadworkds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 790 | N/A 39 | Mahia | Morere 3401 | 2024-10-30 15:28 | 2024-10-30 15:46 | 0.18523 | 0.010291 | 268 | 4824 | Unplanned | Lightning | Lightning in the area | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 791 | N/A 39 | Mahia | Mahia 3301 | 2024-10-30 15:28 | 2024-10-30 15:51 | 0.77917 | 0.036017 | 938 | 20292 | Unplanned | Lightning | Lightning in the area | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 792 | 77898 | 2507 Tiniroto Road | Ruakituri 2003 | 2024-10-30 18:49 | 2024-10-30 20:00 | 0.0027263 | 3.8398e-05 | 1 | 71 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 793 | 78039 | Panikau Road | Dalton 0502 | 2024-10-30 20:29 | 2024-10-30 23:00 | 0.052183 | 0.00034558 | 9 | 1359 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 794 | 5582 | Panikau Road | Dalton 0502 | 2024-10-30 20:30 | 2024-10-30 22:00 | 0.031102 | 0.00034558 | 9 | 810 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 795 | 3269 | Kaiti Mall | Wainui 0504 | 2024-10-30 21:02 | 2024-10-30 23:56 | 0.40088 | 0.0023039 | 60 | 5232.0263 | Planned | Planned | Upgrade 400V S/Board at TX A256 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 796 | 78238 | 2151 Tiniroto Road | Ruakituri 2003 | 2024-10-31 07:55 | 2024-10-31 08:55 | 0.0023039 | 3.8398e-05 | 1 | 60 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 797 | 3265 | Panikau Road | Dalton 0502 | 2024-10-31 08:30 | 2024-10-31 15:29 | 0.46657 | 0.0011135 | 29 | 6082.2653 | Planned | Planned | Replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 798 | 3271 | 5416 Te Araroa Road | Hicks Bay 0102 | 2024-10-31 11:01 | 2024-10-31 12:30 | 0.037592 | 0.00042238 | 11 | 489.9878 | Planned | Planned | Upgrade TX J286 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 799 | 3245A | Wharekopae Road | Tahora 1103 | 2024-10-31 16:01 | 2024-10-31 16:48 | 0.10106 | 0.0021503 | 56 | 0 | Planned | Planned | Removing Generator Truck 300kVA after work in Ngatapa Sub | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 800 | 5584 | Arakini Road | Tauwhareparae 0404 | 2024-10-31 19:25 | 2024-10-31 21:45 | 0.016127 | 0.00011519 | 3 | 420 | Unplanned | Unknown cause | Replace DDO fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 801 | 78650 | 6 Hillcrest Road | Borough Two 3205 | 2024-10-31 20:05 | 2024-10-31 23:30 | 0.0078716 | 3.8398e-05 | 1 | 205 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 802 | 3280 | Wharerata road | Muriwai 0905 | 2024-11-01 08:30 | 2024-11-01 13:29 | 0.26406 | 0.00088315 | 23 | 2417.1328 | Planned | Planned | Install new Pole & TX at C628 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 803 | 78847 | Bushy Knoll Cell Site | Tiniroto 1003 | 2024-11-01 12:13 | 2024-11-01 15:30 | 0.015129 | 7.6796e-05 | 2 | 394 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 804 | 8612 | 526 Tuparoa Road | Ruatoria 0201 | 2024-11-01 17:28 | 2024-11-01 19:10 | 0.0039166 | 3.8398e-05 | 1 | 102 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 805 | 78981 | 526 Tuparoa Road | Ruatoria 0201 | 2024-11-01 17:28 | 2024-11-01 18:30 | 0.0023807 | 3.8398e-05 | 1 | 62 | Unplanned | Wildlife | Replace fusewire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 806 | N/A 40 | Pehiri Sub & Ngatapa Sub | W O Kuri 1001 | 2024-11-02 06:51 | 2024-11-02 07:41 | 0.090235 | 0.0018047 | 47 | 2350 | Unplanned | Unknown cause | 50Kv cb22 Tripped (EF). Supply restored via 11kV to Ngatapa and Pehiri sub feeders. 50kV circuits closed back IN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 807 | N/A 40 | Pehiri Sub & Ngatapa Sub | Parikanapa 1002 | 2024-11-02 06:51 | 2024-11-02 08:08 | 0.088699 | 0.0011519 | 30 | 2310 | Unplanned | Unknown cause | 50Kv cb22 Tripped (EF). Supply restored via 11kV to Ngatapa and Pehiri sub feeders. 50kV circuits closed back IN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 808 | N/A 40 | Pehiri Sub & Ngatapa Sub | Tahunga 1004 | 2024-11-02 06:51 | 2024-11-02 08:08 | 0.14488 | 0.0018815 | 49 | 3773 | Unplanned | Unknown cause | 50Kv cb22 Tripped (EF). Supply restored via 11kV to Ngatapa and Pehiri sub feeders. 50kV circuits closed back IN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 809 | N/A 40 | Pehiri Sub & Ngatapa Sub | Tiniroto 1003 | 2024-11-02 06:51 | 2024-11-02 08:09 | 0.37438 | 0.0047998 | 125 | 9750 | Unplanned | Unknown cause | 50Kv cb22 Tripped (EF). Supply restored via 11kV to Ngatapa and Pehiri sub feeders. 50kV circuits closed back IN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 810 | N/A 40 | Pehiri Sub & Ngatapa Sub | Tahora 1103 | 2024-11-02 06:51 | 2024-11-02 09:02 | 0.67293 | 0.0057981 | 151 | 17525 | Unplanned | Unknown cause | 50Kv cb22 Tripped (EF). Supply restored via 11kV to Ngatapa and Pehiri sub feeders. 50kV circuits closed back IN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 811 | N/A 40 | Pehiri Sub & Ngatapa Sub | Ngatapa 1102 | 2024-11-02 06:51 | 2024-11-02 08:50 | 0.31986 | 0.0026879 | 70 | 8330 | Unplanned | Unknown cause | 50Kv cb22 Tripped (EF). Supply restored via 11kV to Ngatapa and Pehiri sub feeders. 50kV circuits closed back IN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 812 | N/A 40 | Pehiri Sub & Ngatapa Sub | Totangi 1101 | 2024-11-02 06:51 | 2024-11-02 09:02 | 0.070422 | 0.00053757 | 14 | 1834 | Unplanned | Unknown cause | 50Kv cb22 Tripped (EF). Supply restored via 11kV to Ngatapa and Pehiri sub feeders. 50kV circuits closed back IN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 813 | 80087 | 1235 Panikau Road | Dalton 0502 | 2024-11-03 04:53 | 2024-11-03 09:00 | 0.085359 | 0.00034558 | 9 | 2223 | Unplanned | Vegetation | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 814 | 3274 | Queen Street | Borough Two 3205 | 2024-11-03 08:41 | 2024-11-03 15:28 | 0.43758 | 0.0010751 | 28 | 4470.8016 | Planned | Planned | Replace Link Boxes 11212 & 11201 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 815 | 79868 | 1857 Ruakaka Road | Tiniroto 1003 | 2024-11-03 16:49 | 2024-11-03 19:00 | 0.0050301 | 3.8398e-05 | 1 | 131 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 816 | 29712 | Gladstone/Childers/Palmerston/Wellington/Stanley | Childers 0605 | 2024-11-04 10:45 | 2024-11-04 17:30 | 2.2912 | 0.076681 | 1997 | 59669 | Unplanned | Defective Equipment | RMU B6542/B6541/B6540/B6539 - Faulted during switching operation 3273 when breaking a parallel. Able to Isolate & restore all customers except Wellington Street. 300kVA generator installed @ TX B40. GGHS off for whole period. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 817 | 3275 | Titirangi Road | Frasertown 3103 | 2024-11-05 08:35 | 2024-11-05 16:23 | 0.28752 | 0.00061437 | 16 | 3746.3002 | Planned | Planned | Isolation to cut trees | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 818 | 81949 | 757 Whakaangiangi Road | Awatere 0101 | 2024-11-06 05:44 | 2024-11-06 08:50 | 0.014284 | 7.6796e-05 | 2 | 372 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 819 | 3277 | Kiore Road | Tauwhareparae 0404 | 2024-11-06 08:32 | 2024-11-06 15:36 | 0.17909 | 0.00042238 | 11 | 2332.985 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 820 | 82018 | 2108 tiniroto Road | Ruakituri 2003 | 2024-11-06 08:58 | 2024-11-06 10:45 | 0.0041086 | 3.8398e-05 | 1 | 107 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 821 | 3276 | Titirangi Road | Frasertown 3103 | 2024-11-07 08:36 | 2024-11-07 14:36 | 0.22117 | 0.00061437 | 16 | 2881.7694 | Planned | Planned | Cut Trees away for O/Head | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 822 | 3281 | Wharekiri Road | Dalton 0502 | 2024-11-07 09:01 | 2024-11-07 14:21 | 0.31947 | 0.00099835 | 26 | 8320 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 823 | 3278 | Kiore Road | Tauwhareparae 0404 | 2024-11-08 08:32 | 2024-11-08 14:33 | 0.15248 | 0.00042238 | 11 | 1986.3386 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 824 | 29690 | Matawai Road | Waimata 0903 | 2024-11-09 09:57 | 2024-11-09 12:34 | 0.11454 | 0.00072956 | 19 | 2983 | Unplanned | Third Party Interference | Car V's Pole D658 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 825 | 3273 | Cobden / Derby / Childers | City 0602 | 2024-11-09 21:18 | 2024-11-09 21:55 | 0.013478 | 0.00072956 | 19 | 258.0021 | Unplanned | Human Error | Error by controller. Started switching in wrong place | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 826 | 3287 | Bushmere Road | Bell 1406 | 2024-11-11 09:01 | 2024-11-11 10:25 | 0.041931 | 0.00049917 | 13 | 546.3894 | Planned | Planned | Install 11kV/400V line brakes at pole C5340 / C5342 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 827 | 3279 | Kiore Road | Tauwhareparae 0404 | 2024-11-12 08:38 | 2024-11-12 15:57 | 0.18542 | 0.00042238 | 11 | 2415.5198 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 828 | 3282 | Waihi Road | Frasertown 3103 | 2024-11-12 09:04 | 2024-11-12 17:40 | 0.35664 | 0.00069116 | 18 | 3746.5877 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 829 | 29691 | Bloomfield Road | Bell 1406 | 2024-11-12 10:29 | 2024-11-12 15:41 | 0.046654 | 0.0011519 | 30 | 1215 | Unplanned | Human Error | To install & Remove 11kV line breat @ Pole C5270. Overlooked when prepping switching for 110kV | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 830 | 86025 | 352 Mahaki Settlement Rd | Matawai 1204 | 2024-11-12 18:01 | 2024-11-12 20:50 | 0.051914 | 0.00030718 | 8 | 1352 | Unplanned | Defective Equipment | Re-fixed crossarm to pole, re-livened | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 831 | 86294 | 1235 Panikau Road | Dalton 0502 | 2024-11-13 03:54 | 2024-11-13 14:22 | 0.21703 | 0.00034558 | 9 | 5652 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 832 | 86317 | Tutamoe Stn, Tolaga Bay | Tauwhareparae 0404 | 2024-11-13 06:07 | 2024-11-13 10:00 | 0.098414 | 0.00042238 | 11 | 2563 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 833 | 3293 | Awapuni Road | Willows 0702 | 2024-11-13 09:02 | 2024-11-13 10:15 | 0.019621 | 0.00026879 | 7 | 255.5687 | Planned | Planned | To replace defected Ampacts | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 834 | 3283 | Ramotu Road | Frasertown 3103 | 2024-11-13 09:12 | 2024-11-13 14:02 | 0.11135 | 0.00038398 | 10 | 1440.5529 | Planned | Planned | Install new TX W4271 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 835 | 3290 | Kiore Road | Tauwhareparae 0404 | 2024-11-14 08:31 | 2024-11-14 15:06 | 0.12134 | 0.00030718 | 8 | 1580.4854 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 836 | 3289 | Bushmere Road | Bell 1406 | 2024-11-14 09:01 | 2024-11-14 10:37 | 0.047921 | 0.00049917 | 13 | 624.3894 | Planned | Planned | Rejoin 11kV lin breaks @ Pole C5340 & C5342 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 837 | 3292 | Waihi Road | Frasertown 3103 | 2024-11-14 09:13 | 2024-11-14 16:44 | 0.17318 | 0.00038398 | 10 | 2035.7814 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 838 | 29733 | Mahia | Mahia 3301 | 2024-11-14 09:18 | 2024-11-14 17:10 | 1.8585 | 0.0086012 | 224 | 48401 | Unplanned | Defective Equipment | Burnt-outx-arm. Failed Insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 839 | 3295 | Taumata Road | Tahora 1103 | 2024-11-15 08:30 | 2024-11-15 15:52 | 0.37165 | 0.00084476 | 22 | 4842.1603 | Planned | Planned | Replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 840 | 3291 | Kiore Road | Tauwhareparae 0404 | 2024-11-15 08:35 | 2024-11-15 11:30 | 0.013439 | 7.6796e-05 | 2 | 175.0253 | Planned | Planned | Replaced LV poles beyond TX G144 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 841 | 3294 | Waihi Road | Frasertown 3103 | 2024-11-15 09:03 | 2024-11-15 14:50 | 0.13324 | 0.00038398 | 10 | 1735.6662 | Planned | Planned | Replace 11kv Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 842 | 3288 | Anzac St / Kahutia Street | Anzac 0604 | 2024-11-15 17:15 | 2024-11-15 17:38 | 0.11807 | 0.0054141 | 141 | 1060.4677 | Planned | Planned | Phase out @ Gas switch B751 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 843 | 3320 | Childers Road | Childers 0605 | 2024-11-15 21:17 | 2024-11-15 21:41 | 0.048842 | 0.0020351 | 53 | 1272 | Planned | Planned | Phase out of Childers feeder cable - Urgent Work | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 844 | 88272 | 927 Koranga Valley road | Matawai 1204 | 2024-11-16 07:54 | 2024-11-16 13:15 | 0.012326 | 3.8398e-05 | 1 | 321 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 845 | 88294 | 121 Maraehare Riad | Awatere 0101 | 2024-11-16 08:23 | 2024-11-16 10:45 | 0.027263 | 0.00019199 | 5 | 710 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 846 | 3299 | Gladstone Road | Campion 0802 | 2024-11-16 09:01 | 2024-11-16 13:59 | 0.51492 | 0.0017279 | 45 | 6716.6634 | Planned | Planned | Replace TX C433 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 847 | 3296 | Taumata Road | Tahora 1103 | 2024-11-18 08:30 | 2024-11-18 16:30 | 0.40433 | 0.00084476 | 22 | 4945.2114 | Planned | Planned | Replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 848 | 29746 | Patutahi/Pehiri/Ngatapa Subs | Ngatapa Sub 11 | 2024-11-18 13:25 | 2024-11-18 13:29 | 0.00015359 | 3.8398e-05 | 1 | 4 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 849 | 29746 | Patutahi/Pehiri/Ngatapa Subs | Totangi 1101 | 2024-11-18 13:25 | 2024-11-18 13:29 | 0.0021503 | 0.00053757 | 14 | 56 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 850 | 29746 | Patutahi/Pehiri/Ngatapa Subs | Ngatapa 1102 | 2024-11-18 13:25 | 2024-11-18 13:29 | 0.010751 | 0.0026879 | 70 | 280 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 851 | 29746 | Patutahi/Pehiri/Ngatapa Subs | Tahora 1103 | 2024-11-18 13:25 | 2024-11-18 13:29 | 0.023192 | 0.0057981 | 151 | 604 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 852 | 29746 | Patutahi/Pehiri/Ngatapa Subs | Pehiri Sub 10 | 2024-11-18 13:25 | 2024-11-18 13:29 | 0.00015359 | 3.8398e-05 | 1 | 4 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 853 | 29746 | Patutahi/Pehiri/Ngatapa Subs | W O Kuri 1001 | 2024-11-18 13:25 | 2024-11-18 13:29 | 0.0072188 | 0.0018047 | 47 | 188 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 854 | 29746 | Patutahi/Pehiri/Ngatapa Subs | Parikanapa 1002 | 2024-11-18 13:25 | 2024-11-18 13:29 | 0.0046078 | 0.0011519 | 30 | 120 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 855 | 29746 | Patutahi/Pehiri/Ngatapa Subs | Tiniroto 1003 | 2024-11-18 13:25 | 2024-11-18 13:29 | 0.019199 | 0.0047998 | 125 | 500 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 856 | 29746 | Patutahi/Pehiri/Ngatapa Subs | Tahunga 1004 | 2024-11-18 13:25 | 2024-11-18 13:29 | 0.007526 | 0.0018815 | 49 | 196 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 857 | 29746 | Patutahi/Pehiri/Ngatapa Subs | Lavenham 0902 | 2024-11-18 13:25 | 2024-11-18 14:02 | 0.57497 | 0.017241 | 449 | 14974 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 858 | 29746 | Patutahi/Pehiri/Ngatapa Subs | Waimata 0903 | 2024-11-18 13:25 | 2024-11-18 14:02 | 0.92205 | 0.02492 | 649 | 24013 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 859 | 29746 | Patutahi/Pehiri/Ngatapa Subs | Te Arai 0906 | 2024-11-18 13:25 | 2024-11-18 14:02 | 0.33245 | 0.0089851 | 234 | 8658 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 860 | 29746 | Patutahi/Pehiri/Ngatapa Subs | Puha Sub 12 | 2024-11-18 13:25 | 2024-11-18 14:02 | 0.0014207 | 3.8398e-05 | 1 | 37 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 861 | 29746 | Patutahi/Pehiri/Ngatapa Subs | Muriwai 0905 | 2024-11-18 13:25 | 2024-11-18 14:15 | 0.79292 | 0.015858 | 413 | 20650 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 862 | 90289 | 362 Whakaangiangi Rd | Awatere 0101 | 2024-11-19 09:12 | 2024-11-19 11:10 | 0.004531 | 3.8398e-05 | 1 | 118 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 863 | N/A 44 | Te Reinga / Mahurangi / Whakapunaki | Ruakituri 2003 | 2024-11-19 14:29 | 2024-11-19 17:04 | 0.18393 | 0.0013055 | 34 | 4790 | Unplanned | Defective Equipment | Faulty lightning arrestor @ TX W1778 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 864 | 29751 | Waiapu Road | Inland 0301 | 2024-11-20 04:36 | 2024-11-21 11:45 | 0.60918 | 0.0061437 | 160 | 15865 | Unplanned | Wildlife | Suspect bird strike - Conductor down across river | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 865 | 3302 | Stout Street | Aberdeen 0609 | 2024-11-20 07:20 | 2024-11-20 07:34 | 0.03763 | 0.0026879 | 70 | 350.9408 | Planned | Planned | Replace Oil RMU to Gas CFC RMU | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 866 | 3304 | Wheatstone Road | Dalton 0502 | 2024-11-20 08:32 | 2024-11-20 14:24 | 0.39197 | 0.0011135 | 29 | 5109.8127 | Planned | Planned | Replace HV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 867 | 3297 | Taumata Road | Tahora 1103 | 2024-11-20 08:34 | 2024-11-20 15:32 | 0.48151 | 0.0011519 | 30 | 6277.2227 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 868 | 29750 | Waiomatatini Road | Tiki Tiki 0206 | 2024-11-20 12:27 | 2024-11-20 13:52 | 0.055485 | 0.00065277 | 17 | 1445 | Unplanned | Third Party Interference | Repaired broken conductor between poles J2904 & J2905. Digger contact on conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 869 | 29755 | Te Hau Road | Whatatutu 1201 | 2024-11-20 16:10 | 2024-11-20 18:48 | 0.091003 | 0.00057597 | 15 | 2370 | Unplanned | Third Party Interference | Digger came in contact with HV line @ pole E1976 - E1977 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 870 | 90912 | 110 Te Hau Rd, Whatatutu | Whatatutu 1201 | 2024-11-20 16:10 | 2024-11-20 18:20 | 0.11481 | 0.00088315 | 23 | 2990 | Unplanned | Human Error | 0 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 871 | 3302 A | Stout Street | Aberdeen 0609 | 2024-11-20 17:17 | 2024-11-20 17:34 | 0.045694 | 0.0026879 | 70 | 456.223 | Planned | Planned | Replace Oil RMU to Gas CFC RMU | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 872 | 3338 | Hicks Bay / Lottin Point / Waikura Valley | Hicks Bay 0102 | 2024-11-21 09:00 | 2024-11-21 13:57 | 1.0378 | 0.0034942 | 91 | 27027 | Planned | Planned | To replace pole J4074 - Urgent Work | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 873 | 3298 | Waihi Road | Frasertown 3103 | 2024-11-21 09:02 | 2024-11-21 15:49 | 0.15628 | 0.00038398 | 10 | 2035.7814 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 874 | 91416 | 2750 Ihunga Road | Mata 0304 | 2024-11-21 11:24 | 2024-11-21 15:35 | 0.2024 | 0.00080636 | 21 | 5271 | Unplanned | Defective Equipment | Checked fuses H188 Puketoro side Ok. Drove the loop to fuses H272. Centre Hv DDO was burnt out. Replaced with new, held in when closed | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 875 | 1634 | 4378 Wharekopae Road | Tahora 1103 | 2024-11-21 12:32 | 2024-11-21 16:39 | 0.55009 | 0.0022271 | 58 | 14326 | Planned | Planned | Replace Pole D5060 - Urgent Work | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 876 | N/A 45 | Mata Road | Mata 0304 | 2024-11-21 15:27 | 2024-11-21 15:31 | 0.0046078 | 0.0011519 | 30 | 120 | Unplanned | Lightning | To Allow close on HV Fuses H272 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 877 | N/A 46 | Whangara/Glenroy/Waiomoko | Dalton 0502 | 2024-11-22 05:22 | 2024-11-22 09:14 | 0.75644 | 0.0067197 | 175 | 19700 | Unplanned | Unknown cause | Line Patrolled - no obvious fault found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 878 | 91871 | Café 287, SH2 | Brickworks 3201 | 2024-11-22 05:49 | 2024-11-22 07:00 | 0.013631 | 0.00019199 | 5 | 355 | Unplanned | Adverse Weather | Patrol line. Replaced middle and right side HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 879 | 3303 | Taumata Road | Tahora 1103 | 2024-11-22 08:30 | 2024-11-22 16:17 | 0.38667 | 0.00084476 | 22 | 5037.5946 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 880 | 3301 | Kanakanaia Road | Kanakanaia 1202 | 2024-11-22 09:02 | 2024-11-22 15:57 | 0.43025 | 0.0010367 | 27 | 4838.0106 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 881 | 92006 | Kiore Bay Road, Tolaga Bay | Tauwhareparae 0404 | 2024-11-22 13:32 | 2024-11-22 16:47 | 0.059901 | 0.00030718 | 8 | 1560 | Unplanned | Wildlife | Un bine wire off pin let wires float cut head off pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 882 | 29764 | Rangikohua Road | Tauwhareparae 0404 | 2024-11-22 15:05 | 2024-11-22 16:47 | 0.025957 | 0.00030718 | 8 | 676 | Unplanned | Wildlife | Bird caused the fire on pole G1522 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 883 | 92086 | 200 Faulkner road | Tahora 1103 | 2024-11-22 17:27 | 2024-11-22 19:30 | 0.014169 | 0.00011519 | 3 | 369 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 884 | 29765 | Wheatstone Road | Dalton 0502 | 2024-11-23 06:54 | 2024-11-23 09:34 | 1.5988 | 0.031525 | 821 | 41638 | Unplanned | Defective Equipment | Wire down failed crimp (cu) Steel conductor A3567 - A14 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 885 | 92578 | 109 Somerton Road | Haisman 0804 | 2024-11-23 09:55 | 2024-11-23 11:45 | 0.30411 | 0.0027647 | 72 | 7920 | Unplanned | Wildlife | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 886 | 3307 | Wharekopae Road | Ngatapa 1102 | 2024-11-25 09:01 | 2024-11-25 15:49 | 0.078332 | 0.00019199 | 5 | 1020.1958 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 887 | 3306 | Kabul Street | Borough One 3204 | 2024-11-25 15:32 | 2024-11-25 17:22 | 1.1193 | 0.010175 | 265 | 14723.3076 | Planned | Planned | Replace X-arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 888 | 3447 | Waiomoko Road / Glenroy Rd / Pa Rd | Dalton 0502 | 2024-11-26 08:33 | 2024-11-26 11:05 | 0.50778 | 0.0033406 | 87 | 13224 | Planned | Planned | Remove ABS A271 - Urgent Work | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 889 | 3311 | Lottin Point Road | Hicks Bay 0102 | 2024-11-26 08:34 | 2024-11-26 14:31 | 0.15079 | 0.00042238 | 11 | 1964.406 | Planned | Planned | Replace Pole & Install TX H5493 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 890 | 3309 | Taylors Bay | Mahia 3301 | 2024-11-26 09:04 | 2024-11-26 16:07 | 0.77963 | 0.0018431 | 48 | 10170.7112 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 891 | 94426 | 1333 Ngakoroa Rd, Ormond | Waimata 0903 | 2024-11-26 10:45 | 2024-11-26 13:04 | 0.0053373 | 3.8398e-05 | 1 | 139 | Unplanned | Unknown cause | Possible tree hit lines yesterday by tree cutters in the area | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 892 | 29774 | Waimata Valley Road | Waimata 0903 | 2024-11-26 12:29 | 2024-11-26 15:58 | 0.048151 | 0.00023039 | 6 | 1254 | Unplanned | Human Error | Tree team (Arbc) dropped tree thru HV @ Pole G550 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 893 | 3310 | Glenelg Road | Waimata 0903 | 2024-11-26 12:32 | 2024-11-26 14:11 | 0.0076028 | 7.6796e-05 | 2 | 99.0076 | Planned | Planned | Install new cable up pole D595 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 894 | 29778 | Freyberg / Kabul / Clyde | Borough One 3204 | 2024-11-27 08:05 | 2024-11-27 09:17 | 1.68 | 0.03141 | 818 | 43751 | Unplanned | Defective Equipment | Cable fault between W231 - W263 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 895 | 3308 | Wharekopae Road | Ngatapa 1102 | 2024-11-27 09:02 | 2024-11-27 15:01 | 0.068924 | 0.00019199 | 5 | 897.6723 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 896 | 3312 | Moana Road | Dalton 0502 | 2024-11-27 09:12 | 2024-11-27 10:19 | 0.092616 | 0.0013823 | 36 | 1207.6671 | Planned | Planned | Replace LA on Crucifix | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 897 | 3313 | Winifred Road | Dalton 0502 | 2024-11-27 11:11 | 2024-11-27 12:00 | 0.088431 | 0.0018047 | 47 | 1153.5781 | Planned | Planned | Replace LA on Crucifix | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 898 | 3314 | Wairere Road | Tamarau 0503 | 2024-11-27 13:32 | 2024-11-27 14:07 | 0.080636 | 0.0023039 | 60 | 1052.4191 | Planned | Planned | Replace LA on Crucifix | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 899 | 95129 | 8km marker Arikihi Road, Tolaga Bay | Tauwhareparae 0404 | 2024-11-27 15:18 | 2024-11-27 17:07 | 0.012556 | 0.00011519 | 3 | 327 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 900 | 3318 | Tyndall / Rutene Rd cnr | Wainui 0504 | 2024-11-28 06:59 | 2024-11-28 08:09 | 0.0026879 | 3.8398e-05 | 1 | 15.5006 | Planned | Planned | Install Stubb pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 901 | 3315 | Waikura Valley Road | Hicks Bay 0102 | 2024-11-28 08:34 | 2024-11-28 15:29 | 0.62147 | 0.0014975 | 39 | 8104.6187 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 902 | 3317 | Frasertown Road | Nuhaka 3203 | 2024-11-28 08:37 | 2024-11-28 11:49 | 0.30964 | 0.0016127 | 42 | 4039.1121 | Planned | Planned | Upgrade TX W1759 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 903 | 3316 | Waikura Valley Road | Hicks Bay 0102 | 2024-11-29 08:33 | 2024-11-29 11:58 | 0.30699 | 0.0014975 | 39 | 4008.0126 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 904 | 3321 | Whakato Road | Muriwai 0905 | 2024-11-29 09:01 | 2024-11-29 15:49 | 1.4413 | 0.0035326 | 92 | 18834.3002 | Planned | Planned | Replace poles upgrade TX install new TX | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 905 | N/A 47 | Tolaga Bay 50kV | Rototahi 0403 | 2024-11-30 06:30 | 2024-11-30 06:50 | 0.16588 | 0.008294 | 216 | 4320 | Unplanned | Unknown cause | LFI on Centre phase Tolaga - Tokomaru 50kV Plashing. Restored Tolaga Bay to Norman 0853. Aerial Patrol Tol-Tok 50kV Monday 2/12: Unable to identify fault cause. Closed G6L | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 906 | N/A 47 | Tolaga Bay 50kV | Town 0402 | 2024-11-30 06:30 | 2024-11-30 07:00 | 0.23615 | 0.0078716 | 205 | 6150 | Unplanned | Unknown cause | LFI on Centre phase Tolaga - Tokomaru 50kV Plashing. Restored Tolaga Bay to Norman 0853. Aerial Patrol Tol-Tok 50kV Monday 2/12: Unable to identify fault cause. Closed G6L | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 907 | N/A 47 | Tolaga Bay 50kV | Toko Tie 0401 | 2024-11-30 06:30 | 2024-11-30 07:01 | 0.099988 | 0.0032254 | 84 | 2604 | Unplanned | Unknown cause | LFI on Centre phase Tolaga - Tokomaru 50kV Plashing. Restored Tolaga Bay to Norman 0853. Aerial Patrol Tol-Tok 50kV Monday 2/12: Unable to identify fault cause. Closed G6L | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 908 | N/A 47 | Tolaga Bay 50kV | Tauwhareparae 0404 | 2024-11-30 06:30 | 2024-11-30 07:09 | 0.19257 | 0.0056061 | 146 | 5015 | Unplanned | Unknown cause | LFI on Centre phase Tolaga - Tokomaru 50kV Plashing. Restored Tolaga Bay to Norman 0853. Aerial Patrol Tol-Tok 50kV Monday 2/12: Unable to identify fault cause. Closed G6L | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 909 | 96699 | 1945 Te Araroa Road | Tiki Tiki 0206 | 2024-11-30 07:30 | 2024-11-30 09:35 | 0.0047998 | 3.8398e-05 | 1 | 125 | Unplanned | Defective Equipment | Replaced fuse holder & DDO fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 910 | 97666 | 599 Arakihi Road, Tolaga Bay | Tauwhareparae 0404 | 2024-12-01 10:57 | 2024-12-01 12:15 | 0.0089851 | 0.00011519 | 3 | 234 | Unplanned | Unknown cause | Fuse fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 911 | 3448 | Seeka Coolstore | Chalmers 0707 | 2024-12-02 08:29 | 2024-12-03 10:48 | 0.12126 | 7.6796e-05 | 2 | 3158 | Planned | Planned | New metering not onsite by 2/12. Outage ran overnight to allow for new metering on 3/12. Equipment did not arrive as planned. Site restored until new equipment available | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 912 | 3319 | Nelson Road | Haisman 0804 | 2024-12-02 09:15 | 2024-12-02 11:30 | 0.34205 | 0.0025343 | 66 | 3473.5192 | Planned | Planned | To cut in 11kV line breaks @ C5735 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 913 | 98794 | 326 Matokitoki Valley Road | Whangara 0506 | 2024-12-03 05:52 | 2024-12-03 07:30 | 0.011289 | 0.00011519 | 3 | 294 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 914 | 99476 | 3100 Mata Rd, Huiarus | Mata 0304 | 2024-12-03 07:39 | 2024-12-04 18:10 | 0.15904 | 7.6796e-05 | 2 | 4142 | Unplanned | Adverse Weather | Replace Fuse - Rang Customer. Ok to attend later in the day. Still wingy. Running on generator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 915 | 3322 | Rotoparu Road | Frasertown 3103 | 2024-12-03 08:34 | 2024-12-03 14:47 | 0.085935 | 0.00023039 | 6 | 1119.2578 | Planned | Planned | Cutting trees | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 916 | 3325 | Woodland Rd / Kakariki Rd | Raupunga 3101 | 2024-12-03 09:46 | 2024-12-03 10:33 | 0.019852 | 0.00042238 | 11 | 258.6092 | Planned | Planned | Install fault indicators between W1015 & W5300 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 917 | 29818 | Matokitoki Valley Road | Whangara 0506 | 2024-12-03 16:09 | 2024-12-03 17:07 | 0.084629 | 0.0014591 | 38 | 2204 | Unplanned | Defective Equipment | Replace HV fuse TX B79 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 918 | 3323 | Te Araroa | Te Araroa Sub 01 | 2024-12-03 17:06 | 2024-12-03 17:07 | 3.8398e-05 | 3.8398e-05 | 1 | 0.50002 | Planned | Planned | 50kV pole changes | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 919 | 3323 | Te Araroa | Awatere 0101 | 2024-12-03 17:06 | 2024-12-03 17:07 | 0.0034942 | 0.0034942 | 91 | 45.659 | Planned | Planned | 50kV pole changes | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 920 | 3323 | Te Araroa | Hicks Bay 0102 | 2024-12-03 17:06 | 2024-12-03 17:07 | 0.0096763 | 0.0096763 | 252 | 127.2192 | Planned | Planned | 50kV pole changes | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 921 | 3323 | Te Araroa | Te Araroa 0103 | 2024-12-03 17:06 | 2024-12-03 17:07 | 0.0049533 | 0.0049533 | 129 | 64.8195 | Planned | Planned | 50kV pole changes | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 922 | 3326 | Taumata Road | Tahora 1103 | 2024-12-04 08:31 | 2024-12-04 15:14 | 0.10832 | 0.00026879 | 7 | 1410.8791 | Planned | Planned | To replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 923 | 3324 | Nelson Road | Haisman 0804 | 2024-12-04 09:00 | 2024-12-04 11:23 | 0.3624 | 0.0025343 | 66 | 4730.9592 | Planned | Planned | To close 11kv line breaks @ Pole C5735 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 924 | 3454 A | Morere Road | Morere 3401 | 2024-12-04 10:49 | 2024-12-04 11:00 | 0.016895 | 0.0015359 | 40 | 440 | Planned | Planned | To install 1kVA TX @ Remote switch W810 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 925 | 3454 | Morere Road | Morere 3401 | 2024-12-04 11:00 | 2024-12-04 13:58 | 1.1141 | 0.0062589 | 163 | 29014 | Planned | Planned | To install 1kVA TX @ Remote switch W810 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 926 | 3454 B | Morere Road | Morere 3401 | 2024-12-04 14:00 | 2024-12-04 14:04 | 0.0061437 | 0.0015359 | 40 | 160 | Planned | Planned | To install 1kVA TX @ Remote switch W810 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 927 | 100168 | 77 Matukoa Road | Hicks Bay 0102 | 2024-12-05 08:15 | 2024-12-05 11:15 | 0.055293 | 0.00030718 | 8 | 1440 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 928 | 3441 | Black Street, Victoria Street | Borough One 3204 | 2024-12-05 09:03 | 2024-12-05 16:03 | 0.9515 | 0.0022655 | 59 | 12418.0693 | Planned | Planned | Replace Link Box 11842 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 929 | 3328 | Mangatu Road | Whatatutu 1201 | 2024-12-05 09:07 | 2024-12-05 13:17 | 0.24959 | 0.00099835 | 26 | 3032.024 | Planned | Planned | Cut trees | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 930 | 3442 | Waihi Road | Frasertown 3103 | 2024-12-05 09:33 | 2024-12-05 10:43 | 0.010751 | 0.00015359 | 4 | 140.0215 | Planned | Planned | Replace TX W171 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 931 | 3330 | Whaanga Street | Morere 3401 | 2024-12-05 10:13 | 2024-12-05 12:25 | 0.060822 | 0.00046078 | 12 | 1584 | Planned | Planned | Install LV road x-ing pole opp W1266 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 932 | 29852 | Arakihi Road | Tauwhareparae 0404 | 2024-12-05 15:00 | 2024-12-05 16:40 | 0.011519 | 0.00011519 | 3 | 300 | Unplanned | Defective Equipment | Faulty Transformer G266 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 933 | 3329 | Waiapu Road | Te Araroa Sub 01 | 2024-12-05 17:07 | 2024-12-05 17:08 | 3.8398e-05 | 3.8398e-05 | 1 | 0.50002 | Planned | Planned | Replacing 50kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 934 | 3329 | Waiapu Road | Awatere 0101 | 2024-12-05 17:07 | 2024-12-05 17:08 | 0.0034942 | 0.0034942 | 91 | 45.659 | Planned | Planned | Replacing 50kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 935 | 3329 | Waiapu Road | Hicks Bay 0102 | 2024-12-05 17:07 | 2024-12-05 17:08 | 0.0096763 | 0.0096763 | 252 | 127.2192 | Planned | Planned | Replacing 50kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 936 | 3329 | Waiapu Road | Te Araroa 0103 | 2024-12-05 17:07 | 2024-12-05 17:08 | 0.0049533 | 0.0049533 | 129 | 64.8195 | Planned | Planned | Replacing 50kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 937 | 100431 | 1737 Ohuka Road | Ruakituri 2003 | 2024-12-05 17:57 | 2024-12-05 19:00 | 0.024191 | 0.00038398 | 10 | 630 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 938 | 3327 | Taumata Road | Tahora 1103 | 2024-12-06 08:32 | 2024-12-06 16:40 | 0.13117 | 0.00026879 | 7 | 1673.4497 | Planned | Planned | Replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 939 | 101800 | 1945 Te Araroa Road | Tiki Tiki 0206 | 2024-12-07 15:40 | 2024-12-07 17:50 | 0.0049917 | 3.8398e-05 | 1 | 130 | Unplanned | Defective Equipment | HV tube just sitting in S/S holder & Blown. Couldn't get new fuse wire in. Replaced with new Betacom HV tube +2a HV DDI Link | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 940 | 3335 | Lahore Street | Borough Two 3205 | 2024-12-08 09:03 | 2024-12-08 16:17 | 1.0665 | 0.0024575 | 64 | 13922.1294 | Planned | Planned | Replace RMU W263 / W264 / W265 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 941 | 29854 | Wharerata Road | Muriwai 0905 | 2024-12-08 21:35 | 2024-12-09 12:33 | 0.99455 | 0.0094843 | 247 | 25901 | Unplanned | Vegetation | Tree fell on the line which broke the conductor at pole C3566 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 942 | N/A 48 | Massey Road | Aberdeen 0609 | 2024-12-10 08:26 | 2024-12-10 09:35 | 2.2351 | 0.055332 | 1441 | 58208 | Unplanned | Third Party Interference | Cable damaged by contractor working on the bridge at Massey Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 943 | 3443 | Waiapu Road, Hicks Bay | Te Araroa Sub 01 | 2024-12-10 17:08 | 2024-12-10 17:09 | 3.8398e-05 | 3.8398e-05 | 1 | 0.50002 | Planned | Planned | Replace 50kV poles - run generator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 944 | 3443 | Waiapu Road, Hicks Bay | Awatere 0101 | 2024-12-10 17:08 | 2024-12-10 17:09 | 0.0034942 | 0.0034942 | 91 | 45.659 | Planned | Planned | Replace 50kV poles - run generator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 945 | 3443 | Waiapu Road, Hicks Bay | Hicks Bay 0102 | 2024-12-10 17:08 | 2024-12-10 17:09 | 0.0096763 | 0.0096763 | 252 | 127.2192 | Planned | Planned | Replace 50kV poles - run generator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 946 | 3443 | Waiapu Road, Hicks Bay | Te Araroa 0103 | 2024-12-10 17:08 | 2024-12-10 17:09 | 0.0049533 | 0.0049533 | 129 | 64.8195 | Planned | Planned | Replace 50kV poles - run generator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 947 | 3476 | Bright Street | Port A 1501 | 2024-12-11 06:00 | 2024-12-11 06:11 | 0.013094 | 0.0011903 | 31 | 341 | Planned | Planned | Isolate TX B167 to liven RMU B1047 - Urgent | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 948 | 3340 | Taumata Road | Tahora 1103 | 2024-12-11 08:32 | 2024-12-11 15:42 | 0.11558 | 0.00026879 | 7 | 1505.4045 | Planned | Planned | 11kV Pole changes | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 949 | 3333 | Fox Street | Whangara 0506 | 2024-12-11 09:04 | 2024-12-11 10:24 | 0.26418 | 0.0033022 | 86 | 3451.3597 | Planned | Planned | Replace 11kV insulator stand offs on pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 950 | 3331 | Riverside Road | Harris 1502 | 2024-12-11 11:07 | 2024-12-11 11:31 | 0.052529 | 0.0021887 | 57 | 685.4971 | Planned | Planned | Replace standoff insulators on pole B2079 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 951 | 3332 | Stafford Street | Harris 1502 | 2024-12-11 12:30 | 2024-12-11 13:00 | 0.12095 | 0.0040318 | 105 | 1581.3501 | Planned | Planned | Replace 11kV insulator cable stand offs on pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 952 | 3334 | Harris Street | Harris 1502 | 2024-12-11 14:02 | 2024-12-11 14:22 | 0.056061 | 0.0028031 | 73 | 732.0462 | Planned | Planned | Replace 11kV cable stand-off | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 953 | 3445 | Ngakaroa Road | Waimata 0903 | 2024-12-12 09:02 | 2024-12-12 16:00 | 0.35311 | 0.00084476 | 22 | 4601.8842 | Planned | Planned | To remove trees | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 954 | 3444 | Waiapu Road | Te Araroa Sub 01 | 2024-12-12 17:39 | 2024-12-12 17:40 | 3.8398e-05 | 3.8398e-05 | 1 | 0 | Planned | Planned | Replaced 50kV poles. Outage for Te Araroa feeders when changing back from islanded generator to main supply | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 955 | 3444 | Waiapu Road | Awatere 0101 | 2024-12-12 17:39 | 2024-12-12 17:40 | 0.0034942 | 0.0034942 | 91 | 0 | Planned | Planned | Replaced 50kV poles. Outage for Te Araroa feeders when changing back from islanded generator to main supply | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 956 | 3444 | Waiapu Road | Hicks Bay 0102 | 2024-12-12 17:39 | 2024-12-12 17:40 | 0.0096763 | 0.0096763 | 252 | 0 | Planned | Planned | Replaced 50kV poles. Outage for Te Araroa feeders when changing back from islanded generator to main supply | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 957 | 3444 | Waiapu Road | Te Araroa 0103 | 2024-12-12 17:39 | 2024-12-12 17:40 | 0.0049533 | 0.0049533 | 129 | 0 | Planned | Planned | Replaced 50kV poles. Outage for Te Araroa feeders when changing back from islanded generator to main supply | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 958 | 29844 | YMCA Road | Mahia 3301 | 2024-12-12 18:00 | 2024-12-12 18:36 | 0.0013823 | 3.8398e-05 | 1 | 36 | Unplanned | Defective Equipment | Jumper off @ TX W1516 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 959 | N/A 59 | Tuai | Tuai Sub | 2024-12-13 05:59 | 2024-12-13 06:16 | 0.00065277 | 3.8398e-05 | 1 | 17 | Unplanned | Defective Equipment | W53 fail to Trip on Scada. 110kV CB 302 Trip under Intertrip | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 960 | N/A 59 | Tuai | Lake | 2024-12-13 05:59 | 2024-12-13 06:16 | 0.0065277 | 0.00038398 | 10 | 170 | Unplanned | Defective Equipment | W53 fail to Trip on Scada. 110kV CB 302 Trip under Intertrip | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 961 | N/A 59 | Tuai | Village 2002 | 2024-12-13 05:59 | 2024-12-13 06:16 | 0.11619 | 0.0068349 | 178 | 3026 | Unplanned | Defective Equipment | W53 fail to Trip on Scada. 110kV CB 302 Trip under Intertrip | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 962 | N/A 59 | Tuai | Ruakituri 2003 | 2024-12-13 05:59 | 2024-12-13 06:16 | 0.10575 | 0.0062205 | 162 | 2754 | Unplanned | Defective Equipment | W53 fail to Trip on Scada. 110kV CB 302 Trip under Intertrip | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 963 | 29878 | YMCA Road | Mahia 3301 | 2024-12-13 11:52 | 2024-12-13 19:45 | 0.018162 | 3.8398e-05 | 1 | 473 | Unplanned | Defective Equipment | To replace faulty transformer W1516 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 964 | 3449 | Riverside Road | Waimata 0903 | 2024-12-14 09:05 | 2024-12-14 11:07 | 0.042161 | 0.00034558 | 9 | 549.2799 | Planned | Planned | Install new TX | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 965 | 105562 | 362 Whakaangiangi Road | Awatere 0101 | 2024-12-14 11:09 | 2024-12-14 14:15 | 0.007142 | 3.8398e-05 | 1 | 186 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 966 | 29879 | Back Ormond Road | Waimata 0903 | 2024-12-14 17:38 | 2024-12-14 21:30 | 0.12683 | 0.00069116 | 18 | 3303 | Unplanned | Defective Equipment | Blown cable termination | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 967 | 29846 | Motu | Matawai 1204 | 2024-12-14 17:51 | 2024-12-17 16:04 | 0.98203 | 0.004723 | 123 | 25575 | Unplanned | Defective Equipment | HW Pole broke, needed bucket truck to cut jumpers. Install generator at TX F120 - High Winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 968 | 29883 | Wharerata Road / Paritu Road | Muriwai 0905 | 2024-12-16 03:01 | 2024-12-20 12:09 | 0.8203 | 0.0054141 | 141 | 21363 | Unplanned | Vegetation | Pole down @ C3775 (Btwn C184 & C189) L/break @ Pole C3768. Pole down byd HV fuses C3145 (Genset @ TX C190 1 x customer off byd C3145) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 969 | 107633 | 503 Lake Road, Patutahi | Lavenham 0902 | 2024-12-16 05:24 | 2024-12-16 09:22 | 0.054832 | 0.00023039 | 6 | 1428 | Unplanned | Unknown cause | D2045 access very limited with new native growth | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 970 | 3451 A | Waiapu road | Te Araroa Sub 01 | 2024-12-16 17:12 | 2024-12-16 17:13 | 3.8398e-05 | 3.8398e-05 | 1 | 0.50002 | Planned | Planned | Replace 50kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 971 | 3451 A | Waiapu road | Awatere 0101 | 2024-12-16 17:12 | 2024-12-16 17:13 | 0.0034942 | 0.0034942 | 91 | 45.659 | Planned | Planned | Replace 50kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 972 | 3451 A | Waiapu road | Hicks Bay 0102 | 2024-12-16 17:12 | 2024-12-16 17:13 | 0.0096763 | 0.0096763 | 252 | 127.2192 | Planned | Planned | Replace 50kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 973 | 3451 A | Waiapu road | Te Araroa 0103 | 2024-12-16 17:12 | 2024-12-16 17:13 | 0.0049533 | 0.0049533 | 129 | 64.8195 | Planned | Planned | Replace 50kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 974 | 3451 A | Waiapu road | Ruatoria Sub 02 | 2024-12-16 17:12 | 2024-12-16 17:13 | 3.8398e-05 | 3.8398e-05 | 1 | 0.50002 | Planned | Planned | Replace 50kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 975 | 3451 A | Waiapu road | Ruatoria 0201 | 2024-12-16 17:12 | 2024-12-16 17:13 | 0.011827 | 0.011827 | 308 | 155.8213 | Planned | Planned | Replace 50kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 976 | 3451 A | Waiapu road | Makarika 0204 | 2024-12-16 17:12 | 2024-12-16 17:13 | 0.004339 | 0.004339 | 113 | 56.7452 | Planned | Planned | Replace 50kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 977 | 3451 A | Waiapu road | Tiki Tiki 0206 | 2024-12-16 17:12 | 2024-12-16 17:13 | 0.012134 | 0.012134 | 316 | 159.9171 | Planned | Planned | Replace 50kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 978 | 3451 A | Waiapu road | Inland 0301 | 2024-12-16 17:12 | 2024-12-16 17:13 | 0.0046462 | 0.0046462 | 121 | 60.7811 | Planned | Planned | Replace 50kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 979 | 108419 | 418 Waiatai Road | Nuhaka 3203 | 2024-12-17 06:40 | 2024-12-17 08:20 | 0.053757 | 0.00053757 | 14 | 1400 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 980 | N/A 50 | North Clyde / McLean St / Tawhara Valley | Brickworks 3201 | 2024-12-17 07:45 | 2024-12-17 10:05 | 1.4764 | 0.046654 | 1215 | 38450 | Unplanned | Adverse Weather | Line patrol unable to identify any fault cause. Suspect wind clashing conductor at sewage plant | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 981 | N/A 50 | North Clyde / McLean St / Tawhara Valley | Borough One 3204 | 2024-12-17 08:52 | 2024-12-17 08:58 | 0.18869 | 0.031448 | 819 | 4914 | Unplanned | Adverse Weather | Line patrol unable to identify any fault cause. Suspect wind clashing conductor at sewage plant | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 982 | 29886 | 1851 Tiniroto Road | W O Kuri 1001 | 2024-12-17 09:06 | 2024-12-17 10:27 | 0.012441 | 0.00015359 | 4 | 324 | Unplanned | Vegetation | Tree through LV Lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 983 | 3455 | 116A Darwin Road | Whangara 0506 | 2024-12-17 09:13 | 2024-12-17 10:50 | 0.055869 | 0.00057597 | 15 | 727.919 | Planned | Planned | Cut in new distribution box | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 984 | 108555 | 1001 Tahora Rd | Tahora 1103 | 2024-12-17 10:36 | 2024-12-17 18:10 | 0.41838 | 0.00092155 | 24 | 10896 | Unplanned | Adverse Weather | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 985 | 108572 | 63 Thomas Rd | Rototahi 0403 | 2024-12-17 11:21 | 2024-12-18 | 0.087432 | 0.00011519 | 3 | 2277 | Unplanned | Vegetation | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 986 | 29889 | Tiniroto Rd / Ruakaka Rd | Tiniroto 1003 | 2024-12-17 12:06 | 2024-12-17 16:16 | 0.46707 | 0.0032638 | 85 | 12164 | Unplanned | Vegetation | Tree through line @ Pole D3290 - High Winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 987 | 108657 | 1370 Rangitukia road, Tikitiki | Tiki Tiki 0206 | 2024-12-17 13:51 | 2024-12-17 18:50 | 0.55109 | 0.0018431 | 48 | 14352 | Unplanned | Vegetation | Cut 8 x branches out of 11kV | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 988 | 29891 | 341 East Coast Road | Mahia 3301 | 2024-12-17 15:22 | 2024-12-17 19:54 | 0.093998 | 0.00034558 | 9 | 2448 | Unplanned | Defective Equipment | TX W1788 x-arm failure | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 989 | N/A 49 | Rangitukia Road | Tiki Tiki 0206 | 2024-12-17 15:54 | 2024-12-17 18:48 | 0.32408 | 0.004147 | 108 | 8440 | Unplanned | Vegetation | Trees contacting o/head 11kV @ Pole J1189 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 990 | 29951 | SH2 Nuhaka - Morere | Morere 3401 | 2024-12-17 15:57 | 2024-12-18 13:39 | 0.71881 | 0.0032638 | 85 | 18720 | Unplanned | Vegetation | Tree through HV @ Pole W962 - High Winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 991 | 108812 | 1734 Bushy Knoll Road | Tiniroto 1003 | 2024-12-17 18:18 | 2024-12-18 15:02 | 0.23884 | 0.00019199 | 5 | 6220 | Unplanned | Vegetation | Trees making contact in zone | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 992 | 29892 | Kaiwitri Road | Waimata 0903 | 2024-12-17 18:26 | 2024-12-17 20:13 | 0.0082172 | 7.6796e-05 | 2 | 214 | Unplanned | Vegetation | Tree in LV | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 993 | 29895 | Motu Road, Matohora Road | Matawai 1204 | 2024-12-18 07:50 | 2024-12-18 15:25 | 0.4617 | 0.0023423 | 61 | 12024 | Unplanned | Vegetation | Tree through 11kV before TX F118 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 994 | 29952 | Waiatai Road | Nuhaka 3203 | 2024-12-18 08:30 | 2024-12-18 10:01 | 0.048919 | 0.00053757 | 14 | 1274 | Unplanned | Vegetation | Trees brought down HV conductor - High Winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 995 | 3481 | Waihi Road | Frasertown 3103 | 2024-12-18 09:00 | 2024-12-18 13:23 | 0.99977 | 0.0038014 | 99 | 26037 | Planned | Planned | Cut tree on 50kV line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 996 | N/A 51 | Onepoto Road | Hicks Bay 0102 | 2024-12-18 10:02 | 2024-12-18 15:04 | 0.59141 | 0.0019583 | 51 | 15402 | Unplanned | Vegetation | Trees in line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 997 | 29955 | Rangitukia Road | Tiki Tiki 0206 | 2024-12-18 16:17 | 2024-12-18 17:45 | 0.17602 | 0.004147 | 108 | 4584 | Unplanned | Vegetation | Trees in Line @ Pole J1245 - High Winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 998 | 29897 | Dunston Road | Dunstan 1403 | 2024-12-18 18:37 | 2024-12-18 19:21 | 0.013516 | 0.00030718 | 8 | 352 | Unplanned | Defective Equipment | Broken 11kV Jumper Lineside TX C3965 Fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 999 | 29956 | Waimata Valley Road | Waimata 0903 | 2024-12-19 12:57 | 2025-01-14 13:27 | 0.37377 | 0.003763 | 98 | 9734 | Unplanned | Vegetation | Wires down @ Pole E1213 & Pole E1215 - High Winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1000 | N/A 52 | Waipiro Rd / Kopuaroa Rd | Inland 0301 | 2024-12-19 16:31 | 2024-12-20 17:17 | 0.36739 | 0.0039934 | 104 | 9568 | Unplanned | Vegetation | Trees through HV lines @ H2216 - H2214, H1977 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1001 | 110708 | B79 Matoketoke Valley Rd | Whangara 0506 | 2024-12-20 15:31 | 2024-12-20 16:11 | 0.0015359 | 3.8398e-05 | 1 | 40 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1002 | 111229 | 404 Armstrong Road | Whatatutu 1201 | 2024-12-21 08:20 | 2024-12-21 14:00 | 0.013055 | 3.8398e-05 | 1 | 340 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1003 | N/A 60 | Caves Rd, Matokitiki Valley Road | Whangara 0506 | 2024-12-22 11:15 | 2024-12-22 15:35 | 0.1842 | 0.0016895 | 44 | 4797 | Unplanned | Vegetation | Tree branch hanging on line at Pole A3478 - A3479 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1004 | 113109 | 78 Matakaoa Road | Hicks Bay 0102 | 2024-12-22 17:10 | 2024-12-22 20:00 | 0.052221 | 0.00030718 | 8 | 1360 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1005 | 113441 | 532 Waiatai Road | Nuhaka 3203 | 2024-12-23 07:02 | 2024-12-23 08:30 | 0.047306 | 0.00053757 | 14 | 1232 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1006 | 114324 | 597 Whakarau Road | Matawai 1204 | 2024-12-24 07:06 | 2024-12-24 10:00 | 0.0066813 | 3.8398e-05 | 1 | 174 | Unplanned | Wildlife | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1007 | 115098 | 209 Erepiti Road | Ruakituri 2003 | 2024-12-25 09:37 | 2024-12-25 11:30 | 0.004339 | 3.8398e-05 | 1 | 113 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1008 | 116541 | Waiatai Road | Nuhaka 3203 | 2024-12-26 19:15 | 2024-12-28 20:00 | 1.5724 | 0.00053757 | 14 | 40950 | Unplanned | Vegetation | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1009 | 29985 | Ruakituri | Ruakituri 2003 | 2024-12-27 05:21 | 2025-01-10 12:52 | 9.5092 | 0.035941 | 936 | 247649 | Unplanned | Adverse Weather | High Winds - conductor clashing | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1010 | 29962 | Ihungia Road | Mata 0304 | 2024-12-27 06:16 | 2024-12-28 16:22 | 0.27516 | 0.00061437 | 16 | 7166 | Unplanned | Vegetation | Tree thru line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1011 | N/A 61 | North Clyde / McLean St / Tawhara Valley | Brickworks 3201 | 2024-12-27 07:02 | 2024-12-27 21:44 | 2.5255 | 0.023692 | 617 | 65772 | Unplanned | Adverse Weather | Conductor clashing during heavy wind - at sewage plant | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1012 | 29917 | Maungatiaki Road | Nuhaka 3203 | 2024-12-27 08:10 | 2024-12-30 20:57 | 2.8815 | 0.01367 | 356 | 75044 | Unplanned | Vegetation | Tree through line @ Pole W1761 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1013 | 29963 | Kaiwaitau Road | Mahia 3301 | 2024-12-27 09:35 | 2024-12-28 11:58 | 2.4619 | 0.0048382 | 126 | 64114 | Unplanned | Adverse Weather | High winds brought down conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1014 | 29965 | Tiniroto | Tiniroto 1003 | 2024-12-27 11:12 | 2024-12-28 16:05 | 3.3799 | 0.0095227 | 248 | 88022 | Unplanned | Vegetation | Trees thru lines D2348 - D3249 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1015 | 29969 | Mangaone Road | Morere 3401 | 2024-12-27 11:30 | 2024-12-28 18:58 | 0.79745 | 0.00042238 | 11 | 20768 | Unplanned | Vegetation | Tree thru line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1016 | 116609 | 987 Mangpoike Road | Frasertown 3103 | 2024-12-27 12:28 | 2024-12-28 18:20 | 0.20643 | 0.00011519 | 3 | 5376 | Unplanned | Defective Equipment | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1017 | 116670 | 2601 Wharekopae Road | Ngatapa 1102 | 2024-12-27 13:42 | 2024-12-27 14:45 | 0.0096763 | 0.00015359 | 4 | 252 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1018 | 29967 | Whakaki | Nuhaka 3203 | 2024-12-27 13:59 | 2024-12-28 14:58 | 1.05 | 0.0017279 | 45 | 27345 | Unplanned | Vegetation | Tree through HV Lines W8134 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1019 | 29959 | Rototahia | Rototahi 0403 | 2024-12-27 14:06 | 2024-12-29 11:58 | 3.378 | 0.023423 | 610 | 87973 | Unplanned | Vegetation | Tree thru line @ E2993 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1020 | 29912 | Mahia | Mahia 3301 | 2024-12-27 14:37 | 2024-12-28 11:57 | 32.9165 | 0.10886 | 2835 | 857245 | Unplanned | Adverse Weather | 33kV Conductor clashing - 1st fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1021 | 29912 | Mahia | Morere 3401 | 2024-12-27 14:37 | 2024-12-27 21:16 | 2.487 | 0.01966 | 512 | 64768 | Unplanned | Adverse Weather | 33kV Conductor clashing - 1st fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1022 | N/A 54 | Kokahu Road | Morere 3401 | 2024-12-27 14:45 | 2024-12-28 22:15 | 0.58058 | 0.00030718 | 8 | 15120 | Unplanned | Adverse Weather | Line Clash | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1023 | N/A 55 | Titirangi | Frasertown 3103 | 2024-12-27 14:57 | 2024-12-28 19:52 | 1.0659 | 0.00061437 | 16 | 27760 | Unplanned | Adverse Weather | High Winds - Tangled conductors | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1024 | N/A 69 | Manders Road | Waimata 0903 | 2024-12-27 19:35 | 2024-12-27 22:21 | 0.12111 | 0.00072956 | 19 | 3154 | Unplanned | Adverse Weather | High wind suspect conductor clash | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1025 | 29961 | Waipiro Bay | Inland 0301 | 2024-12-27 19:45 | 2024-12-29 13:06 | 0.33464 | 0.0026879 | 70 | 8715 | Unplanned | Vegetation | Tree thru line - H2246 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1026 | N/A 53 | Goodwin Road | Whangara 0506 | 2024-12-27 20:35 | 2024-12-28 08:48 | 0.42219 | 0.00057597 | 15 | 10995 | Unplanned | Vegetation | Tree on line - Windy | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1027 | 117247 | 410 Goodwin Road | Whangara 0506 | 2024-12-27 21:01 | 2024-12-28 10:00 | 0.44868 | 0.00057597 | 15 | 11685 | Unplanned | Vegetation | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1028 | N/A 65 | Morere | Morere 3401 | 2024-12-27 21:50 | 2024-12-28 10:52 | 2.192 | 0.0028031 | 73 | 57086 | Unplanned | Adverse Weather | Suspect clashing - High Winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1029 | 29968 | Mangapoike | Frasertown 3103 | 2024-12-27 23:24 | 2024-12-28 17:40 | 2.7094 | 0.0046846 | 122 | 70562 | Unplanned | Vegetation | Tree thru line check zone - windy | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1030 | 117451 | 1235 Panikau Road | Rototahi 0403 | 2024-12-28 08:05 | 2024-12-28 18:30 | 0.21599 | 0.00034558 | 9 | 5625 | Unplanned | Adverse Weather | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1031 | 29913 | Mahia East Coast Road | Mahia 3301 | 2024-12-28 09:25 | 2024-12-28 10:15 | 0.044158 | 0.00088315 | 23 | 1150 | Unplanned | Adverse Weather | Repaired broken LV wires - High wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1032 | 29979 | Rangiahua Road | Frasertown 3103 | 2024-12-28 09:59 | 2025-01-06 16:16 | 0.05514 | 7.6796e-05 | 2 | 1436 | Unplanned | Vegetation | Tree thru line W4064 - High Winds - Install Gen | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1033 | 29964 | Matawai | Matawai 1204 | 2024-12-28 10:23 | 2024-12-28 13:44 | 0.65929 | 0.0092155 | 240 | 17170 | Unplanned | Defective Equipment | Failed inline crimp - Windy | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1034 | 117691 | 758 Glenroy Road | Dalton 0502 | 2024-12-28 10:47 | 2024-12-28 17:00 | 0.014322 | 3.8398e-05 | 1 | 373 | Unplanned | Adverse Weather | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1035 | 118044 | 4513 Rukeliti Road | Inland 0301 | 2024-12-28 15:06 | 2024-12-28 17:00 | 0.043774 | 0.00038398 | 10 | 1140 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1036 | 118297 | 401 Titirangi Road | Frasertown 3103 | 2024-12-28 18:25 | 2024-12-28 20:25 | 0.073724 | 0.00061437 | 16 | 1920 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1037 | 29972 | Mangaone Road | Morere 3401 | 2024-12-28 18:58 | 2024-12-29 20:19 | 0.64167 | 0.00042238 | 11 | 16711 | Unplanned | Defective Equipment | Conductor off the insulator & fell on the ground at Pole W8065. Bindings rusted away due to age. The Pole & crossare needs replacemnt in the near future | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1038 | 29970 | Kaiwaitau Road | Mahia 3301 | 2024-12-28 21:20 | 2024-12-28 21:41 | 0.0024191 | 0.00011519 | 3 | 63 | Unplanned | Adverse Weather | Blown jumper at TX - High winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1039 | 118630 | 249 Makanga Road | Mahia 3301 | 2024-12-29 08:31 | 2024-12-29 10:30 | 0.036555 | 0.00030718 | 8 | 952 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1040 | 118687 | 63 Thomas Rd | Rototahi 0403 | 2024-12-29 09:25 | 2024-12-29 10:30 | 0.0074876 | 0.00011519 | 3 | 195 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1041 | 29971 | Mahia | Mahia 3301 | 2024-12-29 11:00 | 2024-12-30 17:29 | 0.56184 | 0.00030718 | 8 | 14632 | Unplanned | Defective Equipment | Failed insulator, burnt x-arm steel pole. Replaced pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1042 | 118864 | 703 Waiapu Road | Makarika 0204 | 2024-12-29 12:43 | 2024-12-29 13:45 | 0.011903 | 0.00019199 | 5 | 310 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1043 | 29975 | Lake Road | Frasertown 3103 | 2024-12-29 15:21 | 2025-01-01 14:06 | 0.163 | 3.8398e-05 | 1 | 4245 | Unplanned | Lightning | Lightning blew TX | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1044 | 116988 | 200 Faulkner road | Tahora 1103 | 2024-12-29 17:08 | 2024-12-29 19:00 | 0.012902 | 0.00011519 | 3 | 336 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1045 | 29918 | Hereheretau Road | Nuhaka 3203 | 2024-12-29 19:05 | 2024-12-30 13:24 | 0.42199 | 0.00038398 | 10 | 10990 | Unplanned | Vegetation | Tree on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1046 | N/A 62 | Muriwai Feeder | Muriwai 0905 | 2024-12-30 06:00 | 2024-12-30 07:06 | 1.0467 | 0.015858 | 413 | 27258 | Unplanned | Vegetation | Tree branch across line at Pole C924 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1047 | 119468 | 593 Waipiro Road | Inland 0301 | 2024-12-30 06:53 | 2024-12-30 08:00 | 0.051453 | 0.00076796 | 20 | 1340 | Unplanned | Wildlife | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1048 | 119965 | Tawera Road | Te Arai 0906 | 2024-12-30 15:56 | 2024-12-31 10:30 | 0.21388 | 0.00019199 | 5 | 5570 | Unplanned | Vegetation | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1049 | 119992 | 846 Erepeti Road | Ruakituri 2003 | 2024-12-30 16:08 | 2024-12-30 20:30 | 0.060362 | 0.00023039 | 6 | 1572 | Unplanned | Lightning | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1050 | 120005 | 338 Tuahau Road | Tauwhareparae 0404 | 2024-12-30 16:29 | 2025-01-01 09:00 | 0.093346 | 3.8398e-05 | 1 | 2431 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1051 | 120169 | 409 Hokoroa Road | Tauwhareparae 0404 | 2024-12-30 18:43 | 2024-12-30 20:00 | 0.011827 | 0.00015359 | 4 | 308 | Unplanned | Lightning | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1052 | 120300 | 1692 Parikanapa Road | Parikanapa 1002 | 2024-12-30 21:11 | 2024-12-31 08:00 | 0.049841 | 7.6796e-05 | 2 | 1298 | Unplanned | Lightning | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1053 | 120327 | 36 Saddler Road | Te Arai 0906 | 2024-12-30 21:55 | 2024-12-31 10:15 | 0.028415 | 3.8398e-05 | 1 | 740 | Unplanned | Lightning | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1054 | N/A 85 | 213 Taurau Valley Road | Te Arai 0906 | 2024-12-30 22:00 | 2024-12-31 10:00 | 0.055293 | 7.6796e-05 | 2 | 1440 | Unplanned | Lightning | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1055 | N/A 86 | 216 Taurau Valley Road | Te Arai 0906 | 2024-12-30 22:00 | 2024-12-31 10:00 | 0.027647 | 3.8398e-05 | 1 | 720 | Unplanned | Lightning | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1056 | 120478 | 145 Rere Farm Settlement road | Tahora 1103 | 2024-12-31 06:49 | 2024-12-31 08:10 | 0.024882 | 0.00030718 | 8 | 648 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1057 | 29977 | Matanui Road | Tauwhareparae 0404 | 2024-12-31 07:08 | 2025-01-02 20:12 | 0.70345 | 0.00019199 | 5 | 18320 | Unplanned | Unknown cause | Check cause | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1058 | 120501 | 201 Matanui Road | Tauwhareparae 0404 | 2024-12-31 07:08 | 2024-12-31 09:00 | 0.021503 | 0.00019199 | 5 | 560 | Unplanned | Lightning | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1059 | 120496 | 1271 Rakaura Road | Matawai 1204 | 2024-12-31 07:10 | 2024-12-31 10:00 | 0.013055 | 7.6796e-05 | 2 | 340 | Unplanned | Lightning | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1060 | 120533 | 49 Makarika Road | Seaside 0302 | 2024-12-31 07:49 | 2024-12-31 09:15 | 0.016511 | 0.00019199 | 5 | 430 | Unplanned | Lightning | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1061 | N/A 57 | Waitangi Road | Kanakanaia 1202 | 2024-12-31 09:25 | 2024-12-31 22:57 | 0.37415 | 0.00046078 | 12 | 9744 | Unplanned | Vegetation | Tree thru lines - high winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1062 | 120620 | 3276 Te Araroa Road | Awatere 0101 | 2024-12-31 09:39 | 2024-12-31 11:45 | 0.0048382 | 3.8398e-05 | 1 | 126 | Unplanned | Lightning | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1063 | 120630 | 721 Tapuaeroa Road | Tiki Tiki 0206 | 2024-12-31 09:56 | 2024-12-31 11:48 | 0.0086012 | 7.6796e-05 | 2 | 224 | Unplanned | Lightning | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1064 | 120663 | 1880 East Cape Road | Tiki Tiki 0206 | 2024-12-31 10:40 | 2024-12-31 11:40 | 0.0046078 | 7.6796e-05 | 2 | 120 | Unplanned | Lightning | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1065 | N/A 56 | Tawera Road | Te Arai 0906 | 2024-12-31 10:52 | 2024-12-31 12:32 | 0.019199 | 0.00019199 | 5 | 500 | Unplanned | Adverse Weather | High Winds - Clashing | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1066 | 120736 | Thatcher road | Tiki Tiki 0206 | 2024-12-31 12:05 | 2024-12-31 13:40 | 0.0036478 | 3.8398e-05 | 1 | 95 | Unplanned | Lightning | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1067 | 120815 | 112 Onepoto Road | Hicks Bay 0102 | 2024-12-31 13:51 | 2024-12-31 14:50 | 0.015858 | 0.00026879 | 7 | 413 | Unplanned | Lightning | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1068 | 119960 | 327 Heliburton Road | Raupunga 3101 | 2024-12-31 15:35 | 2024-12-31 18:10 | 0.0059517 | 3.8398e-05 | 1 | 155 | Unplanned | Lightning | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1069 | 120946 | 1884 Tapuaeroa Road | Tiki Tiki 0206 | 2024-12-31 16:07 | 2024-12-31 17:20 | 0.011212 | 0.00015359 | 4 | 292 | Unplanned | Lightning | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1070 | 120955 | 75 Church Lane | Raupunga 3101 | 2024-12-31 16:35 | 2024-12-31 17:30 | 0.0042238 | 7.6796e-05 | 2 | 110 | Unplanned | Lightning | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1071 | N/A 63 | North Clyde / McLean St / Tawhara Valley | Brickworks 3201 | 2024-12-31 17:26 | 2024-12-31 18:44 | 1.6832 | 0.023692 | 617 | 43836 | Unplanned | Adverse Weather | Suspect Wind Clash @ sewage plant | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1072 | 120101 | 473 Hiririroa Road | Totangi 1101 | 2024-12-31 17:58 | 2024-12-31 19:00 | 0.0047614 | 7.6796e-05 | 2 | 124 | Unplanned | Lightning | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1073 | 120673 | 1005 Hiririroa Road | Totangi 1101 | 2024-12-31 18:31 | 2024-12-31 19:30 | 0.0022655 | 3.8398e-05 | 1 | 59 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1074 | 29976 | Ihungia Road | Mata 0304 | 2024-12-31 18:48 | 2025-01-01 13:19 | 0.5355 | 0.00061437 | 16 | 13946 | Unplanned | Vegetation | Tree fell over line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1075 | N/A 58 | Kaiti | Kaiti Sub 05 | 2024-12-31 19:16 | 2024-12-31 19:45 | 0.0011135 | 3.8398e-05 | 1 | 29 | Unplanned | Vegetation | Tree @ B5038. Heavy rain & Wind, Flash over | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1076 | N/A 58 | Kaiti | Herschell 0501 | 2024-12-31 19:16 | 2024-12-31 19:45 | 0.19598 | 0.0067581 | 176 | 5104 | Unplanned | Vegetation | Tree @ B5038. Heavy rain & Wind, Flash over | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1077 | N/A 58 | Kaiti | Dalton 0502 | 2024-12-31 19:16 | 2024-12-31 19:45 | 0.91422 | 0.031525 | 821 | 23809 | Unplanned | Vegetation | Tree @ B5038. Heavy rain & Wind, Flash over | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1078 | N/A 58 | Kaiti | Tamarau 0503 | 2024-12-31 19:16 | 2024-12-31 19:45 | 1.177 | 0.040587 | 1057 | 30653 | Unplanned | Vegetation | Tree @ B5038. Heavy rain & Wind, Flash over | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1079 | N/A 58 | Kaiti | Wainui 0504 | 2024-12-31 19:16 | 2024-12-31 19:45 | 0.72603 | 0.025036 | 652 | 18908 | Unplanned | Vegetation | Tree @ B5038. Heavy rain & Wind, Flash over | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1080 | N/A 58 | Kaiti | Whangara 0506 | 2024-12-31 19:16 | 2024-12-31 19:45 | 0.65588 | 0.022616 | 589 | 17081 | Unplanned | Vegetation | Tree @ B5038. Heavy rain & Wind, Flash over | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1081 | 29973 | Tiniroto road | Tiniroto 1003 | 2024-12-31 19:27 | 2024-12-31 23:58 | 0.44907 | 0.0032638 | 85 | 11695 | Unplanned | Vegetation | Tree thru line D386 - High Winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1082 | 120225 | 4029 Tauwhareparae Rd | Tauwhareparae 0404 | 2024-12-31 19:49 | 2025-01-01 10:00 | 0.065353 | 7.6796e-05 | 2 | 1702 | Unplanned | Defective Equipment | Replacr fuses & wire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1083 | 120249 | 91 Marumoko Road | Matawai 1204 | 2024-12-31 19:59 | 2024-12-31 21:00 | 0.0023423 | 3.8398e-05 | 1 | 61 | Unplanned | Lightning | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1084 | 120315 | 899 Poroporo Road | Tiki Tiki 0206 | 2024-12-31 21:30 | 2024-12-31 23:00 | 0.044926 | 0.00049917 | 13 | 1170 | Unplanned | Lightning | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1085 | 121468 | 5591 Matawai Road | Mata 0304 | 2025-01-01 08:48 | 2025-01-01 09:20 | 0.0012287 | 3.8398e-05 | 1 | 32 | Unplanned | Lightning | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1086 | 121577 | 4539 Te Araroa Road | Hicks Bay 0102 | 2025-01-01 11:31 | 2025-01-01 14:15 | 0.0062973 | 3.8398e-05 | 1 | 164 | Unplanned | Lightning | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1087 | 121605 | 146 Matanui Road | Tauwhareparae 0404 | 2025-01-01 12:22 | 2025-01-02 08:00 | 0.045233 | 3.8398e-05 | 1 | 1178 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1088 | 121670 | 481 Te Araroa Road | Tiki Tiki 0206 | 2025-01-01 13:24 | 2025-01-01 14:30 | 0.0025343 | 3.8398e-05 | 1 | 66 | Unplanned | Lightning | Replace fusewire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1089 | 120896 | Onenui Station | Mahia 3301 | 2025-01-01 14:54 | 2025-01-01 16:30 | 0.0073724 | 7.6796e-05 | 2 | 192 | Unplanned | Lightning | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1090 | 29919 | Tiniroto | Tiniroto 1003 | 2025-01-02 08:27 | 2025-01-02 15:24 | 0.5959 | 0.004531 | 118 | 15519 | Unplanned | Vegetation | Tree through the line at D3289 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1091 | 29922 | Hikuwai | Mata 0304 | 2025-01-02 11:43 | 2025-01-02 17:10 | 0.37292 | 0.0032638 | 85 | 9712 | Unplanned | Vegetation | Tree across the line @ H714 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1092 | N/A 66 | Kahunganga | Raupunga 3101 | 2025-01-02 13:20 | 2025-01-02 17:58 | 0.20865 | 0.00095995 | 25 | 5434 | Unplanned | Adverse Weather | High winds causing trees to clash conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1093 | 29924 | Tahora | Matawai 1204 | 2025-01-02 14:07 | 2025-01-04 11:58 | 0.3169 | 0.00011519 | 3 | 8253 | Unplanned | Lightning | Lightnening blew TX | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1094 | 123326 | 8 Judd Road | Lavenham 0902 | 2025-01-03 14:52 | 2025-01-03 16:00 | 0.013055 | 0.00019199 | 5 | 340 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1095 | 122848 | 350 Erepeti Rd | Ruakituri 2003 | 2025-01-03 19:15 | 2025-01-03 20:30 | 0.0028799 | 3.8398e-05 | 1 | 75 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1096 | 122844 | 404 Armstrong Road | Whatatutu 1201 | 2025-01-03 19:19 | 2025-01-03 20:55 | 0.0036862 | 3.8398e-05 | 1 | 96 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1097 | 123742 | 1341 Mahia Settlement Road | Mahia 3301 | 2025-01-04 07:45 | 2025-01-04 09:45 | 0.04147 | 0.00034558 | 9 | 1080 | Unplanned | Lightning | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1098 | 123772 | 4988 Te Araroa Road | Hicks Bay 0102 | 2025-01-04 08:05 | 2025-01-04 10:00 | 0.013247 | 0.00011519 | 3 | 345 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1099 | 29984 | Ruakitori | Ruakituri 2003 | 2025-01-04 12:07 | 2025-01-10 12:53 | 0.33806 | 0.00015359 | 4 | 8804 | Unplanned | Vegetation | High wind tree thru line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1100 | 124086 | 1945 Te Araroa Road | Tiki Tiki 0206 | 2025-01-04 13:32 | 2025-01-04 14:55 | 0.003187 | 3.8398e-05 | 1 | 83 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1101 | 29925 | Mahia | Mahia 3301 | 2025-01-04 16:01 | 2025-01-04 21:09 | 2.1516 | 0.073571 | 1916 | 56033 | Unplanned | Adverse Weather | Indication showed loss of phase, found jumper off arm W8783. High Winds use generator, High Winds Clashing | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1102 | 29926 | Whatatutu | Whatatutu 1201 | 2025-01-04 17:59 | 2025-01-04 23:40 | 0.72538 | 0.0048382 | 126 | 18891 | Unplanned | Adverse Weather | Wires down at pole E714 - High Winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1103 | 29927 | 6590 Waiapu Road | Makarika 0204 | 2025-01-05 13:58 | 2025-01-06 12:08 | 0.15674 | 0.0028031 | 73 | 4082 | Unplanned | Lightning | Suspected Lightning strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1104 | 125577 | 701 Tapuaeroa Rd | Tiki Tiki 0206 | 2025-01-05 21:53 | 2025-01-06 10:53 | 0.059901 | 7.6796e-05 | 2 | 1560 | Unplanned | Lightning | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1105 | 29930 | Ruakaka Road | Tiniroto 1003 | 2025-01-06 09:57 | 2025-01-06 18:04 | 0.15977 | 0.00088315 | 23 | 4161 | Unplanned | Defective Equipment | Faulty TX | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1106 | 125694 | 55A Waititi Road | Morere 3401 | 2025-01-06 13:14 | 2025-01-06 15:00 | 0.016281 | 0.00015359 | 4 | 424 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1107 | 29980 | Awapuni Road | Awapuni 0606 | 2025-01-06 15:40 | 2025-01-06 15:51 | 0.12875 | 0.013439 | 350 | 3353 | Unplanned | Human Error | 2 x feeder tripped whilst parralling, for planned switching | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1108 | N/A 64 | Ihungia Road | Mata 0304 | 2025-01-07 00:46 | 2025-01-07 01:44 | 0.035633 | 0.00061437 | 16 | 928 | Unplanned | Unknown cause | Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1109 | 29931 | SH2 Waihua Mohaka | Raupunga 3101 | 2025-01-07 01:28 | 2025-01-07 11:38 | 4.65 | 0.013247 | 345 | 121099 | Unplanned | Adverse Environment | Pine tree thru line W6346 - W1195. All 3 wires (out of zone) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1110 | 126286 | 4876 Tiniroto Road | Tiniroto 1003 | 2025-01-07 11:39 | 2025-01-08 10:08 | 0.051799 | 3.8398e-05 | 1 | 1349 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1111 | 126324 | Matanui Rd 1km W/Shed + Quarters | Tauwhareparae 0404 | 2025-01-07 15:48 | 2025-01-07 17:35 | 0.0082172 | 7.6796e-05 | 2 | 214 | Unplanned | Lightning | Been out since lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1112 | 126712 | 158 Waihau Road | Rototahi 0403 | 2025-01-08 06:31 | 2025-01-08 23:15 | 0.11565 | 0.00011519 | 3 | 3012 | Unplanned | Lightning | Lightning early hrs. Also birds nestat TX A849 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1113 | N/A 65a | Tolaga Bay | Tolaga Bay Sub | 2025-01-10 23:56 | 2025-01-11 00:30 | 0.0013055 | 3.8398e-05 | 1 | 34 | Unplanned | Unknown cause | Patrol nothing found E/F. Fault indicator didn't detect fault, therefore fault in first part of line. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1114 | N/A 65a | Tolaga Bay | Toko Tie 0401 | 2025-01-10 23:56 | 2025-01-11 00:30 | 0.10966 | 0.0032254 | 84 | 2856 | Unplanned | Unknown cause | Patrol nothing found E/F. Fault indicator didn't detect fault, therefore fault in first part of line. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1115 | N/A 65a | Tolaga Bay | Town 0402 | 2025-01-10 23:56 | 2025-01-11 00:30 | 0.26763 | 0.0078716 | 205 | 6970 | Unplanned | Unknown cause | Patrol nothing found E/F. Fault indicator didn't detect fault, therefore fault in first part of line. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1116 | N/A 65a | Tolaga Bay | Rototahi 0403 | 2025-01-10 23:56 | 2025-01-11 00:30 | 0.282 | 0.008294 | 216 | 7344 | Unplanned | Unknown cause | Patrol nothing found E/F. Fault indicator didn't detect fault, therefore fault in first part of line. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1117 | N/A 65a | Tolaga Bay | Tauwhareparae 0404 | 2025-01-10 23:56 | 2025-01-11 00:30 | 0.19061 | 0.0056061 | 146 | 4964 | Unplanned | Unknown cause | Patrol nothing found E/F. Fault indicator didn't detect fault, therefore fault in first part of line. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1118 | 128338 | 4314 Ihungia Road | Mata 0304 | 2025-01-11 06:59 | 2025-01-11 09:10 | 0.020121 | 0.00015359 | 4 | 524 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1119 | 30000 | Harris Street | Harris 1502 | 2025-01-11 12:49 | 2025-01-13 17:26 | 0.94751 | 0.0047614 | 124 | 24676 | Unplanned | Defective Equipment | GM TX caught on fire. Internal fault. Install generator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1120 | 129026 | Lake Rd, Patutahi | Lavenham 0902 | 2025-01-12 08:57 | 2025-01-12 11:00 | 0.028338 | 0.00023039 | 6 | 738 | Unplanned | Wildlife | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1121 | 129623 | 6239 Matawai Road | Matawai 1204 | 2025-01-13 06:41 | 2025-01-13 09:05 | 0.016588 | 0.00011519 | 3 | 432 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1122 | 129631 | 3 Bond road | Waimata 0903 | 2025-01-13 06:55 | 2025-01-13 08:05 | 0.053757 | 0.00076796 | 20 | 1400 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1123 | 129699 | 12.5km Tapuaeroa Rd | Tiki Tiki 0206 | 2025-01-13 08:10 | 2025-01-13 10:15 | 0.0047998 | 3.8398e-05 | 1 | 125 | Unplanned | Lightning | Apparently been off since lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1124 | 129694 | 457 Woodlands Road | Raupunga 3101 | 2025-01-13 08:37 | 2025-01-13 10:55 | 0.015897 | 0.00011519 | 3 | 414 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1125 | 3480 | Christopher Rd / Pa Road | Dalton 0502 | 2025-01-14 09:03 | 2025-01-14 16:07 | 1.4164 | 0.0033406 | 87 | 15581.3783 | Planned | Planned | Replace 50kV pole A1054 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1126 | 3458 | Bushmere Road | Waimata 0903 | 2025-01-14 09:05 | 2025-01-14 13:47 | 0.40065 | 0.0014207 | 37 | 5225.6735 | Planned | Planned | Replace ABS 495 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1127 | 30657 | Frasertown | Frasertown 3103 | 2025-01-15 06:00 | 2025-01-15 10:16 | 2.584 | 0.025419 | 662 | 67296 | Unplanned | Wildlife | Duck hit/broken line W979 - W813 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1128 | 3460 | Wellington Street | Childers 0605 | 2025-01-15 09:03 | 2025-01-15 09:29 | 0.088853 | 0.0034174 | 89 | 1160.954 | Planned | Planned | Replace 11kV Cable stand-off | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1129 | 130988 | Andrews Road, Whangara | Dalton 0502 | 2025-01-15 09:06 | 2025-01-15 12:25 | 0.022924 | 0.00011519 | 3 | 597 | Unplanned | Wildlife | Fuse tube also burnt had to replace | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1130 | 3459 | Aberdeen road | Gladstone 0607 | 2025-01-15 11:02 | 2025-01-15 11:50 | 0.13455 | 0.0028031 | 73 | 1756.911 | Planned | Planned | Replace 11kV cable stand-off | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1131 | 131027 | 197 Archillies Street | Borough Two 3205 | 2025-01-15 11:05 | 2025-01-15 13:10 | 0.047998 | 0.00038398 | 10 | 1250 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1132 | 3461 | Chalmers Road | Chalmers 0707 | 2025-01-15 13:05 | 2025-01-15 13:36 | 0.11189 | 0.0036094 | 94 | 1462.2589 | Planned | Planned | Replace 11kV crucitix standoffs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1133 | 3462 | Main Rd, Makaraka | Campion 0802 | 2025-01-15 14:31 | 2025-01-15 14:50 | 0.039396 | 0.0020735 | 54 | 514.0637 | Planned | Planned | Replace 11kV cable stand-offs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1134 | 30659 | Wainui Rd | Dalton 0502 | 2025-01-16 05:39 | 2025-01-16 07:45 | 0.60408 | 0.010598 | 276 | 15732 | Unplanned | Adverse Environment | Salt buildup on ABS A2188 which caused tracking | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1135 | 3463 | Kiore Road | Tauwhareparae 0404 | 2025-01-16 09:02 | 2025-01-16 12:38 | 0.066352 | 0.00030718 | 8 | 864.2949 | Planned | Planned | Replace pole G1522 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1136 | 131730 | 165 Glendening Road | Raupunga 3101 | 2025-01-16 16:45 | 2025-01-16 18:50 | 0.043198 | 0.00034558 | 9 | 1125 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1137 | 131755 | 459 Waiomatatini Road | Ruatoria 0201 | 2025-01-16 17:31 | 2025-01-16 18:48 | 0.041393 | 0.00053757 | 14 | 1078 | Unplanned | Vegetation | Multiple branches near 11kvnear pole J1688 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1138 | 131813 | 168 Karaua Road | Muriwai 0905 | 2025-01-16 18:25 | 2025-01-16 20:30 | 0.014399 | 0.00011519 | 3 | 375 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1139 | 3473 A | Cambridge Tce | Crawford 1504 | 2025-01-17 08:38 | 2025-01-17 09:43 | 0.22463 | 0.0034558 | 90 | 2935.1083 | Planned | Planned | Replace 11kV cable standoff insulators | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1140 | 3497 | Waimata Valley Rd / Manders Road | Waimata 0903 | 2025-01-17 09:03 | 2025-01-17 10:51 | 0.1327 | 0.0012287 | 32 | 3456 | Planned | Planned | To make repairs @ Pole E1168 - Urgent Work | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1141 | 3472 | Tuparoa road | Ruatoria 0201 | 2025-01-17 09:10 | 2025-01-17 12:35 | 0.15743 | 0.00076796 | 20 | 2051.5743 | Planned | Planned | Install 2ph 30kVA TX J1591 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1142 | 3475 | Ranfurly Street | Crawford 1504 | 2025-01-17 10:32 | 2025-01-17 11:15 | 0.20639 | 0.0047998 | 125 | 2700.3993 | Planned | Planned | Replace 11kV cable standoff insulators | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1143 | 3474 | Owen Road | Crawford 1504 | 2025-01-17 12:36 | 2025-01-17 13:23 | 0.1534 | 0.0032638 | 85 | 2004.0195 | Planned | Planned | Replace HV cable stand-offs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1144 | 132342 | 225 Maclaurin Road | Haisman 0804 | 2025-01-17 16:18 | 2025-01-17 18:20 | 0.0093691 | 7.6796e-05 | 2 | 244 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1145 | 133618 | 204 Pa Rd | Dalton 0502 | 2025-01-19 10:13 | 2025-01-19 12:20 | 0.13654 | 0.0010751 | 28 | 3556 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1146 | 3478 | Wharekopae Road | Tahunga 1004 | 2025-01-20 15:01 | 2025-01-20 16:16 | 0.15021 | 0.0030718 | 80 | 1958.1712 | Planned | Planned | To connect generator. Phase rotation incorrect required subsequant outage. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1147 | 134449 | Waiomatatini Road | Ruatoria 0201 | 2025-01-20 16:28 | 2025-01-20 18:54 | 0.078486 | 0.00053757 | 14 | 2044 | Unplanned | Defective Equipment | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1148 | 30717 | Waiomatatini Road | Ruatoria 0201 | 2025-01-20 18:24 | 2025-01-20 18:57 | 0.01774 | 0.00053757 | 14 | 462 | Unplanned | Defective Equipment | Temporary restrain of conductor to provide clearance from LV underbuilt. Shackle pulled out. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1149 | 3477 | Somerton Road | Haisman 0804 | 2025-01-21 08:03 | 2025-01-21 15:14 | 0.38064 | 0.00088315 | 23 | 4960.8774 | Planned | Planned | Cut trees | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1150 | 134949 | 653 Mangapoiki Road | Frasertown 3103 | 2025-01-21 08:58 | 2025-01-21 10:00 | 0.0047614 | 7.6796e-05 | 2 | 124 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1151 | 3479 | Wharekopare Road | Tahora 1103 | 2025-01-22 12:30 | 2025-01-22 13:13 | 0.092462 | 0.0021503 | 56 | 0 | Planned | Planned | To disconnect and remove 300kVA Gen Truck at pole D5035 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1152 | 3485 | Riverside Road | Whangara 0506 | 2025-01-23 08:55 | 2025-01-23 13:41 | 0.043927 | 0.00015359 | 4 | 572.1106 | Planned | Planned | Realign o/head 11kV line. Install 3 x new poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1153 | 136307 | 113 Riuohangi Road | Frasertown 3103 | 2025-01-23 18:28 | 2025-01-23 19:30 | 0.014284 | 0.00023039 | 6 | 372 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1154 | 136682 | 127 Blucks Pit | Morere 3401 | 2025-01-24 08:22 | 2025-01-24 10:20 | 0.0090619 | 7.6796e-05 | 2 | 236 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1155 | 3508 | Waiomatatini | Ruatoria 0201 | 2025-01-24 09:01 | 2025-01-24 12:13 | 0.10321 | 0.00053757 | 14 | 2688 | Planned | Planned | Urgent Work to replace faulty pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1156 | 3507 | Mitchell Rd/ Churchill Ave | Borough Two 3205 | 2025-01-24 09:02 | 2025-01-24 10:36 | 0.36455 | 0.0038782 | 101 | 9494 | Planned | Planned | Urgent Work to repair pulled out insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1157 | 3446 | Ngakaroa Road | Waimata 0903 | 2025-01-24 09:03 | 2025-01-24 16:15 | 0.36493 | 0.00084476 | 22 | 4590.8749 | Planned | Planned | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1158 | 30671 | Otoi road | Raupunga 3101 | 2025-01-24 12:11 | 2025-01-24 13:28 | 0.03548 | 0.00046078 | 12 | 924 | Unplanned | Defective Equipment | Cracked at HV insulator on pole W5064 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1159 | 138449 | Tahora settlement Rd | Tahora 1103 | 2025-01-26 16:09 | 2025-01-26 17:30 | 0.018661 | 0.00023039 | 6 | 486 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1160 | 138931 | Nuhaka River Road | Morere 3401 | 2025-01-27 10:51 | 2025-01-27 12:20 | 0.0068349 | 7.6796e-05 | 2 | 178 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1161 | 139073 | 362 Whakaangiangi Rd | Awatere 0101 | 2025-01-27 14:26 | 2025-01-29 15:11 | 0.11231 | 3.8398e-05 | 1 | 2925 | Unplanned | Defective Equipment | 1xddo kept blowing. Without lv fuses in also. Will need TX + DDO's replaced. Ancient | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1162 | 30677 | Tiniroto road | Frasertown 3103 | 2025-01-27 16:02 | 2025-01-27 20:15 | 0.34696 | 0.0029183 | 76 | 9036 | Unplanned | Vegetation | Tree fallen across lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1163 | 139223 | 404 Armstrong Road | Whatatutu 1201 | 2025-01-27 18:41 | 2025-01-27 20:40 | 0.0045694 | 3.8398e-05 | 1 | 119 | Unplanned | Vegetation | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1164 | 139259 | 2253 Te Araroa Road | Awatere 0101 | 2025-01-27 18:56 | 2025-01-27 20:30 | 0.010828 | 0.00011519 | 3 | 282 | Unplanned | Adverse Weather | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1165 | 139532 | 454 Tauwhareparae Rd, Mangaheia stn | Tauwhareparae 0404 | 2025-01-28 08:47 | 2025-01-28 10:45 | 0.004531 | 3.8398e-05 | 1 | 118 | Unplanned | Adverse Weather | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1166 | 30722 | Whakaangiangi Road | Awatere 0101 | 2025-01-28 11:53 | 2025-01-28 12:55 | 0.038091 | 0.00061437 | 16 | 992 | Unplanned | Lightning | Replace TX J324 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1167 | 140110 | 27 Marumoko Road | Matawai 1204 | 2025-01-29 08:00 | 2025-01-29 10:00 | 0.22117 | 0.0018431 | 48 | 5760 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1168 | 3482 | Hikuwai Drive | Mata 0304 | 2025-01-29 08:34 | 2025-01-29 16:32 | 0.018354 | 3.8398e-05 | 1 | 239.0092 | Planned | Planned | Replace 50kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1169 | 3483 | Waiapu Road | Mata 0304 | 2025-01-30 08:34 | 2025-01-30 15:10 | 0.015206 | 3.8398e-05 | 1 | 198.0076 | Planned | Planned | 11kV isolated for safety. Replace 50kV pole H1158 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1170 | 140733 | Makarika / Karewa cnr | Makarika 0204 | 2025-01-30 08:54 | 2025-01-30 10:15 | 0.012441 | 0.00015359 | 4 | 324 | Unplanned | Wildlife | Line patrol completed. Lots of ducks/geese in paddocks | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1171 | 3490 | 1900 Te Araroa Road | Tiki Tiki 0206 | 2025-01-30 12:28 | 2025-01-30 14:59 | 0.023192 | 0.00015359 | 4 | 244.0375 | Planned | Planned | Replace TX J35 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1172 | 3496 | 1900 Te Araroa Road | Hicks Bay 0102 | 2025-01-31 08:00 | 2025-01-31 12:14 | 2.5456 | 0.010022 | 261 | 23725.4141 | Planned | Planned | Install new HV links @ J596 & associated s/gear | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1173 | 3488c | Tuai | Ruakituri 2003 | 2025-01-31 09:06 | 2025-01-31 17:46 | 3.2516 | 0.0062589 | 163 | 36277.8671 | Planned | Planned | Tuai Sub 5yr maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1174 | 3488a | Tuai | Lake | 2025-01-31 09:23 | 2025-01-31 10:11 | 0.0042238 | 0.0011519 | 30 | 0 | Planned | Planned | Tuai Sub 5yr maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1175 | 3488a | Tuai | Village 2002 | 2025-01-31 09:23 | 2025-01-31 10:11 | 0.073916 | 0.020159 | 525 | 0 | Planned | Planned | Tuai Sub 5yr maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1176 | N/A 67 | All Tuai Sub | Tuai-Wairoa A 5004 | 2025-01-31 12:36 | 2025-01-31 12:46 | 0.13478 | 0.013478 | 351 | 3510 | Unplanned | Human Error | Switch CB's over for MTC | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1177 | 3488b | Tuai | Lake | 2025-01-31 17:37 | 2025-01-31 17:44 | 0.0026879 | 0.00038398 | 10 | 0 | Planned | Planned | Tuai Sub 5yr maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1178 | 3488b | Tuai | Village 2002 | 2025-01-31 17:37 | 2025-01-31 17:44 | 0.047038 | 0.0067197 | 175 | 0 | Planned | Planned | Tuai Sub 5yr maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1179 | 142593 | 1226 Mangapoike Road | Frasertown 3103 | 2025-02-01 17:55 | 2025-02-01 18:30 | 0.0026879 | 7.6796e-05 | 2 | 70 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1180 | 142675 | 4029 Tauwhareparae Rd | Tauwhareparae 0404 | 2025-02-01 20:00 | 2025-02-02 08:35 | 0.057981 | 7.6796e-05 | 2 | 1510 | Unplanned | Lightning | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1181 | N/A 68 | Tiniroto Rd, Ruakaka Road | Tiniroto 1003 | 2025-02-01 21:25 | 2025-02-02 08:45 | 0.51768 | 0.0057597 | 150 | 13482 | Unplanned | Wildlife | Possum at pole D3559. Pole has possum guard, may have climbed via stay wire. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1182 | 142830 | 209 Browns Beach Road | Muriwai 0905 | 2025-02-02 06:30 | 2025-02-02 08:15 | 0.024191 | 0.00023039 | 6 | 630 | Unplanned | Lightning | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1183 | 142833 | 213 Taurau Valley Road | Te Arai 0906 | 2025-02-02 06:36 | 2025-02-02 09:15 | 0.012211 | 7.6796e-05 | 2 | 318 | Unplanned | Lightning | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1184 | 30691 | Wharerata Road | Muriwai 0905 | 2025-02-02 06:45 | 2025-02-12 10:27 | 0.56146 | 3.8398e-05 | 1 | 14622 | Unplanned | Lightning | Replace TX C394 - Power not needed, no access | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1185 | 3499 | Bright Street | City 0602 | 2025-02-02 07:39 | 2025-02-02 13:45 | 0.084322 | 0.00023039 | 6 | 1098.3732 | Planned | Planned | To replace RMU B1047, B510, B511, B512 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1186 | 142881 | 564 Centennial Marine Drive | JNL_A 1405 | 2025-02-02 08:28 | 2025-02-02 09:00 | 0.0086012 | 0.00026879 | 7 | 224 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1187 | 142951 | 36 Saddler Road | Te Arai 0906 | 2025-02-02 10:09 | 2025-02-02 11:30 | 0.0031102 | 3.8398e-05 | 1 | 81 | Unplanned | Lightning | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1188 | 30746 | Matanui Road | Tauwhareparae 0404 | 2025-02-02 12:30 | 2025-02-03 12:21 | 0.1099 | 7.6796e-05 | 2 | 2862 | Unplanned | Lightning | Replaced TX G233 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1189 | 143354 | 708 Mahunga Road | Mahia 3301 | 2025-02-02 20:04 | 2025-02-03 09:00 | 0.14898 | 0.00019199 | 5 | 3880 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1190 | 143631 | 4988 Te Araroa Road | Hicks Bay 0102 | 2025-02-03 11:28 | 2025-02-03 13:30 | 0.014054 | 0.00011519 | 3 | 366 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1191 | 143739 | 1435 Waingake Road | Te Arai 0906 | 2025-02-03 15:27 | 2025-02-03 17:33 | 0.0096763 | 7.6796e-05 | 2 | 252 | Unplanned | Lightning | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1192 | 143360 | 1116 Motu Road | Matawai 1204 | 2025-02-03 19:35 | 2025-02-03 22:15 | 0.024575 | 0.00015359 | 4 | 640 | Unplanned | Lightning | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1193 | 3492 | Ohuka Road | Ruakituri 2003 | 2025-02-04 09:06 | 2025-02-04 14:40 | 0.12825 | 0.00038398 | 10 | 1670.6412 | Planned | Planned | Replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1194 | 3491 | 4258 Te Araroa Road | Te Araroa 0103 | 2025-02-04 10:01 | 2025-02-04 11:17 | 0.0087548 | 0.00011519 | 3 | 114.0311 | Planned | Planned | Upgrade TX J280 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1195 | 3493 | Ohuka Road | Ruakituri 2003 | 2025-02-05 09:14 | 2025-02-05 13:56 | 0.10828 | 0.00038398 | 10 | 1410.6336 | Planned | Planned | Replace 11kV poles & TX | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1196 | 144940 | 143 Matanui Road | Tauwhareparae 0404 | 2025-02-05 10:49 | 2025-02-05 12:50 | 0.0092923 | 7.6796e-05 | 2 | 242 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1197 | 30052 | Browns Beach Road | Muriwai 0905 | 2025-02-07 14:28 | 2025-02-08 08:56 | 0.092155 | 0.00023039 | 6 | 2400 | Unplanned | Defective Equipment | Replace faulty TX | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1198 | 30749 | Tauwharepaere | Tauwhareparae 0404 | 2025-02-08 11:34 | 2025-02-10 16:37 | 0.40671 | 0.0020351 | 53 | 10592 | Unplanned | Third Party Interference | Replace Poles & conductor after tree-feller brought tree down through line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1199 | 30053 | Morere | Morere 3401 | 2025-02-08 19:06 | 2025-02-09 15:24 | 0.68921 | 0.0032638 | 85 | 17949 | Unplanned | Adverse Environment | Large slip, slow moving causes wire to tension up and snap | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1200 | 30054 | Back Ormond Road / Waimata Valley | Waimata 0903 | 2025-02-08 22:01 | 2025-02-09 15:18 | 1.5124 | 0.027339 | 712 | 39388 | Unplanned | Third Party Interference | Car hit Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1201 | N/A 70 | Tolaga Bay | Tauwhareparae 0404 | 2025-02-08 23:45 | 2025-02-08 23:54 | 0.050455 | 0.0056061 | 146 | 1314 | Unplanned | Unknown cause | Patrol no cause found. Suspect insulator flash over | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1202 | N/A 70 | Tolaga Bay | Toko Tie 0401 | 2025-02-08 23:45 | 2025-02-08 23:56 | 0.03548 | 0.0032254 | 84 | 924 | Unplanned | Unknown cause | Patrol no cause found. Suspect insulator flash over | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1203 | N/A 70 | Tolaga Bay | Town 0402 | 2025-02-08 23:45 | 2025-02-08 23:56 | 0.086588 | 0.0078716 | 205 | 2255 | Unplanned | Unknown cause | Patrol no cause found. Suspect insulator flash over | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1204 | N/A 70 | Tolaga Bay | Rototahi 0403 | 2025-02-08 23:45 | 2025-02-08 23:57 | 0.099528 | 0.008294 | 216 | 2592 | Unplanned | Unknown cause | Patrol no cause found. Suspect insulator flash over | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1205 | N/A 70 | Tolaga Bay | Tolaga Bay Sub | 2025-02-08 23:45 | 2025-02-08 23:53 | 0.00030718 | 3.8398e-05 | 1 | 8 | Unplanned | Unknown cause | Patrol no cause found. Suspect insulator flash over | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1206 | 148093 | 279 Tahora Settlement Road | Tahora 1103 | 2025-02-09 18:36 | 2025-02-09 21:20 | 0.15113 | 0.00092155 | 24 | 3936 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1207 | 148378 | 183 Tuparoa Road | Ruatoria 0201 | 2025-02-10 07:43 | 2025-02-10 09:23 | 0.076796 | 0.00076796 | 20 | 2000 | Unplanned | Wildlife | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1208 | 3515 | Lake, Village, Ruakituri | Tuai Sub | 2025-02-11 06:45 | 2025-02-11 17:33 | 0.026955 | 0.026955 | 702 | 702 | Planned | Planned | Transpower disconnector maintenance @ Tuai | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1209 | N/A 71 | Tolaga Bay Sub | Rototahi 0403 | 2025-02-11 07:39 | 2025-02-11 07:48 | 0.074646 | 0.008294 | 216 | 1944 | Unplanned | Human Error | Open 50kV CB H14 as part of SW3498. H14 was suppling Tolaga Bay as the Gis - Tol 50kV was under fault conditions | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1210 | N/A 71 | Tolaga Bay Sub | Town 0402 | 2025-02-11 07:39 | 2025-02-11 07:50 | 0.086588 | 0.0078716 | 205 | 2255 | Unplanned | Human Error | Open 50kV CB H14 as part of SW3498. H14 was suppling Tolaga Bay as the Gis - Tol 50kV was under fault conditions | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1211 | N/A 71 | Tolaga Bay Sub | Toko Tie 0401 | 2025-02-11 07:39 | 2025-02-11 07:50 | 0.03548 | 0.0032254 | 84 | 924 | Unplanned | Human Error | Open 50kV CB H14 as part of SW3498. H14 was suppling Tolaga Bay as the Gis - Tol 50kV was under fault conditions | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1212 | N/A 71 | Tolaga Bay Sub | Tauwhareparae 0404 | 2025-02-11 07:39 | 2025-02-11 07:50 | 0.061667 | 0.0056061 | 146 | 1606 | Unplanned | Human Error | Open 50kV CB H14 as part of SW3498. H14 was suppling Tolaga Bay as the Gis - Tol 50kV was under fault conditions | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1213 | 3498 | Waiapu Road | Inland 0301 | 2025-02-11 07:56 | 2025-02-11 14:32 | 0.36079 | 0.0017279 | 45 | 5164.3129 | Unplanned | Human Error | Switching error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1214 | 30005 | Peel Street | Reads Quay 0603 | 2025-02-11 08:24 | 2025-02-11 20:05 | 0.013171 | 0.00030718 | 8 | 343 | Unplanned | Defective Equipment | Replace faulty TX | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1215 | 3498 A | Waiapu Road | Inland 0301 | 2025-02-11 15:22 | 2025-02-11 15:25 | 0.15321 | 0.051069 | 1330 | 0 | Planned | Planned | Replace 50kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1216 | 30010 | Matawai Rd, Bushmere Road | Waimata 0903 | 2025-02-11 22:11 | 2025-02-11 22:51 | 0.11827 | 0.0029566 | 77 | 3080 | Unplanned | Defective Equipment | Blown jumper on Links D4318 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1217 | 3495 | Waireka Road | Frasertown 3103 | 2025-02-12 09:03 | 2025-02-12 13:05 | 0.13009 | 0.00053757 | 14 | 3388 | Planned | Planned | Replace pole W5019 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1218 | 149956 | 195 Russell Road, Ngatapa | Ngatapa 1102 | 2025-02-12 17:40 | 2025-02-12 19:00 | 0.03379 | 0.00042238 | 11 | 880 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1219 | 30015 | Tiniroto Rd / Lavenham Rd | Lavenham 0902 | 2025-02-13 13:43 | 2025-02-13 16:31 | 0.62504 | 0.017241 | 449 | 16278 | Unplanned | Third Party Interference | Pole D1389 down due to Car V's Pole D1389 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1220 | 3501 | Tokomaru Bay | Rua-Te Araroa 50kV | 2025-02-13 14:29 | 2025-02-13 14:30 | 0.018201 | 0.018201 | 474 | 0 | Planned | Planned | Replacing 50kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1221 | 1710 A | Tauwhareparae Rd | Tauwhareparae 0404 | 2025-02-14 09:02 | 2025-02-14 12:42 | 0.41731 | 0.0020351 | 53 | 10868 | Planned | Planned | Replace poles & conductor after tree-feller brought tree down through line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1222 | 151086 | 207 Rockhill Road | W O Kuri 1001 | 2025-02-14 10:17 | 2025-02-14 12:20 | 0.014169 | 0.00011519 | 3 | 369 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1223 | 150887 | 1926 Rakaroa Road | Matawai 1204 | 2025-02-14 20:44 | 2025-02-15 00:10 | 0.08701 | 0.00042238 | 11 | 2266 | Unplanned | Lightning | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1224 | 152519 | 109 Shanks Road | Te Arai 0906 | 2025-02-16 07:29 | 2025-02-16 09:30 | 0.023231 | 0.00019199 | 5 | 605 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1225 | 3509 | Gladstone Rd / Lytton Rd | Lytton 0701 | 2025-02-16 08:31 | 2025-02-16 12:30 | 0.68828 | 0.0028799 | 75 | 8994.8983 | Planned | Planned | Replace TX B94 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1226 | 30058 | Ruakaka Road | Tiniroto 1003 | 2025-02-16 08:49 | 2025-02-16 09:56 | 0.036017 | 0.00053757 | 14 | 938 | Unplanned | Defective Equipment | Cracked insulator @ HV fuses D295 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1227 | 153233 | 673 Hokoroa Road | Tauwhareparae 0404 | 2025-02-17 08:33 | 2025-02-17 10:00 | 0.013363 | 0.00015359 | 4 | 348 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1228 | 30022 | Waima | Seaside 0302 | 2025-02-17 10:16 | 2025-02-17 11:06 | 0.092155 | 0.0018431 | 48 | 2400 | Unplanned | Vegetation | Tree through 11kV lind at pole H2679 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1229 | 30024 | waima | Seaside 0302 | 2025-02-17 14:04 | 2025-02-17 17:05 | 0.3336 | 0.0018431 | 48 | 8688 | Unplanned | Vegetation | Tree brought down through 11kV | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1230 | 3503 | Wheatstone Road | Dalton 0502 | 2025-02-18 08:32 | 2025-02-18 12:34 | 0.26948 | 0.0011135 | 29 | 3514.8127 | Planned | Planned | 3503/1 Max McLean installed HV Pole & TX A292. 3503 Electrinet unable to complete work due to wind conditions | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1231 | 3494 | Putere Road | Raupunga 3101 | 2025-02-18 09:03 | 2025-02-18 13:29 | 0.24513 | 0.00092155 | 24 | 3195.3176 | Planned | Planned | Replace pole W5096 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1232 | 153888 | 21 Makatote Rd, Waipiro | Makarika 0204 | 2025-02-18 09:06 | 2025-02-18 12:24 | 0.11404 | 0.00057597 | 15 | 2970 | Unplanned | Defective Equipment | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1233 | 30028 | Puhinga Road | Makarika 0204 | 2025-02-18 11:54 | 2025-02-18 12:24 | 0.017279 | 0.00057597 | 15 | 450 | Unplanned | Defective Equipment | Resag conductor @ pole H1575 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1234 | 154511 | 31 Tiniroto Road, | Frasertown 3103 | 2025-02-19 06:12 | 2025-02-19 07:40 | 0.0067581 | 7.6796e-05 | 2 | 176 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1235 | 154537 | Beach Road, Tokomaru Bay | Seaside 0302 | 2025-02-19 07:10 | 2025-02-19 09:45 | 0.28568 | 0.0018431 | 48 | 7440 | Unplanned | Wildlife | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1236 | 30069 | Wainui Rd / Wheatstone Road | Tamarau 0503 | 2025-02-19 08:32 | 2025-02-19 14:12 | 1.1666 | 0.040587 | 1057 | 30382 | Unplanned | Third Party Interference | Digger came in contact with the OH lind @ Pole A4287 & LV line touched HV. Broken LV X-Arm, LV line down and TX A59 failed (faulty) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1237 | 3512 | Jacob Lane | Nelson 0803 | 2025-02-19 08:39 | 2025-02-19 16:18 | 0.12337 | 0.00026879 | 7 | 1606.9318 | Planned | Planned | Replace TX C646 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1238 | 3514 | Pa Road | Dalton 0502 | 2025-02-19 09:08 | 2025-02-19 13:04 | 0.16311 | 0.00069116 | 18 | 2125.8661 | Planned | Planned | Replace/Relocate 400V pole mtce TX A123 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1239 | 30035 | 92 Lavenham Road | Lavenham 0902 | 2025-02-20 08:24 | 2025-02-20 11:17 | 0.039857 | 0.00023039 | 6 | 1038 | Unplanned | Third Party Interference | Car V's Pole - @ Pole D2011 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1240 | 3511 | Waikura Road | Hicks Bay 0102 | 2025-02-20 08:33 | 2025-02-20 13:28 | 0.44177 | 0.0014975 | 39 | 5762.1366 | Planned | Planned | Replace pole J4219 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1241 | 30074 | Waitahaia Rd / Mata Rd | Mata 0304 | 2025-02-20 08:47 | 2025-02-20 12:43 | 0.18923 | 0.00080636 | 21 | 4928 | Unplanned | Defective Equipment | Broken insulator at pole H4496 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1242 | 3502 A | Lake Road | Frasertown 3103 | 2025-02-20 09:00 | 2025-02-20 09:03 | 0.0018431 | 0.00061437 | 16 | 24.0147 | Planned | Planned | Replace ABS W982 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1243 | 3502 | Lake Road | Frasertown 3103 | 2025-02-20 09:00 | 2025-02-20 14:35 | 1.3362 | 0.0040702 | 106 | 17431.936 | Planned | Planned | Replace ABS W982 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1244 | 155298 | 497 Ormond Valley Road | Waimata 0903 | 2025-02-20 11:13 | 2025-02-20 13:40 | 0.19191 | 0.0013055 | 34 | 4998 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1245 | 155433 | 298 Ormond Valley Road | Waimata 0903 | 2025-02-20 14:43 | 2025-02-20 15:40 | 0.0021887 | 3.8398e-05 | 1 | 57 | Unplanned | Unknown cause | Replace fus | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1246 | 3510 A | Waikura Valley Road | Hicks Bay 0102 | 2025-02-21 08:33 | 2025-02-21 12:32 | 0.35791 | 0.0014975 | 39 | 9321 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1247 | 156158 | 2317 Kanakania Road | Kanakanaia 1202 | 2025-02-21 16:22 | 2025-02-21 19:30 | 0.0072188 | 3.8398e-05 | 1 | 188 | Unplanned | Vegetation | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1248 | 30078 | Mahia Penensular | Mahia 3301 | 2025-02-22 01:58 | 2025-02-22 11:35 | 3.5951 | 0.016242 | 423 | 93627 | Unplanned | Defective Equipment | Cracked glass insulator burnt arm, pulled through | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1249 | 3513 | Taumata Road | Tahora 1103 | 2025-02-22 08:33 | 2025-02-22 14:35 | 0.097301 | 0.00026879 | 7 | 1267.3669 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1250 | 157604 | 209 Browns Beach Road | Muriwai 0905 | 2025-02-23 11:39 | 2025-02-23 13:00 | 0.018661 | 0.00023039 | 6 | 486 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1251 | 3518 | Tapuaeroa Road | Tiki Tiki 0206 | 2025-02-24 09:04 | 2025-02-24 14:59 | 0.2181 | 0.00061437 | 16 | 2841.7448 | Planned | Planned | Cut trees | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1252 | 3516 | Waihi Road | Frasertown 3103 | 2025-02-25 09:03 | 2025-02-25 14:44 | 0.14403 | 0.00042238 | 11 | 1876.2922 | Planned | Planned | Replace 11kV pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1253 | 3523 | Te Araroa | Awatere 0101 | 2025-02-25 09:04 | 2025-02-25 13:24 | 0.099835 | 0.00038398 | 10 | 1300.6336 | Planned | Planned | Change 50kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1254 | N/A 75 | Wharerata Road | Muriwai 0905 | 2025-02-25 10:10 | 2025-02-25 11:06 | 0.25343 | 0.0051453 | 134 | 6600 | Unplanned | Human Error | Cut tree branch, contacted HV conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1255 | N/A 72 | Tolaga Sub | Rototahi 0403 | 2025-02-25 12:29 | 2025-02-25 12:39 | 0.061821 | 0.0061821 | 161 | 1610 | Unplanned | Wildlife | Flock of Canadian goose birds located in the area | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1256 | N/A 72 | Tolaga Sub | Town 0402 | 2025-02-25 12:29 | 2025-02-25 12:45 | 0.12595 | 0.0078716 | 205 | 3280 | Unplanned | Wildlife | Flock of Canadian goose birds located in the area | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1257 | N/A 72 | Tolaga Sub | Toko Tie 0401 | 2025-02-25 12:29 | 2025-02-25 12:47 | 0.058058 | 0.0032254 | 84 | 1512 | Unplanned | Wildlife | Flock of Canadian goose birds located in the area | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1258 | N/A 72 | Tolaga Sub | Tauwhareparae 0404 | 2025-02-25 12:29 | 2025-02-25 12:47 | 0.10091 | 0.0056061 | 146 | 2628 | Unplanned | Wildlife | Flock of Canadian goose birds located in the area | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1259 | 158959 | 75 Maraehara Road | Tiki Tiki 0206 | 2025-02-25 14:31 | 2025-02-25 17:00 | 0.0057213 | 3.8398e-05 | 1 | 149 | Unplanned | Wildlife | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1260 | 159055 | 171 Pauakiri Road | Mata 0304 | 2025-02-25 17:18 | 2025-02-25 18:40 | 0.012595 | 0.00015359 | 4 | 328 | Unplanned | Wildlife | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1261 | 159702 | 1584 Mangapoike Road | Frasertown 3103 | 2025-02-26 17:29 | 2025-02-26 19:00 | 0.0069884 | 7.6796e-05 | 2 | 182 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1262 | 159673 | 48 Mangamaia Road | Whatatutu 1201 | 2025-02-26 17:29 | 2025-02-26 19:45 | 0.13055 | 0.00095995 | 25 | 3400 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1263 | 160078 | 187 Berry Road | Tiniroto 1003 | 2025-02-27 08:33 | 2025-02-27 11:30 | 0.09515 | 0.00053757 | 14 | 2478 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1264 | 3522 | Lake Road | Frasertown 3103 | 2025-02-27 09:02 | 2025-02-27 17:01 | 1.8393 | 0.0038398 | 100 | 20980.2519 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1265 | 30045 | Mangamaia Road | Whatatutu 1201 | 2025-02-27 11:24 | 2025-02-27 12:08 | 0.042238 | 0.00095995 | 25 | 1100 | Unplanned | Defective Equipment | Replaced insulator @ pole E2162 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1266 | 3524 | Stanley Road | Lytton 0701 | 2025-02-27 17:30 | 2025-02-27 22:02 | 0.38644 | 0.0014207 | 37 | 5040.6735 | Planned | Planned | Replace GM TX | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1267 | 3521 A | Tauwhareparae Rd | Rototahi 0403 | 2025-02-28 08:30 | 2025-02-28 17:01 | 2.4919 | 0.0048766 | 127 | 30628.6373 | Planned | Planned | Isolate to remove roof | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1268 | 3526 | Riverside / Goodwin Rd | Whangara 0506 | 2025-02-28 08:31 | 2025-02-28 16:30 | 0.9932 | 0.0020735 | 54 | 12959.8165 | Planned | Planned | Replace HV pole and install prop pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1269 | 3525 A | Te Araroa Road | Awatere 0101 | 2025-02-28 09:04 | 2025-02-28 14:55 | 0.053911 | 0.00015359 | 4 | 702.1078 | Planned | Planned | Replace 50kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1270 | 30049 | Managapa / Balance Village / Whataupoko | Aberdeen 0609 | 2025-02-28 09:49 | 2025-02-28 10:29 | 1.531 | 0.096417 | 2511 | 39872 | Unplanned | Defective Equipment | HV cable failed btwn RMU B6212 - RMU B344 & switching error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1271 | 3525 | Te Araroa Road | Awatere 0101 | 2025-02-28 16:31 | 2025-02-28 16:32 | 0.018162 | 0.018162 | 473 | 240.7954 | Planned | Planned | Replace 50kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1272 | 3517 | Waiapu Road | Makarika 0204 | 2025-03-01 09:00 | 2025-03-01 12:19 | 0.51131 | 0.0026111 | 68 | 6666.7145 | Planned | Planned | Cut Trees | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1273 | 3528 | Wainui Road | Dalton 0502 | 2025-03-03 09:13 | 2025-03-03 11:44 | 0.39427 | 0.0026111 | 68 | 5147.4052 | Planned | Planned | Cut-out sample lengths of O/Head conductor for assessment. Change cross arm @ pole A2114 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1274 | 162864 | Browns Beach Road | Muriwai 0905 | 2025-03-03 11:56 | 2025-03-03 14:56 | 0.013823 | 7.6796e-05 | 2 | 360 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1275 | 3529 | SH35 Okitu & Makarori | Dalton 0502 | 2025-03-03 13:32 | 2025-03-03 15:32 | 0.31333 | 0.0026111 | 68 | 4090.6532 | Planned | Planned | Cut & replace small section of HV conductor for testing | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1276 | 3527 | Totangi Road | Totangi 1101 | 2025-03-04 08:02 | 2025-03-04 16:46 | 0.41174 | 0.00080636 | 21 | 5337.411 | Planned | Planned | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1277 | 30093 | Armstrong Road | Whatatutu 1201 | 2025-03-05 07:57 | 2025-03-05 12:32 | 0.13117 | 0.00092155 | 24 | 3416 | Unplanned | Defective Equipment | Replace broken staywire @ pole E3507 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1278 | 3531 | Ormond Valley Road | Waimata 0903 | 2025-03-05 09:36 | 2025-03-05 10:49 | 0.092501 | 0.0012671 | 33 | 892.129 | Planned | Planned | Replace HV stub pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1279 | N/A 74 | Tawhara Valley | Brickworks 3201 | 2025-03-05 12:44 | 2025-03-05 16:31 | 0.36877 | 0.0062205 | 162 | 9604 | Unplanned | Adverse Weather | Line clashing between W1138 & W1021 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1280 | N/A 73 | Tawhara Road | Brickworks 3201 | 2025-03-05 18:30 | 2025-03-05 19:04 | 0.19502 | 0.0062205 | 162 | 5079 | Unplanned | Adverse Weather | Line clash between W1138 & W1021 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1281 | 164342 | 39 Kiwi Road, Wairoa | Nuhaka 3203 | 2025-03-05 18:55 | 2025-03-05 21:05 | 0.014975 | 0.00011519 | 3 | 390 | Unplanned | Defective Equipment | Faulty lightning arestors | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1282 | 30107 | Tiniroto / Ruakaka Road | Tiniroto 1003 | 2025-03-05 23:18 | 2025-03-06 16:16 | 0.79046 | 0.0031486 | 82 | 20586 | Unplanned | Vegetation | 3 span HV down Poles D3536 - D310. Tree thru line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1283 | 30106 | Panikau Road | Dalton 0502 | 2025-03-06 04:23 | 2025-03-06 14:15 | 0.66713 | 0.0021503 | 56 | 17374 | Unplanned | Vegetation | Tree branch through HV lines byd HV fuses A168 at pole A3779 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1284 | 30152 | Waihua Valley Rd / Cricklewood Rd | Raupunga 3101 | 2025-03-06 11:03 | 2025-03-06 16:19 | 0.26694 | 0.00084476 | 22 | 6952 | Unplanned | Adverse Weather | Repair conductor after clash, high winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1285 | 30109 | Wairoa / Mahia Region | Mahia 3301 | 2025-03-06 13:04 | 2025-03-07 18:24 | 2.9773 | 0.11132 | 2899 | 77538 | Unplanned | Defective Equipment | Faulty Insulator Failed - Conductor on Arm Burnt Down Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1286 | 30109 | Wairoa / Mahia Region | Morere 3401 | 2025-03-06 13:04 | 2025-03-07 18:22 | 0.66598 | 0.020581 | 536 | 17344 | Unplanned | Defective Equipment | Faulty Insulator Failed - Conductor on Arm Burnt Down Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1287 | 165300 | 2753 Whangara Road | Rototahi 0403 | 2025-03-07 09:28 | 2025-03-07 11:02 | 0.0036094 | 3.8398e-05 | 1 | 94 | Unplanned | Adverse Weather | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1288 | 30109 | Wairoa / Mahia Region | Frasertown 3103 | 2025-03-07 17:59 | 2025-03-07 18:02 | 0.055408 | 0.018469 | 481 | 1443 | Unplanned | Defective Equipment | Faulty Insulator Failed - Conductor on Arm Burnt Down Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1289 | 30109 | Wairoa / Mahia Region | Brickworks 3201 | 2025-03-07 17:59 | 2025-03-07 18:02 | 0.07096 | 0.023653 | 616 | 1848 | Unplanned | Defective Equipment | Faulty Insulator Failed - Conductor on Arm Burnt Down Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1290 | 30109 | Wairoa / Mahia Region | Borough Two 3205 | 2025-03-07 17:59 | 2025-03-07 18:02 | 0.076374 | 0.025458 | 663 | 1989 | Unplanned | Defective Equipment | Faulty Insulator Failed - Conductor on Arm Burnt Down Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1291 | 30109 | Wairoa / Mahia Region | Borough One 3204 | 2025-03-07 17:59 | 2025-03-07 18:02 | 0.094344 | 0.031448 | 819 | 2457 | Unplanned | Defective Equipment | Faulty Insulator Failed - Conductor on Arm Burnt Down Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1292 | 30109 | Wairoa / Mahia Region | Affco 3202 | 2025-03-07 17:59 | 2025-03-07 18:22 | 0.032677 | 0.0014207 | 37 | 851 | Unplanned | Defective Equipment | Faulty Insulator Failed - Conductor on Arm Burnt Down Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1293 | 30109 | Wairoa / Mahia Region | Nuhaka 3203 | 2025-03-07 17:59 | 2025-03-07 18:21 | 0.16726 | 0.0076028 | 198 | 4356 | Unplanned | Defective Equipment | Faulty Insulator Failed - Conductor on Arm Burnt Down Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1294 | 30109 | Wairoa / Mahia Region | Kiwi Sub 32 | 2025-03-07 17:59 | 2025-03-07 18:27 | 0.0010751 | 3.8398e-05 | 1 | 28 | Unplanned | Defective Equipment | Faulty Insulator Failed - Conductor on Arm Burnt Down Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1295 | 30109 | Wairoa / Mahia Region | Raupunga 3101 | 2025-03-07 17:59 | 2025-03-07 18:11 | 0.19399 | 0.016166 | 421 | 5052 | Unplanned | Defective Equipment | Faulty Insulator Failed - Conductor on Arm Burnt Down Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1296 | 30109 | Wairoa / Mahia Region | Wairoa Sub 31 | 2025-03-07 17:59 | 2025-03-07 18:02 | 0.00023039 | 7.6796e-05 | 2 | 6 | Unplanned | Defective Equipment | Faulty Insulator Failed - Conductor on Arm Burnt Down Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1297 | 165674 | Whakaki | Nuhaka 3203 | 2025-03-07 19:15 | 2025-03-08 11:45 | 1.9387 | 0.0019583 | 51 | 50490 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1298 | 30110 | Moana Road | Dalton 0502 | 2025-03-08 05:59 | 2025-03-08 08:48 | 0.89552 | 0.0052989 | 138 | 23322 | Unplanned | Adverse Weather | ABS A2188 arcing across shackles - Salt Build Up | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1299 | 3554 | Nelson Road | Nelson 0803 | 2025-03-08 09:00 | 2025-03-08 17:41 | 0.020005 | 3.8398e-05 | 1 | 521 | Planned | Planned | Upgrade 400V fuse rack TX C325 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1300 | N/A 76 | SH2 Whakaki | Nuhaka 3203 | 2025-03-08 11:39 | 2025-03-08 11:45 | 0.0025343 | 0.00042238 | 11 | 66 | Unplanned | Defective Equipment | Blown 40a fuse - centre phase @ W8167 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1301 | 166888 | 180Monck Road | Waimata 0903 | 2025-03-09 09:45 | 2025-03-09 11:00 | 0.0028799 | 3.8398e-05 | 1 | 75 | Unplanned | Lightning | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1302 | 30113 | Waimata Valley Road | Waimata 0903 | 2025-03-09 10:09 | 2025-03-10 10:12 | 0.11082 | 7.6796e-05 | 2 | 2886 | Unplanned | Lightning | Faulty Transformer G188 caused by Lightning in the area | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1303 | 3550 | Waimoatatini | Tiki Tiki 0206 | 2025-03-10 09:00 | 2025-03-10 12:36 | 0.21564 | 0.00099835 | 26 | 5616 | Planned | Planned | Replace Switch J1048 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1304 | 3534 | Lucknow Street | Borough Two 3205 | 2025-03-10 09:32 | 2025-03-10 10:35 | 0.24433 | 0.0038782 | 101 | 3216.7529 | Planned | Planned | Replace X-arm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1305 | 167733 | 1400 Wharerata Road | Muriwai 0905 | 2025-03-10 12:26 | 2025-03-10 13:45 | 0.0030334 | 3.8398e-05 | 1 | 79 | Unplanned | Vegetation | Tree in lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1306 | N/A 77 | Whakaangiangi Road | Awatere 0101 | 2025-03-11 01:15 | 2025-03-11 08:29 | 0.51503 | 0.0012287 | 32 | 13413 | Unplanned | Wildlife | Possum on Pole J2997 - Centre phase | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1307 | 3563 | Renner Road | Lavenham 0902 | 2025-03-11 08:51 | 2025-03-12 16:48 | 1.1777 | 0.00061437 | 16 | 30672 | Planned | Planned | Problem with pole, left off overnight, fixed next day | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1308 | 3536 | Mahia | Mahia 3301 | 2025-03-11 09:00 | 2025-03-11 11:11 | 1.8762 | 0.014322 | 373 | 48863 | Unplanned | Human Error | Shutdown cancelled as customer notification failed due to alternative date 12/2/25 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1309 | 168534 | 202 Otoi Road | Raupunga 3101 | 2025-03-11 16:40 | 2025-03-11 18:00 | 0.0030718 | 3.8398e-05 | 1 | 80 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1310 | N/A 78 | 50kV Ring | Patutahi Sub 09 | 2025-03-11 23:17 | 2025-03-11 23:56 | 0.0014975 | 3.8398e-05 | 1 | 39 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1311 | N/A 78 | 50kV Ring | Lavenham 0902 | 2025-03-11 23:17 | 2025-03-11 23:56 | 0.67239 | 0.017241 | 449 | 17511 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1312 | N/A 78 | 50kV Ring | Waimata 0903 | 2025-03-11 23:17 | 2025-03-11 23:56 | 0.97189 | 0.02492 | 649 | 25311 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1313 | N/A 78 | 50kV Ring | Muriwai 0905 | 2025-03-11 23:17 | 2025-03-11 23:56 | 0.61848 | 0.015858 | 413 | 16107 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1314 | N/A 78 | 50kV Ring | Te Arai 0906 | 2025-03-11 23:17 | 2025-03-11 23:56 | 0.35042 | 0.0089851 | 234 | 9126 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1315 | N/A 78 | 50kV Ring | Pehiri Sub 10 | 2025-03-11 23:17 | 2025-03-11 23:56 | 0.0014975 | 3.8398e-05 | 1 | 39 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1316 | N/A 78 | 50kV Ring | W O Kuri 1001 | 2025-03-11 23:17 | 2025-03-11 23:56 | 0.070384 | 0.0018047 | 47 | 1833 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1317 | N/A 78 | 50kV Ring | Parikanapa 1002 | 2025-03-11 23:17 | 2025-03-11 23:56 | 0.044926 | 0.0011519 | 30 | 1170 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1318 | N/A 78 | 50kV Ring | Tiniroto 1003 | 2025-03-11 23:17 | 2025-03-11 23:56 | 0.18719 | 0.0047998 | 125 | 4875 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1319 | N/A 78 | 50kV Ring | Tahunga 1004 | 2025-03-11 23:17 | 2025-03-11 23:56 | 0.073379 | 0.0018815 | 49 | 1911 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1320 | N/A 78 | 50kV Ring | Ngatapa Sub 11 | 2025-03-11 23:17 | 2025-03-11 23:56 | 0.0014975 | 3.8398e-05 | 1 | 39 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1321 | N/A 78 | 50kV Ring | Totangi 1101 | 2025-03-11 23:17 | 2025-03-11 23:56 | 0.020965 | 0.00053757 | 14 | 546 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1322 | N/A 78 | 50kV Ring | Ngatapa 1102 | 2025-03-11 23:17 | 2025-03-11 23:56 | 0.10483 | 0.0026879 | 70 | 2730 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1323 | N/A 78 | 50kV Ring | Tahora 1103 | 2025-03-11 23:17 | 2025-03-11 23:56 | 0.22613 | 0.0057981 | 151 | 5889 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1324 | N/A 78 | 50kV Ring | Puha Sub 12 | 2025-03-11 23:17 | 2025-03-12 00:02 | 0.0017279 | 3.8398e-05 | 1 | 45 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1325 | N/A 78 | 50kV Ring | Whatatutu 1201 | 2025-03-11 23:17 | 2025-03-12 00:02 | 0.42161 | 0.0093691 | 244 | 10980 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1326 | N/A 78 | 50kV Ring | Kanakanaia 1202 | 2025-03-11 23:17 | 2025-03-12 00:02 | 0.3093 | 0.0068732 | 179 | 8055 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1327 | N/A 78 | 50kV Ring | Te Karaka 1203 | 2025-03-11 23:17 | 2025-03-12 00:02 | 0.31448 | 0.0069884 | 182 | 8190 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1328 | N/A 78 | 50kV Ring | Matawai 1204 | 2025-03-11 23:17 | 2025-03-12 00:02 | 0.66525 | 0.014783 | 385 | 17325 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1329 | N/A 78 | 50kV Ring | Dunstan 1403 | 2025-03-11 23:17 | 2025-03-12 | 0.018162 | 0.00042238 | 11 | 473 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1330 | N/A 78 | 50kV Ring | JNL_A 1405 | 2025-03-11 23:17 | 2025-03-12 | 0.033022 | 0.00076796 | 20 | 860 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1331 | N/A 78 | 50kV Ring | Bell 1406 | 2025-03-11 23:17 | 2025-03-12 | 0.39131 | 0.0091003 | 237 | 10191 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1332 | N/A 78 | 50kV Ring | Waipaoa 1408 | 2025-03-11 23:17 | 2025-03-12 | 0.0099067 | 0.00023039 | 6 | 258 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1333 | 3506 A | Tokomaru Bay Sub | Ruatoria Sub 02 | 2025-03-12 16:17 | 2025-03-12 16:18 | 3.8398e-05 | 3.8398e-05 | 1 | 0.50002 | Planned | Planned | 50Kv S/Gear maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1334 | 3506 A | Tokomaru Bay Sub | Ruatoria 0201 | 2025-03-12 16:17 | 2025-03-12 16:18 | 0.011903 | 0.011903 | 310 | 156.845 | Planned | Planned | 50Kv S/Gear maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1335 | 3506 A | Tokomaru Bay Sub | Makarika 0204 | 2025-03-12 16:17 | 2025-03-12 16:18 | 0.004339 | 0.004339 | 113 | 56.7452 | Planned | Planned | 50Kv S/Gear maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1336 | 3506 A | Tokomaru Bay Sub | Tiki Tiki 0206 | 2025-03-12 16:17 | 2025-03-12 16:18 | 0.012134 | 0.012134 | 316 | 159.9171 | Planned | Planned | 50Kv S/Gear maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1337 | 3506 A | Tokomaru Bay Sub | Tokomaru Bay Sub 03 | 2025-03-12 16:17 | 2025-03-12 16:18 | 7.6796e-05 | 7.6796e-05 | 2 | 1.0001 | Planned | Planned | 50Kv S/Gear maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1338 | 3506 A | Tokomaru Bay Sub | Inland 0301 | 2025-03-12 16:17 | 2025-03-12 16:18 | 0.0061437 | 0.0061437 | 160 | 80.4915 | Planned | Planned | 50Kv S/Gear maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1339 | 3506 A | Tokomaru Bay Sub | Seaside 0302 | 2025-03-12 16:17 | 2025-03-12 16:18 | 0.004531 | 0.004531 | 118 | 59.2673 | Planned | Planned | 50Kv S/Gear maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1340 | 3506 | Tokomaru Bay Sub | Te Araroa Sub 01 | 2025-03-12 16:30 | 2025-03-12 16:31 | 3.8398e-05 | 3.8398e-05 | 1 | 0.50002 | Planned | Planned | 50Kv S/Gear maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1341 | 3506 | Tokomaru Bay Sub | Awatere 0101 | 2025-03-12 16:30 | 2025-03-12 16:31 | 0.0033022 | 0.0033022 | 86 | 43.142 | Planned | Planned | 50Kv S/Gear maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1342 | 3506 | Tokomaru Bay Sub | Hicks Bay 0102 | 2025-03-12 16:30 | 2025-03-12 16:31 | 0.0098299 | 0.0098299 | 256 | 129.2582 | Planned | Planned | 50Kv S/Gear maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1343 | 3506 | Tokomaru Bay Sub | Te Araroa 0103 | 2025-03-12 16:30 | 2025-03-12 16:31 | 0.0049533 | 0.0049533 | 129 | 64.8195 | Planned | Planned | 50Kv S/Gear maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1344 | 3553 | Tawhara Valley | Brickworks 3201 | 2025-03-13 09:01 | 2025-03-13 16:11 | 0.31371 | 0.00072956 | 19 | 8170 | Planned | Planned | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1345 | 3505 | Tokomaru Bay Sub | Te Araroa Sub 01 | 2025-03-13 16:30 | 2025-03-13 16:31 | 3.8398e-05 | 3.8398e-05 | 1 | 0.50002 | Planned | Planned | Stitch MTC | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1346 | 3505 | Tokomaru Bay Sub | Awatere 0101 | 2025-03-13 16:30 | 2025-03-13 16:31 | 0.0034942 | 0.0034942 | 91 | 45.659 | Planned | Planned | Stitch MTC | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1347 | 3505 | Tokomaru Bay Sub | Hicks Bay 0102 | 2025-03-13 16:30 | 2025-03-13 16:31 | 0.0098299 | 0.0098299 | 256 | 129.2582 | Planned | Planned | Stitch MTC | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1348 | 3505 | Tokomaru Bay Sub | Te Araroa 0103 | 2025-03-13 16:30 | 2025-03-13 16:31 | 0.0049533 | 0.0049533 | 129 | 64.8195 | Planned | Planned | Stitch MTC | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1349 | 30157 | Te Araroa Road | Awatere 0101 | 2025-03-13 16:47 | 2025-03-14 14:14 | 0.015359 | 0.00030718 | 8 | 400 | Unplanned | Adverse Environment | Pole J2437A - In Slip Zone. Conductors down to 1mt above ground. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1350 | N/A 79 | Mahia | Mahia 3301 | 2025-03-15 14:15 | 2025-03-15 19:04 | 7.5869 | 0.030987 | 807 | 197586 | Unplanned | Third Party Interference | Isolate power lines for a large fire in Mahia | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1351 | 30615 | Queen St / Paul St | Borough Two 3205 | 2025-03-17 13:36 | 2025-03-17 15:17 | 0.073686 | 0.00072956 | 19 | 1919 | Unplanned | Defective Equipment | 11kV cable btwn W255 - W1557 (tx) failed. Backfed through LV | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1352 | 173027 | 1435 Waingake Road | Te Arai 0906 | 2025-03-18 08:54 | 2025-03-18 10:15 | 0.0031102 | 3.8398e-05 | 1 | 81 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1353 | 3539 | Clifton & Lyall Road | Frasertown 3103 | 2025-03-18 09:03 | 2025-03-18 16:15 | 0.87417 | 0.0020351 | 53 | 11399.14 | Planned | Planned | To replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1354 | N/A 81 | Tiniroto Road | W O Kuri 1001 | 2025-03-19 03:01 | 2025-03-19 05:39 | 0.28272 | 0.0018047 | 47 | 7363 | Unplanned | Unknown cause | W-O-Kuri feeder tripped. Restored via Panikauapa feeder. Cause unknown. MCB Tripped on CB which prevented the spring recharge | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1355 | N/A 80 | Waimata | Waimata 0903 | 2025-03-19 05:20 | 2025-03-19 07:00 | 1.1581 | 0.02492 | 649 | 30160 | Unplanned | Unknown cause | Waimata feeder tripped. Restored after sectionalisng. Cause unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1356 | 3541 | Kirkpatrick Road | Te Arai 0906 | 2025-03-19 10:00 | 2025-03-19 12:12 | 0.060822 | 0.00046078 | 12 | 720.3318 | Planned | Planned | Install TX fuses C2817 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1357 | N/A 82 | Tolaga, Toko | Toko Tie 0401 | 2025-03-19 10:47 | 2025-03-19 11:03 | 0.11112 | 0.016703 | 435 | 2894 | Unplanned | Unknown cause | E/F thru G326 (Tokotie) tripped. Gen 5 CB 1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1358 | 3540 | Clifton & Lyall Road | Frasertown 3103 | 2025-03-20 09:00 | 2025-03-20 14:49 | 0.70372 | 0.0020351 | 53 | 9176.5266 | Planned | Planned | Pole replacements - See Waihua fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1359 | 3556 | Raupunga Road | Raupunga 3101 | 2025-03-20 09:21 | 2025-03-20 11:47 | 0.022424 | 0.00015359 | 4 | 292.0922 | Planned | Planned | To connect new lines to new TX W22784 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1360 | 30143 | Waihua | Raupunga 3101 | 2025-03-20 10:52 | 2025-03-21 21:35 | 5.6334 | 0.025228 | 657 | 146711 | Unplanned | Vegetation | Forestry Block tree through line W1159 - W6359 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1361 | N/A 83 | Kaiti, Whataupoko | Whangara 0506 | 2025-03-20 11:16 | 2025-03-20 12:50 | 1.1848 | 0.022616 | 589 | 30855 | Unplanned | Unknown cause | Inst O/C CB A472 - Line patrolled - No ovious cause of fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1362 | 174564 | 330 Sheltons Road | Rototahi 0403 | 2025-03-20 16:24 | 2025-03-20 17:12 | 0.02949 | 0.00061437 | 16 | 768 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1363 | 30145 | Ihungia Road | Mata 0304 | 2025-03-21 00:51 | 2025-03-21 13:31 | 0.29371 | 0.00061437 | 16 | 7649 | Unplanned | Vegetation | Tree through HV lines at pole H650 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1364 | N/A 84 | Thomas Rd | Rototahi 0403 | 2025-03-21 06:55 | 2025-03-21 08:37 | 0.01175 | 0.00011519 | 3 | 306 | Unplanned | Vegetation | Tree branch on HV btwn Pole A858 - A859 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1365 | 174195 | 63 Thomas Road | Rototahi 0403 | 2025-03-21 06:55 | 2025-03-21 08:55 | 0.013823 | 0.00011519 | 3 | 360 | Unplanned | Vegetation | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1366 | 174979 | 209 Browns Beach Road | Muriwai 0905 | 2025-03-21 08:31 | 2025-03-21 10:30 | 0.027416 | 0.00023039 | 6 | 714 | Unplanned | Wildlife | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1367 | 175570 | 165 Glendening Road | Raupunga 3101 | 2025-03-22 08:56 | 2025-03-22 10:30 | 0.0072188 | 7.6796e-05 | 2 | 188 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1368 | 176948 | 124 Iwitea Road | Nuhaka 3203 | 2025-03-24 07:34 | 2025-03-24 09:10 | 0.062666 | 0.00065277 | 17 | 1632 | Unplanned | Wildlife | Replace fuses - Possible bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1369 | 177016 | Berry Road, Tiniroto | Tiniroto 1003 | 2025-03-24 09:51 | 2025-03-24 12:30 | 0.085474 | 0.00053757 | 14 | 2226 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1370 | 3543 | Ahirau Road | Te Karaka 1203 | 2025-03-24 11:01 | 2025-03-24 12:17 | 0.029183 | 0.00038398 | 10 | 380.1459 | Planned | Planned | Install HV fuses TX E1824 (TX not installed) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1371 | 177060 | 89 Walker Road | Ruatoria 0201 | 2025-03-24 12:21 | 2025-03-24 14:30 | 0.0049533 | 3.8398e-05 | 1 | 129 | Unplanned | Wildlife | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1372 | 3547 | Te Araroa Road | Awatere 0101 | 2025-03-25 09:01 | 2025-03-25 16:04 | 0.58473 | 0.0013823 | 36 | 7624.5251 | Planned | Planned | Replace 50kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1373 | 3565 | Tauwhareparae Rd | Tauwhareparae 0404 | 2025-03-25 09:02 | 2025-03-25 13:57 | 0.57678 | 0.0019583 | 51 | 7523.3153 | Planned | Planned | Install Recloser | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1374 | 3581 | Mangahaurini Gorge | Inland 0301 | 2025-03-25 11:07 | 2025-03-25 13:41 | 0.0059133 | 3.8398e-05 | 1 | 154 | Planned | Planned | Urgent Shutdown - To Remove at risk tree @ pole H2408 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1375 | 3547 A | Te Araroa Road | Awatere 0101 | 2025-03-25 16:30 | 2025-03-25 16:31 | 0.018162 | 0.018162 | 473 | 473 | Planned | Planned | Replace 50kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1376 | 3546 | Wharekopare Road | Tahora 1103 | 2025-03-26 08:32 | 2025-03-26 16:44 | 1.0957 | 0.0022271 | 58 | 14299.7761 | Planned | Planned | Replace HV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1377 | 3548 | Bushmere Road | Bushmere 0805 | 2025-03-26 09:01 | 2025-03-26 14:14 | 0.55285 | 0.0017663 | 46 | 7211.7157 | Planned | Planned | Replace ABS D399 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1378 | 3566 | Tauwhareparae Rd | Tauwhareparae 0404 | 2025-03-27 09:00 | 2025-03-27 16:58 | 0.92282 | 0.0019583 | 51 | 11486.3437 | Planned | Planned | Install new SW/GR | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1379 | 179128 | 35 Nicks Head Road | Muriwai 0905 | 2025-03-28 07:50 | 2025-03-28 09:24 | 0.0036094 | 3.8398e-05 | 1 | 94 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1380 | 3551 | Wharekopae Road | Tahora 1103 | 2025-03-28 08:30 | 2025-03-28 16:42 | 1.0957 | 0.0022271 | 58 | 14299.7761 | Planned | Planned | Replace 11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1381 | 3567 | Aberdeen Road | Gladstone 0607 | 2025-03-28 08:35 | 2025-03-28 13:08 | 1.7611 | 0.0064509 | 168 | 23079.9313 | Planned | Planned | Tree cutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1382 | 3561 | Waiapu Road | Mata 0304 | 2025-03-28 08:44 | 2025-03-28 14:14 | 0.063357 | 0.00019199 | 5 | 825.2016 | Planned | Planned | 11kV deenergised only for 50kV pole change | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Wairoa | 1383 | 179169 | Kiwi Road | Affco 3202 | 2025-03-28 10:06 | 2025-03-28 10:40 | 0.0013055 | 3.8398e-05 | 1 | 34 | Unplanned | Unknown cause | Replace fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1384 | 179209 | 904 Poroporo Road | Tiki Tiki 0206 | 2025-03-28 10:52 | 2025-03-28 13:00 | 0.063894 | 0.00049917 | 13 | 1664 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1385 | 179241 | 211 Gordon Road | Te Arai 0906 | 2025-03-28 12:49 | 2025-03-28 14:00 | 0.032715 | 0.00046078 | 12 | 852 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1386 | 30188 | Watson Park | Willows 0702 | 2025-03-28 12:50 | 2025-03-28 13:27 | 0.0014207 | 3.8398e-05 | 1 | 37 | Unplanned | Defective Equipment | Blown HV jumpers at TX HV Fuses B1965 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1387 | 180613 | 416 Waiomatatini Road | Tiki Tiki 0206 | 2025-03-30 08:20 | 2025-03-30 09:50 | 0.0034558 | 3.8398e-05 | 1 | 90 | Unplanned | Unknown cause | Replace fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1388 | 30190 | Waimata Valley Rd / Kawatiri Road | Waimata 0903 | 2025-03-31 05:58 | 2025-03-31 08:41 | 1.3897 | 0.02492 | 649 | 36193 | Unplanned | Defective Equipment | Broken HV conductor between Pole D1423 - D1424. Pin loose tripped over flashover to top of pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1389 | 3552 | Wharekopae Road | Tahora 1103 | 2025-03-31 08:30 | 2025-03-31 15:36 | 0.94874 | 0.0022271 | 58 | 12381.5134 | Planned | Planned | Replace poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Firstlight Network | 2025 | Gisborne | 1390 | 30199 | Paparatu Road | Te Arai 0906 | 2025-03-31 16:52 | 2025-03-31 20:07 | 0.10629 | 0.00061437 | 16 | 2768 | Unplanned | Defective Equipment | Burnt HV pole C863. Insulator failed, tracked thru arm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 9 | 8556 | OHOPE | HARBOUR | 2024-04-03 08:45 | 2024-04-03 15:15 | 0.64195 | 0.019001 | 270 | 16690 | Planned | Planned interruption | Tree works Maraetotara Road Wainui Road and Burma Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 10 | 8547 | WAIOTAHI | OPOTIKI | 2024-04-04 09:50 | 2024-04-04 13:58 | 0.11447 | 0.0004616 | 12 | 2976 | Planned | Planned interruption | TREE WORKS PAERATA RIDGE ROAD. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 11 | 8561 | OHOPE | HARBOUR | 2024-04-05 09:04 | 2024-04-05 12:39 | 0.20674 | 0.0009616 | 25 | 5375 | Planned | Planned interruption | PAPAROA ROAD DEFECTS. Manual to less 2hours | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 12 | 8564 | PLAINS | TE TEKO | 2024-04-05 09:01 | 2024-04-05 10:44 | 0.04358 | 0.0004231 | 11 | 1133 | Planned | Planned interruption | TREE WORKS - MOODY ROAD. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 13 | 8577 | KAWERAU | KEA FEEDER | 2024-04-11 09:00 | 2024-04-11 15:29 | 0.10473 | 0.0002692 | 7 | 2723 | Planned | Planned interruption | OVER HEAD TO UNDERGROUND Te Kore Drive alignment. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 14 | 8502B | PLAINS | WESTBANK | 2024-04-16 10:00 | 2024-04-16 14:16 | 0.16739 | 0.0006539 | 17 | 4352 | Planned | Planned interruption | Low HV Line Remediation. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 15 | 8557 | OHOPE | HARBOUR | 2024-04-16 08:45 | 2024-04-16 13:56 | 0.96965 | 0.013 | 211 | 25210 | Planned | Planned interruption | Tree work Wainui and McCoy Roads. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 16 | 8579 | EAST BANK | THORNTON | 2024-04-16 09:01 | 2024-04-16 13:17 | 0.54156 | 0.0021155 | 55 | 14080 | Planned | Planned interruption | Replace Crossarms Thornton Beach Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 17 | 8580 | STATION RD | PIRIPAI | 2024-04-16 09:30 | 2024-04-16 11:59 | 0.03439 | 0.0002308 | 6 | 894 | Planned | Planned interruption | Paroa school transformer and pillar works. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 18 | 8562A | STATION RD | MOKOROA | 2024-04-17 09:01 | 2024-04-17 14:51 | 0.06731 | 0.0001923 | 5 | 1750 | Planned | Planned interruption | Tree Works Mokorua Reserve. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 19 | 8562B | STATION RD | MOKOROA | 2024-04-18 09:01 | 2024-04-18 14:56 | 0.06827 | 0.0001923 | 5 | 1775 | Planned | Planned interruption | Tree Works Mokorua Reserve | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 20 | 8591 | WAIOTAHI | HOSPITAL | 2024-04-16 09:00 | 2024-04-16 15:42 | 0.12562 | 0.0003462 | 9 | 3266 | Planned | Planned interruption | Replace Pole and transformer Upgrade, Re -letter dropped 9 ICP.apoligies given to other notified and advised of outage not affetcting them | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 21 | 8599 | PLAINS | AWAKERI | 2024-04-18 09:01 | 2024-04-18 14:35 | 0.3944 | 0.0011924 | 31 | 10254 | Planned | Planned interruption | Awakeri Lines Project Shut 1 Contractor advertised. V11 also sent | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 22 | 8584 | KAWERAU | PLATEAU | 2024-04-19 09:00 | 2024-04-19 14:07 | 0.08266 | 0.0002692 | 7 | 2149 | Planned | Planned interruption | Replace ABS 670 with Sectos, Rmove ABS 1137 and Remove CB 1150 & Maintenance on RMC 230 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 23 | 8581 | TE KAHA | TE KAHA | 2024-04-19 10:00 | 2024-04-19 13:45 | 1.5837 | 0.0070387 | 183 | 41175 | Planned | Planned interruption | Remove ABS 971 & Install Sectos & Vegetation Work | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 24 | 8573 | GALATEA | MINGINUI | 2024-04-22 10:35 | 2024-04-22 12:51 | 0.61725 | 0.0045386 | 118 | 16048 | Planned | Planned interruption | Tree Works Ruatahuna Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 25 | 8582 | PLAINS | TE TEKO | 2024-04-23 09:03 | 2024-04-23 14:13 | 0.41732 | 0.0013462 | 35 | 10850 | Planned | Planned interruption | New TX Install Matahina. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 26 | 8583 | PLAINS | MANAWAHE | 2024-04-23 09:45 | 2024-04-23 14:27 | 0.8885 | 0.019155 | 283 | 23100 | Planned | Planned interruption | Manawahe Feeder low lines project. Manual calc required Complex. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 27 | 8585 | WAIOTAHI | OTARA | 2024-04-24 09:02 | 2024-04-24 14:53 | 1.7686 | 0.0050387 | 131 | 45981 | Planned | Planned interruption | Change ABS to Sectos 3422 / Links 3424. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 28 | 8560 | KAWERAU | PLATEAU | 2024-05-02 10:01 | 2024-05-02 13:18 | 0.00758 | 3.85e-05 | 1 | 197 | Planned | Planned interruption | Tree works Onepu Road Kawerau. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 29 | 8574 | STATION RD | RUATOKI | 2024-05-07 09:01 | 2024-05-07 15:06 | 0.19655 | 0.0005385 | 14 | 5110 | Planned | Planned interruption | Vegetation Control at 540 Wite Pine Bush Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 30 | 8575 | OHOPE | HARBOUR | 2024-04-30 09:00 | 2024-04-30 12:22 | 0.29524 | 0.0014616 | 38 | 7676 | Planned | Planned interruption | Vegetation Control Harbour Road Ohope. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 31 | 8576 | WAIOTAHI | COAST | 2024-05-08 10:01 | 2024-05-08 13:40 | 0.23586 | 0.001077 | 28 | 6132 | Planned | Planned interruption | Vegetation Control Hawai. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 32 | 8586 | KAWERAU | ONEPU | 2024-05-01 09:06 | 2024-05-01 13:42 | 1.23 | 0.0045387 | 118 | 31979 | Planned | Planned interruption | Replace ABS 67 with Sectos 3442 / Links 3444. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 33 | 8589 | GALATEA | MINGINUI | 2024-05-02 09:00 | 2024-05-02 14:15 | 0.36348 | 0.0011539 | 30 | 9450 | Planned | Planned interruption | Whirinaki Road Defects. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 34 | 8592 | GALATEA | GALATEA | 2024-04-30 09:00 | 2024-04-30 13:08 | 0.08585 | 0.0003462 | 9 | 2232 | Planned | Planned interruption | 33kV & 11kV Crossarm replacements Galaea. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 35 | 8596 | GALATEA | MINGINUI | 2024-05-01 10:08 | 2024-05-01 13:35 | 0.03185 | 0.0001539 | 4 | 828 | Planned | Planned interruption | Tree Works Minginui Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 36 | 8597 | OHOPE | HARBOUR | 2024-05-03 09:07 | 2024-05-03 15:09 | 0.34809 | 0.0009616 | 25 | 9050 | Planned | Planned interruption | Paparoa Road Defects Stage 2. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 37 | 8598 | STATION RD | MOKOROA | 2024-05-08 09:04 | 2024-05-08 12:50 | 0.52156 | 0.0023078 | 60 | 13560 | Planned | Planned interruption | Tree Works Burma Road. ISO6042 open and backfed from McGarvey Feeder due to a fault. Advertised accordingly. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 38 | 8600 | KAINGAROA | DUNN ROAD | 2024-05-08 09:03 | 2024-05-08 13:23 | 1.8401 | 0.0070772 | 184 | 47840 | Planned | Planned interruption | Kaingaroa T1 & T2, RMC95 & 20A019 Maintenance. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 39 | 8601 | KAWERAU | KEA FEEDER | 2024-05-05 09:30 | 2024-05-05 11:24 | 0.00877 | 7.69e-05 | 2 | 228 | Planned | Planned interruption | Sequal Shut. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 40 | 8603 | PLAINS | AWAKERI | 2024-05-03 09:00 | 2024-05-03 13:46 | 0.82503 | 0.0028847 | 75 | 21450 | Planned | Planned interruption | Awakeri Lines FY25 Shut 2. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 41 | 8604 | STATION RD | RUATOKI | 2024-05-09 09:31 | 2024-05-09 12:56 | 1.1906 | 0.0058079 | 151 | 30955 | Planned | Planned interruption | Vegetation Works Ruatoki and Replace ABS 516 to Sectos 3542. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 42 | 8610 | EAST BANK | THORNTON | 2024-05-08 09:01 | 2024-05-08 13:35 | 0.30563 | 0.0011154 | 29 | 7946 | Planned | Planned interruption | McLean Road BOPRC Mandery. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 43 | 8615 | WAIOTAHI | WAIMANA | 2024-05-17 09:00 | 2024-05-17 14:25 | 1.025 | 0.003154 | 82 | 26650 | Planned | Planned interruption | Replace Poles and Install new gen Connection Point | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 44 | 8612 | WAIOTAHI | WAIMANA | 2024-05-14 10:02 | 2024-05-14 11:41 | 0.15993 | 0.0016154 | 42 | 4158 | Planned | Planned interruption | Install generation Point. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 45 | 8616 | WAIOTAHI | WAIMANA | 2024-05-23 09:01 | 2024-05-23 13:13 | 0.7948 | 0.003154 | 82 | 20664 | Planned | Planned interruption | Replace Poles beyond 3412. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 46 | 8629 | OHOPE | HARBOUR | 2024-05-30 09:31 | 2024-05-30 12:06 | 0.07154 | 0.0004616 | 12 | 1860 | Planned | Planned interruption | Tree Works McCoy Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 47 | 8636 | STATION RD | PIRIPAI | 2024-05-31 09:05 | 2024-05-31 13:47 | 0.71587 | 0.0025386 | 66 | 18612 | Planned | Planned interruption | Paeroa Road Defects. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 48 | 8618A | OHOPE | HARBOUR | 2024-05-29 09:01 | 2024-05-29 13:51 | 0.84522 | 0.013 | 211 | 21975 | Planned | Planned interruption | Tree Works Waimana and McCoy Roads. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 49 | 8627 | GALATEA | GALATEA | 2024-05-24 09:06 | 2024-05-24 13:01 | 0.18078 | 0.0007693 | 20 | 4700 | Planned | Planned interruption | Crossarm replacements. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 50 | 8656 | WAIOTAHI | OPOTIKI | 2024-06-01 10:13 | 2024-06-01 12:29 | 0.04185 | 0.0003077 | 8 | 1088 | Planned | Planned interruption | Relocate load from Lionks 629 to new Links 1295.09:03 is internal switchyard no ICP affected as Transpower local service is not a registered ICP as recovered under transmission losses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 51 | 8632 | WAIOTAHI | WAIMANA | 2024-05-30 09:00 | 2024-05-30 14:48 | 1.054 | 0.021578 | 425 | 27404 | Planned | Planned interruption | Waimana Lines Shut 4B. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 52 | 8620 | WAIOTAHI | WAIMANA | 2024-05-28 09:03 | 2024-05-28 15:29 | 1.9174 | 0.019501 | 425 | 49851 | Planned | Planned interruption | Waimana Lines Shut 4. Manual Completed | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 53 | 8631 | GALATEA | GALATEA | 2024-06-05 10:00 | 2024-06-05 13:46 | 0.113 | 0.0005 | 13 | 2938 | Planned | Planned interruption | Tree works Kopuriki Road between P29069 & P29067. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 54 | 8634 | WAIOTAHI | WAIMANA | 2024-06-05 10:00 | 2024-06-05 15:02 | 0.67495 | 0.008385 | 136 | 17548 | Planned | Planned interruption | Waimana Lines Shut 6. manual check | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 55 | 8624 | STATION RD | ANGLE RD | 2024-06-06 09:47 | 2024-06-06 13:00 | 0.68295 | 0.0035386 | 92 | 17756 | Planned | Planned interruption | Shift Pole and PMTX 27M031. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 56 | 8635 | WAIOTAHI | WAIMANA | 2024-06-07 09:27 | 2024-06-07 13:26 | 1.002 | 0.0041925 | 109 | 26051 | Planned | Planned interruption | Tree Works Ohiwa Harbour Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 57 | 8637 | WAIOTAHI | WAIMANA | 2024-06-06 09:00 | 2024-06-06 14:46 | 0.79249 | 0.008385 | 136 | 20604 | Planned | Planned interruption | Waimana Lines Shut 7. Manual Check | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 58 | 8633 | OHOPE | HARBOUR | 2024-06-11 09:00 | 2024-06-11 11:28 | 0.25616 | 0.0017308 | 45 | 6660 | Planned | Planned interruption | Vegetation Control Harbour Road Feeder. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 59 | 8657 | TE KAHA | TE KAHA | 2024-06-12 08:05 | 2024-06-12 14:46 | 0.7393 | 0.090465 | 1202 | 19221 | Planned | Planned interruption | Local Service Swap te kaha Please also see unscheduled Tab for 1042 Operation due to CT Fault after initial relivening as 8657R1US and manual calc for line 9 as canceled with out Notice. Manual calc and will need to include 18 icp included for 8669 as advertising cancelation oversite | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 60 | 8642 | WAIOTAHI | WAIMANA | 2024-06-13 10:02 | 2024-06-13 15:09 | 0.70203 | 0.008385 | 136 | 18252 | Planned | Planned interruption | Waimana Lines Shut 8. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 61 | 8614C | PLAINS | TE TEKO | 2024-06-19 10:00 | 2024-06-19 13:38 | 0.6708 | 0.003077 | 80 | 17440 | Planned | Planned interruption | TREE WORKS GALATEA ROAD. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 62 | 8653 | GALATEA | Golf Road Feeder | 2024-06-19 09:00 | 2024-06-19 11:49 | 0.039 | 0.0002308 | 6 | 1014 | Planned | Planned interruption | WHIRINAKI ROAD LINES SHUT 1. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 63 | 8643 | WAIOTAHI | WAIMANA | 2024-06-20 10:01 | 2024-06-20 13:35 | 0.02469 | 0.0001154 | 3 | 642 | Planned | Planned interruption | TX STRUCTURE UPGRADE 30S006. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 64 | 8684 | TE KAHA | WAIHAU BAY | 2024-06-20 08:30 | 2024-06-20 10:24 | 0.057 | 0.0005 | 13 | 1482 | Planned | Planned interruption | CONTRACTOR ADVERTISED - NOTIFICATION ON FILE - REMOVE REDUNDANT OH HV LINE. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 65 | 8628 | PLAINS | TE TEKO | 2024-06-18 09:02 | 2024-06-18 13:06 | 0.63818 | 0.0026155 | 68 | 16592 | Planned | Planned interruption | Te Teko Lines Shut Sites 1-8. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 66 | 8644 | STATION RD | MOKOROA | 2024-06-24 09:11 | 2024-06-24 13:45 | 0.05269 | 0.0001923 | 5 | 1370 | Planned | Planned interruption | Mokorua Tree Works. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 67 | 8630 | PLAINS | TE TEKO | 2024-06-21 09:01 | 2024-06-21 13:35 | 0.71664 | 0.0026155 | 68 | 18632 | Planned | Planned interruption | Te Teko Lines Shut 1 - Sites 9 - 12. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 68 | 8662 | PLAINS | MANAWAHE | 2024-06-26 09:44 | 2024-06-26 13:38 | 0.38701 | 0.0016539 | 43 | 10062 | Planned | Planned interruption | VEGETATION CONTROL HEPBURN ROAD. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 69 | 8665 | GALATEA | Golf Road Feeder | 2024-06-26 09:01 | 2024-06-26 13:59 | 0.16843 | 0.0005769 | 15 | 4379 | Planned | Planned interruption | WHIRINAKI ROAD LINES SHUT 3. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 70 | 8672 | STATION RD | MOKOROA | 2024-06-25 09:32 | 2024-06-25 12:16 | 0.08843 | 0.0006154 | 16 | 2299 | Planned | Planned interruption | SHIFT TRANSFORMER 28M010. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 71 | 8673 | STATION RD | CITY SOUTH | 2024-06-26 09:01 | 2024-06-26 11:14 | 0.28647 | 0.0021539 | 56 | 7448 | Planned | Planned interruption | MAHNAFIX MAINTENANCE 27M036. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 72 | 8675 | STATION RD | MOKOROA | 2024-06-27 09:01 | 2024-06-27 11:03 | 0.18301 | 0.0015001 | 39 | 4758 | Planned | Planned interruption | MAGNAFIX MAINTENANCE 28M012. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 73 | 8676 | STATION RD | MOKOROA | 2024-06-27 12:01 | 2024-06-27 14:11 | 0.25501 | 0.0019616 | 51 | 6630 | Planned | Planned interruption | MAGNAFIX MAINTENANCE 28M018. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 74 | 8623A | WAIOTAHI | WAIMANA | 2024-07-03 10:02 | 2024-07-03 14:15 | 0.13624 | 0.0005385 | 14 | 3542 | Planned | Planned interruption | Waimana Shut from Links 921. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 75 | 8640 | PLAINS | TE TEKO | 2024-07-02 09:05 | 2024-07-02 12:11 | 0.05723 | 0.0003077 | 8 | 1488 | Planned | Planned interruption | Upgrade bottm of transformer structure 24P023 and replace with fluorine and upgrade LV at P425865. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 76 | 8650 | STATION RD | RUATOKI | 2024-07-05 09:01 | 2024-07-05 12:41 | 0.27078 | 0.0012308 | 32 | 7040 | Planned | Planned interruption | Tree works Grace and Sisam Valley Roads. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 77 | 8664 | GALATEA | Golf Road Feeder | 2024-07-01 09:00 | 2024-07-01 13:34 | 0.36832 | 0.0029232 | 76 | 9576 | Planned | Planned interruption | Whirinaki Road Lines Shut 2. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 78 | 8677 | OHOPE | POHUTUKAWA | 2024-07-01 09:32 | 2024-07-01 12:52 | 1.0231 | 0.0051156 | 133 | 26600 | Planned | Planned interruption | Magnefix Maintenance West End. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 79 | 8678 | PLAINS | AWAITI | 2024-07-02 09:03 | 2024-07-02 13:28 | 0.1427 | 0.0005385 | 14 | 3710 | Planned | Planned interruption | Isolation for shelter belt trimming. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 80 | 8679 | PLAINS | MANAWAHE | 2024-07-03 09:34 | 2024-07-03 12:41 | 0.02877 | 0.0001539 | 4 | 748 | Planned | Planned interruption | Tree works Mimiha Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 81 | 8681 | PLAINS | TE TEKO | 2024-07-04 09:21 | 2024-07-04 14:31 | 1.0612 | 0.0034232 | 89 | 27590 | Planned | Planned interruption | Tree works SH30 Te Teko. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 82 | 8638 | PLAINS | TE TEKO | 2024-07-11 09:01 | 2024-07-11 12:18 | 0.70468 | 0.0035771 | 93 | 18321 | Planned | Planned interruption | HV Outage to enable LV works | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 83 | 8645 | WAIOTAHI | WAIMANA | 2024-07-09 10:01 | 2024-07-09 12:39 | 0.03039 | 0.0001923 | 5 | 790 | Planned | Planned interruption | Waimana TX Links 30T013--> Upgading Bottom of TX and Reconduct LV from TX to Pole 487681 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 84 | 8654 | WAIOTAHI | HOSPITAL | 2024-07-10 10:00 | 2024-07-10 14:38 | 1.9065 | 0.009885 | 257 | 49567 | Planned | Planned interruption | HV shut to enable LV works Union st Opotiki, Unscheduled Cart vs Pole Shut slight overrun to allow for resource to perform isolations for Fault job manual check. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 85 | 8666 | GALATEA | Golf Road Feeder | 2024-07-08 09:02 | 2024-07-08 13:39 | 0.15981 | 0.0005769 | 15 | 4155 | Planned | Planned interruption | Whirinakli lines shut 4. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 86 | 8682 | WAIOTAHI | WAIMANA | 2024-07-09 09:04 | 2024-07-09 13:49 | 0.38367 | 0.0013462 | 35 | 9975 | Planned | Planned interruption | Tree Works Ruatuna Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 87 | 8683 | PLAINS | MANAWAHE | 2024-07-10 09:00 | 2024-07-10 13:58 | 0.12608 | 0.0004231 | 11 | 3278 | Planned | Planned interruption | Tree works Ross Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 88 | 8699 | OHOPE | HARBOUR | 2024-07-17 09:00 | 2024-07-17 15:24 | 2.7915 | 0.0072695 | 189 | 72576 | Planned | Planned interruption | HARBOUR ROAD SHUT 1. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 89 | 8705 | PLAINS | MANAWAHE | 2024-07-12 09:02 | 2024-07-12 11:48 | 0.07662 | 0.0004616 | 12 | 1992 | Planned | Planned interruption | TRANSFORMER INSTALL FOR HAUONE PUMP TRUST. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 90 | 8710 | PLAINS | WESTBANK | 2024-07-17 09:00 | 2024-07-17 13:51 | 0.01119 | 3.85e-05 | 1 | 291 | Planned | Planned interruption | TRANSFORMER 24L032 UPGRADE. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 91 | 8689 | PLAINS | TE TEKO | 2024-07-18 09:01 | 2024-07-18 14:42 | 0.2982 | 0.0008846 | 23 | 7753 | Planned | Planned interruption | LAMBERT ROAD - SHUT 1. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 92 | 8694 | WAIOTAHI | COAST | 2024-07-18 09:30 | 2024-07-18 10:28 | 0.01115 | 0.0001923 | 5 | 290 | Planned | Planned interruption | TRANSFORMER UPGRADE TO 75kVA. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 93 | 8693 | PLAINS | MANAWAHE | 2024-07-22 09:32 | 2024-07-22 13:14 | 0.28178 | 0.0012693 | 33 | 7326 | Planned | Planned interruption | Tree Works Mimiha Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 94 | 8688 | OHOPE | HARBOUR | 2024-07-23 09:31 | 2024-07-23 13:05 | 0.09877 | 0.0004616 | 12 | 2568 | Planned | Planned interruption | Tree Works McCoy Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 95 | 8690 | PLAINS | TE TEKO | 2024-07-23 09:04 | 2024-07-23 14:03 | 0.0575 | 0.0001923 | 5 | 1495 | Planned | Planned interruption | Lambert Shut 2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 96 | 8696 | PLAINS | MANAWAHE | 2024-07-24 09:32 | 2024-07-24 11:53 | 0.63995 | 0.0045386 | 118 | 16638 | Planned | Planned interruption | VEGETATION CONTROL WORKS MANAWAHE FEEDER. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 97 | 8700 | OHOPE | HARBOUR | 2024-07-19 09:01 | 2024-07-19 14:12 | 1.7477 | 0.005731 | 149 | 45439 | Planned | Planned interruption | HARBOUR ROAD - SHUT 2. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 98 | 8701 | OHOPE | HARBOUR | 2024-07-24 09:02 | 2024-07-24 13:14 | 0.95958 | 0.0038078 | 99 | 24948 | Planned | Planned interruption | HARBOUR ROAD - SHUT 3. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 99 | 8708 | GALATEA | Golf Road Feeder | 2024-07-25 10:00 | 2024-07-25 14:14 | 0.37125 | 0.0014616 | 38 | 9652 | Planned | Planned interruption | GOLF ROAD O/H LINE DEFECTS. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 100 | 8691 | PLAINS | TE TEKO | 2024-07-31 09:00 | 2024-07-31 13:39 | 0.25755 | 0.0009231 | 24 | 6696 | Planned | Planned interruption | Lambert Road Shut 3. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 101 | 8695 | PLAINS | MANAWAHE | 2024-07-25 09:34 | 2024-07-25 12:29 | 0.02019 | 0.0001154 | 3 | 525 | Planned | Planned interruption | Upgrade Transformer 24L013 from 50kVA to 100kVA. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 102 | 8703 | PLAINS | MANAWAHE | 2024-07-31 09:30 | 2024-07-31 13:13 | 0.09435 | 0.0004231 | 11 | 2453 | Planned | Planned interruption | Tree Works Matata Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 103 | 8692 | PLAINS | TE TEKO | 2024-08-06 09:02 | 2024-08-06 13:32 | 1.1735 | 0.0043463 | 113 | 30510 | Planned | Planned interruption | Lambert Road Shut 4. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 104 | 8697A | STATION RD | PIRIPAI | 2024-08-06 09:01 | 2024-08-06 12:43 | 0.27324 | 0.0012308 | 32 | 7104 | Planned | Planned interruption | Keepa Road Lines Work. Manual | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 105 | 8704 | PLAINS | MANAWAHE | 2024-08-05 09:06 | 2024-08-05 12:19 | 0.51221 | 0.0026539 | 69 | 13317 | Planned | Planned interruption | Tree Works SH2 West. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 106 | 8715 | TE KAHA | TE KAHA | 2024-08-08 09:31 | 2024-08-08 14:05 | 1.37 | 0.0050002 | 130 | 35620 | Planned | Planned interruption | VEGETATION CONTROL WORKS TE KAHA FEEDER. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 107 | 8709 | STATION RD | RUATOKI | 2024-08-06 09:32 | 2024-08-06 11:57 | 0.03346 | 0.0002308 | 6 | 870 | Planned | Planned interruption | VEGETATION CONTROL WORKS. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 108 | 8714 | KAWERAU | KAWERAU | 2024-08-06 09:33 | 2024-08-06 09:42 | 0.04362 | 0.0048463 | 126 | 1134 | Planned | Planned interruption | REPLACE FAULT INDICATORS AT RMC 188. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 109 | 8721 | PLAINS | TE TEKO | 2024-08-13 09:02 | 2024-08-13 13:08 | 0.06623 | 0.0002692 | 7 | 1722 | Planned | Planned interruption | Tree Works Kawerau Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 110 | 8723 | KAWERAU | KEA FEEDER | 2024-08-13 09:01 | 2024-08-13 15:49 | 0.12554 | 0.0003077 | 8 | 3264 | Planned | Planned interruption | Te Kore Reworks. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 111 | 8729 | STATION RD | TANEATUA | 2024-08-13 09:01 | 2024-08-13 14:36 | 0.24482 | 0.0007308 | 19 | 6365 | Planned | Planned interruption | Taneatua Low Lines. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 112 | 8716 | PLAINS | TE TEKO | 2024-08-20 09:30 | 2024-08-20 13:50 | 0.34001 | 0.0013077 | 34 | 8840 | Planned | Planned interruption | Tree works galatea Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 113 | 8725 | PLAINS | TE TEKO | 2024-08-21 09:03 | 2024-08-21 13:57 | 0.42971 | 0.0014616 | 38 | 11172 | Planned | Planned interruption | Military Road Shut 1. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 114 | 8720 | STATION RD | ANGLE RD | 2024-08-25 09:30 | 2024-08-25 13:39 | 0.04789 | 0.0001923 | 5 | 1245 | Planned | Planned interruption | Relocate and Rename Transformer 27M013 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 115 | 8726 | STATION RD | MOKOROA | 2024-08-27 09:00 | 2024-08-27 10:51 | 0.29693 | 0.0026924 | 70 | 7720 | Planned | Planned interruption | Replace Motor Mechs RMC 163. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 116 | 8728 | KAWERAU | ONEPU | 2024-08-27 09:01 | 2024-08-27 12:55 | 0.027 | 0.0001154 | 3 | 702 | Planned | Planned interruption | Tree Works Norske Ponds. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 117 | 8740 | PLAINS | AWAITI | 2024-08-29 09:10 | 2024-08-29 16:37 | 1.3032 | 0.003154 | 82 | 33883 | Planned | Planned interruption | INSTALLING NEW TX, ABS, LINKS AT GRIEVES RD, EDGEHAVEN LANE. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 118 | 8755 | OHOPE | HARBOUR | 2024-08-30 09:00 | 2024-08-30 14:48 | 0.16062 | 0.0004616 | 12 | 4176 | Planned | Planned interruption | Mccoy rd OH Replacements Shut 1. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 119 | 8762 | PLAINS | AWAKERI | 2024-09-04 09:30 | 2024-09-04 13:14 | 0.03446 | 0.0001539 | 4 | 896 | Planned | Planned interruption | OH TX 25O022 TO GMTX 25O102-CHANGEOVER SERVICES. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 120 | 8763 | PLAINS | AWAKERI | 2024-09-05 09:31 | 2024-09-05 13:21 | 0.03539 | 0.0001539 | 4 | 920 | Planned | Planned interruption | OH TX 25O021 TO 25O101-> CHANGEOVER LV SERVICES. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 121 | 8746 | GALATEA | JOLLY ROAD | 2024-09-11 09:30 | 2024-09-11 14:13 | 0.22859 | 0.0008077 | 21 | 5943 | Planned | Planned interruption | TREE WORKS TROUTBECK ROAD, GALATEA. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 122 | 8782 | KOPE | EIVERS | 2024-09-11 20:30 | 2024-09-11 22:23 | 0.10866 | 0.0009616 | 25 | 2825 | Planned | Planned interruption | RMC 18 - 5 YEARLY MAINTENANCE. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 123 | 8747 | TE KAHA | WAIHAU BAY | 2024-09-10 09:23 | 2024-09-10 15:36 | 0.10043 | 0.0002692 | 7 | 2611 | Planned | Planned interruption | OH->UG CONVERSION ORETE POINT ROAD still auditable as notified customers still went off KP | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 124 | 8748 | STATION RD | RUATOKI | 2024-09-10 09:02 | 2024-09-10 13:38 | 0.67941 | 0.0024616 | 64 | 17664 | Planned | Planned interruption | TREE WORKS WHITEPINE BUSH ROAD. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 125 | 8739 | OHOPE | HARBOUR | 2024-09-05 09:00 | 2024-09-05 13:09 | 0.03831 | 0.0001539 | 4 | 996 | Planned | Planned interruption | 621 Wainui Road Tree Works. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 126 | 8771 | PLAINS | AWAKERI | 2024-09-12 09:31 | 2024-09-12 15:45 | 0.11508 | 0.0003077 | 8 | 2992 | Planned | Planned interruption | Replace 25O017 and rename 25O100. - CONTRACTOR ADVERTISED | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 127 | 8772 | PLAINS | AWAKERI | 2024-09-13 09:34 | 2024-09-13 12:07 | 0.04119 | 0.0002692 | 7 | 1071 | Planned | Planned interruption | Repalce Transformer 25O020 and rename 25O099. CONTRACTOR ADVERTISED | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 128 | 8775 | PLAINS | AWAITI | 2024-09-03 09:13 | 2024-09-03 13:00 | 0.03492 | 0.0001539 | 4 | 908 | Planned | Planned interruption | Edgehaven/Hogbin RD--> Replace TX Arms on 24O032. Manual Done | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 129 | 8791 | PLAINS | TE TEKO | 2024-09-13 09:01 | 2024-09-13 11:13 | 0.01523 | 0.0001154 | 3 | 396 | Planned | Planned interruption | Powell Road & Te Teko Road Defect 25O056. Manual to 2 hour | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 130 | 8792 | PLAINS | TE TEKO | 2024-09-13 09:01 | 2024-09-13 11:55 | 0.03346 | 0.0001923 | 5 | 870 | Planned | Planned interruption | Powell Road & Te Teko Road Defect 24O027. Manual | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 131 | 8778 | GALATEA | JOLLY ROAD | 2024-09-26 09:00 | 2024-09-26 10:48 | 0.08723 | 0.0008077 | 21 | 2268 | Planned | Planned interruption | Install DDO Arm and Liven New Transformer 24A057 - No new ICPs yet. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 132 | 8793 | PLAINS | AWAKERI | 2024-09-27 09:00 | 2024-09-27 14:20 | 0.42244 | 0.0013461 | 35 | 10983 | Planned | Planned interruption | FNSF Project Shut Three. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 133 | 8751 | KAWERAU | ONEPU | 2024-09-18 09:02 | 2024-09-18 13:35 | 0.32551 | 0.0011924 | 31 | 8463 | Planned | Planned interruption | replace rotten crossarm on Onepu Springs Road. Over Run Manual | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 134 | 8754 | STATION RD | TANEATUA | 2024-09-19 09:01 | 2024-09-19 12:04 | 0.31674 | 0.0017308 | 45 | 8235 | Planned | Planned interruption | Tree works 699 taneatua Road. Manual | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 135 | 8757 | STATION RD | PIRIPAI | 2024-09-20 09:01 | 2024-09-20 10:54 | 0.19993 | 0.0017693 | 46 | 5198 | Planned | Planned interruption | Magnefix Maintenance 27L009. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 136 | 8758 | STATION RD | PIRIPAI | 2024-09-20 12:02 | 2024-09-20 13:48 | 0.13862 | 0.0013077 | 34 | 3604 | Planned | Planned interruption | Magnefix Maintenance 27L012. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 137 | 8761 | KAWERAU | KEA FEEDER | 2024-09-21 09:30 | 2024-09-21 13:14 | 0.01723 | 7.69e-05 | 2 | 448 | Planned | Planned interruption | Upgrade Transformer 23S083 Paroa Street Kawerau. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 138 | 8774 | PLAINS | AWAKERI | 2024-09-19 09:00 | 2024-09-19 13:50 | 0.48856 | 0.0017308 | 45 | 12702 | Planned | Planned interruption | FNSF Shut One. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 139 | 8776 | GALATEA | GALATEA | 2024-09-19 09:00 | 2024-09-19 11:19 | 0.1497 | 0.001077 | 28 | 3892 | Planned | Planned interruption | Install DDO Arm and liven Transformer. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 140 | 8783 | PLAINS | AWAKERI | 2024-09-25 09:00 | 2024-09-25 13:43 | 0.67403 | 0.0025385 | 66 | 17524 | Planned | Planned interruption | FNSF Shut Two. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 141 | 8800 | PLAINS | AWAKERI | 2024-10-01 09:01 | 2024-10-01 14:18 | 0.35394 | 0.0011539 | 30 | 9202 | Planned | Planned interruption | FNSF Shut 4. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 142 | 8749 | STATION RD | ANGLE RD | 2024-10-02 10:02 | 2024-10-02 11:46 | 0.22401 | 0.0021539 | 56 | 5824 | Planned | Planned interruption | Replace Crossarms on Pole P21837. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 143 | 8828 | PLAINS | TE TEKO | 2024-10-04 08:00 | 2024-10-04 17:14 | 0.03092 | 0.0006156 | 16 | 804 | Planned | Planned interruption | Isolation for Transpower works Part scheduled adjusted in manual | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 144 | 8829 | PLAINS | TE TEKO | 2024-10-07 09:04 | 2024-10-07 11:24 | 0.02154 | 0.0001539 | 4 | 560 | Planned | Planned interruption | Isoaltion to return Line to Normal Configuration/ manual Adjust 4 minutes for 2 hour and 24 min Over run | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 145 | 8756 | OHOPE | HARBOUR | 2024-10-07 09:00 | 2024-10-07 12:36 | 0.0997 | 0.0004616 | 12 | 2592 | Planned | Planned interruption | McCoy Road OH Replacements shut 2 Manual to 2 hour. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 146 | 8805 | PLAINS | AWAKERI | 2024-10-08 09:06 | 2024-10-08 15:35 | 0.33013 | 0.0008847 | 23 | 8583 | Planned | Planned interruption | Combined 8805 and 8811 FNSF Project | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 147 | 8784 | WAIOTAHI | COAST | 2024-10-09 10:04 | 2024-10-09 13:00 | 0.35878 | 0.0020385 | 53 | 9328 | Planned | Planned interruption | NC1 Connection 225 Waiapu Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 148 | 8825 | GALATEA | GALATEA | 2024-10-09 09:00 | 2024-10-09 12:31 | 0.00812 | 3.85e-05 | 1 | 211 | Planned | Planned interruption | Upgrade Transformer 24A009 to new 200KVA 24A055. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 149 | 8808 | OHOPE | HARBOUR | 2024-10-23 08:45 | 2024-10-23 13:07 | 0.69991 | 0.013116 | 213 | 18197 | Planned | Planned interruption | Tree works at 827 Wainui Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 150 | 8814 | PLAINS | AWAKERI | 2024-10-23 09:39 | 2024-10-23 14:02 | 0.42486 | 0.0016154 | 42 | 11046 | Planned | Planned interruption | 33kV Te Rahu South WBM South Split Shut 2. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 151 | 8819 | EAST BANK | THORNTON | 2024-10-10 09:00 | 2024-10-10 12:34 | 0.32924 | 0.0015385 | 40 | 8560 | Planned | Planned interruption | Replace assets on Thornton Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 152 | 8827 | PLAINS | TE TEKO | 2024-10-22 09:00 | 2024-10-22 13:33 | 0.0105 | 3.85e-05 | 1 | 273 | Planned | Planned interruption | Tree Works Galatea Road Wiseman Property. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 153 | 8764 | WAIOTAHI | HOSPITAL | 2024-10-22 09:30 | 2024-10-22 12:41 | 1.1782 | 0.0094619 | 246 | 30632 | Planned | Planned interruption | replace Links and Crossarm and Transformer 32O060. <amual due to complex advertising glitch | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 154 | 8834 | STATION RD | PIRIPAI | 2024-10-23 01:03 | 2024-10-24 00:54 | 0.35005 | 0.0017693 | 35 | 9101 | Planned | Planned interruption | Generation install / removal and Crossarm replacement P13632. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 155 | 8753 | PLAINS | TE TEKO | 2024-10-16 09:32 | 2024-10-16 14:49 | 0.86569 | 0.0027309 | 71 | 22507 | Planned | Planned interruption | Powell Road Defects. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 156 | 8785 | GALATEA | MURUPARA | 2024-10-10 09:24 | 2024-10-10 11:23 | 0.06408 | 0.0005385 | 14 | 1666 | Planned | Planned interruption | 6 year maintenance ISO 9082. Manual required | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 157 | 8818 | STATION RD | RUATOKI | 2024-10-15 09:09 | 2024-10-15 14:50 | 1.4427 | 0.0042309 | 110 | 37510 | Planned | Planned interruption | Tree Works Fosters rd Both sides of Isolation Point | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 158 | 8824 | GALATEA | JOLLY ROAD | 2024-10-16 09:01 | 2024-10-16 13:02 | 0.2132 | 0.0008846 | 23 | 5543 | Planned | Planned interruption | Upgrade existing tx 24A022 to 200KVA GM 24A059. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 159 | 8607B | KOPE | REX MORPETH | 2024-10-17 09:00 | 2024-10-17 14:06 | 1.2005 | 0.0039232 | 102 | 31212 | Planned | Planned interruption | RMC 327 Final Commissioning and Change overs , Please also see 8607BUS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 160 | 8846 | GALATEA | JOLLY ROAD | 2024-10-31 09:00 | 2024-10-31 14:09 | 0.01189 | 3.85e-05 | 1 | 309 | Planned | Planned interruption | Upgrade Transformer site and underground Some HV | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 161 | 8822 | KOPE | REX MORPETH | 2024-10-31 09:01 | 2024-10-31 12:10 | 0.13085 | 0.0006923 | 18 | 3402 | Planned | Planned interruption | Pak Nsave ev Chatgers Upgrade Total Pad | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 162 | 8809 | STATION RD | TANEATUA | 2024-11-01 09:00 | 2024-11-01 12:36 | 0.01662 | 7.69e-05 | 2 | 432 | Planned | Planned interruption | Tree works 53 Wharenui Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 163 | 8768 | KOPE | KING ST | 2024-11-01 09:00 | 2024-11-01 10:44 | 0.38801 | 0.0037309 | 97 | 10088 | Planned | Planned interruption | 28M029 Maintenance. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 164 | 8770 | KAWERAU | KAWERAU | 2024-11-08 09:08 | 2024-11-08 11:11 | 0.60083 | 0.0048848 | 127 | 15621 | Planned | Planned interruption | Magnefix Maintenance 22S076 & 22S078. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 165 | 8810 | STATION RD | TANEATUA | 2024-11-08 09:01 | 2024-11-08 12:26 | 0.46521 | 0.0022693 | 59 | 12095 | Planned | Planned interruption | Tree Works 719 Rewatu Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 166 | 8817 | STATION RD | RUATOKI | 2024-11-12 09:00 | 2024-11-12 13:14 | 0.62525 | 0.0024616 | 64 | 16256 | Planned | Planned interruption | Tree Works White Pine Bush. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 167 | 8833 | KOPE | VICTORIA | 2024-11-04 13:56 | 2024-11-05 13:56 | 0.21493 | 0.0001538 | 4 | 5588 | Planned | Planned interruption | Temporary removal and maintenance of RMC24. Two days. Note notification was for 05/11/2024 to 06/11/2024 - but outage was 04/11/2024 to 06/11/2024. Manual Required was under customer request | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 168 | 8835 | WAIOTAHI | HOSPITAL | 2024-11-14 09:01 | 2024-11-14 12:30 | 0.9325 | 0.0044617 | 116 | 24244 | Planned | Planned interruption | Tree Works Wellington Road Opotiki. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 169 | 8838 | STATION RD | RUATOKI | 2024-11-13 09:01 | 2024-11-13 13:10 | 0.00958 | 3.85e-05 | 1 | 249 | Planned | Planned interruption | Tree Works 844A Rewatu Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 170 | 8841 | PLAINS | AWAKERI | 2024-11-06 09:02 | 2024-11-06 14:10 | 0.08293 | 0.0002692 | 7 | 2156 | Planned | Planned interruption | FNSF Pole Install Shut 1. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 171 | 8845 | PLAINS | AWAKERI | 2024-11-13 09:00 | 2024-11-13 14:39 | 0.11735 | 0.0003462 | 9 | 3051 | Planned | Planned interruption | FNSF Pole Install Shut 2. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 172 | 8851 | PLAINS | MANAWAHE | 2024-11-08 09:03 | 2024-11-08 14:59 | 0.13693 | 0.0003846 | 10 | 3560 | Planned | Planned interruption | Manawahe Road NC1 and Defects. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 173 | 8852 | PLAINS | AWAKERI | 2024-11-18 11:01 | 2024-11-18 14:17 | 0.45986 | 0.0023462 | 61 | 11956 | Planned | Planned interruption | New 3/50kVA Transformer 1773 SH30. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 174 | 8832 | EAST BANK | THORNTON | 2024-11-15 09:01 | 2024-11-15 12:07 | 0.04292 | 0.0002308 | 6 | 1116 | Planned | Planned interruption | Replace two transformers. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 175 | 8847 | PLAINS | AWAKERI | 2024-11-15 09:00 | 2024-11-15 13:12 | 0.21324 | 0.0008462 | 22 | 5544 | Planned | Planned interruption | FNSF Pole Install Shut 3. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 176 | 8854 | TE KAHA | WAIHAU BAY | 2024-11-19 08:45 | 2024-11-19 15:23 | 0.69472 | 0.0052309 | 91 | 18062 | Planned | Planned interruption | Whangapararoa Shut 1.Manual | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 177 | 8807 | OHOPE | HARBOUR | 2024-11-20 09:00 | 2024-11-20 12:52 | 0.58002 | 0.0025001 | 65 | 15080 | Planned | Planned interruption | Tree works Stanley Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 178 | 8849 | WAIOTAHI | HOSPITAL | 2024-11-20 09:01 | 2024-11-20 12:33 | 0.66864 | 0.003154 | 82 | 17384 | Planned | Planned interruption | WINDSOR STREET, OPOTIKI--> NEW CONNECTIONS FOR KAINGA ORA. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 179 | 8856 | TE KAHA | WAIHAU BAY | 2024-11-20 08:16 | 2024-11-20 11:57 | 0.03735 | 0.0002308 | 6 | 971 | Planned | Planned interruption | Multiple Transformer upgrades separate sites same letter drop rfs Manual Required FFS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 180 | 8858 | TE KAHA | WAIHAU BAY | 2024-11-21 08:45 | 2024-11-21 13:35 | 0.42071 | 0.0052309 | 91 | 10938 | Planned | Planned interruption | Whangaparoa Defects Shut 2 Manual. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 181 | 8864 | TE KAHA | WAIHAU BAY | 2024-11-22 09:00 | 2024-11-22 12:11 | 0.62445 | 0.0032694 | 85 | 16235 | Planned | Planned interruption | Waihau bay Shut 3. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 182 | 8816 | WAIOTAHI | WAIMANA | 2024-11-26 09:02 | 2024-11-26 11:26 | 0.19385 | 0.0013462 | 35 | 5040 | Planned | Planned interruption | Tree Works Ruatuna Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 183 | 8848 | PLAINS | AWAKERI | 2024-11-26 09:01 | 2024-11-26 13:54 | 0.09016 | 0.0003077 | 8 | 2344 | Planned | Planned interruption | FNSF Pole Install Shut 4. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 184 | 8837 | WAIOTAHI | WAIMANA | 2024-11-28 09:01 | 2024-11-28 13:39 | 0.1497 | 0.0005385 | 14 | 3892 | Planned | Planned interruption | Tree Works Waiotahe Valley. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 185 | 8850 | STATION RD | PIRIPAI | 2024-11-29 09:07 | 2024-11-29 11:37 | 0.02308 | 0.0001539 | 4 | 600 | Planned | Planned interruption | "Works" Coastlands. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 186 | 8867 | WAIOTAHI | OTARA | 2024-12-05 09:40 | 2024-12-05 13:03 | 0.01562 | 7.69e-05 | 2 | 406 | Planned | Planned interruption | Tree Works Waiata Rd, Otara. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 187 | 8863 | TE KAHA | WAIHAU BAY | 2024-12-10 09:01 | 2024-12-10 14:26 | 1.0625 | 0.0032694 | 85 | 27625 | Planned | Planned interruption | Waihau Bay Lines Shut 1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 188 | 8853 | PLAINS | TE TEKO | 2024-12-11 09:32 | 2024-12-11 12:17 | 0.06981 | 0.0004231 | 11 | 1815 | Planned | Planned interruption | 322 Hydro Rd Control Tech. New 11KV UG_3/30KVA GMTX_3/63A | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 189 | 8871 | PLAINS | TE TEKO | 2024-12-11 09:00 | 2024-12-11 10:56 | 0.24539 | 0.0021155 | 55 | 6380 | Planned | Planned interruption | New Pole < New PMTX Installation at 25 Mcivor Road Manual reqd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 190 | 8872 | PLAINS | TE TEKO | 2024-12-12 09:30 | 2024-12-12 12:12 | 0.00623 | 3.85e-05 | 1 | 162 | Planned | Planned interruption | Tree works Galatea Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 191 | 8859 | TE KAHA | WAIHAU BAY | 2024-12-13 09:00 | 2024-12-13 14:18 | 1.113 | 0.0035001 | 91 | 28938 | Planned | Planned interruption | Whangaparoa Defects Shut 3. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 192 | 8866 | TE KAHA | WAIHAU BAY | 2024-12-12 09:02 | 2024-12-12 13:40 | 0.13901 | 0.0005 | 13 | 3614 | Planned | Planned interruption | Waiahu Bay Lines Shut 2. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 193 | 8874 | PLAINS | MANAWAHE | 2024-12-17 09:01 | 2024-12-17 13:57 | 1.1961 | 0.007808 | 203 | 31096 | Planned | Planned interruption | Manawahe Road Link Defects Shut 2. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 194 | 8875 | STATION RD | MOKOROA | 2024-12-12 09:01 | 2024-12-12 11:14 | 0.30693 | 0.0023078 | 60 | 7980 | Planned | Planned interruption | New pole mount transformer and line build for new connection. Manual up to 2 hours | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 195 | 8865 | TE KAHA | WAIHAU BAY | 2024-12-11 | 2024-12-11 12:57 | 0.06369 | 0.0003077 | 15 | 1656 | Planned | Planned interruption | Transformer Structure Upgrade.8865A 44C005,8865B 44B001, BB65D 44C025, Cancelled without Notice 8865C 44B002 Manual entry required Outside times and cancelled without notice | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 196 | 8873 | PLAINS | AWAKERI | 2025-01-14 09:00 | 2025-01-14 16:38 | 0.27993 | 0.0006154 | 16 | 7278 | Planned | Planned interruption | Far North Stringing Shut 1 38 min over run. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 197 | 8878 | PLAINS | AWAKERI | 2025-01-16 09:01 | 2025-01-16 16:49 | 0.39602 | 0.0008462 | 22 | 10296 | Planned | Planned interruption | Far North Stringing Shut 2 49 minute over run. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 198 | 8880 | STATION RD | TANEATUA | 2025-01-17 09:01 | 2025-01-17 14:41 | 0.58848 | 0.0017308 | 45 | 15300 | Planned | Planned interruption | Tree Works 777 Taneatua Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 199 | 8881 | PLAINS | AWAKERI | 2025-01-21 09:00 | 2025-01-21 17:47 | 0.44594 | 0.0008462 | 22 | 11594 | Planned | Planned interruption | FNSF Shut Stringing shut 3 Over run 107 minutes. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 200 | 8884 | PLAINS | AWAKERI | 2025-01-22 09:00 | 2025-01-22 12:26 | 0.12489 | 0.0006154 | 16 | 3247 | Planned | Planned interruption | FNSF Shut 4 Connect Jumpers. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 201 | 8876 | STATION RD | MOKOROA | 2025-01-22 09:01 | 2025-01-22 12:56 | 0.54233 | 0.0023078 | 60 | 14100 | Planned | Planned interruption | Remove PMTX and strip OH Line. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 202 | 8889 | WAIOTAHI | WAIMANA | 2025-01-23 09:01 | 2025-01-23 13:41 | 0.15078 | 0.0005385 | 14 | 3920 | Planned | Planned interruption | Tree works Waiotahe Valley. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 203 | 8890 | WAIOTAHI | WAIMANA | 2025-01-24 09:02 | 2025-01-24 12:11 | 2.6265 | 0.016424 | 427 | 68287 | Planned | Planned interruption | Tree works Burnett Road area. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 204 | 8882 | WAIOTAHI | OTARA | 2025-01-29 09:00 | 2025-01-29 13:31 | 0.36482 | 0.0013462 | 35 | 9485 | Planned | Planned interruption | Otara East Road--> Low Lines & Pole Replacement from Lines Team & Tree Works From Vege Team | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 205 | 8885 | WAIOTAHI | HOSPITAL | 2025-01-30 09:00 | 2025-01-30 13:42 | 0.31455 | 0.0011154 | 29 | 8178 | Planned | Planned interruption | Hospital Feeder Defects as Planned (NMS abnormality pulled 32O017 into advertising ICP count within Tolerance) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 206 | 8886 | PLAINS | MANAWAHE | 2025-01-30 09:03 | 2025-01-30 14:28 | 0.1125 | 0.0003462 | 9 | 2925 | Planned | Planned interruption | Tree works Matata Straights. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 207 | 8898 | KOPE | VICTORIA | 2025-02-01 12:00 | 2025-02-01 13:12 | 0.43267 | 0.0062695 | 163 | 11249 | Planned | Planned interruption | Upgrade Links 27M120 at Pole P10742 James Street | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 208 | 8893 | STATION RD | ANGLE RD | 2025-02-03 09:01 | 2025-02-03 14:11 | 0.6081 | 0.0019616 | 51 | 15810 | Planned | Planned interruption | Powdrell RD--> Raise Low Lines, Replace Pole and Conductors. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 209 | 8894 | PLAINS | TE TEKO | 2025-02-04 09:31 | 2025-02-04 11:22 | 0.05123 | 0.0004616 | 12 | 1332 | Planned | Planned interruption | 15 Hydro Road - HV Line Retensioning. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 210 | 8895 | KOPE | VICTORIA | 2025-02-11 09:04 | 2025-02-11 13:39 | 1.0049 | 0.003654 | 95 | 26125 | Planned | Planned interruption | RMC 19 Oil and Magnefix Links 103 at 27M034. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 211 | 8899 | KOPE | VICTORIA | 2025-02-04 09:00 | 2025-02-04 13:24 | 0.55848 | 0.0021155 | 55 | 14520 | Planned | Planned interruption | Connect new RMC 356 and 27M180 for Hinemoa Pump. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 212 | 8900 | OHOPE | HARBOUR | 2025-02-13 09:02 | 2025-02-13 13:07 | 0.03769 | 0.0001539 | 4 | 980 | Planned | Planned interruption | Tree works 633 Wainui Road. (Slight overrun). | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 213 | 8877 | PLAINS | AWAKERI | 2025-02-14 09:05 | 2025-02-14 15:01 | 0.48871 | 0.0019616 | 51 | 12706 | Planned | Planned interruption | SH30 Awakeri Defects and Projects (Install Links 3215). | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 214 | 8908 | EAST BANK | THORNTON | 2025-02-14 09:00 | 2025-02-14 13:04 | 0.46925 | 0.0019232 | 50 | 12200 | Planned | Planned interruption | NC1 at 957 Thornton Road - Instsall new transformer. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 215 | 8896D | WAIOTAHI | COAST | 2025-02-18 09:35 | 2025-02-18 12:59 | 0.23539 | 0.0011539 | 30 | 6120 | Planned | Planned interruption | 11KV Isolation for 50 KV Pole Replacement Jobs. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 216 | 8932 | PLAINS | MANAWAHE | 2025-02-18 08:31 | 2025-02-18 13:51 | 0.01231 | 3.85e-05 | 1 | 320 | Planned | Planned interruption | Manawahe Lines FY25 Shut 1 at McIvor Rd - Manual required. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 217 | 8924 | PLAINS | MANAWAHE | 2025-02-19 09:31 | 2025-02-19 14:06 | 0.11635 | 0.0004231 | 11 | 3025 | Planned | Planned interruption | Manawahe Site 4 Only--> Pole Move And Replace | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 218 | 8897 | KAWERAU | ONEPU | 2025-02-19 09:16 | 2025-02-19 14:21 | 0.01173 | 3.85e-05 | 1 | 305 | Planned | Planned interruption | Tree Works --> Kawerau Straights near Tamaoho Drive. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 219 | 8916 | GALATEA | GALATEA | 2025-02-20 10:01 | 2025-02-20 13:48 | 0.08731 | 0.0003846 | 10 | 2270 | Planned | Planned interruption | Tree Works at 189 Kopuriki Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 220 | 8931 | WAIOTAHI | WAIMANA | 2025-02-26 09:01 | 2025-02-26 11:00 | 0.00458 | 3.85e-05 | 1 | 119 | Planned | Planned interruption | Oruamanganui Drive HDBC Removal--> Replacing TX Arms.Manual required under 2 hours | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 221 | 8950 | PLAINS | MANAWAHE | 2025-02-26 09:01 | 2025-02-26 13:29 | 0.01031 | 3.85e-05 | 1 | 268 | Planned | Planned interruption | Manawahe Lines FY25 Section 2--> Work to finish at P14626. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 222 | 8896C | TE KAHA | TE KAHA | 2025-02-18 08:48 | 2025-02-18 15:34 | 0.39863 | 0.09108 | 1184 | 10364 | Planned | Planned interruption | Generation for 50kV Outage - Manual Required. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 223 | 8910 | KOPE | MCGARVEY | 2025-02-24 18:30 | 2025-02-24 20:37 | 0.15143 | 0.0011924 | 31 | 3937 | Planned | Planned interruption | RMC 156--> 5 Year OIL Repalcement. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 224 | 8933 | PLAINS | MANAWAHE | 2025-02-19 08:31 | 2025-02-19 16:45 | 0.019 | 3.85e-05 | 1 | 494 | Planned | Planned interruption | Manawahe Mcivor shut 2. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 225 | 8923 | STATION RD | ANGLE RD | 2025-02-21 09:00 | 2025-02-21 14:10 | 1.3312 | 0.0043079 | 112 | 34610 | Planned | Planned interruption | Safety Isolations for 33KV Works. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 226 | 8914 | WAIOTAHI | OTARA | 2025-02-27 09:30 | 2025-02-27 13:24 | 0.58502 | 0.0025001 | 65 | 15210 | Planned | Planned interruption | Tree Works 2920 Waioeka Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 227 | 8926 | STATION RD | ANGLE RD | 2025-02-27 09:01 | 2025-02-27 14:03 | 0.63887 | 0.0021155 | 55 | 16610 | Planned | Planned interruption | SH30 AWAKERI CROSSARM REPLACEMENT. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 228 | 8925 | STATION RD | TANEATUA | 2025-02-28 09:02 | 2025-02-28 12:34 | 0.22016 | 0.0010385 | 27 | 5724 | Planned | Planned interruption | Replace Burnt Crossarms at P22261 & P22260. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 229 | 8915 | OHOPE | HARBOUR | 2025-02-28 09:00 | 2025-02-28 12:33 | 0.15566 | 0.0007308 | 19 | 4047 | Planned | Planned interruption | Tree Works --> 693A Stanley Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 230 | 8927 | WAIOTAHI | COAST | 2025-02-28 09:22 | 2025-02-28 12:56 | 1.0371 | 0.0048463 | 126 | 26964 | Planned | Planned interruption | SH35--> 2 x 11KV STRUCTURE UPGRADES. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 231 | 8928 | WAIOTAHI | HOSPITAL | 2025-02-28 09:03 | 2025-02-28 13:37 | 1.188 | 0.0044233 | 115 | 30886 | Planned | Planned interruption | Opotiki High Street Defects. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 232 | 8929 | GALATEA | JOLLY ROAD | 2025-02-28 09:11 | 2025-02-28 13:11 | 0.33786 | 0.0015001 | 39 | 8784 | Planned | Planned interruption | Crossarm Replacement. Manual Done | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 233 | 8944 | PLAINS | AWAKERI | 2025-03-05 09:02 | 2025-03-05 13:48 | 0.022 | 7.69e-05 | 2 | 572 | Planned | Planned interruption | FNSF Stringing Site 1-9. CONTRACTOR ADVERTISED | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 234 | 8942 | WAIOTAHI | WAIMANA | 2025-03-11 09:00 | 2025-03-11 13:40 | 0.15078 | 0.0005385 | 14 | 3920 | Planned | Planned interruption | Tree Works Waiotahi Valley. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 235 | 8946 | PLAINS | AWAKERI | 2025-03-14 09:01 | 2025-03-14 16:00 | 2.0527 | 0.0049233 | 128 | 53368 | Planned | Planned interruption | Galatea Road Shut 1. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 236 | 8962 | TE KAHA | TE KAHA | 2025-03-13 09:54 | 2025-03-13 12:32 | 0.04254 | 0.0002692 | 7 | 1106 | Planned | Planned interruption | Upgrade 39J005-->Contractor advertised | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 237 | 8966 | STATION RD | MOKOROA | 2025-03-13 09:30 | 2025-03-13 11:44 | 0.21647 | 0.0016154 | 42 | 5628 | Planned | Planned interruption | Repalce Transformer 28M042. Fault Job Done as Planned outside of Notification PeriodLetter Dropped However Timing does nor meet minimum Notification Requirements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 238 | 8948 | KAWERAU | PLATEAU | 2025-03-18 09:31 | 2025-03-18 12:20 | 0.013 | 7.69e-05 | 2 | 338 | Planned | Planned interruption | ABS 768 Replace with Links. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 239 | 8953 | PLAINS | TE TEKO | 2025-03-20 09:32 | 2025-03-20 13:34 | 0.63295 | 0.0026155 | 68 | 16456 | Planned | Planned interruption | Galatea Rd SHUT 2. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 240 | 8954 | PLAINS | TE TEKO | 2025-03-25 09:04 | 2025-03-25 13:33 | 0.68287 | 0.0025386 | 66 | 17754 | Planned | Planned interruption | Galatea RD Shut 3. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 241 | 8788 | KOPE | MCGARVEY | 2025-03-27 22:01 | 2025-03-28 00:14 | 0.10743 | 0.0008077 | 21 | 2793 | Planned | Planned interruption | RMC 25--> 5 Yearly Maintenance. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 242 | 8945 | KOPE | REX MORPETH | 2025-03-28 01:00 | 2025-03-28 02:46 | 0.08562 | 0.0008077 | 21 | 2226 | Planned | Planned interruption | RMC 245--> Oil Maintenance. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 243 | 8979 | PLAINS | TE TEKO | 2025-03-28 09:00 | 2025-03-28 16:28 | 2.198 | 0.0049233 | 128 | 57146 | Planned | Planned interruption | Te Teko Works Contractor letter dropped. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 244 | 240404B | STATION RD | ANGLE RD | 2024-04-04 12:17 | 2024-04-04 14:08 | 0.36717 | 0.0033078 | 86 | 9546 | Unplanned | Defective Equipment | Replace Pole P12492 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 245 | 240408A | STATION RD | CITY SOUTH | 2024-04-08 17:12 | 2024-04-08 20:05 | 0.17301 | 0.001 | 26 | 4498 | Unplanned | Defective Equipment | Part Powers on City South feeder. Blown Jumper found at ABS1443 outside sub. Cracked insulator on same structure not part of fault replaced during shut. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 246 | 240412A | KAWERAU | PLATEAU | 2024-04-12 01:36 | 2024-04-12 09:59 | 2.8148 | 0.05054 | 1531 | 73181 | Unplanned | Adverse Weather | B + C Phase fault with GND indicated at 1689. Nothing found but was storm conditions at the time so possibly a branch in the line. ICP counts corrected as NMS still has 1129 to EOL on Plateau feeder. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 247 | 240412B | PLAINS | TE TEKO | 2024-04-12 11:03 | 2024-04-12 12:16 | 0.29763 | 0.0040771 | 106 | 7738 | Unplanned | Adverse Weather | SEC 5132 OPEN after B & C phase fault was activated. Branches touched the lines after a tree fell. Lines were found still in place while patrolling. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 248 | 240412C | KAINGAROA | DUNN ROAD | 2024-04-12 14:55 | 2024-04-13 12:08 | 9.0093 | 0.0070772 | 184 | 234232 | Unplanned | Adverse Weather | GL 15 Locked Out --> Broken Cross Arm @ P34311--> Fall Distance Tree | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 249 | 240412D | WAIOTAHI | WAIMANA | 2024-04-12 16:09 | 2024-04-12 23:10 | 0.56675 | 0.0013462 | 35 | 14735 | Unplanned | Adverse Weather | HV Lines Down Between Poles P31978 & P31979. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 250 | 240412E | WAIOTAHI | COAST | 2024-04-12 18:06 | 2024-04-12 18:32 | 0.052 | 0.0020001 | 52 | 1352 | Unplanned | Adverse Weather | B & C Phase AR to Lock out. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 251 | 240412F | GALATEA | GALATEA | 2024-04-12 18:28 | 2024-04-13 10:34 | 1.9217 | 0.015924 | 182 | 49961 | Unplanned | Adverse Weather | A C Ph Inv Time OC Trip to Lockout. Broken X Arm P29352. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 252 | 240414A | KAWERAU | KEA FEEDER | 2024-04-14 08:26 | 2024-04-14 14:49 | 0.05119 | 0.0001924 | 5 | 1331 | Unplanned | Defective Equipment | Re-install Tx 23S077 & Replace Lightning Arrestors on Mt Putauaki spur. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 253 | 240417A | GALATEA | MINGINUI | 2024-04-17 10:56 | 2024-04-17 12:47 | 0.00854 | 7.69e-05 | 2 | 222 | Unplanned | Vegetation | No power fault at 24F007 - possibly possum or trees - Isolation to cut tree. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 254 | 240417C | TE KAHA | WAIHAU BAY | 2024-04-17 18:45 | 2024-04-17 20:33 | 0.04569 | 0.0004231 | 11 | 1188 | Unplanned | Defective Equipment | Broken Guy 42D013. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 255 | 240420A | STATION RD | CITY SOUTH | 2024-04-20 20:53 | 2024-04-21 00:05 | 2.1122 | 0.018616 | 484 | 54914 | Unplanned | Vegetation | 3 Phase Current lockout SR37 including Bus Coupler - Branch on line across DDOs at 27M072 and Broken DDO Jumper to Main Line. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 256 | 240425A | WAIOTAHI | COAST | 2024-04-25 | 2024-04-26 | 0.63752 | 0.0013078 | 34 | 16575 | Unplanned | Wildlife | Wildlife - Possum | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 257 | 240428A | WAIOTAHI | OTARA | 2024-04-28 06:05 | 2024-04-28 13:45 | 0.35205 | 0.0033078 | 43 | 9153 | Unplanned | Vegetation | Trees in line burning at 566 Pakihi Rd. Toatoa ?? Opotiki. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 258 | 240430A | KOPE | MCGARVEY | 2024-04-30 14:03 | 2024-04-30 15:09 | 2.6626 | 0.072503 | 1478 | 69225 | Unplanned | 3rd Party interference | McGarvey Feeder trip - Cable damaged by WDC contractor. Network in abnormal configuration due to fault at 6042 on Mokoroa. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 259 | 240501A | WAIOTAHI | COAST | 2024-05-01 22:02 | 2024-05-01 22:29 | 0.41052 | 0.017501 | 455 | 10673 | Unplanned | Cause unknown | Unknown Fault. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 260 | 240504A | TE KAHA | TE KAHA | 2024-05-04 06:42 | 2024-05-04 12:41 | 4.636 | 0.090388 | 1175 | 120532 | Unplanned | Defective Equipment | 50 KV loss of supply Waiotahi Broken ISB Insulator/bracket., bolt sheared off, not rusty | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 261 | 240506A | PLAINS | AWAITI | 2024-05-06 09:05 | 2024-05-06 13:15 | 0.25963 | 0.0010385 | 27 | 6750 | Unplanned | Defective Equipment | Lines Down Sutherland Raod. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 262 | 240509A | GALATEA | GALATEA | 2024-05-09 08:52 | 2024-05-09 12:00 | 0.93046 | 0.005231 | 136 | 24191 | Unplanned | Cause unknown | Reclose Beyond 3952 with loss of indication 9022 and Open / Protection under investigation. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 263 | 240510A | STATION RD | MOKOROA | 2024-05-10 09:05 | 2024-05-10 12:44 | 0.82192 | 0.0038079 | 99 | 21369 | Unplanned | Defective Equipment | Replacement of faulty Isolator 6042 top of Gorge Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 264 | 240512A | STATION RD | RUATOKI | 2024-05-12 09:43 | 2024-05-12 10:02 | 0.02062 | 0.0024616 | 64 | 536 | Unplanned | Defective Equipment | DDO broken and stuck in place at transformer 26O037 - Isolated for safe removal as requested by field staff. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 265 | 240512B | WAIOTAHI | WAIMANA | 2024-05-12 19:09 | 2024-05-13 09:07 | 0.22393 | 0.0005385 | 14 | 5822 | Unplanned | Defective Equipment | Damage at Links 563 - Old Stainless type broken duren fault so isolated to replace all three. Patrol of last section left til daylight. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 266 | 240513A | TE KAHA | WAIHAU BAY | 2024-05-13 19:07 | 2024-05-13 20:45 | 0.00377 | 3.85e-05 | 1 | 98 | Unplanned | Defective Equipment | Replace Transformer 40F032 - High voltage issues. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 267 | 240515A | OHOPE | HARBOUR | 2024-05-15 13:41 | 2024-05-15 15:44 | 0.86949 | 0.011231 | 292 | 22606 | Unplanned | Defective Equipment | Broken King Bolt HV Crossarm.- | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 268 | 240515B | STATION RD | ANGLE RD | 2024-05-15 15:19 | 2024-05-15 18:46 | 0.05573 | 0.0002692 | 7 | 1449 | Unplanned | Defective Equipment | 11kV Lines down McGee Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 269 | 240516A | WAIOTAHI | HOSPITAL | 2024-05-16 19:40 | 2024-05-17 14:56 | 0.04446 | 3.85e-05 | 1 | 1156 | Unplanned | 3rd Party interference | Class C Portion Car vs Transformer Please also see Class I Portion 240516A-I. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 270 | 240517B | PLAINS | MANAWAHE | 2024-05-17 19:45 | 2024-05-17 20:30 | 0.34444 | 0.0076541 | 199 | 8955 | Unplanned | Defective Equipment | Broken Guy Hanging in DDOs no Spiggots. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 271 | 240520A | STATION RD | PIRIPAI | 2024-05-20 15:40 | 2024-05-20 16:35 | 0.20943 | 0.0038078 | 99 | 5445 | Unplanned | Defective Equipment | Broken Stub Pole at Transformer 27M140 9 Huna Road Whakatane. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 272 | 240521A | WAIOTAHI | WAIMANA | 2024-05-21 06:34 | 2024-05-21 13:49 | 6.3752 | 0.077695 | 1010 | 165748 | Unplanned | Lightning | Wire down on Looney Road - CB 7072 malfunctioning + Blown Jumper at 7012. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 273 | 240521B | WAIOTAHI | WAIMANA | 2024-05-21 14:04 | 2024-05-21 15:25 | 0.00935 | 0.0001154 | 3 | 243 | Unplanned | Lightning | Replace blown transformer 29T023. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 274 | 8617US | STATION RD | MOKOROA | 2024-05-22 09:00 | 2024-05-22 13:38 | 0.05346 | 0.0001923 | 5 | 1390 | Unplanned | Planned Shutdown | Tree Works Mokorua Reserve. No evidence of Move to alt date or adjustment notification via letter drop | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 275 | 240522A | TE KAHA | TE KAHA | 2024-05-22 11:43 | 2024-05-22 14:15 | 0.06862 | 0.0005001 | 13 | 1784 | Unplanned | Lightning | Replacing a Blown TX 39J020 and replacing TX LINKS ON TX 39J008. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 276 | 240522B | PLAINS | WESTBANK | 2024-05-22 19:10 | 2024-05-22 19:26 | 0.05108 | 0.0031924 | 83 | 1328 | Unplanned | Defective Equipment | Transformer reported to be overloaded and leaking oil. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 277 | 240526A-C | PLAINS | AWAKERI | 2024-05-26 15:42 | 2024-05-26 21:46 | 0.58802 | 0.0016154 | 42 | 15288 | Unplanned | 3rd Party interference | Replace Pole Hstructure due to damage from Car V Pole. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 278 | 240529B | TE KAHA | WAIHAU BAY | 2024-05-29 17:59 | 2024-05-30 02:35 | 8.1194 | 0.026886 | 699 | 211096 | Unplanned | Defective Equipment | Line down. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 279 | 240606A | TE KAHA | WAIHAU BAY | 2024-06-06 22:46 | 2024-06-06 23:52 | 0.87792 | 0.013539 | 349 | 22825 | Unplanned | Wildlife | Phase Ground Fault beyond 8022. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 280 | 8647 | PLAINS | MANAWAHE | 2024-06-07 09:01 | 2024-06-07 13:22 | 0.05019 | 0.0001923 | 5 | 1305 | Unplanned | Planned Shutdown | Manawahe Lines Shut 1. Original shut shared number with 8648 so 2 lots of dates advertised , Letter drop advertising. Letter drop outside required advertising Period (KP) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 281 | 8635US | WAIOTAHI | WAIMANA | 2024-06-07 09:27 | 2024-06-07 13:29 | 0.00969 | 0.0027694 | 72 | 252 | Unplanned | Defective Equipment | FUSE SAVERS 7092 FAILED TO OPERATE. ISOLATION MOVED BACK TO ABS 902. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 282 | 240609A | GALATEA | JOLLY ROAD | 2024-06-09 06:33 | 2024-06-09 06:58 | 0.19458 | 0.0093465 | 243 | 5059 | Unplanned | Cause unknown | CB GL28 Lockout - Unknown cause. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 283 | 8657R1US | TE KAHA | TE KAHA | 2024-06-12 15:54 | 2024-06-12 15:56 | 0.09047 | 0.045233 | 1176 | 2352 | Unplanned | Defective Equipment | CT wiring Fault 1042 after Planned Outage short duration Outage to Rectify Issue. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 284 | 240613A | TE KAHA | TE KAHA | 2024-06-13 09:31 | 2024-06-13 11:50 | 0.92492 | 0.0066541 | 173 | 24047 | Unplanned | Defective Equipment | Term Insulator poulled away from Crossarm - rusted and broken. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 285 | 240614A | OHOPE | HARBOUR | 2024-06-14 14:00 | 2024-06-14 16:56 | 0.16924 | 0.0009616 | 25 | 4400 | Unplanned | Human Error | Clashing Lines due to Sag new K type structure? | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 286 | 240614B | PLAINS | AWAITI | 2024-06-14 16:53 | 2024-06-14 19:22 | 0.00573 | 3.85e-05 | 1 | 149 | Unplanned | Vegetation | Blown transformer 24O014 Following Tree On LV Fault. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 287 | 240615A | PLAINS | WESTBANK | 2024-06-15 12:10 | 2024-06-15 13:35 | 0.09154 | 0.001077 | 28 | 2380 | Unplanned | Defective Equipment | Broken Jumper Greigs Road P24752. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 288 | 240616A | STATION RD | RUATOKI | 2024-06-16 13:02 | 2024-06-16 18:17 | 0.0727 | 0.0002308 | 6 | 1890 | Unplanned | Vegetation | LINES DOWN FROM FALLING TREE | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 289 | 240617A | TE KAHA | TE KAHA | 2024-06-17 12:49 | 2024-06-17 20:07 | 0.05885 | 0.0070388 | 183 | 1530 | Unplanned | Defective Equipment | FEEDER TRIPPED DUE TO CLOSING LINKS ON BLOWN TRANSFROMER. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 290 | 240618A | WAIOTAHI | WAIMANA | 2024-06-18 09:32 | 2024-06-18 10:05 | 0.06346 | 0.0019232 | 50 | 1650 | Unplanned | Cause unknown | UNKNOWN TRIPPING OF CB 3082 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 291 | 240618B | PLAINS | AWAITI | 2024-06-18 19:14 | 2024-06-19 12:08 | 0.117 | 0.0001154 | 3 | 3042 | Unplanned | Defective Equipment | Transformer Take Off isolated for safety. X Arm rotten, HV Pin hanging. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 292 | 240619A | EAST BANK | THORNTON | 2024-06-19 08:34 | 2024-06-19 15:02 | 0.01492 | 3.85e-05 | 1 | 388 | Unplanned | Planned Shutdown | Unscheduled Outage to Shift HV Cable for regional Council Pump Works supply fed council Pump isolated at Council request. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 293 | 240621A | PLAINS | MANAWAHE | 2024-06-21 13:58 | 2024-06-21 14:13 | 0.12347 | 0.0082311 | 214 | 3210 | Unplanned | Human Error | TRIPPING OF CB 5002 - Human Error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 294 | 240622A | GALATEA | GALATEA | 2024-06-22 09:03 | 2024-06-22 14:02 | 0.1042 | 0.0011154 | 29 | 2709 | Unplanned | Defective Equipment | Replace Transformer 24Z039 due to high voltage - DDO broke on isolation so outage needed to replace them. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 295 | 8648 | PLAINS | MANAWAHE | 2024-06-25 09:04 | 2024-06-25 12:54 | 0.04423 | 0.0001923 | 5 | 1150 | Unplanned | Planned Shutdown | MANAWAHE LINES FY25 (SECTION 1) SHUT 2. Original advertising file sent under wrong reference number 8647 , 8647 was later canceled which made our revision only advertised and put shutdown outside of Advertising timeframe allthough customer did receive notification. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 296 | 240626A | WAIOTAHI | COAST | 2024-06-26 03:20 | 2024-06-27 03:21 | 0.96277 | 0.00112 | 17 | 25031 | Unplanned | Adverse Weather | Tripping of CB 1356 - weather related - wind blown debris | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 297 | 240626C | WAIOTAHI | COAST | 2024-06-26 13:27 | 2024-06-26 14:24 | 0.99754 | 0.017501 | 455 | 25935 | Unplanned | Defective Equipment | Blown Jumper to DDO Links Tx 34O057. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 298 | 240701A | PLAINS | WESTBANK | 2024-07-01 19:02 | 2024-07-01 21:11 | 0.02481 | 0.0001923 | 5 | 645 | Unplanned | Defective Equipment | Wire off pin. Broken Binder no correct sub cause. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 299 | 240702A | STATION RD | ANGLE RD | 2024-07-02 14:13 | 2024-07-02 16:06 | 0.06954 | 0.0006154 | 16 | 1808 | Unplanned | Defective Equipment | Broken Jumper 26M001. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 300 | 240702B | EAST BANK | THORNTON | 2024-07-02 14:42 | 2024-07-02 15:04 | 0.00592 | 0.0002692 | 7 | 154 | Unplanned | Defective Equipment | Crossarm Tilted Nut Come off King Bolt | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 301 | 240702C | STATION RD | RUATOKI | 2024-07-02 18:02 | 2024-07-02 23:34 | 2.7455 | 0.0082695 | 215 | 71380 | Unplanned | 3rd Party interference | CB 3912 Locked out - Car Vs Pole Reid Road, Ruatoki | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 302 | 240710B | WAIOTAHI | OPOTIKI | 2024-07-10 10:09 | 2024-07-10 20:13 | 5.1996 | 0.056964 | 1481 | 135185 | Unplanned | 3rd Party interference | Car Vs Pole at 45 Woodlands Road, Opotiki and Broken Jumper Found During Testing. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 303 | 240715A-C | GALATEA | Golf Road Feeder | 2024-07-16 10:06 | 2024-07-16 16:43 | 1.2979 | 0.0032694 | 85 | 33745 | Unplanned | 3rd Party interference | Leaning Pole P27114 after hit by a Car. Please also see 240715A-I for class I Portion | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 304 | 240716B | KAWERAU | ONEPU | 2024-07-16 18:42 | 2024-07-17 12:09 | 0.28113 | 0.0021924 | 57 | 7309 | Unplanned | Cause unknown | Unknown three phase to ground fault. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 305 | 240709D | KAINGAROA | DUNN ROAD | 2024-07-17 15:14 | 2024-07-17 15:47 | 0.23101 | 0.0070003 | 182 | 6006 | Unplanned | 3rd Party interference | Truck clipped Lines with High load | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 306 | 240729A | OHOPE | POHUTUKAWA | 2024-07-29 18:33 | 2024-07-29 22:54 | 2.068 | 0.0079234 | 206 | 53766 | Unplanned | 3rd Party interference | Car V Pole Pole Pohutukawa Ave near 4 square. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 307 | 240804A | STATION RD | RUATOKI | 2024-08-04 00:56 | 2024-08-04 01:24 | 0.3334 | 0.021424 | 557 | 8668 | Unplanned | Cause unknown | B+C Fault - CB SR35 Reclosed with SEC3012 Open. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 308 | 240811A | PLAINS | MANAWAHE | 2024-08-11 13:11 | 2024-08-11 13:56 | 0.20424 | 0.0045386 | 118 | 5310 | Unplanned | Defective Equipment | Broken Stay Wire on Transformer DDOs 22M021. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 309 | 240812A | PLAINS | AWAITI | 2024-08-12 19:39 | 2024-08-12 20:46 | 0.0335 | 0.0005 | 13 | 871 | Unplanned | Defective Equipment | Broken DDO - Replace all three. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 310 | 240813A | STATION RD | ANGLE RD | 2024-08-13 03:28 | 2024-08-13 04:12 | 0.02877 | 0.0006539 | 17 | 748 | Unplanned | Cause unknown | Two blown fuses at ISO 1196 RMC 152. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 311 | 240813B | PLAINS | AWAITI | 2024-08-13 06:24 | 2024-08-13 13:40 | 1.0979 | 0.02127 | 553 | 28544 | Unplanned | Defective Equipment | Found lines down between poles P34204 and P34205. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 312 | 240813C | PLAINS | AWAITI | 2024-08-13 16:06 | 2024-08-13 17:44 | 0.07162 | 0.0007308 | 19 | 1862 | Unplanned | Defective Equipment | Blown Jumper and Burnt DDOs at Links 2474. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 313 | 240818A | WAIOTAHI | COAST | 2024-08-18 10:12 | 2024-08-18 13:30 | 0.02285 | 0.0001154 | 3 | 594 | Unplanned | Vegetation | Transformer bushing damaged by falling tree. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 314 | 240819A | TE KAHA | TE KAHA | 2024-08-19 09:02 | 2024-08-19 10:58 | 0.77634 | 0.0066926 | 174 | 20184 | Unplanned | Defective Equipment | DEFECTIVE KING BOLT - 11KV ARM TWISTED ONTO LV ARM | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 315 | 240819B | WAIOTAHI | COAST | 2024-08-19 12:45 | 2024-08-19 14:14 | 0.01027 | 0.0001154 | 3 | 267 | Unplanned | Vegetation | Part of 240818A falling tree fault. Remove HV links for LV line repair. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 316 | 240823A | GALATEA | Golf Road Feeder | 2024-08-23 10:30 | 2024-08-23 11:54 | 0.00646 | 7.69e-05 | 2 | 168 | Unplanned | 3rd Party interference | Earth wire stolen from transformer 22B001. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 317 | 240825A | STATION RD | RUATOKI | 2024-08-25 14:03 | 2024-08-25 15:50 | 0.06996 | 0.0006539 | 17 | 1819 | Unplanned | 3rd Party interference | Tractor Vs Lines. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 318 | 240901A | STATION RD | RUATOKI | 2024-09-01 02:08 | 2024-09-01 13:16 | 2.5926 | 0.016654 | 433 | 67406 | Unplanned | 3rd Party interference | Car V Pole P14485 with 28S020 322 Reid Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 319 | 240914A | STATION RD | RUATOKI | 2024-09-14 17:53 | 2024-09-14 21:15 | 3.1221 | 0.018424 | 433 | 81172 | Unplanned | Defective Equipment | Blown Sectos 2672. Replaced on 240917A. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 320 | 240914B | TE KAHA | WAIHAU BAY | 2024-09-14 19:17 | 2024-09-14 23:09 | 0.23201 | 0.001 | 26 | 6032 | Unplanned | Defective Equipment | Wire down P23078 to P23076. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 321 | 240915A | WAIOTAHI | OTARA | 2024-09-15 09:37 | 2024-09-15 11:40 | 0.00946 | 7.69e-05 | 2 | 246 | Unplanned | Defective Equipment | Faulty Transformer 33P028. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 322 | 240901B-C | STATION RD | TANEATUA | 2024-09-16 08:38 | 2024-09-16 12:02 | 0.10985 | 0.0005385 | 14 | 2856 | Unplanned | Adverse Weather | report Tree on lines with wire down - 460 SH2 Waimana Gorge. Class C Portion. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 323 | 240916C | WAIOTAHI | WAIMANA | 2024-09-16 09:16 | 2024-09-17 10:59 | 0.92557 | 0.0041155 | 50 | 24064 | Unplanned | Lightning | Unknown cause - Suspect lightning. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 324 | 240916B | STATION RD | ANGLE RD | 2024-09-16 12:53 | 2024-09-16 20:23 | 1.0927 | 0.0084233 | 219 | 28409 | Unplanned | 3rd Party interference | Digger contacted Line wire Down Powdrell road associated Fault causing grass fire at L:inks 2366 Repaired during fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 325 | 240917A | STATION RD | RUATOKI | 2024-09-17 09:32 | 2024-09-17 11:01 | 0.06504 | 0.0007308 | 19 | 1691 | Unplanned | Defective Equipment | Replace Faulty Sectos 2672 - blown on 240914A. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 326 | 240917B | WAIOTAHI | WAIMANA | 2024-09-17 15:39 | 2024-09-17 20:37 | 0.02292 | 7.69e-05 | 2 | 596 | Unplanned | Lightning | Replace lightning damaged 30X001. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 327 | 240920B | PLAINS | AWAKERI | 2024-09-20 10:00 | 2024-09-20 11:41 | 0.00777 | 7.69e-05 | 2 | 202 | Unplanned | Planned Shutdown | Isolation for safety to remove redundant overhead | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 328 | 240920C-C | EAST BANK | THORNTON | 2024-09-20 22:43 | 2024-09-21 06:59 | 0.47371 | 0.0009616 | 25 | 12316 | Unplanned | 3rd Party interference | Car-V-Pole and replcement of old ABS to a new Sectos 3652. This is the Class C portion - see 240920C-I for the Class I portion. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 329 | 240926A | GALATEA | Golf Road Feeder | 2024-09-26 07:01 | 2024-09-26 11:08 | 0.61972 | 0.0029232 | 76 | 16112 | Unplanned | Wildlife | Bird found as cause of fault which brokke a dead-end. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 330 | 241001A | STATION RD | TANEATUA | 2024-10-01 07:09 | 2024-10-01 10:43 | 0.3464 | 0.016808 | 554 | 9006 | Unplanned | Defective Equipment | Phase Down Tanetua Feeder - Failure at Links 2384. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 331 | 241001C | WAIOTAHI | HOSPITAL | 2024-10-01 10:21 | 2024-10-01 10:44 | 0.06104 | 0.0026539 | 69 | 1587 | Unplanned | Planned Shutdown | Unscheduled Tap Change due to high voltage. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 332 | 241002A | STATION RD | RUATOKI | 2024-10-02 06:39 | 2024-10-02 17:40 | 3.2667 | 0.0082696 | 215 | 84930 | Unplanned | 3rd Party interference | Car Vs Pole--> Ruatoki Valley Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 333 | 241002B | PLAINS | MANAWAHE | 2024-10-02 09:45 | 2024-10-02 14:00 | 1.7403 | 0.032463 | 844 | 45246 | Unplanned | Defective Equipment | PL32 Tripping--> Found Blown Lightning Arrestor at Pole P15500. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 334 | 241002C | GALATEA | JOLLY ROAD | 2024-10-02 23:41 | 2024-10-03 00:53 | 0.108 | 0.0015001 | 39 | 2808 | Unplanned | Defective Equipment | BLOWN TX JUMPER -> MAINLINE OITAGE REQUIRED. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 335 | 241003B | STATION RD | TANEATUA | 2024-10-03 05:11 | 2024-10-03 13:44 | 0.4806 | 0.0013078 | 34 | 12495 | Unplanned | Adverse Weather | Lines Down In River. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 336 | 241003A | PLAINS | AWAKERI | 2024-10-03 09:49 | 2024-10-03 12:00 | 0.46356 | 0.0035386 | 92 | 12052 | Unplanned | Defective Equipment | Extra outage required during planned FNSF works due to bad crossarm at CB 6122. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 337 | 241003D | WAIOTAHI | COAST | 2024-10-03 11:35 | 2024-10-04 11:27 | 0.60356 | 0.0004231 | 11 | 15692 | Unplanned | Adverse Weather | Broken Cross Arm at 36M008. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 338 | 241003C | WAIOTAHI | WAIMANA | 2024-10-03 11:36 | 2024-10-04 11:36 | 0.96304 | 0.001077 | 14 | 25038 | Unplanned | Adverse Weather | Links Down at 1546--> Tree through Line by wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 339 | 241003E | GALATEA | JOLLY ROAD | 2024-10-03 18:49 | 2024-10-03 20:52 | 0.00946 | 7.69e-05 | 2 | 246 | Unplanned | Lightning | Replace Single Phase 30KVA transformer 25X005. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 340 | 241004A | WAIOTAHI | WAIMANA | 2024-10-04 15:59 | 2024-10-04 17:59 | 1.0247 | 0.0085388 | 222 | 26640 | Unplanned | Defective Equipment | Blown Jumper at Pole P32397--> Eagles Rd, Waimana. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 341 | 241005A | KAINGAROA | DUNN ROAD | 2024-10-05 01:32 | 2024-10-05 04:22 | 1.1901 | 0.0070003 | 182 | 30940 | Unplanned | Wildlife | DIF Protection Operation Kaingaroa T2--> Possum Found to be the Cause. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 342 | 241005B | STATION RD | RUATOKI | 2024-10-05 21:58 | 2024-10-05 22:59 | 0.18301 | 0.0030001 | 78 | 4758 | Unplanned | Defective Equipment | Multiple Part Power at Downwards Road--> Blown Jumper at Links 2694 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 343 | 241007A | PLAINS | AWAKERI | 2024-10-07 11:47 | 2024-10-07 12:47 | 0.00231 | 3.85e-05 | 1 | 60 | Unplanned | Planned Shutdown | FNSF Unplanned TX Upgrade extra to FNSF works. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 344 | 241007B | WAIOTAHI | HOSPITAL | 2024-10-07 16:01 | 2024-10-07 17:16 | 0.70964 | 0.0094619 | 246 | 18450 | Unplanned | Defective Equipment | Part Power at 1691 SH2 Waiotahi--> Blown Jumper to DDO 32O015. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 345 | 241008A | WAIOTAHI | OPOTIKI | 2024-10-08 13:40 | 2024-10-08 16:16 | 0.006 | 3.85e-05 | 1 | 156 | Unplanned | 3rd Party interference | 33P061 TX Door Blown and Leaning on The Bushing. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 346 | 241009A | GALATEA | Golf Road Feeder | 2024-10-09 08:35 | 2024-10-09 09:38 | 0.46283 | 0.0073464 | 191 | 12033 | Unplanned | Wildlife | Reported Lined Down--> Isolated for Safety Transformer only 1 link down reloaded and closed customers still Had Power. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 347 | 241009B | GALATEA | Golf Road Feeder | 2024-10-09 12:48 | 2024-10-09 13:04 | 0.13416 | 0.0083849 | 218 | 3488 | Unplanned | Cause unknown | UNKNOWN FEEDER TRIPPING - AUTORECLOSER WAS DISABLED AT THE TIME | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 348 | 241009C | GALATEA | Golf Road Feeder | 2024-10-09 17:15 | 2024-10-09 18:17 | 0.01754 | 0.0003078 | 8 | 456 | Unplanned | Defective Equipment | Blown Jumper--> Golf Road Feeder. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 349 | 241010A | GALATEA | Golf Road Feeder | 2024-10-10 18:36 | 2024-10-10 20:12 | 0.02908 | 0.0003078 | 8 | 756 | Unplanned | Defective Equipment | Bypass/ Removal of Defective ABS 738. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 350 | 241011A | KAWERAU | ONEPU | 2024-10-11 07:14 | 2024-10-11 11:24 | 0.13901 | 0.0021924 | 57 | 3614 | Unplanned | Cause unknown | All 3 Phases and Ground Fault at ISO 3041which Tripped KAW CB 2792- Onepu Feeder, Ghost tripping. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 351 | 241011B | GALATEA | JOLLY ROAD | 2024-10-11 15:12 | 2024-10-11 19:57 | 0.59498 | 0.0094234 | 245 | 15469 | Unplanned | 3rd Party interference | GL28 Jolly RD Feeder Tripped--> Reported Truck Hit the Lines at Waitaruna RD Causing Feeder Trip. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 352 | 241013A | PLAINS | AWAKERI | 2024-10-13 01:38 | 2024-10-13 15:10 | 1.4248 | 0.049156 | 442 | 37044 | Unplanned | Defective Equipment | Cable Fault ISO3063 to Links447--> Generation ON from Links 447 to EOL at 15:10. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 353 | 241014A | PLAINS | AWAKERI | 2024-10-14 13:42 | 2024-10-14 14:38 | 0.05169 | 0.0009231 | 24 | 1344 | Unplanned | Defective Equipment | Disconnection of Generation to allow for return to normal supply following cable fault repair. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 354 | 241015B | KOPE | KING ST | 2024-10-15 16:48 | 2024-10-15 22:17 | 0.49352 | 0.0015001 | 39 | 12831 | Unplanned | 3rd Party interference | Car VS RMC 175. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 355 | 241017A | PLAINS | WESTBANK | 2024-10-17 | 2024-10-18 23:58 | 0.77726 | 0.0006152 | 2 | 20208 | Unplanned | Defective Equipment | Blown HV Fuses on 25M056 - unknown cause, . | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 356 | 8607BUS | KOPE | REX MORPETH | 2024-10-17 09:00 | 2024-10-17 14:40 | 0.98081 | 0.0028847 | 75 | 25500 | Unplanned | Planned Shutdown | Unscheduled Portion of shut due to Advertising Oversight. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 357 | 8786 | GALATEA | MINGINUI | 2024-10-18 09:20 | 2024-10-18 11:21 | 0.13962 | 0.0011539 | 30 | 3630 | Unplanned | Planned Shutdown | Entec 9052 6-year maintenance. Manual Required Initial Advertising sent as PLC | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 358 | 241026A | PLAINS | MANAWAHE | 2024-10-26 21:28 | 2024-10-26 23:17 | 0.30605 | 0.0028078 | 73 | 7957 | Unplanned | Vegetation | Vegetation touching at Pole P15749. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 359 | 241027A | STATION RD | RUATOKI | 2024-10-27 10:23 | 2024-10-27 11:52 | 0.26701 | 0.0030001 | 78 | 6942 | Unplanned | Defective Equipment | Broken Jumper at Links 1773. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 360 | 241030A | WAIOTAHI | WAIMANA | 2024-10-30 03:50 | 2024-10-30 08:59 | 7.7423 | 0.038925 | 1012 | 201291 | Unplanned | Vegetation | TREE BRANCH ON LINE BETWEEN POLES P32032 AND P32031. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 361 | 241030B | TE KAHA | WAIHAU BAY | 2024-10-30 05:15 | 2024-10-30 15:09 | 3.4272 | 0.021347 | 353 | 89104 | Unplanned | Defective Equipment | Blown insulator. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 362 | 241101A | WAIOTAHI | WAIMANA | 2024-11-01 13:04 | 2024-11-01 16:25 | 0.00773 | 3.85e-05 | 1 | 201 | Unplanned | Defective Equipment | LV Fusing and cables burnt in transformer 29T041. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 363 | 241103A | WAIOTAHI | HOSPITAL | 2024-11-03 14:12 | 2024-11-03 17:14 | 1.7221 | 0.0094619 | 246 | 44772 | Unplanned | Defective Equipment | Broken Insulator. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 364 | 241112A | EAST BANK | THORNTON | 2024-11-14 05:35 | 2024-11-14 09:40 | 1.1931 | 0.0090002 | 208 | 31020 | Unplanned | Wildlife | CB 634 AB Ground Fault - Bird Strike at 1213 Thornton Road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 365 | 241122B | GALATEA | MINGINUI | 2024-11-22 18:54 | 2024-11-23 12:18 | 2.7543 | 0.0097695 | 127 | 71610 | Unplanned | Vegetation | CB 2042 tripping - Trees trimmed past Links 773. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 366 | 241126A | PLAINS | WESTBANK | 2024-11-26 23:02 | 2024-11-27 01:11 | 0.41182 | 0.0031924 | 83 | 10707 | Unplanned | Defective Equipment | Suspected blown cable to transformer 25M041. See also 241128A. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 367 | 241128A | PLAINS | WESTBANK | 2024-11-28 09:06 | 2024-11-28 14:44 | 1.079 | 0.0031924 | 83 | 28054 | Unplanned | Defective Equipment | Replace blown transformer 25M041. See also 241126A. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 368 | 241130B | TE KAHA | WAIHAU BAY | 2024-11-30 19:19 | 2024-11-30 20:04 | 0.00865 | 0.0001923 | 5 | 225 | Unplanned | Vegetation | Dead Tree resting on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 369 | 241204A | PLAINS | MANAWAHE | 2024-12-04 03:23 | 2024-12-04 11:36 | 0.39305 | 0.0031925 | 74 | 10219 | Unplanned | 3rd Party interference | Car Vs Pole P15757. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 370 | 241205A | EAST BANK | THORNTON | 2024-12-05 17:26 | 2024-12-05 18:35 | 0.15128 | 0.0021924 | 57 | 3933 | Unplanned | Defective Equipment | Repair Pulled out termination at Pole P24876. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 371 | 241206A | WAIOTAHI | WAIMANA | 2024-12-06 20:43 | 2024-12-07 00:07 | 0.45709 | 0.0031155 | 81 | 11884 | Unplanned | Wildlife | Line Down between Poles P31659 & P31660 - Suspected Bird Strike. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 372 | 241207A | WAIOTAHI | HOSPITAL | 2024-12-09 01:20 | 2024-12-09 11:04 | 5.5998 | 0.025616 | 666 | 145589 | Unplanned | Lightning | B- Phase Ground--> Lightning arrestors. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 373 | 241207C | WAIOTAHI | WAIMANA | 2024-12-09 17:01 | 2024-12-09 18:22 | 0.71153 | 0.024309 | 593 | 18499 | Unplanned | Defective Equipment | Replace Loose DDOs on 30P010. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 374 | 241214A | PLAINS | MANAWAHE | 2024-12-14 09:06 | 2024-12-14 16:08 | 0.06493 | 0.0001539 | 4 | 1688 | Unplanned | Defective Equipment | Cable Fault. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 375 | 241217A | WAIOTAHI | FACTORY | 2024-12-17 15:17 | 2024-12-17 20:15 | 0.28655 | 0.0009616 | 25 | 7450 | Unplanned | Vegetation | Tree through lines past Links 2084. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 376 | 241217B | WAIOTAHI | COAST | 2024-12-17 23:14 | 2024-12-18 07:45 | 0.4324 | 0.0008462 | 22 | 11242 | Unplanned | Cause unknown | No cause found for blown links at 869. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 377 | 241218A | STATION RD | PIRIPAI | 2024-12-18 06:45 | 2024-12-18 08:10 | 0.44644 | 0.016116 | 419 | 11607 | Unplanned | Wildlife | Bird Strike blown jumper at P10884. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 378 | 241218B | WAIOTAHI | COAST | 2024-12-18 11:22 | 2024-12-18 11:57 | 0.02423 | 0.0006923 | 18 | 630 | Unplanned | Defective Equipment | Crossarm hanging down at P20464.. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 379 | 241221A | STATION RD | ANGLE RD | 2024-12-21 09:44 | 2024-12-21 12:29 | 0.03808 | 0.0002308 | 6 | 990 | Unplanned | Defective Equipment | Burnt out LV Rack Transformer isolated for repairs at HV | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 380 | 241223A | KAWERAU | PLATEAU | 2024-12-23 12:55 | 2024-12-23 16:00 | 1.3824 | 0.020309 | 528 | 35942 | Unplanned | Defective Equipment | HV Cable Fault on Plateau Feeder between ISO 1515 RMC 65 and ISO 1636 RMC 204. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 381 | 241224A | PLAINS | MANAWAHE | 2024-12-24 07:55 | 2024-12-24 09:37 | 1.8248 | 0.018039 | 469 | 47443 | Unplanned | Cause unknown | CB 5052 tripped - Nothing found. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 382 | 241227A | STATION RD | RUATOKI | 2024-12-27 09:53 | 2024-12-27 10:40 | 0.07412 | 0.001577 | 41 | 1927 | Unplanned | Defective Equipment | Report of Low line - was a road crossing and a broken term insulator ? Rework under 250121A due to re use of old live line clamp. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 383 | 241229A | TE KAHA | WAIHAU BAY | 2024-12-29 13:09 | 2024-12-29 14:35 | 0.49948 | 0.0058079 | 151 | 12986 | Unplanned | Vegetation | HV Lines burning Banana tree at Motor Camp. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 384 | 241230A | WAIOTAHI | WAIMANA | 2024-12-30 00:51 | 2024-12-30 03:15 | 1.054 | 0.0085388 | 222 | 27402 | Unplanned | Cause unknown | CB 7052 tripped but did not alarm. comms failed . Required faultman on site to check and operate. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 385 | 241231A | KAWERAU | KEA FEEDER | 2024-12-31 12:51 | 2025-01-01 10:43 | 0.27405 | 0.0039233 | 51 | 7125 | Unplanned | Vegetation | Vegetation on line. Majority of Affected ICP Industrial Urban | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 386 | 241231B | WAIOTAHI | WAIMANA | 2024-12-31 15:59 | 2024-12-31 17:17 | 0.003 | 3.85e-05 | 1 | 78 | Unplanned | Lightning | Transformer 30T035 hit by lightning. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 387 | 250103A | KAWERAU | PLATEAU | 2025-01-03 09:12 | 2025-01-03 11:12 | 0.00462 | 3.85e-05 | 1 | 120 | Unplanned | Defective Equipment | Change 23P016 and repair LV Spur. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 388 | 250107A | GALATEA | MINGINUI | 2025-01-07 14:50 | 2025-01-07 15:51 | 0.00235 | 3.85e-05 | 1 | 61 | Unplanned | Defective Equipment | Broken Jumper at Pole P18014. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 389 | 250110A | EAST BANK | THORNTON | 2025-01-10 13:41 | 2025-01-10 14:48 | 0.00515 | 7.69e-05 | 2 | 134 | Unplanned | Cause unknown | Blown fuse 25M200 in RMC 302 - Fault Job 21214. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 390 | 250112A | GALATEA | GALATEA | 2025-01-12 07:07 | 2025-01-12 07:45 | 0.24855 | 0.0069619 | 181 | 6462 | Unplanned | Cause unknown | Feeder tripping and cause unknown. Sectionaliser 9022 Open. Investigate Cause of Open both 9022 and GL21 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 391 | 250116A | STATION RD | RUATOKI | 2025-01-16 13:10 | 2025-01-16 14:14 | 0.01477 | 0.0002308 | 6 | 384 | Unplanned | Defective Equipment | LV Fuse Carrier burnt at Transformer 27T003. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 392 | 250121A | STATION RD | RUATOKI | 2025-01-23 10:43 | 2025-01-23 12:40 | 0.17551 | 0.0015001 | 39 | 4563 | Unplanned | Defective Equipment | Sparking Jumpers at Pole P13978. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 393 | 250124A | KAWERAU | KEA FEEDER | 2025-01-24 16:58 | 2025-01-24 18:32 | 0.04539 | 0.0019616 | 51 | 1180 | Unplanned | Cause unknown | Feeder Tripping -Unknown cause - also tripped CB 3582. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 394 | 250125A | TE KAHA | WAIHAU BAY | 2025-01-25 12:21 | 2025-01-25 13:54 | 0.01789 | 0.0001923 | 5 | 465 | Unplanned | Defective Equipment | Jumper Broken for the TX 41F001. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 395 | 250127A | WAIOTAHI | COAST | 2025-01-27 13:14 | 2025-01-27 13:52 | 0.25578 | 0.006731 | 175 | 6650 | Unplanned | Cause unknown | CB 3312 Tripped on B-Phase to Ground Fault - unknown cause. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 396 | 250129A | WAIOTAHI | COAST | 2025-01-29 10:27 | 2025-01-29 11:24 | 0.01096 | 0.0001923 | 5 | 285 | Unplanned | Defective Equipment | High Voltage on transformer 34O026 to tap down. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 397 | 250129C | WAIOTAHI | COAST | 2025-01-29 18:30 | 2025-01-29 19:25 | 0.01058 | 0.0001923 | 5 | 275 | Unplanned | Defective Equipment | Repair DDO and transformer dropper. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 398 | 250129B | GALATEA | MINGINUI | 2025-01-29 18:35 | 2025-01-29 23:01 | 0.04092 | 0.0001539 | 4 | 1064 | Unplanned | Defective Equipment | Replace termination arm and DDO arms at 25F003. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 399 | 250130B | WAIOTAHI | COAST | 2025-01-30 12:10 | 2025-01-30 15:55 | 0.04327 | 0.0001923 | 5 | 1125 | Unplanned | Defective Equipment | Change out Transformer due to flickering Power Possibly failed Tap selector. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 400 | 250207B | WAIOTAHI | COAST | 2025-02-07 11:52 | 2025-02-07 12:16 | 0.01569 | 0.0006539 | 17 | 408 | Unplanned | Cause unknown | Blown Fuse on Links 1401. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 401 | 250207C | GALATEA | JOLLY ROAD | 2025-02-07 18:31 | 2025-02-08 02:17 | 0.11854 | 0.0002693 | 7 | 3082 | Unplanned | 3rd Party interference | HV Lines Down. Farmer dropped tree on line. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 402 | 250214A | WAIOTAHI | WAIMANA | 2025-02-14 16:32 | 2025-02-15 00:52 | 0.25989 | 0.0096543 | 241 | 6757 | Unplanned | Defective Equipment | HV Cable fault past Links 795 Ohiwa. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 403 | 250216B | TE KAHA | WAIHAU BAY | 2025-02-16 19:15 | 2025-02-16 23:37 | 4.8815 | 0.018847 | 490 | 126914 | Unplanned | Defective Equipment | B Phase to Ground fault past Sectionaliser 8012. 42D001 found with broken crossarm. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 404 | 250216A | OHOPE | POHUTUKAWA | 2025-02-17 10:59 | 2025-02-17 14:15 | 2.3219 | 0.011847 | 308 | 60368 | Unplanned | 3rd Party interference | Replace damaged Pole P12608 on Pohutukawa Ave. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 405 | 250218A | STATION RD | TANEATUA | 2025-02-18 16:55 | 2025-02-18 20:22 | 2.9318 | 0.052502 | 494 | 76225 | Unplanned | Cause unknown | Several trippings on feeders - unknown cause. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 406 | 250221A | WAIOTAHI | WAIMANA | 2025-02-21 21:51 | 2025-02-22 15:22 | 0.12127 | 0.0001154 | 3 | 3153 | Unplanned | Defective Equipment | Broken transforemr crossarm and damaged transformer. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 407 | 250224A | PLAINS | AWAITI | 2025-02-24 11:08 | 2025-02-24 12:22 | 0.21285 | 0.0033078 | 86 | 5534 | Unplanned | 3rd Party interference | Lines down 53 Braemar Road - Digger. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 408 | 250304A | KAINGAROA | DUNN ROAD | 2025-03-04 22:31 | 2025-03-05 12:51 | 6.0635 | 0.0071157 | 185 | 157644 | Unplanned | Vegetation | Tree on line between P34299 and P34300. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 409 | 250306A | WAIOTAHI | COAST | 2025-03-06 20:37 | 2025-03-06 21:24 | 1.1714 | 0.024924 | 648 | 30456 | Unplanned | Defective Equipment | Jumper off on the live side of Links 3574 (at ISOLATOR 3572) - replace damaged Ddo at the same time. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 410 | 250308A | WAIOTAHI | COAST | 2025-03-07 10:37 | 2025-03-07 14:55 | 0.08931 | 0.0003462 | 9 | 2322 | Unplanned | Defective Equipment | Blown transformer 33O023 - Generation used - Originally started as 250307B. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 411 | 250307A | PLAINS | AWAITI | 2025-03-07 12:25 | 2025-03-07 14:27 | 0.10585 | 0.0010001 | 26 | 2752 | Unplanned | Defective Equipment | Faulty Transformer 24M036. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 412 | 250307C | STATION RD | RUATOKI | 2025-03-07 17:00 | 2025-03-07 23:36 | 0.06093 | 0.0001539 | 4 | 1584 | Unplanned | 3rd Party interference | Car V Transformer. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 413 | 250308B | KAWERAU | PLATEAU | 2025-03-08 20:17 | 2025-03-09 01:11 | 1.7851 | 0.020309 | 528 | 46411 | Unplanned | Defective Equipment | FEEDER TRIPPING -> UG CABLE FAULT BETWEEN 1515 AND 1636. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 414 | 250310A | PLAINS | AWAKERI | 2025-03-10 10:29 | 2025-03-10 11:36 | 0.00773 | 0.0001154 | 3 | 201 | Unplanned | Defective Equipment | Broken Jumper at Pole P24148. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 415 | 8965 | PLAINS | AWAITI | 2025-03-12 09:14 | 2025-03-12 11:24 | 0.005 | 3.85e-05 | 1 | 130 | Unplanned | Planned Shutdown | Upgrade 23M039- Contractor Advertised No Letter, single customer affected converstation between Contractor and Consumer as NMS wrong job to be Updated | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 416 | 250313B | GALATEA | MINGINUI | 2025-03-13 04:13 | 2025-03-13 08:53 | 2.8109 | 0.010039 | 261 | 73080 | Unplanned | Cause unknown | Unknown tripping of CB 9002. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 417 | 250315A | STATION RD | RUATOKI | 2025-03-15 20:41 | 2025-03-16 00:58 | 0.54041 | 0.021347 | 555 | 14050 | Unplanned | Vegetation | SEC 6012 Trip - Tree on line at 27O039. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 418 | 250327A | STATION RD | RUATOKI | 2025-03-27 01:49 | 2025-03-27 04:04 | 0.67526 | 0.0064233 | 151 | 17556 | Unplanned | Wildlife | Possum on P19513--> B C Phase to Ground--> CB 3832 Locked OUT | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Horizon Networks | 2025 |  | 419 | 250330a | GALATEA | JOLLY ROAD | 2025-03-30 17:02 | 2025-03-30 19:08 | 0.19628 | 0.0049232 | 128 | 5103 | Unplanned | Cause unknown | Cause unknown. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 9 | J.24.03.0076 | G31 | G31 | 2024-05-04 09:07 | 2024-05-04 12:36 | 0.041224 | 0.000197 | 9 | 209 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 10 | J.24.03.0077 | ASY_2772 | ASY_2772 | 2024-05-04 09:06 | 2024-05-04 10:07 | 0.001348 | 2.2e-05 | 1 | 61.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 11 | J.24.03.0083 | U82 | U82 | 2024-02-04 11:12 | 2024-02-04 11:18 | 0.005128 | 0.000789 | 36 | 6.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 12 | J.24.03.0086 | T41 | T41 | 2024-04-04 09:41 | 2024-04-04 15:06 | 0.49357 | 0.0016 | 73 | 308.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 13 | J.24.03.0087 | T42 | T42 | 2024-04-04 09:33 | 2024-04-04 14:09 | 0.18157 | 0.000657 | 30 | 276.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 14 | J.24.03.0089 | U92 | U92 | 2024-04-04 08:26 | 2024-04-04 14:02 | 0.022057 | 6.6e-05 | 3 | 335.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 15 | J.24.03.0091 | ASY_2692 | ASY_2692 | 2024-10-04 09:53 | 2024-10-04 17:30 | 0.20011 | 0.000438 | 20 | 456.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 16 | J.24.03.0102 | X54 | X54 | 2024-12-04 10:05 | 2024-12-04 15:11 | 0.026896 | 8.8e-05 | 4 | 306.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 17 | J.24.03.0106 | N44 | N44 | 2024-03-04 08:15 | 2024-03-04 16:37 | 0.78327 | 0.0016 | 73 | 489.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 18 | J.24.03.0107 | N34 | N34 | 2024-03-04 11:01 | 2024-03-04 16:05 | 10.823 | 0.035764 | 1632 | 302.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 19 | J.24.03.0111 | T41 | T41 | 2024-11-04 10:05 | 2024-11-04 17:23 | 0.028824 | 6.6e-05 | 3 | 438.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 20 | J.24.03.0112 | H31 | H31 | 2024-04-16 10:05 | 2024-04-16 17:05 | 0.027588 | 6.6e-05 | 3 | 419.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 21 | J.24.03.0129 | H31 | H31 | 2024-04-17 10:04 | 2024-04-17 15:45 | 0.13444 | 0.000394 | 18 | 340.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 22 | J.24.03.0135 | U32 | U32 | 2024-08-04 11:28 | 2024-08-04 14:29 | 0.095091 | 0.000526 | 24 | 180.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 23 | J.24.03.0137 | P35 | P35 | 2024-04-17 10:42 | 2024-04-17 13:24 | 0.007092 | 4.4e-05 | 2 | 161.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 24 | J.24.03.0149 | P55 | P55 | 2024-04-19 10:07 | 2024-04-19 16:47 | 0.017502 | 4.4e-05 | 2 | 399.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 25 | J.24.03.0162 | T41 | T41 | 2024-04-22 10:07 | 2024-04-22 15:13 | 0.067047 | 0.000219 | 10 | 306 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 26 | J.24.03.0163 | G31 | G31 | 2024-04-23 10:07 | 2024-04-23 16:09 | 0.047528 | 0.000131 | 6 | 361.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 27 | J.24.03.0164 | T42 | T42 | 2024-04-23 10:05 | 2024-04-23 16:13 | 0.072544 | 0.000197 | 9 | 367.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 28 | J.24.03.0167 | L51 | L51 | 2024-04-30 10:06 | 2024-04-30 15:59 | 0.30945 | 0.000877 | 40 | 353 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 29 | J.24.03.0173 | G31 | G31 | 2024-10-04 11:01 | 2024-10-04 14:29 | 0.009105 | 4.4e-05 | 2 | 207.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 30 | J.24.03.0195 | G32 | G32 | 2024-09-04 10:07 | 2024-09-04 15:40 | 1.7286 | 0.005194 | 237 | 332.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 31 | J.24.03.0210 | X54 | X54 | 2024-04-19 10:14 | 2024-04-19 15:03 | 0.3668 | 0.001271 | 58 | 288.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 32 | J.24.03.0234 | Y43 | Y43 | 2024-04-23 10:08 | 2024-04-23 16:20 | 0.040185 | 0.00011 | 5 | 366.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 33 | J.24.03.0235 | U42 | U42 | 2024-04-23 10:09 | 2024-04-23 12:56 | 0.014594 | 8.8e-05 | 4 | 166.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 34 | J.24.03.0245 | S36 | S36 | 2024-04-17 10:35 | 2024-04-17 15:21 | 0.20662 | 0.000723 | 33 | 285.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 35 | J.24.04.0003 | X52 | X52 | 2024-01-04 12:00 | 2024-01-04 13:24 | 0.003689 | 4.4e-05 | 2 | 84.2 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 36 | J.24.04.0009 | W21 | W21 | 2024-02-04 21:35 | 2024-03-04 06:10 | 1.9273 | 0.005917 | 540 | 162.9 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 37 | J.24.04.0011 | SW65 | SW65 | 2024-02-05 10:03 | 2024-02-05 16:20 | 0.28901 | 0.000767 | 35 | 376.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 38 | J.24.04.0014 | U42 | U42 | 2024-03-04 10:33 | 2024-03-04 13:28 | 0.003832 | 2.2e-05 | 1 | 174.9 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 39 | J.24.04.0018 | G32 | G32 | 2024-03-04 16:03 | 2024-03-04 16:57 | 0.005939 | 0.00011 | 5 | 54.2 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 40 | J.24.04.0019 | SW65 | SW65 | 2024-03-04 18:35 | 2024-03-04 21:58 | 0.022225 | 0.00011 | 5 | 202.8 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 41 | J.24.04.0020 | H31 | H31 | 2024-03-04 19:04 | 2024-03-04 20:36 | 0.008117 | 8.8e-05 | 4 | 92.6 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 42 | J.24.04.0021 | SW65 | SW65 | 2024-04-04 07:05 | 2024-04-04 09:14 | 0.014111 | 0.00011 | 5 | 128.8 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 43 | J.24.04.0022 | SW66 | SW66 | 2024-04-24 10:02 | 2024-04-24 16:48 | 0.89933 | 0.002213 | 101 | 406.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 44 | J.24.04.0026 | L51 | L51 | 2024-04-04 18:02 | 2024-04-04 18:57 | 0.004878 | 8.8e-05 | 4 | 55.7 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 45 | J.24.04.0035 | U42 | U42 | 2024-07-05 10:03 | 2024-07-05 17:14 | 0.75616 | 0.001753 | 80 | 431.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 46 | J.24.04.0036 | U42 | U42 | 2024-08-05 10:04 | 2024-08-05 16:14 | 0.64946 | 0.001753 | 80 | 370.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 47 | J.24.04.0037 | X53 | X53 | 2024-05-04 17:00 | 2024-05-04 18:23 | 0.001823 | 2.2e-05 | 1 | 83.2 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 48 | J.24.04.0049 | Y23 | Y23 | 2024-08-04 11:31 | 2024-08-04 15:13 | 1.5389 | 0.012382 | 565 | 124.3 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 49 | J.24.04.0053 | P35 | P35 | 2024-02-05 12:04 | 2024-02-05 13:22 | 0.003489 | 0.000131 | 6 | 26.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 50 | J.24.04.0055 | X52 | X52 | 2024-08-04 19:50 | 2024-08-04 21:01 | 0.036948 | 0.000526 | 24 | 70.3 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 51 | J.24.04.0057 | KAI_7 | KAI_7 | 2024-04-30 10:08 | 2024-04-30 13:48 | 0.019218 | 8.8e-05 | 4 | 219.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 52 | J.24.04.0059 | SB1142 | SB1142 | 2024-03-05 10:27 | 2024-03-05 11:52 | 0.038926 | 0.00046 | 21 | 84.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 53 | J.24.04.0060 | KAI_6 | KAI_6 | 2024-04-05 09:01 | 2024-04-05 16:44 | 0.28392 | 0.000614 | 28 | 462.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 54 | J.24.04.0062 | P45 | P45 | 2024-08-05 10:33 | 2024-08-05 16:15 | 0.17619 | 0.000548 | 25 | 321.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 55 | J.24.04.0063 | L51 | L51 | 2024-10-05 10:51 | 2024-10-05 17:00 | 0.03241 | 8.8e-05 | 4 | 369.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 56 | J.24.04.0064 | P35 | P35 | 2024-09-04 19:04 | 2024-09-04 20:21 | 0.008428 | 0.00011 | 5 | 76.9 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 57 | J.24.04.0067 | ASY_2762 | ASY_2762 | 2024-10-04 10:32 | 2024-10-04 12:30 | 0.005206 | 4.4e-05 | 2 | 118.8 | Unplanned | Adverse Environment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 58 | J.24.04.0069 | O76 | O76 | 2024-01-05 10:09 | 2024-01-05 12:00 | 0.37359 | 0.003375 | 154 | 110.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 59 | J.24.04.0071 | N34 | N34 | 2024-05-14 10:14 | 2024-05-14 16:40 | 1.2609 | 0.003265 | 149 | 386.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 60 | J.24.04.0072 | N34 | N34 | 2024-05-14 12:03 | 2024-05-14 16:44 | 9.4257 | 0.033989 | 1551 | 277.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 61 | J.24.04.0073 | K36 | K36 | 2024-10-04 15:28 | 2024-10-04 17:09 | 0.010983 | 0.00011 | 5 | 100.2 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 62 | J.24.04.0074 | H31 | H31 | 2024-11-04 02:06 | 2024-11-04 05:22 | 0.20151 | 0.00103 | 47 | 195.7 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 63 | J.24.04.0075 | H31 | H31 | 2024-11-04 02:06 | 2024-11-04 17:02 | 0.18757 | 0.000241 | 11 | 778.1 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 64 | J.24.04.0077 | K33 | K33 | 2024-03-05 10:05 | 2024-03-05 14:52 | 0.018816 | 6.6e-05 | 3 | 286.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 65 | J.24.04.0081 | H31 | H31 | 2024-06-05 11:26 | 2024-06-05 14:07 | 0.007059 | 4.4e-05 | 2 | 161.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 66 | J.24.04.0083 | SW62 | SW62 | 2024-12-04 05:22 | 2024-12-04 07:35 | 0.01173 | 8.8e-05 | 4 | 133.8 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 67 | J.24.04.0084 | Y23 | Y23 | 2024-12-04 07:07 | 2024-12-04 09:07 | 0.002624 | 2.2e-05 | 1 | 119.8 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 68 | J.24.04.0086 | SW64 | SW64 | 2024-12-04 09:10 | 2024-12-04 10:18 | 0.004482 | 6.6e-05 | 3 | 68.2 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 69 | J.24.04.0088 | SW66 | SW66 | 2024-12-04 19:55 | 2024-12-04 21:29 | 0.006163 | 6.6e-05 | 3 | 93.8 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 70 | J.24.04.0090 | Y23 | Y23 | 2024-04-13 08:46 | 2024-04-13 08:56 | 0.000217 | 2.2e-05 | 1 | 9.9 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 71 | J.24.04.0094 | KAI_7 | KAI_7 | 2024-04-15 09:02 | 2024-04-15 09:59 | 0.003723 | 6.6e-05 | 3 | 56.6 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 72 | J.24.04.0096 | N44 | N44 | 2024-05-20 10:27 | 2024-05-20 17:08 | 0.017589 | 4.4e-05 | 2 | 401.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 73 | J.24.04.0097 | SW65 | SW65 | 2024-04-15 10:23 | 2024-04-15 10:42 | 0.23691 | 0.013017 | 594 | 18.2 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 74 | J.24.04.0099 | H31 | H31 | 2024-04-15 10:49 | 2024-04-15 11:48 | 0.042221 | 0.000723 | 33 | 58.4 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 75 | J.24.04.0101 | H31 | H31 | 2024-04-15 10:49 | 2024-04-15 15:45 | 0.1619 | 0.000548 | 25 | 295.5 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 76 | J.24.04.0102 | U92 | U92 | 2024-06-05 10:35 | 2024-06-05 16:57 | 0.01674 | 4.4e-05 | 2 | 382 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 77 | J.24.04.0103 | U92 | U92 | 2024-07-05 10:40 | 2024-07-05 17:23 | 0.017675 | 4.4e-05 | 2 | 403.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 78 | J.24.04.0108 | X56 | X56 | 2024-09-05 10:01 | 2024-09-05 13:07 | 0.077217 | 0.000416 | 19 | 185.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 79 | J.24.04.0110 | SW63 | SW63 | 2024-05-22 10:34 | 2024-05-22 16:47 | 0.016344 | 4.4e-05 | 2 | 372.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 80 | J.24.04.0112 | X52 | X52 | 2024-04-16 16:20 | 2024-04-16 17:19 | 0.001286 | 2.2e-05 | 1 | 58.7 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 81 | J.24.04.0114 | L52 | L52 | 2024-04-16 17:49 | 2024-04-16 19:28 | 0.002151 | 2.2e-05 | 1 | 98.2 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 82 | J.24.04.0118 | ASY_2692 | ASY_2692 | 2024-07-05 10:24 | 2024-07-05 16:38 | 0.016391 | 4.4e-05 | 2 | 374 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 83 | J.24.04.0122 | KAI_6 | KAI_6 | 2024-04-17 20:02 | 2024-04-17 22:01 | 0.010507 | 8.8e-05 | 4 | 119.9 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 84 | J.24.04.0124 | KAI_5 | KAI_5 | 2024-04-18 10:03 | 2024-04-18 10:54 | 0.003389 | 6.6e-05 | 3 | 51.6 | Unplanned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 85 | J.24.04.0125 | KAI_4 | KAI_4 | 2024-05-28 09:50 | 2024-05-28 18:01 | 0.52087 | 0.001118 | 61 | 389.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 86 | J.24.04.0126 | SW66 | SW66 | 2024-04-18 11:18 | 2024-04-18 21:40 | 1.8021 | 0.00767 | 350 | 234.9 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 87 | J.24.04.0128 | SW66 | SW66 | 2024-04-18 19:16 | 2024-04-18 20:56 | 0.006561 | 6.6e-05 | 3 | 99.8 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 88 | J.24.04.0130 | X52 | X52 | 2024-04-19 07:41 | 2024-04-19 08:38 | 0.007497 | 0.000131 | 6 | 57 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 89 | J.24.04.0132 | K37 | K37 | 2024-05-28 10:05 | 2024-05-28 17:17 | 1.7433 | 0.004032 | 184 | 432.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 90 | J.24.04.0135 | X55 | X55 | 2024-04-19 17:52 | 2024-04-19 19:33 | 0.003272 | 6.6e-05 | 3 | 49.8 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 91 | J.24.04.0137 | G31 | G31 | 2024-04-19 21:47 | 2024-04-20 00:02 | 0.065182 | 0.000482 | 22 | 135.2 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 92 | J.24.04.0151 | P45 | P45 | 2024-04-22 09:05 | 2024-04-22 10:09 | 0.007995 | 0.000131 | 6 | 60.8 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 93 | J.24.04.0152 | SW62 | SW62 | 2024-09-05 10:36 | 2024-09-05 14:53 | 0.045021 | 0.000175 | 8 | 256.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 94 | J.24.04.0155 | SB1132 | SB1132 | 2024-05-15 10:14 | 2024-05-15 18:20 | 0.010652 | 2.2e-05 | 1 | 486.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 95 | J.24.04.0156 | U92 | U92 | 2024-05-29 09:42 | 2024-05-29 16:19 | 0.48655 | 0.001227 | 56 | 396.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 96 | J.24.04.0160 | ASY_2762 | ASY_2762 | 2024-04-22 13:06 | 2024-04-22 13:44 | 0.000836 | 2.2e-05 | 1 | 38.1 | Unplanned | Human Error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 97 | J.24.04.0163 | U42 | U42 | 2024-04-22 15:31 | 2024-04-22 17:28 | 0.007728 | 6.6e-05 | 3 | 117.6 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 98 | J.24.04.0166 | SW66 | SW66 | 2024-05-15 12:48 | 2024-05-15 13:26 | 0.000831 | 2.2e-05 | 1 | 37.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 99 | J.24.04.0170 | X55 | X55 | 2024-04-23 16:07 | 2024-04-23 17:30 | 0.00362 | 4.4e-05 | 2 | 82.6 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 100 | J.24.04.0174 | SB1142 | SB1142 | 2024-05-15 09:37 | 2024-05-15 16:06 | 0.10106 | 0.000263 | 12 | 384.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 101 | J.24.04.0175 | K35 | K35 | 2024-05-21 09:56 | 2024-05-21 18:00 | 0.30177 | 0.000636 | 29 | 474.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 102 | J.24.04.0179 | U42 | U42 | 2024-05-17 11:33 | 2024-05-17 13:21 | 0.007098 | 6.6e-05 | 3 | 108 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 103 | J.24.04.0183 | SW65 | SW65 | 2024-04-25 16:24 | 2024-04-25 17:50 | 0.0304 | 0.000351 | 16 | 86.7 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 104 | J.24.04.0184 | KAI_7 | KAI_7 | 2024-04-25 17:24 | 2024-04-25 18:24 | 0.002641 | 4.4e-05 | 2 | 60.3 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 105 | J.24.04.0191 | KAI_6 | KAI_6 | 2024-04-26 18:33 | 2024-04-26 19:52 | 0.003452 | 4.4e-05 | 2 | 78.8 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 106 | J.24.04.0192 | Y43 | Y43 | 2024-04-26 20:44 | 2024-04-30 15:58 | 0.29021 | 8.8e-05 | 4 | 3310.7 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 107 | J.24.04.0194 | H31 | H31 | 2024-04-26 21:48 | 2024-04-27 09:54 | 0.43115 | 0.000789 | 36 | 546.5 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 108 | J.24.04.0197 | X52 | X52 | 2024-04-27 09:49 | 2024-04-27 11:50 | 0.010631 | 8.8e-05 | 4 | 121.3 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 109 | J.24.04.0202 | X52 | X52 | 2024-04-27 15:27 | 2024-04-27 16:30 | 0.001385 | 2.2e-05 | 1 | 63.2 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 110 | J.24.04.0206 | SW66 | SW66 | 2024-04-28 03:54 | 2024-04-28 16:14 | 0.040978 | 0.000131 | 6 | 311.7 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 111 | J.24.04.0208 | G33 | G33 | 2024-04-28 07:40 | 2024-04-28 09:27 | 0.009412 | 8.8e-05 | 4 | 107.4 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 112 | J.24.04.0212 | L53 | L53 | 2024-04-28 09:57 | 2024-04-28 12:54 | 0.027303 | 0.000153 | 7 | 178 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 113 | J.24.04.0222 | G33 | G33 | 2024-04-30 07:50 | 2024-04-30 10:04 | 0.020589 | 0.000153 | 7 | 134.2 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 114 | J.24.04.0224 | X54 | X54 | 2024-05-13 11:13 | 2024-05-13 15:24 | 0.01098 | 4.4e-05 | 2 | 250.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 115 | J.24.04.0228 | ASY_2772 | ASY_2772 | 2024-05-16 11:02 | 2024-05-16 13:32 | 0.013209 | 8.8e-05 | 4 | 150.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 116 | J.24.04.0231 | SB1082 | SB1082 | 2024-05-18 11:07 | 2024-05-18 11:56 | 0.001081 | 2.2e-05 | 1 | 49.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 117 | J.24.05.0006 | U42 | U42 | 2024-02-05 10:02 | 2024-02-05 12:18 | 0.014896 | 0.00011 | 5 | 136 | Unplanned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 118 | J.24.05.0010 | X56 | X56 | 2024-05-20 10:20 | 2024-05-20 18:06 | 0.010217 | 2.2e-05 | 1 | 466.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 119 | J.24.05.0011 | T43 | T43 | 2024-02-05 14:44 | 2024-02-05 18:17 | 0.29355 | 0.002739 | 125 | 107.2 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 120 | J.24.05.0012 | W21 | W21 | 2024-05-22 10:07 | 2024-05-22 16:54 | 0.053491 | 0.000131 | 6 | 406.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 121 | J.24.05.0025 | W21 | W21 | 2024-03-05 18:05 | 2024-03-05 20:36 | 0.14619 | 0.000964 | 44 | 151.6 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 122 | J.24.05.0028 | G31 | G31 | 2024-05-24 10:29 | 2024-05-24 15:51 | 0.028178 | 8.8e-05 | 4 | 321.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 123 | J.24.05.0029 | KAI_4 | KAI_4 | 2024-05-27 09:36 | 2024-05-27 15:47 | 0.063173 | 0.000175 | 8 | 360.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 124 | J.24.05.0037 | SW66 | SW66 | 2024-04-05 16:09 | 2024-04-05 17:02 | 0.001154 | 2.2e-05 | 1 | 52.7 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 125 | J.24.05.0038 | H31 | H31 | 2024-05-05 10:38 | 2024-05-05 14:38 | 0.005255 | 2.2e-05 | 1 | 239.8 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 126 | J.24.05.0040 | H31 | H31 | 2024-05-05 14:03 | 2024-05-05 14:38 | 0.010682 | 0.000307 | 14 | 34.8 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 127 | J.24.05.0048 | U42 | U42 | 2024-06-05 08:41 | 2024-06-05 09:35 | 0.19128 | 0.003572 | 163 | 53.6 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 128 | J.24.05.0052 | U42 | U42 | 2024-06-05 12:34 | 2024-06-05 13:06 | 0.024506 | 0.000767 | 35 | 32 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 129 | J.24.05.0053 | U82 | U82 | 2024-06-05 12:36 | 2024-06-05 13:06 | 0.053191 | 0.001797 | 82 | 29.6 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 130 | J.24.05.0054 | U42 | U42 | 2024-08-05 09:34 | 2024-08-05 17:12 | 0.48131 | 0.001052 | 48 | 457.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 131 | J.24.05.0055 | X56 | X56 | 2024-06-05 13:25 | 2024-06-05 15:47 | 0.00311 | 2.2e-05 | 1 | 141.9 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 132 | J.24.05.0061 | X57 | X57 | 2024-05-22 11:10 | 2024-05-22 13:00 | 0.004838 | 4.4e-05 | 2 | 110.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 133 | J.24.05.0066 | P35 | P35 | 2024-07-05 15:44 | 2024-07-05 19:56 | 0.005515 | 2.2e-05 | 1 | 251.7 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 134 | J.24.05.0070 | U42 | U42 | 2024-08-05 08:07 | 2024-08-05 08:56 | 0.005373 | 0.00011 | 5 | 49 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 135 | J.24.05.0075 | U42 | U42 | 2024-05-14 09:35 | 2024-05-14 18:33 | 0.34206 | 0.000636 | 29 | 538.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 136 | J.24.05.0081 | SW66 | SW66 | 2024-05-31 11:28 | 2024-05-31 12:29 | 0.002692 | 4.4e-05 | 2 | 61.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 137 | J.24.05.0084 | SW63 | SW63 | 2024-05-31 14:37 | 2024-05-31 15:30 | 0.001164 | 2.2e-05 | 1 | 53.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 138 | J.24.05.0085 | X56 | X56 | 2024-04-06 09:49 | 2024-04-06 15:08 | 0.041995 | 0.000131 | 6 | 319.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 139 | J.24.05.0086 | ASY_2772 | ASY_2772 | 2024-05-31 10:13 | 2024-05-31 12:17 | 0.048821 | 0.000394 | 18 | 123.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 140 | J.24.05.0087 | KAI_6 | KAI_6 | 2024-05-30 10:08 | 2024-05-30 17:08 | 0.046061 | 0.00011 | 5 | 420.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 141 | J.24.05.0088 | G31 | G31 | 2024-05-29 09:17 | 2024-05-29 18:19 | 0.90264 | 0.001753 | 81 | 508.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 142 | J.24.05.0101 | KAI_7 | KAI_7 | 2024-10-05 23:56 | 2024-11-05 01:01 | 0.004259 | 6.6e-05 | 3 | 64.8 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 143 | J.24.05.0105 | SW66 | SW66 | 2024-11-05 11:56 | 2024-11-05 13:34 | 0.00216 | 2.2e-05 | 1 | 98.6 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 144 | J.24.05.0107 | Y23 | Y23 | 2024-11-05 19:01 | 2024-11-05 22:30 | 0.22382 | 0.001074 | 49 | 208.4 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 145 | J.24.05.0110 | ASY_2772 | ASY_2772 | 2024-11-05 23:33 | 2024-12-05 00:36 | 0.35252 | 0.005588 | 255 | 63.1 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 146 | J.24.05.0117 | X55 | X55 | 2024-04-06 10:18 | 2024-04-06 11:32 | 0.001618 | 2.2e-05 | 1 | 73.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 147 | J.24.05.0118 | X53 | X53 | 2024-04-06 12:28 | 2024-04-06 12:57 | 0.000639 | 2.2e-05 | 1 | 29.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 148 | J.24.05.0119 | H41 | H41 | 2024-06-06 10:10 | 2024-06-06 13:41 | 0.09695 | 0.00046 | 21 | 210.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 149 | J.24.05.0121 | X55 | X55 | 2024-04-06 14:43 | 2024-04-06 15:20 | 0.00162 | 4.4e-05 | 2 | 37 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 150 | J.24.05.0122 | KAI_4 | KAI_4 | 2024-05-13 12:53 | 2024-05-13 13:21 | 0.000615 | 2.2e-05 | 1 | 28.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 151 | J.24.05.0123 | P35 | P35 | 2024-11-06 10:04 | 2024-11-06 17:18 | 1.2465 | 0.002871 | 131 | 434.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 152 | J.24.05.0124 | U92 | U92 | 2024-05-06 11:06 | 2024-05-06 12:16 | 0.035551 | 0.000504 | 23 | 70.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 153 | J.24.05.0126 | P35 | P35 | 2024-11-06 17:15 | 2024-11-06 17:18 | 0.000703 | 0.000285 | 13 | 2.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 154 | J.24.05.0127 | U42 | U42 | 2024-11-06 11:08 | 2024-11-06 12:36 | 0.003875 | 4.4e-05 | 2 | 88.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 155 | J.24.05.0128 | P35 | P35 | 2024-12-06 10:03 | 2024-12-06 16:14 | 0.11952 | 0.000329 | 15 | 363.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 156 | J.24.05.0132 | X54 | X54 | 2024-06-13 10:26 | 2024-06-13 17:06 | 0.25385 | 0.000636 | 29 | 399.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 157 | J.24.05.0134 | X54 | X54 | 2024-06-14 10:08 | 2024-06-14 16:44 | 0.069469 | 0.000175 | 8 | 396.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 158 | J.24.05.0136 | X52 | X52 | 2024-05-14 14:19 | 2024-05-14 16:14 | 0.010075 | 8.8e-05 | 4 | 114.9 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 159 | J.24.05.0137 | ASY_2772 | ASY_2772 | 2024-05-06 10:20 | 2024-05-06 15:20 | 0.013108 | 4.4e-05 | 2 | 299.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 160 | J.24.05.0138 | ASY_2772 | ASY_2772 | 2024-05-06 17:32 | 2024-05-06 17:42 | 0.00424 | 0.000416 | 19 | 10.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 161 | J.24.05.0141 | X57 | X57 | 2024-06-13 10:53 | 2024-06-13 15:29 | 0.018167 | 6.6e-05 | 3 | 276.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 162 | J.24.05.0147 | P25 | P25 | 2024-06-14 11:00 | 2024-06-14 17:15 | 0.64162 | 0.001709 | 78 | 375.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 163 | J.24.05.0150 | ASY_2762 | ASY_2762 | 2024-05-15 17:03 | 2024-05-15 17:10 | 0.03426 | 0.004383 | 200 | 7.8 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 164 | J.24.05.0152 | SB1072 | SB1072 | 2024-05-18 13:18 | 2024-05-18 14:02 | 0.000951 | 2.2e-05 | 1 | 43.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 165 | J.24.05.0158 | L51 | L51 | 2024-05-29 09:07 | 2024-05-29 09:44 | 0.000802 | 2.2e-05 | 1 | 36.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 166 | J.24.05.0160 | L52 | L52 | 2024-05-29 11:40 | 2024-05-29 16:32 | 0.49899 | 0.001709 | 78 | 291.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 167 | J.24.05.0161 | L51 | L51 | 2024-05-29 17:04 | 2024-05-29 17:28 | 0.021295 | 0.00195 | 89 | 10.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 168 | J.24.05.0162 | L51 | L51 | 2024-05-30 09:05 | 2024-05-30 09:56 | 0.000487 | 2.2e-05 | 2 | 11.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 169 | J.24.05.0163 | L52 | L52 | 2024-05-30 10:40 | 2024-05-30 16:51 | 0.63306 | 0.001709 | 78 | 370.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 170 | J.24.05.0164 | L51 | L51 | 2024-05-30 17:45 | 2024-05-30 18:04 | 0.003237 | 0.00195 | 89 | 1.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 171 | J.24.05.0165 | L52 | L52 | 2024-05-31 09:50 | 2024-05-31 10:17 | 0.000592 | 2.2e-05 | 1 | 27 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 172 | J.24.05.0166 | L51 | L51 | 2024-05-31 11:21 | 2024-05-31 17:26 | 0.71157 | 0.00195 | 89 | 364.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 173 | J.24.05.0167 | L52 | L52 | 2024-05-31 17:31 | 2024-05-31 18:23 | 0.022844 | 0.001687 | 77 | 13.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 174 | J.24.05.0168 | KAI_7 | KAI_7 | 2024-05-17 16:58 | 2024-05-17 17:30 | 0.3792 | 0.011943 | 545 | 31.8 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 175 | J.24.05.0169 | KAI_7 | KAI_7 | 2024-05-17 16:58 | 2024-05-17 19:17 | 0.069859 | 0.000504 | 23 | 138.6 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 176 | J.24.05.0175 | U42 | U42 | 2024-05-18 17:44 | 2024-05-18 18:37 | 0.005853 | 0.00011 | 5 | 53.4 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 177 | J.24.05.0181 | KAI_7 | KAI_7 | 2024-05-20 09:14 | 2024-05-20 10:28 | 0.004837 | 6.6e-05 | 3 | 73.6 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 178 | J.24.05.0183 | SW66 | SW66 | 2024-10-06 12:19 | 2024-10-06 14:12 | 0.009875 | 8.8e-05 | 4 | 112.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 179 | J.24.05.0185 | SW63 | SW63 | 2024-10-06 09:45 | 2024-10-06 11:24 | 0.008615 | 8.8e-05 | 4 | 98.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 180 | J.24.05.0186 | SW66 | SW66 | 2024-10-06 15:20 | 2024-10-06 16:01 | 0.000895 | 2.2e-05 | 1 | 40.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 181 | J.24.05.0187 | P45 | P45 | 2024-06-13 10:22 | 2024-06-13 15:11 | 0.082361 | 0.000285 | 13 | 289.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 182 | J.24.05.0188 | X56 | X56 | 2024-06-14 10:08 | 2024-06-14 15:33 | 0.007105 | 2.2e-05 | 1 | 324.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 183 | J.24.05.0192 | Y23 | Y23 | 2024-07-06 10:14 | 2024-07-06 16:36 | 0.18414 | 0.000482 | 22 | 381.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 184 | J.24.05.0193 | X52 | X52 | 2024-06-13 10:03 | 2024-06-13 16:01 | 0.023524 | 6.6e-05 | 3 | 357.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 185 | J.24.05.0194 | SW65 | SW65 | 2024-05-20 21:56 | 2024-05-20 23:29 | 0.002045 | 2.2e-05 | 1 | 93.3 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 186 | J.24.05.0199 | SW66 | SW66 | 2024-06-14 09:51 | 2024-06-14 10:38 | 0.00102 | 2.2e-05 | 1 | 46.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 187 | J.24.05.0200 | SW63 | SW63 | 2024-06-14 11:41 | 2024-06-14 13:00 | 0.008702 | 0.00011 | 5 | 79.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 188 | J.24.05.0201 | SW66 | SW66 | 2024-06-14 14:34 | 2024-06-14 15:34 | 0.003965 | 6.6e-05 | 3 | 60.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 189 | J.24.05.0202 | X53 | X53 | 2024-05-21 17:35 | 2024-05-21 18:52 | 0.001673 | 2.2e-05 | 1 | 76.4 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 190 | J.24.05.0204 | K36 | K36 | 2024-05-22 01:07 | 2024-05-22 02:48 | 0.004452 | 4.4e-05 | 2 | 101.6 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 191 | J.24.05.0209 | K37 | K37 | 2024-06-20 10:40 | 2024-06-20 14:35 | 0.13991 | 0.000636 | 29 | 220.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 192 | J.24.05.0211 | SW65 | SW65 | 2024-05-22 15:02 | 2024-05-22 17:08 | 0.005515 | 4.4e-05 | 2 | 125.8 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 193 | J.24.05.0214 | O76 | O76 | 2024-05-23 01:34 | 2024-05-23 04:33 | 0.5973 | 0.003331 | 152 | 179.3 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 194 | J.24.05.0219 | T43 | T43 | 2024-05-23 13:05 | 2024-05-23 17:23 | 0.00861 | 6.6e-05 | 3 | 131 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 195 | J.24.05.0221 | X54 | X54 | 2024-06-27 11:12 | 2024-06-27 15:27 | 0.38495 | 0.001512 | 69 | 254.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 196 | J.24.05.0223 | X54 | X54 | 2024-10-06 10:36 | 2024-10-06 16:17 | 0.076114 | 0.000241 | 11 | 315.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 197 | J.24.05.0225 | ASY_2692 | ASY_2692 | 2024-05-24 12:10 | 2024-05-24 12:56 | 0.002042 | 4.4e-05 | 2 | 46.6 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 198 | J.24.05.0227 | X54 | X54 | 2024-06-14 10:21 | 2024-06-14 13:05 | 0.003586 | 2.2e-05 | 1 | 163.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 199 | J.24.05.0229 | X56 | X56 | 2024-06-17 11:28 | 2024-06-17 12:56 | 0.001915 | 2.2e-05 | 1 | 87.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 200 | J.24.05.0230 | T43 | T43 | 2024-06-17 13:54 | 2024-06-17 15:25 | 0.005987 | 6.6e-05 | 3 | 91.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 201 | J.24.05.0232 | X56 | X56 | 2024-06-17 14:22 | 2024-06-17 17:40 | 0.008672 | 4.4e-05 | 2 | 197.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 202 | J.24.05.0233 | T43 | T43 | 2024-06-18 10:20 | 2024-06-18 13:42 | 0.004428 | 2.2e-05 | 1 | 202.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 203 | J.24.05.0262 | U42 | U42 | 2024-06-19 09:45 | 2024-06-19 15:55 | 0.039675 | 0.00011 | 5 | 362.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 204 | J.24.05.0267 | T41 | T41 | 2024-06-17 10:28 | 2024-06-17 18:24 | 0.10874 | 0.000285 | 13 | 381.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 205 | J.24.05.0269 | X55 | X55 | 2024-06-18 10:46 | 2024-06-18 11:21 | 0.000786 | 2.2e-05 | 1 | 35.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 206 | J.24.05.0270 | N44 | N44 | 2024-05-28 10:44 | 2024-05-28 12:02 | 0.001692 | 2.2e-05 | 1 | 77.2 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 207 | J.24.05.0273 | SB1142 | SB1142 | 2024-06-19 09:35 | 2024-06-19 14:56 | 0.01404 | 4.4e-05 | 2 | 320.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 208 | J.24.05.0274 | X56 | X56 | 2024-06-17 11:45 | 2024-06-17 17:08 | 0.021244 | 6.6e-05 | 3 | 323.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 209 | J.24.05.0284 | G32 | G32 | 2024-01-07 09:45 | 2024-01-07 16:47 | 0.11112 | 0.000263 | 12 | 422.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 210 | J.24.05.0288 | X52 | X52 | 2024-06-18 10:08 | 2024-06-18 15:31 | 0.099235 | 0.000307 | 14 | 323.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 211 | J.24.05.0289 | X52 | X52 | 2024-06-20 10:07 | 2024-06-20 12:08 | 0.037077 | 0.000307 | 14 | 120.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 212 | J.24.05.0290 | U42 | U42 | 2024-11-06 09:43 | 2024-11-06 13:06 | 0.16429 | 0.000811 | 37 | 202.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 213 | J.24.05.0299 | X52 | X52 | 2024-06-19 10:07 | 2024-06-19 15:23 | 0.25599 | 0.000811 | 37 | 315.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 214 | J.24.05.0300 | L51 | L51 | 2024-05-30 09:52 | 2024-05-30 09:56 | 0.006782 | 0.001928 | 88 | 3.5 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 215 | J.24.05.0301 | G31 | G31 | 2024-05-07 14:21 | 2024-05-07 15:29 | 0.002962 | 4.4e-05 | 2 | 67.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 216 | J.24.05.0304 | SW64 | SW64 | 2024-06-17 11:09 | 2024-06-17 14:16 | 0.004081 | 2.2e-05 | 1 | 186.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 217 | J.24.05.0305 | X52 | X52 | 2024-06-19 10:09 | 2024-06-19 14:28 | 0.056642 | 0.000219 | 10 | 258.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 218 | J.24.05.0306 | X52 | X52 | 2024-06-21 10:05 | 2024-06-21 11:51 | 0.002324 | 2.2e-05 | 1 | 106.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 219 | J.24.05.0307 | T43 | T43 | 2024-05-07 10:36 | 2024-05-07 12:56 | 0.059261 | 0.00046 | 21 | 128.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 220 | J.24.05.0311 | X52 | X52 | 2024-06-19 10:22 | 2024-06-19 17:29 | 1.0196 | 0.002389 | 109 | 426.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 221 | J.24.05.0312 | X52 | X52 | 2024-06-19 10:21 | 2024-06-19 11:09 | 0.003151 | 6.6e-05 | 3 | 47.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 222 | J.24.05.0313 | KAI_6 | KAI_6 | 2024-06-21 14:02 | 2024-06-21 14:56 | 0.003561 | 6.6e-05 | 3 | 54.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 223 | J.24.05.0314 | X54 | X54 | 2024-06-26 10:08 | 2024-06-26 16:02 | 0.35013 | 0.001008 | 46 | 347.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 224 | J.24.05.0321 | SW65 | SW65 | 2024-03-07 10:05 | 2024-03-07 17:40 | 0.6584 | 0.00149 | 68 | 441.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 225 | J.24.05.0324 | W21 | W21 | 2024-06-27 10:13 | 2024-06-27 14:51 | 0.006082 | 2.2e-05 | 1 | 277.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 226 | J.24.06.0001 | G32 | G32 | 2024-01-06 10:13 | 2024-01-06 11:39 | 0.003791 | 4.4e-05 | 2 | 86.5 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 227 | J.24.06.0004 | WPR_1172 | WPR_1172 | 2024-01-06 13:32 | 2024-01-06 18:00 | 3.5395 | 0.05632 | 5108 | 31.6 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 228 | J.24.06.0005 | W21 | W21 | 2024-01-06 13:41 | 2024-01-06 21:13 | 0.52508 | 0.001161 | 53 | 452.1 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 229 | J.24.06.0009 | ASY_2772 | ASY_2772 | 2024-01-06 14:31 | 2024-01-06 16:11 | 0.013151 | 0.000131 | 6 | 100 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 230 | J.24.06.0011 | X56 | X56 | 2024-01-06 18:23 | 2024-01-06 20:00 | 0.012649 | 0.000131 | 6 | 96.2 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 231 | J.24.06.0017 | KAI_7 | KAI_7 | 2024-03-06 09:09 | 2024-03-06 10:35 | 0.020743 | 0.000241 | 11 | 86.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 232 | J.24.06.0018 | Y23 | Y23 | 2024-03-06 13:22 | 2024-03-06 18:27 | 0.36458 | 0.012382 | 565 | 29.4 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 233 | J.24.06.0019 | P55 | P55 | 2024-03-06 14:00 | 2024-03-06 15:24 | 0.001842 | 2.2e-05 | 1 | 84.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 234 | J.24.06.0020 | SW63 | SW63 | 2024-06-20 10:33 | 2024-06-20 11:23 | 0.017293 | 0.000351 | 16 | 49.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 235 | J.24.06.0024 | SW66 | SW66 | 2024-06-20 10:28 | 2024-06-20 11:09 | 0.001811 | 4.4e-05 | 2 | 41.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 236 | J.24.06.0025 | SW66 | SW66 | 2024-06-20 12:05 | 2024-06-20 12:33 | 0.001224 | 4.4e-05 | 2 | 27.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 237 | J.24.06.0026 | SW63 | SW63 | 2024-06-20 14:11 | 2024-06-20 14:58 | 0.001016 | 2.2e-05 | 1 | 46.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 238 | J.24.06.0030 | CUL_1242 | CUL_1242 | 2024-05-06 12:34 | 2024-05-06 13:52 | 0.14996 | 0.004317 | 197 | 34.7 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 239 | J.24.06.0039 | X54 | X54 | 2024-06-06 07:22 | 2024-06-06 09:57 | 0.010191 | 6.6e-05 | 3 | 155 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 240 | J.24.06.0041 | G33 | G33 | 2024-06-26 10:25 | 2024-06-26 12:31 | 0.044394 | 0.000373 | 17 | 119.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 241 | J.24.06.0042 | H41 | H41 | 2024-06-26 14:32 | 2024-06-26 15:41 | 0.001507 | 2.2e-05 | 1 | 68.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 242 | J.24.06.0043 | H31 | H31 | 2024-06-27 10:03 | 2024-06-27 11:06 | 0.002798 | 4.4e-05 | 2 | 63.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 243 | J.24.06.0047 | W22 | W22 | 2024-09-07 10:07 | 2024-09-07 18:04 | 0.512 | 0.001074 | 49 | 476.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 244 | J.24.06.0048 | W23 | W23 | 2024-09-07 15:41 | 2024-09-07 17:10 | 0.029448 | 0.000329 | 15 | 89.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 245 | J.24.06.0049 | T42 | T42 | 2024-05-07 12:15 | 2024-05-07 15:24 | 0.008273 | 4.4e-05 | 2 | 188.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 246 | J.24.06.0051 | SB1142 | SB1142 | 2024-11-07 09:10 | 2024-11-07 16:18 | 0.037352 | 8.8e-05 | 8 | 213.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 247 | J.24.06.0052 | H21 | H21 | 2024-06-26 10:13 | 2024-06-26 16:18 | 0.087798 | 0.000241 | 11 | 364.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 248 | J.24.06.0053 | X52 | X52 | 2024-06-06 15:45 | 2024-06-06 16:40 | 0.001209 | 2.2e-05 | 1 | 55.2 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 249 | J.24.06.0061 | G31 | G31 | 2024-06-24 10:09 | 2024-06-24 16:28 | 0.074638 | 0.000197 | 9 | 378.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 250 | J.24.06.0065 | SW66 | SW66 | 2024-08-06 05:59 | 2024-08-06 07:00 | 0.005286 | 8.8e-05 | 4 | 60.3 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 251 | J.24.06.0068 | H31 | H31 | 2024-09-06 03:35 | 2024-09-06 05:09 | 0.11773 | 0.001249 | 57 | 94.3 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 252 | J.24.06.0070 | WPR_1132 | WPR_1132 | 2024-10-06 07:29 | 2024-11-06 18:38 | 0.046219 | 2.2e-05 | 1 | 2109.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 253 | J.24.06.0071 | H41 | H41 | 2024-06-13 10:07 | 2024-06-13 15:49 | 0.007482 | 2.2e-05 | 1 | 341.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 254 | J.24.06.0074 | P45 | P45 | 2024-11-07 10:08 | 2024-11-07 17:52 | 0.24986 | 0.000548 | 25 | 456.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 255 | J.24.06.0077 | SB1142 | SB1142 | 2024-11-06 10:41 | 2024-11-06 16:14 | 0.014611 | 4.4e-05 | 2 | 333.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 256 | J.24.06.0086 | P45 | P45 | 2024-06-27 10:16 | 2024-06-27 16:23 | 0.016087 | 4.4e-05 | 2 | 367.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 257 | J.24.06.0093 | X54 | X54 | 2024-02-07 11:03 | 2024-02-07 15:42 | 0.018337 | 6.6e-05 | 3 | 278.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 258 | J.24.06.0095 | L51 | L51 | 2024-05-07 10:08 | 2024-05-07 15:53 | 0.075532 | 0.000219 | 10 | 344.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 259 | J.24.06.0100 | H21 | H21 | 2024-12-06 19:14 | 2024-12-06 19:48 | 0.004451 | 0.000131 | 6 | 33.9 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 260 | J.24.06.0104 | X52 | X52 | 2024-12-06 22:54 | 2024-06-13 00:34 | 0.008783 | 8.8e-05 | 4 | 100.2 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 261 | J.24.06.0108 | Y33 | Y33 | 2024-06-13 12:28 | 2024-06-13 12:32 | 0.00017 | 4.4e-05 | 2 | 3.9 | Unplanned | Human Error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 262 | J.24.06.0111 | W21 | W21 | 2024-06-13 12:56 | 2024-06-13 15:14 | 0.10433 | 0.000833 | 38 | 125.3 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 263 | J.24.06.0112 | SW65 | SW65 | 2024-04-07 10:11 | 2024-04-07 12:56 | 0.018054 | 0.00011 | 5 | 164.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 264 | J.24.06.0121 | U42 | U42 | 2024-12-07 09:22 | 2024-12-07 14:39 | 0.24329 | 0.000767 | 35 | 317.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 265 | J.24.06.0126 | H21 | H21 | 2024-06-14 07:37 | 2024-06-14 09:42 | 0.24857 | 0.00721 | 329 | 34.5 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 266 | J.24.06.0127 | SW64 | SW64 | 2024-02-07 10:30 | 2024-02-07 15:02 | 0.18248 | 0.000789 | 36 | 231.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 267 | J.24.06.0128 | T43 | T43 | 2024-06-14 11:51 | 2024-06-14 13:53 | 0.094112 | 0.000767 | 35 | 122.7 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 268 | J.24.06.0133 | Y23 | Y23 | 2024-08-07 10:44 | 2024-08-07 16:57 | 0.040843 | 0.00011 | 5 | 372.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 269 | J.24.06.0138 | SW66 | SW66 | 2024-06-15 10:06 | 2024-06-15 15:50 | 0.090388 | 0.000263 | 12 | 343.7 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 270 | J.24.06.0142 | X55 | X55 | 2024-06-15 15:25 | 2024-06-15 18:20 | 0.007655 | 4.4e-05 | 2 | 174.7 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 271 | J.24.06.0143 | ASY_2692 | ASY_2692 | 2024-06-15 15:49 | 2024-06-15 17:47 | 0.002591 | 2.2e-05 | 1 | 118.2 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 272 | J.24.06.0144 | ASY_2762 | ASY_2762 | 2024-06-15 17:15 | 2024-06-15 18:25 | 0.001533 | 2.2e-05 | 1 | 70 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 273 | J.24.06.0148 | U82 | U82 | 2024-06-17 09:33 | 2024-06-17 09:59 | 0.001144 | 4.4e-05 | 2 | 26.1 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 274 | J.24.06.0152 | SW66 | SW66 | 2024-06-20 10:16 | 2024-06-20 11:57 | 0.026573 | 0.000263 | 12 | 101.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 275 | J.24.06.0158 | H41 | H41 | 2024-08-07 11:39 | 2024-08-07 17:40 | 0.007888 | 2.2e-05 | 2 | 180 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 276 | J.24.06.0161 | Y23 | Y23 | 2024-02-07 09:41 | 2024-02-07 17:15 | 0.49766 | 0.001096 | 50 | 454.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 277 | J.24.06.0165 | KAI_7 | KAI_7 | 2024-06-18 15:47 | 2024-06-18 18:51 | 0.11286 | 0.000614 | 28 | 183.9 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 278 | J.24.06.0166 | KAI_1 | KAI_1 | 2024-06-18 16:30 | 2024-06-18 16:57 | 0.039888 | 0.001468 | 67 | 27.2 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 279 | J.24.06.0167 | KAI_7 | KAI_7 | 2024-06-18 17:47 | 2024-06-18 18:32 | 0.053449 | 0.001183 | 54 | 45.2 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 280 | J.24.06.0175 | ASY_2772 | ASY_2772 | 2024-11-07 10:37 | 2024-11-07 17:07 | 0.051306 | 0.000131 | 6 | 390.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 281 | J.24.06.0176 | P55 | P55 | 2024-07-16 11:53 | 2024-07-16 13:13 | 0.001745 | 2.2e-05 | 1 | 79.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 282 | J.24.06.0182 | X54 | X54 | 2024-06-20 14:53 | 2024-06-20 15:30 | 0.00081 | 2.2e-05 | 1 | 37 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 283 | J.24.06.0183 | U92 | U92 | 2024-06-20 15:07 | 2024-06-20 17:21 | 0.002952 | 2.2e-05 | 1 | 134.7 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 284 | J.24.06.0187 | SW62 | SW62 | 2024-12-07 10:15 | 2024-12-07 14:22 | 0.027117 | 0.00011 | 5 | 247.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 285 | J.24.06.0190 | P55 | P55 | 2024-07-16 09:48 | 2024-07-16 17:32 | 0.040683 | 8.8e-05 | 4 | 464.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 286 | J.24.06.0192 | X54 | X54 | 2024-06-21 20:51 | 2024-06-21 21:59 | 0.003018 | 4.4e-05 | 2 | 68.9 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 287 | J.24.06.0199 | SB1142 | SB1142 | 2024-07-17 09:36 | 2024-07-17 12:32 | 0.003858 | 2.2e-05 | 1 | 176 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 288 | J.24.06.0201 | W23 | W23 | 2024-06-24 10:13 | 2024-06-24 12:08 | 0.010088 | 8.8e-05 | 4 | 115.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 289 | J.24.06.0203 | X54 | X54 | 2024-07-22 09:41 | 2024-07-22 16:04 | 0.15941 | 0.000416 | 19 | 382.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 290 | J.24.06.0204 | P45 | P45 | 2024-06-27 10:16 | 2024-06-27 10:33 | 0.004528 | 0.000263 | 12 | 17.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 291 | J.24.06.0205 | T43 | T43 | 2024-10-07 10:16 | 2024-10-07 16:00 | 0.052839 | 0.000153 | 7 | 344.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 292 | J.24.06.0208 | SW65 | SW65 | 2024-10-07 10:06 | 2024-10-07 16:09 | 0.44572 | 0.001227 | 56 | 363.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 293 | J.24.06.0209 | SB1142 | SB1142 | 2024-07-17 10:27 | 2024-07-17 15:03 | 0.060345 | 0.000219 | 10 | 275.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 294 | J.24.06.0214 | KAI_6 | KAI_6 | 2024-07-29 11:43 | 2024-07-29 15:29 | 0.014866 | 6.6e-05 | 3 | 226.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 295 | J.24.06.0224 | H31 | H31 | 2024-07-18 10:09 | 2024-07-18 17:13 | 0.34417 | 0.000811 | 37 | 424.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 296 | J.24.06.0225 | H31 | H31 | 2024-07-19 10:03 | 2024-07-19 14:09 | 0.19991 | 0.000811 | 37 | 246.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 297 | J.24.06.0226 | U92 | U92 | 2024-07-23 09:35 | 2024-07-23 17:22 | 1.7412 | 0.003725 | 170 | 467.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 298 | J.24.06.0229 | U92 | U92 | 2024-07-24 09:41 | 2024-07-24 13:49 | 0.9218 | 0.003725 | 170 | 247.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 299 | J.24.06.0230 | X56 | X56 | 2024-07-15 10:09 | 2024-07-15 12:25 | 0.020863 | 0.000153 | 7 | 136 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 300 | J.24.06.0232 | X52 | X52 | 2024-06-26 20:47 | 2024-06-26 21:43 | 0.002445 | 4.4e-05 | 2 | 55.8 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 301 | J.24.07.0001 | KAI_7 | KAI_7 | 2024-01-07 08:33 | 2024-01-07 09:26 | 0.002319 | 4.4e-05 | 2 | 52.9 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 302 | J.24.07.0003 | KAI_4 | KAI_4 | 2024-07-22 14:05 | 2024-07-22 16:28 | 0.32345 | 0.002257 | 103 | 143.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 303 | J.24.07.0006 | S36 | S36 | 2024-07-22 09:50 | 2024-07-22 14:13 | 0.27056 | 0.00103 | 47 | 262.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 304 | J.24.07.0007 | O76 | O76 | 2024-07-26 09:34 | 2024-07-26 14:24 | 0.96482 | 0.003331 | 152 | 289.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 305 | J.24.07.0019 | K19 | K19 | 2024-07-18 23:04 | 2024-07-19 11:31 | 0.48741 | 0.00092 | 42 | 529.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 306 | J.24.07.0023 | E80 | E80 | 2024-02-07 18:59 | 2024-02-07 19:14 | 0.001353 | 8.8e-05 | 4 | 15.4 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 307 | J.24.07.0025 | Y43 | Y43 | 2024-02-07 19:22 | 2024-02-07 20:55 | 0.002033 | 2.2e-05 | 1 | 92.8 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 308 | J.24.07.0026 | K36 | K36 | 2024-02-07 19:59 | 2024-02-07 20:12 | 0.000291 | 2.2e-05 | 1 | 13.3 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 309 | J.24.07.0029 | W21 | W21 | 2024-03-07 11:26 | 2024-03-07 13:41 | 0.011775 | 8.8e-05 | 4 | 134.3 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 310 | J.24.07.0039 | X56 | X56 | 2024-03-07 12:43 | 2024-03-07 13:55 | 0.001573 | 2.2e-05 | 1 | 71.8 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 311 | J.24.07.0041 | L52 | L52 | 2024-01-08 10:38 | 2024-01-08 15:54 | 0.15913 | 0.000504 | 23 | 315.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 312 | J.24.07.0049 | P45 | P45 | 2024-04-07 10:16 | 2024-04-07 12:00 | 0.004579 | 4.4e-05 | 2 | 104.5 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 313 | J.24.07.0055 | Y33 | Y33 | 2024-07-26 10:41 | 2024-07-26 14:32 | 0.20271 | 0.000877 | 40 | 231.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 314 | J.24.07.0057 | W21 | W21 | 2024-04-07 13:36 | 2024-04-07 14:35 | 0.20518 | 0.003506 | 160 | 58.5 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 315 | J.24.07.0074 | ASY_2772 | ASY_2772 | 2024-06-07 15:02 | 2024-06-07 17:08 | 0.013791 | 0.00011 | 5 | 125.9 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 316 | J.24.07.0085 | KAI_4 | KAI_4 | 2024-04-08 09:30 | 2024-04-08 14:54 | 0.13486 | 0.000416 | 19 | 323.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 317 | J.24.07.0088 | K15 | K15 | 2024-12-08 09:30 | 2024-12-08 18:52 | 0.012313 | 2.2e-05 | 1 | 561.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 318 | J.24.07.0092 | KAI_4 | KAI_4 | 2024-08-07 12:58 | 2024-08-07 18:15 | 0.016956 | 0.000175 | 8 | 96.7 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 319 | J.24.07.0093 | ASY_2692 | ASY_2692 | 2024-12-07 11:11 | 2024-12-07 13:18 | 0.008353 | 6.6e-05 | 3 | 127.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 320 | J.24.07.0095 | U42 | U42 | 2024-07-15 11:13 | 2024-07-15 12:38 | 0.007435 | 8.8e-05 | 4 | 84.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 321 | J.24.07.0096 | U42 | U42 | 2024-07-16 12:05 | 2024-07-16 16:07 | 0.015886 | 6.6e-05 | 3 | 241.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 322 | J.24.07.0097 | ASY_2712 | ASY_2712 | 2024-08-08 10:31 | 2024-08-08 16:31 | 0.47773 | 0.001337 | 61 | 357.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 323 | J.24.07.0098 | X56 | X56 | 2024-12-08 10:07 | 2024-12-08 16:29 | 0.46223 | 0.001249 | 57 | 370 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 324 | J.24.07.0100 | T42 | T42 | 2024-08-07 17:35 | 2024-08-07 19:58 | 0.003123 | 2.2e-05 | 1 | 142.5 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 325 | J.24.07.0103 | SW66 | SW66 | 2024-09-07 08:51 | 2024-09-07 10:04 | 0.009712 | 0.000131 | 6 | 73.9 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 326 | J.24.07.0105 | L52 | L52 | 2024-08-13 10:39 | 2024-08-13 15:54 | 0.027551 | 8.8e-05 | 4 | 314.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 327 | J.24.07.0106 | CUL_1242 | CUL_1242 | 2024-09-07 11:22 | 2024-09-07 11:30 | 0.000168 | 2.2e-05 | 1 | 7.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 328 | J.24.07.0113 | T43 | T43 | 2024-09-07 17:39 | 2024-09-07 20:12 | 0.026817 | 0.000175 | 8 | 153 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 329 | J.24.07.0114 | Y23 | Y23 | 2024-05-08 10:03 | 2024-05-08 15:27 | 0.007103 | 2.2e-05 | 1 | 324.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 330 | J.24.07.0116 | T43 | T43 | 2024-06-08 09:46 | 2024-06-08 17:37 | 1.2916 | 0.002739 | 125 | 471.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 331 | J.24.07.0118 | G32 | G32 | 2024-05-08 09:38 | 2024-05-08 16:33 | 2.1119 | 0.005194 | 237 | 406.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 332 | J.24.07.0119 | P45 | P45 | 2024-10-07 14:12 | 2024-10-07 15:43 | 0.011921 | 0.000131 | 6 | 90.7 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 333 | J.24.07.0128 | SW64 | SW64 | 2024-07-31 11:07 | 2024-07-31 12:45 | 0.00431 | 4.4e-05 | 2 | 98.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 334 | J.24.07.0134 | T41 | T41 | 2024-11-07 14:17 | 2024-11-07 15:14 | 0.002497 | 4.4e-05 | 2 | 57 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 335 | J.24.07.0140 | X52 | X52 | 2024-12-07 15:24 | 2024-12-07 16:46 | 0.47318 | 0.005939 | 271 | 79.7 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 336 | J.24.07.0141 | P35 | P35 | 2024-07-29 10:58 | 2024-07-29 15:30 | 0.087836 | 0.000329 | 15 | 267.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 337 | J.24.07.0152 | SW66 | SW66 | 2024-07-14 15:15 | 2024-07-14 18:34 | 0.82249 | 0.007714 | 352 | 106.6 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 338 | J.24.07.0163 | X55 | X55 | 2024-07-15 10:47 | 2024-07-15 14:06 | 0.004377 | 2.2e-05 | 1 | 199.8 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 339 | J.24.07.0164 | X56 | X56 | 2024-07-15 11:10 | 2024-07-15 12:39 | 0.007848 | 8.8e-05 | 4 | 89.5 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 340 | J.24.07.0177 | ASY_2712 | ASY_2712 | 2024-07-16 14:23 | 2024-07-16 15:05 | 0.003663 | 8.8e-05 | 4 | 41.8 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 341 | J.24.07.0180 | KAI_7 | KAI_7 | 2024-07-17 08:54 | 2024-07-17 10:53 | 0.11207 | 0.000942 | 43 | 118.9 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 342 | J.24.07.0183 | KAI_7 | KAI_7 | 2024-06-08 09:37 | 2024-06-08 12:08 | 0.059912 | 0.000394 | 18 | 151.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 343 | J.24.07.0184 | KAI_7 | KAI_7 | 2024-08-08 09:47 | 2024-08-08 13:59 | 0.022065 | 8.8e-05 | 4 | 251.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 344 | J.24.07.0185 | SW66 | SW66 | 2024-09-08 10:03 | 2024-09-08 15:21 | 0.006966 | 2.2e-05 | 1 | 317.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 345 | J.24.07.0186 | KAI_7 | KAI_7 | 2024-08-15 10:29 | 2024-08-15 15:43 | 0.075821 | 0.000241 | 11 | 314.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 346 | J.24.07.0191 | X53 | X53 | 2024-07-17 16:53 | 2024-07-17 18:02 | 0.006018 | 8.8e-05 | 4 | 68.7 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 347 | J.24.07.0195 | SW65 | SW65 | 2024-07-18 07:26 | 2024-07-18 09:46 | 0.049053 | 0.000351 | 16 | 139.9 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 348 | J.24.07.0198 | U42 | U42 | 2024-07-18 09:18 | 2024-07-18 10:50 | 0.084585 | 0.00092 | 42 | 91.9 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 349 | J.24.07.0202 | T43 | T43 | 2024-07-18 11:49 | 2024-07-18 13:46 | 0.020532 | 0.000175 | 8 | 117.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 350 | J.24.07.0203 | ASY_2772 | ASY_2772 | 2024-07-18 13:11 | 2024-07-18 14:12 | 0.003951 | 6.6e-05 | 3 | 60.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 351 | J.24.07.0205 | KAI_6 | KAI_6 | 2024-07-18 16:44 | 2024-07-18 17:33 | 0.001069 | 2.2e-05 | 1 | 48.8 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 352 | J.24.07.0209 | T43 | T43 | 2024-07-18 18:30 | 2024-07-18 21:39 | 0.033211 | 0.000175 | 8 | 189.4 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 353 | J.24.07.0212 | W21 | W21 | 2024-07-19 07:48 | 2024-07-19 10:04 | 0.011914 | 8.8e-05 | 4 | 135.9 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 354 | J.24.07.0215 | W21 | W21 | 2024-07-19 13:55 | 2024-07-19 15:47 | 0.085857 | 0.000833 | 38 | 103.1 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 355 | J.24.07.0217 | G32 | G32 | 2024-07-19 15:04 | 2024-07-19 16:23 | 0.001748 | 2.2e-05 | 1 | 79.8 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 356 | J.24.07.0229 | U92 | U92 | 2024-07-21 23:07 | 2024-07-22 08:28 | 1.2742 | 0.007999 | 365 | 159.3 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 357 | J.24.07.0230 | X55 | X55 | 2024-08-13 11:44 | 2024-08-13 16:17 | 0.011953 | 4.4e-05 | 2 | 272.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 358 | J.24.07.0252 | ASY_2772 | ASY_2772 | 2024-07-25 07:24 | 2024-07-25 08:49 | 0.014896 | 0.000175 | 8 | 85 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 359 | J.24.07.0254 | U42 | U42 | 2024-08-13 10:10 | 2024-08-13 11:49 | 0.082623 | 0.000833 | 38 | 99.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 360 | J.24.07.0259 | SW64 | SW64 | 2024-08-16 10:06 | 2024-08-16 10:46 | 0.001726 | 4.4e-05 | 2 | 39.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 361 | J.24.07.0265 | P25 | P25 | 2024-07-27 09:27 | 2024-07-27 10:07 | 0.006164 | 0.000153 | 7 | 40.2 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 362 | J.24.07.0267 | SB1062 | SB1062 | 2024-07-27 19:14 | 2024-07-27 21:42 | 1.9721 | 0.025333 | 1156 | 77.8 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 363 | J.24.07.0271 | KAI_6 | KAI_6 | 2024-07-28 12:12 | 2024-07-28 12:52 | 0.005167 | 0.000131 | 6 | 39.3 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 364 | J.24.07.0272 | K36 | K36 | 2024-07-28 14:29 | 2024-07-28 15:01 | 0.001408 | 4.4e-05 | 2 | 32.1 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 365 | J.24.07.0273 | U92 | U92 | 2024-07-28 15:27 | 2024-07-28 16:40 | 0.001619 | 2.2e-05 | 1 | 73.9 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 366 | J.24.07.0277 | X57 | X57 | 2024-07-29 13:20 | 2024-07-29 14:11 | 0.14366 | 0.002805 | 128 | 51.2 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 367 | J.24.07.0278 | U92 | U92 | 2024-08-15 10:34 | 2024-08-15 12:03 | 0.050463 | 0.00057 | 26 | 88.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 368 | J.24.07.0279 | X54 | X54 | 2024-08-20 10:04 | 2024-08-20 16:30 | 0.016886 | 4.4e-05 | 2 | 385.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 369 | J.24.07.0280 | X56 | X56 | 2024-08-21 10:07 | 2024-08-21 15:32 | 0.049743 | 0.000153 | 7 | 324.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 370 | J.24.07.0284 | P45 | P45 | 2024-07-30 10:11 | 2024-07-30 11:23 | 0.004761 | 6.6e-05 | 3 | 72.4 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 371 | J.24.07.0285 | SW66 | SW66 | 2024-07-30 10:25 | 2024-07-30 11:54 | 0.019358 | 0.000219 | 10 | 88.3 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 372 | J.24.07.0286 | X54 | X54 | 2024-08-26 10:38 | 2024-08-26 17:49 | 0.20746 | 0.000482 | 22 | 430.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 373 | J.24.07.0287 | W21 | W21 | 2024-07-30 11:03 | 2024-07-30 12:53 | 0.009603 | 8.8e-05 | 4 | 109.6 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 374 | J.24.07.0288 | SW63 | SW63 | 2024-08-15 09:41 | 2024-08-15 12:33 | 0.003752 | 2.2e-05 | 1 | 171.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 375 | J.24.07.0289 | SW66 | SW66 | 2024-08-15 12:16 | 2024-08-15 13:25 | 0.010597 | 0.000153 | 7 | 69.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 376 | J.24.07.0290 | SW66 | SW66 | 2024-07-30 11:46 | 2024-07-30 12:43 | 0.00249 | 4.4e-05 | 2 | 56.8 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 377 | J.24.07.0291 | SW66 | SW66 | 2024-08-15 14:35 | 2024-08-15 15:07 | 0.001422 | 4.4e-05 | 2 | 32.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 378 | J.24.07.0295 | X54 | X54 | 2024-08-28 10:05 | 2024-08-28 15:21 | 0.15942 | 0.000504 | 23 | 316.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 379 | J.24.07.0296 | T43 | T43 | 2024-07-30 12:48 | 2024-07-30 15:46 | 0.031116 | 0.000175 | 8 | 177.5 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 380 | J.24.07.0298 | KAI_7 | KAI_7 | 2024-08-16 09:57 | 2024-08-16 10:44 | 0.003087 | 6.6e-05 | 3 | 47 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 381 | J.24.07.0299 | H41 | H41 | 2024-02-09 10:18 | 2024-02-09 16:29 | 0.05636 | 0.000153 | 7 | 367.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 382 | J.24.07.0300 | T43 | T43 | 2024-07-30 18:07 | 2024-07-31 14:09 | 0.21066 | 0.000175 | 8 | 1201.6 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 383 | J.24.07.0302 | SW66 | SW66 | 2024-07-30 18:48 | 2024-07-30 20:38 | 0.002409 | 2.2e-05 | 1 | 110 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 384 | J.24.07.0305 | G31 | G31 | 2024-08-22 10:42 | 2024-08-22 14:25 | 0.029223 | 0.000131 | 6 | 222.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 385 | J.24.07.0307 | X53 | X53 | 2024-07-31 11:55 | 2024-07-31 13:56 | 0.010633 | 8.8e-05 | 4 | 121.3 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 386 | J.24.07.0311 | U92 | U92 | 2024-07-31 12:33 | 2024-07-31 14:31 | 0.007722 | 6.6e-05 | 3 | 117.5 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 387 | J.24.07.0314 | P55 | P55 | 2024-07-31 12:17 | 2024-07-31 17:37 | 0.53527 | 0.001709 | 78 | 313.1 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 388 | J.24.07.0315 | U42 | U42 | 2024-07-31 23:57 | 2024-01-08 15:43 | 0.020724 | 2.2e-05 | 1 | 945.7 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 389 | J.24.08.0001 | SW63 | SW63 | 2024-08-16 12:09 | 2024-08-16 13:07 | 0.00127 | 2.2e-05 | 1 | 58 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 390 | J.24.08.0002 | U92 | U92 | 2024-01-08 10:31 | 2024-01-08 11:31 | 0.001301 | 2.2e-05 | 1 | 59.4 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 391 | J.24.08.0003 | SW66 | SW66 | 2024-08-16 14:49 | 2024-08-16 15:35 | 0.004004 | 8.8e-05 | 4 | 45.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 392 | J.24.08.0004 | KAI_6 | KAI_6 | 2024-08-23 10:05 | 2024-08-23 17:23 | 0.47002 | 0.001074 | 49 | 437.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 393 | J.24.08.0005 | KAI_7 | KAI_7 | 2024-08-30 10:31 | 2024-08-30 10:46 | 0.000675 | 4.4e-05 | 2 | 15.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 394 | J.24.08.0006 | W21 | W21 | 2024-02-09 11:47 | 2024-02-09 15:29 | 0.004875 | 2.2e-05 | 1 | 222.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 395 | J.24.08.0007 | Y23 | Y23 | 2024-02-09 10:58 | 2024-02-09 14:13 | 0.004281 | 2.2e-05 | 1 | 195.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 396 | J.24.08.0009 | KAI_6 | KAI_6 | 2024-08-16 10:04 | 2024-08-16 13:39 | 0.014089 | 6.6e-05 | 3 | 214.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 397 | J.24.08.0010 | SW65 | SW65 | 2024-08-22 10:08 | 2024-08-22 12:52 | 0.028822 | 0.000175 | 8 | 164.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 398 | J.24.08.0015 | SW62 | SW62 | 2024-01-08 20:54 | 2024-01-08 21:28 | 0.002939 | 8.8e-05 | 4 | 33.5 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 399 | J.24.08.0016 | L52 | L52 | 2024-02-08 08:49 | 2024-02-08 14:01 | 0.52661 | 0.001687 | 77 | 312.1 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 400 | J.24.08.0023 | SW66 | SW66 | 2024-02-08 18:56 | 2024-02-08 19:57 | 0.018633 | 0.000307 | 14 | 60.7 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 401 | J.24.08.0028 | KAI_7 | KAI_7 | 2024-03-08 10:18 | 2024-03-08 13:01 | 0.01076 | 6.6e-05 | 3 | 163.7 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 402 | J.24.08.0029 | KAI_7 | KAI_7 | 2024-03-08 11:27 | 2024-03-08 13:01 | 0.12664 | 0.001337 | 61 | 94.7 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 403 | J.24.08.0030 | KAI_7 | KAI_7 | 2024-03-08 13:41 | 2024-03-08 14:14 | 0.10331 | 0.003134 | 143 | 33 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 404 | J.24.08.0039 | P55 | P55 | 2024-04-08 11:20 | 2024-04-08 13:47 | 0.035564 | 0.000241 | 11 | 147.5 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 405 | J.24.08.0042 | U42 | U42 | 2024-05-08 06:18 | 2024-05-08 08:42 | 0.069192 | 0.000482 | 22 | 143.5 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 406 | J.24.08.0044 | G32 | G32 | 2024-05-08 09:38 | 2024-05-08 16:25 | 0.017817 | 4.4e-05 | 2 | 406.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 407 | J.24.08.0045 | P45 | P45 | 2024-08-27 13:30 | 2024-08-27 16:33 | 0.26483 | 0.001446 | 66 | 183.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 408 | J.24.08.0047 | SW66 | SW66 | 2024-05-08 11:19 | 2024-05-08 11:38 | 0.001676 | 8.8e-05 | 4 | 19.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 409 | J.24.08.0050 | X55 | X55 | 2024-05-08 12:50 | 2024-05-08 14:03 | 0.001602 | 2.2e-05 | 1 | 73.1 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 410 | J.24.08.0052 | SW62 | SW62 | 2024-05-08 13:53 | 2024-05-08 15:31 | 0.006463 | 6.6e-05 | 3 | 98.3 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 411 | J.24.08.0056 | Y33 | Y33 | 2024-10-09 10:09 | 2024-10-09 12:42 | 0.00671 | 4.4e-05 | 2 | 153.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 412 | J.24.08.0057 | T42 | T42 | 2024-08-28 10:18 | 2024-08-28 18:32 | 0.021641 | 4.4e-05 | 2 | 493.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 413 | J.24.08.0063 | KAI_7 | KAI_7 | 2024-02-09 10:00 | 2024-02-09 12:27 | 0.006433 | 4.4e-05 | 2 | 146.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 414 | J.24.08.0070 | SW64 | SW64 | 2024-08-30 10:03 | 2024-08-30 16:58 | 0.04541 | 0.00011 | 5 | 414.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 415 | J.24.08.0071 | X52 | X52 | 2024-02-09 12:18 | 2024-02-09 15:11 | 0.00756 | 4.4e-05 | 2 | 172.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 416 | J.24.08.0073 | K15 | K15 | 2024-08-29 10:07 | 2024-08-29 12:18 | 0.14647 | 0.001118 | 51 | 131.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 417 | J.24.08.0074 | K15 | K15 | 2024-08-30 10:12 | 2024-08-30 14:59 | 0.3125 | 0.001118 | 102 | 139.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 418 | J.24.08.0076 | ASY_2762 | ASY_2762 | 2024-08-08 18:00 | 2024-08-08 19:07 | 0.00147 | 2.2e-05 | 1 | 67.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 419 | J.24.08.0077 | H31 | H31 | 2024-03-09 10:29 | 2024-03-09 16:41 | 0.024447 | 6.6e-05 | 3 | 371.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 420 | J.24.08.0078 | P55 | P55 | 2024-12-09 10:06 | 2024-12-09 16:55 | 1.7588 | 0.004295 | 196 | 409.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 421 | J.24.08.0085 | X52 | X52 | 2024-11-08 22:04 | 2024-12-08 00:41 | 0.12383 | 0.000789 | 36 | 157 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 422 | J.24.08.0088 | SB1162 | SB1162 | 2024-08-31 09:43 | 2024-08-31 17:29 | 0.010217 | 2.2e-05 | 1 | 466.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 423 | J.24.08.0089 | KAI_6 | KAI_6 | 2024-02-09 10:39 | 2024-02-09 10:43 | 7.6e-05 | 2.2e-05 | 1 | 3.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 424 | J.24.08.0090 | SW64 | SW64 | 2024-02-09 16:03 | 2024-02-09 17:43 | 0.021801 | 0.000219 | 10 | 99.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 425 | J.24.08.0091 | SW66 | SW66 | 2024-04-09 09:36 | 2024-04-09 18:19 | 0.11455 | 0.000219 | 10 | 522.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 426 | J.24.08.0092 | P55 | P55 | 2024-05-09 10:05 | 2024-05-09 16:03 | 0.086331 | 0.000241 | 11 | 358.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 427 | J.24.08.0095 | ASY_2772 | ASY_2772 | 2024-12-08 14:04 | 2024-12-08 16:48 | 0.021513 | 0.000131 | 6 | 163.6 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 428 | J.24.08.0096 | P35 | P35 | 2024-12-08 14:25 | 2024-12-08 20:30 | 0.64177 | 0.003178 | 145 | 202 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 429 | J.24.08.0097 | ASY_2772 | ASY_2772 | 2024-12-08 14:28 | 2024-12-08 16:22 | 0.009908 | 8.8e-05 | 4 | 113 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 430 | J.24.08.0099 | ASY_2712 | ASY_2712 | 2024-12-08 14:41 | 2024-12-08 17:37 | 0.019323 | 0.00011 | 5 | 176.4 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 431 | J.24.08.0103 | P55 | P55 | 2024-12-08 14:58 | 2024-12-08 19:52 | 0.038653 | 0.000131 | 6 | 294 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 432 | J.24.08.0105 | U92 | U92 | 2024-12-08 15:02 | 2024-12-08 20:59 | 1.0728 | 0.007999 | 365 | 134.1 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 433 | J.24.08.0110 | P45 | P45 | 2024-12-08 16:15 | 2024-12-08 20:24 | 0.070856 | 0.000285 | 13 | 248.7 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 434 | J.24.08.0113 | Y43 | Y43 | 2024-12-08 16:34 | 2024-12-08 19:45 | 0.021007 | 0.00011 | 5 | 191.7 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 435 | J.24.08.0115 | G32 | G32 | 2024-12-08 15:48 | 2024-12-08 20:00 | 0.06612 | 0.000263 | 12 | 251.4 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 436 | J.24.08.0116 | P35 | P35 | 2024-12-08 17:23 | 2024-08-13 15:25 | 0.016649 | 4.4e-05 | 4 | 189.9 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 437 | J.24.08.0118 | P25 | P25 | 2024-12-08 17:30 | 2024-12-08 19:10 | 0.00435 | 4.4e-05 | 2 | 99.3 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 438 | J.24.08.0121 | L51 | L51 | 2024-12-08 17:44 | 2024-12-08 18:04 | 0.00343 | 0.000175 | 8 | 19.6 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 439 | J.24.08.0122 | P25 | P25 | 2024-12-08 18:33 | 2024-12-08 19:08 | 0.009252 | 0.000263 | 12 | 35.2 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 440 | J.24.08.0125 | W22 | W22 | 2024-12-08 19:34 | 2024-12-08 20:51 | 0.006737 | 8.8e-05 | 4 | 76.9 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 441 | J.24.08.0127 | P45 | P45 | 2024-12-08 20:54 | 2024-12-08 22:07 | 0.020916 | 0.000285 | 13 | 73.4 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 442 | J.24.08.0133 | Y33 | Y33 | 2024-08-13 12:05 | 2024-08-13 13:54 | 0.048168 | 0.000438 | 20 | 109.9 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 443 | J.24.08.0135 | P45 | P45 | 2024-08-13 12:43 | 2024-08-13 13:09 | 0.001731 | 6.6e-05 | 3 | 26.3 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 444 | J.24.08.0147 | G33 | G33 | 2024-11-09 10:14 | 2024-11-09 13:30 | 0.073329 | 0.000373 | 17 | 196.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 445 | J.24.08.0148 | W21 | W21 | 2024-08-13 16:08 | 2024-08-13 17:43 | 0.30509 | 0.003506 | 160 | 87 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 446 | J.24.08.0150 | U92 | U92 | 2024-12-09 10:33 | 2024-12-09 17:10 | 0.65264 | 0.001644 | 75 | 397.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 447 | J.24.08.0153 | U42 | U42 | 2024-08-13 22:26 | 2024-08-14 14:40 | 0.021357 | 2.2e-05 | 1 | 974.6 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 448 | J.24.08.0162 | ASY_2692 | ASY_2692 | 2024-08-14 11:35 | 2024-08-14 12:02 | 0.001821 | 6.6e-05 | 3 | 27.7 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 449 | J.24.08.0163 | SW64 | SW64 | 2024-08-14 13:10 | 2024-08-14 14:18 | 0.001496 | 2.2e-05 | 1 | 68.3 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 450 | J.24.08.0165 | H31 | H31 | 2024-11-09 13:39 | 2024-11-09 16:14 | 0.044352 | 0.000285 | 13 | 155.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 451 | J.24.08.0166 | P35 | P35 | 2024-08-29 12:38 | 2024-08-29 14:32 | 0.005026 | 4.4e-05 | 2 | 114.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 452 | J.24.08.0167 | U32 | U32 | 2024-11-09 10:38 | 2024-11-09 16:43 | 1.543 | 0.004273 | 195 | 361.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 453 | J.24.08.0168 | W21 | W21 | 2024-08-15 09:22 | 2024-08-15 11:30 | 0.002804 | 2.2e-05 | 1 | 128 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 454 | J.24.08.0172 | P45 | P45 | 2024-08-15 14:21 | 2024-08-15 16:45 | 0.052689 | 0.000438 | 20 | 120.2 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 455 | J.24.08.0173 | W23 | W23 | 2024-09-24 10:03 | 2024-09-24 17:55 | 0.25838 | 0.000548 | 25 | 471.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 456 | J.24.08.0174 | X52 | X52 | 2024-08-16 10:30 | 2024-08-16 16:45 | 0.016456 | 4.4e-05 | 2 | 375.5 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 457 | J.24.08.0176 | SW66 | SW66 | 2024-10-09 10:03 | 2024-10-09 15:55 | 0.18527 | 0.000526 | 24 | 352.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 458 | J.24.08.0178 | G33 | G33 | 2024-08-17 03:00 | 2024-08-17 08:19 | 0.020946 | 6.6e-05 | 3 | 318.6 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 459 | J.24.08.0181 | P55 | P55 | 2024-08-18 10:48 | 2024-08-18 11:49 | 0.001346 | 2.2e-05 | 1 | 61.4 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 460 | J.24.08.0186 | P55 | P55 | 2024-08-18 21:50 | 2024-08-19 18:10 | 2.083 | 0.001709 | 78 | 1218.6 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 461 | J.24.08.0188 | T41 | T41 | 2024-08-18 22:07 | 2024-08-19 12:41 | 1.871 | 0.002323 | 106 | 805.4 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 462 | J.24.08.0199 | W21 | W21 | 2024-08-19 11:26 | 2024-08-19 13:13 | 0.080948 | 0.000833 | 38 | 97.2 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 463 | J.24.08.0206 | S34 | S34 | 2024-09-16 10:04 | 2024-09-16 15:52 | 0.007626 | 2.2e-05 | 1 | 348 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 464 | J.24.08.0207 | L52 | L52 | 2024-08-19 10:31 | 2024-08-19 14:20 | 0.020091 | 8.8e-05 | 4 | 229.2 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 465 | J.24.08.0210 | L52 | L52 | 2024-08-19 15:20 | 2024-08-19 16:33 | 0.012821 | 0.000175 | 8 | 73.1 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 466 | J.24.08.0214 | P55 | P55 | 2024-08-19 19:39 | 2024-08-19 23:03 | 0.008937 | 4.4e-05 | 2 | 203.9 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 467 | J.24.08.0217 | KAI_7 | KAI_7 | 2024-08-20 08:53 | 2024-08-20 14:37 | 0.15069 | 0.000438 | 20 | 343.8 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 468 | J.24.08.0221 | W21 | W21 | 2024-08-20 11:26 | 2024-08-20 12:50 | 0.001832 | 2.2e-05 | 1 | 83.6 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 469 | J.24.08.0224 | SB1142 | SB1142 | 2024-06-09 14:29 | 2024-06-09 15:12 | 0.00954 | 0.000219 | 10 | 43.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 470 | J.24.08.0225 | K19 | K19 | 2024-09-15 10:06 | 2024-09-15 14:34 | 0.023533 | 8.8e-05 | 4 | 268.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 471 | J.24.08.0226 | G31 | G31 | 2024-09-09 10:49 | 2024-09-09 12:45 | 0.005067 | 4.4e-05 | 2 | 115.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 472 | J.24.08.0227 | W21 | W21 | 2024-09-09 14:20 | 2024-09-09 15:39 | 0.005166 | 6.6e-05 | 3 | 78.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 473 | J.24.08.0233 | X54 | X54 | 2024-09-16 10:38 | 2024-09-16 17:16 | 0.095994 | 0.000241 | 11 | 398.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 474 | J.24.08.0236 | H31 | H31 | 2024-08-21 15:48 | 2024-08-21 17:34 | 0.004649 | 4.4e-05 | 2 | 106.1 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 475 | J.24.08.0237 | SB1142 | SB1142 | 2024-09-18 10:07 | 2024-09-18 17:22 | 0.6338 | 0.001468 | 67 | 431.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 476 | J.24.08.0238 | SW66 | SW66 | 2024-09-23 10:05 | 2024-09-23 15:15 | 0.033956 | 0.00011 | 5 | 309.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 477 | J.24.08.0242 | ASY_2762 | ASY_2762 | 2024-09-25 10:19 | 2024-09-25 16:32 | 0.008186 | 2.2e-05 | 1 | 373.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 478 | J.24.08.0243 | G33 | G33 | 2024-09-09 10:37 | 2024-09-09 15:58 | 0.077251 | 0.000241 | 11 | 320.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 479 | J.24.08.0245 | H31 | H31 | 2024-08-22 14:01 | 2024-08-22 18:00 | 0.010486 | 4.4e-05 | 2 | 239.3 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 480 | J.24.08.0253 | U32 | U32 | 2024-09-16 10:27 | 2024-09-16 12:18 | 0.012117 | 0.00011 | 5 | 110.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 481 | J.24.08.0258 | K36 | K36 | 2024-08-23 13:52 | 2024-08-23 16:38 | 0.014551 | 8.8e-05 | 4 | 166 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 482 | J.24.08.0259 | H31 | H31 | 2024-08-23 15:29 | 2024-08-23 15:51 | 0.001413 | 6.6e-05 | 3 | 21.5 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 483 | J.24.08.0265 | X52 | X52 | 2024-08-24 08:29 | 2024-08-24 10:39 | 0.00573 | 4.4e-05 | 2 | 130.7 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 484 | J.24.08.0266 | P55 | P55 | 2024-08-24 11:45 | 2024-08-24 13:32 | 0.007025 | 6.6e-05 | 3 | 106.9 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 485 | J.24.08.0272 | ASY_2762 | ASY_2762 | 2024-08-25 10:57 | 2024-08-25 11:38 | 0.00091 | 2.2e-05 | 1 | 41.5 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 486 | J.24.08.0273 | SB1142 | SB1142 | 2024-08-25 19:40 | 2024-08-25 20:05 | 0.59348 | 0.022988 | 1049 | 25.8 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 487 | J.24.08.0279 | U92 | U92 | 2024-09-30 09:42 | 2024-09-30 17:06 | 0.00974 | 2.2e-05 | 1 | 444.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 488 | J.24.08.0280 | U92 | U92 | 2024-01-10 09:05 | 2024-01-10 17:29 | 0.011054 | 2.2e-05 | 1 | 504.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 489 | J.24.08.0281 | N44 | N44 | 2024-02-10 09:16 | 2024-02-10 17:06 | 0.051499 | 0.00011 | 5 | 470 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 490 | J.24.08.0288 | U92 | U92 | 2024-02-10 08:38 | 2024-02-10 17:03 | 0.011076 | 2.2e-05 | 1 | 505.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 491 | J.24.08.0289 | U92 | U92 | 2024-03-10 08:44 | 2024-03-10 15:13 | 0.008521 | 2.2e-05 | 1 | 388.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 492 | J.24.08.0290 | X54 | X54 | 2024-04-10 09:21 | 2024-04-10 10:55 | 0.00205 | 2.2e-05 | 1 | 93.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 493 | J.24.08.0292 | SW62 | SW62 | 2024-09-20 10:04 | 2024-09-20 17:10 | 0.72555 | 0.001731 | 79 | 419.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 494 | J.24.08.0294 | X54 | X54 | 2024-08-10 09:32 | 2024-08-10 16:14 | 0.17906 | 0.000482 | 22 | 371.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 495 | J.24.08.0295 | SW64 | SW64 | 2024-09-26 10:08 | 2024-09-26 17:15 | 0.3184 | 0.000745 | 34 | 427.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 496 | J.24.08.0296 | SW62 | SW62 | 2024-09-13 10:01 | 2024-09-13 17:13 | 1.4018 | 0.003243 | 148 | 432.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 497 | J.24.08.0297 | P25 | P25 | 2024-09-27 10:09 | 2024-09-27 16:37 | 0.44266 | 0.00114 | 52 | 388.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 498 | J.24.08.0298 | X54 | X54 | 2024-08-28 12:48 | 2024-08-28 13:52 | 0.002804 | 4.4e-05 | 2 | 64 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 499 | J.24.08.0302 | KAI_7 | KAI_7 | 2024-08-29 07:53 | 2024-08-29 08:44 | 0.011366 | 0.000219 | 10 | 51.9 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 500 | J.24.08.0303 | ASY_2772 | ASY_2772 | 2024-09-25 10:06 | 2024-09-25 17:59 | 0.29267 | 0.000679 | 31 | 430.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 501 | J.24.08.0305 | ASY_2762 | ASY_2762 | 2024-08-29 11:13 | 2024-08-29 12:10 | 0.065429 | 0.00114 | 52 | 57.4 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 502 | J.24.08.0308 | P55 | P55 | 2024-08-29 13:04 | 2024-08-29 16:59 | 0.02581 | 0.00011 | 5 | 235.6 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 503 | J.24.08.0310 | Y23 | Y23 | 2024-08-29 15:29 | 2024-08-29 16:20 | 0.004454 | 8.8e-05 | 4 | 50.8 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 504 | J.24.08.0312 | Y43 | Y43 | 2024-08-29 16:59 | 2024-08-29 18:04 | 0.002842 | 4.4e-05 | 2 | 64.8 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 505 | J.24.08.0313 | X53 | X53 | 2024-08-29 18:04 | 2024-08-29 18:52 | 0.001046 | 2.2e-05 | 1 | 47.8 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 506 | J.24.08.0315 | Y43 | Y43 | 2024-08-29 19:15 | 2024-08-29 23:00 | 0.093476 | 0.000416 | 19 | 224.5 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 507 | J.24.08.0317 | KAI_5 | KAI_5 | 2024-09-25 10:30 | 2024-09-25 15:49 | 0.020983 | 6.6e-05 | 3 | 319.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 508 | J.24.08.0319 | KAI_6 | KAI_6 | 2024-06-10 09:07 | 2024-06-10 14:07 | 0.059078 | 0.000197 | 9 | 299.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 509 | J.24.08.0321 | X52 | X52 | 2024-10-10 09:00 | 2024-10-10 13:49 | 0.006335 | 2.2e-05 | 1 | 289.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 510 | J.24.08.0322 | ASY_2772 | ASY_2772 | 2024-09-30 08:30 | 2024-09-30 17:51 | 0.54087 | 0.000964 | 44 | 560.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 511 | J.24.08.0324 | P45 | P45 | 2024-08-30 17:04 | 2024-08-31 16:02 | 0.030193 | 2.2e-05 | 1 | 1377.8 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 512 | J.24.08.0325 | W21 | W21 | 2024-08-30 18:32 | 2024-08-30 19:54 | 0.003588 | 4.4e-05 | 2 | 81.9 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 513 | J.24.08.0335 | SW66 | SW66 | 2024-08-31 19:05 | 2024-08-31 21:13 | 0.016852 | 0.000131 | 6 | 128.2 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 514 | J.24.08.0337 | SW66 | SW66 | 2024-08-31 19:22 | 2024-08-31 21:28 | 0.033069 | 0.000263 | 12 | 125.8 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 515 | J.24.09.0003 | T42 | T42 | 2024-01-09 19:56 | 2024-01-09 21:32 | 0.004221 | 4.4e-05 | 2 | 96.3 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 516 | J.24.09.0004 | T43 | T43 | 2024-01-10 08:51 | 2024-01-10 17:55 | 0.11905 | 0.000219 | 10 | 543.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 517 | J.24.09.0005 | KAI_7 | KAI_7 | 2024-02-09 10:52 | 2024-02-09 11:25 | 0.002925 | 8.8e-05 | 4 | 33.4 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 518 | J.24.09.0006 | K19 | K19 | 2024-09-24 10:04 | 2024-09-24 14:53 | 0.10115 | 0.000351 | 16 | 288.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 519 | J.24.09.0007 | W21 | W21 | 2024-09-18 10:39 | 2024-09-18 12:59 | 0.16504 | 0.001183 | 54 | 139.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 520 | J.24.09.0008 | P25 | P25 | 2024-02-09 16:31 | 2024-02-09 20:06 | 2.7723 | 0.025267 | 2305 | 54.9 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 521 | J.24.09.0010 | W23 | W23 | 2024-02-09 17:12 | 2024-02-09 18:27 | 0.004911 | 6.6e-05 | 3 | 74.7 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 522 | J.24.09.0015 | H41 | H41 | 2024-02-09 19:44 | 2024-02-09 20:06 | 0.24084 | 0.022725 | 1037 | 10.6 | Unplanned | Human Error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 523 | J.24.09.0017 | X56 | X56 | 2024-03-09 06:47 | 2024-03-09 08:54 | 0.016697 | 0.000131 | 6 | 127 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 524 | J.24.09.0022 | W23 | W23 | 2024-03-09 10:44 | 2024-03-09 12:45 | 0.0663 | 0.000548 | 25 | 121 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 525 | J.24.09.0023 | T41 | T41 | 2024-03-09 11:01 | 2024-03-09 11:31 | 0.001327 | 4.4e-05 | 2 | 30.3 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 526 | J.24.09.0025 | KAI_7 | KAI_7 | 2024-03-09 11:14 | 2024-03-09 12:10 | 0.001229 | 2.2e-05 | 1 | 56.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 527 | J.24.09.0027 | G31 | G31 | 2024-09-23 10:26 | 2024-09-23 16:33 | 0.01608 | 4.4e-05 | 2 | 366.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 528 | J.24.09.0028 | SW65 | SW65 | 2024-10-14 09:02 | 2024-10-14 14:22 | 0.021044 | 6.6e-05 | 3 | 320.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 529 | J.24.09.0030 | X53 | X53 | 2024-03-09 18:18 | 2024-03-09 19:15 | 0.001252 | 2.2e-05 | 1 | 57.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 530 | J.24.09.0034 | P55 | P55 | 2024-04-09 11:13 | 2024-04-09 12:18 | 0.001431 | 2.2e-05 | 1 | 65.3 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 531 | J.24.09.0042 | SW66 | SW66 | 2024-03-10 10:03 | 2024-03-10 16:56 | 0.56303 | 0.001578 | 144 | 178.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 532 | J.24.09.0044 | SW64 | SW64 | 2024-09-25 10:17 | 2024-09-25 12:51 | 0.006772 | 4.4e-05 | 2 | 154.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 533 | J.24.09.0050 | P25 | P25 | 2024-10-16 09:06 | 2024-10-16 15:26 | 0.04561 | 0.000131 | 11 | 189.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 534 | J.24.09.0052 | SW65 | SW65 | 2024-10-18 09:05 | 2024-10-18 15:36 | 0.14533 | 0.000373 | 17 | 390.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 535 | J.24.09.0056 | X52 | X52 | 2024-07-09 05:30 | 2024-07-09 07:46 | 0.071502 | 0.000526 | 24 | 136 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 536 | J.24.09.0062 | P25 | P25 | 2024-07-09 14:03 | 2024-07-09 16:54 | 0.1725 | 0.001271 | 58 | 135.7 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 537 | J.24.09.0065 | Y43 | Y43 | 2024-11-10 08:38 | 2024-11-10 11:39 | 0.23858 | 0.001424 | 65 | 167.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 538 | J.24.09.0066 | SB1152 | SB1152 | 2024-11-10 12:42 | 2024-11-10 14:49 | 0.33367 | 0.00263 | 120 | 126.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 539 | J.24.09.0067 | T43 | T43 | 2024-01-10 08:51 | 2024-01-10 09:17 | 0.006239 | 0.000241 | 11 | 25.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 540 | J.24.09.0068 | SB1142 | SB1142 | 2024-09-30 10:10 | 2024-09-30 14:46 | 0.20543 | 0.000745 | 34 | 275.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 541 | J.24.09.0073 | U32 | U32 | 2024-10-09 09:29 | 2024-10-09 10:10 | 0.43614 | 0.010957 | 500 | 39.8 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 542 | J.24.09.0077 | U92 | U92 | 2024-10-16 09:02 | 2024-10-16 15:04 | 0.70724 | 0.00195 | 89 | 362.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 543 | J.24.09.0078 | U92 | U92 | 2024-10-17 08:34 | 2024-10-17 13:14 | 0.073633 | 0.000263 | 12 | 280 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 544 | J.24.09.0080 | X54 | X54 | 2024-10-09 17:25 | 2024-10-09 17:59 | 0.002212 | 6.6e-05 | 3 | 33.7 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 545 | J.24.09.0081 | K15 | K15 | 2024-03-10 09:37 | 2024-03-10 13:25 | 0.23473 | 0.00103 | 47 | 227.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 546 | J.24.09.0083 | KAI_4 | KAI_4 | 2024-11-09 17:22 | 2024-11-09 18:32 | 0.004633 | 6.6e-05 | 3 | 70.5 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 547 | J.24.09.0091 | X53 | X53 | 2024-12-09 08:06 | 2024-12-09 12:18 | 0.678 | 0.002695 | 123 | 251.5 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 548 | J.24.09.0093 | P25 | P25 | 2024-10-22 09:12 | 2024-10-22 15:46 | 0.12074 | 0.000307 | 14 | 393.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 549 | J.24.09.0094 | U92 | U92 | 2024-10-22 08:20 | 2024-10-22 14:28 | 0.016125 | 4.4e-05 | 2 | 367.9 | Planned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 550 | J.24.09.0096 | P25 | P25 | 2024-10-14 09:44 | 2024-10-14 16:39 | 0.39164 | 0.000942 | 43 | 415.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 551 | J.24.09.0098 | W23 | W23 | 2024-10-21 09:01 | 2024-10-21 16:30 | 0.94805 | 0.002213 | 101 | 428.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 552 | J.24.09.0105 | SB1172 | SB1172 | 2024-10-15 09:43 | 2024-10-15 15:51 | 0.13702 | 0.000373 | 17 | 367.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 553 | J.24.09.0106 | P25 | P25 | 2024-09-13 11:45 | 2024-09-13 15:44 | 0.97665 | 0.017729 | 810 | 55 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 554 | J.24.09.0111 | SW66 | SW66 | 2024-09-14 17:08 | 2024-09-14 18:13 | 0.001418 | 2.2e-05 | 1 | 64.7 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 555 | J.24.09.0114 | K19 | K19 | 2024-09-15 10:06 | 2024-09-15 14:34 | 0.005883 | 2.2e-05 | 1 | 268.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 556 | J.24.09.0118 | L52 | L52 | 2024-09-15 10:18 | 2024-09-15 14:49 | 0.13682 | 0.000504 | 23 | 271.5 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 557 | J.24.09.0120 | L52 | L52 | 2024-09-15 16:31 | 2024-09-15 20:05 | 0.10786 | 0.000504 | 23 | 214 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 558 | J.24.09.0127 | P55 | P55 | 2024-09-16 17:56 | 2024-09-16 19:45 | 0.007159 | 6.6e-05 | 3 | 108.9 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 559 | J.24.09.0133 | X52 | X52 | 2024-09-16 23:02 | 2024-09-17 03:01 | 0.17794 | 0.000745 | 34 | 238.8 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 560 | J.24.09.0140 | U42 | U42 | 2024-10-23 09:33 | 2024-10-23 12:00 | 0.022478 | 0.000153 | 7 | 146.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 561 | J.24.09.0141 | K36 | K36 | 2024-08-10 09:50 | 2024-08-10 13:40 | 0.02015 | 8.8e-05 | 4 | 229.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 562 | J.24.09.0142 | L52 | L52 | 2024-10-24 09:50 | 2024-10-24 16:41 | 0.20734 | 0.000504 | 23 | 411.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 563 | J.24.09.0146 | SB1142 | SB1142 | 2024-09-18 10:07 | 2024-09-18 17:16 | 0.047017 | 0.00011 | 5 | 429.1 | Unplanned | Human Error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 564 | J.24.09.0151 | P45 | P45 | 2024-11-10 09:18 | 2024-11-10 15:44 | 0.33057 | 0.000855 | 39 | 386.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 565 | J.24.09.0152 | T43 | T43 | 2024-09-18 16:30 | 2024-09-18 17:00 | 0.002003 | 6.6e-05 | 3 | 30.5 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 566 | J.24.09.0162 | X57 | X57 | 2024-09-10 09:04 | 2024-09-10 15:18 | 0.024564 | 6.6e-05 | 3 | 373.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 567 | J.24.09.0163 | P45 | P45 | 2024-10-23 09:17 | 2024-10-23 15:45 | 0.34829 | 0.000898 | 41 | 387.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 568 | J.24.09.0169 | P55 | P55 | 2024-09-20 11:24 | 2024-09-20 17:53 | 0.017047 | 4.4e-05 | 2 | 388.9 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 569 | J.24.09.0171 | P45 | P45 | 2024-09-20 15:40 | 2024-09-20 17:40 | 0.097435 | 0.000811 | 37 | 120.2 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 570 | J.24.09.0174 | ASY_2712 | ASY_2712 | 2024-09-21 10:36 | 2024-09-21 11:45 | 0.004556 | 6.6e-05 | 3 | 69.3 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 571 | J.24.09.0179 | SW66 | SW66 | 2024-09-22 16:26 | 2024-09-22 17:05 | 0.30277 | 0.007714 | 352 | 39.3 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 572 | J.24.09.0183 | P25 | P25 | 2024-10-30 09:11 | 2024-10-30 15:26 | 0.44418 | 0.001183 | 54 | 375.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 573 | J.24.09.0185 | P25 | P25 | 2024-10-31 09:00 | 2024-10-31 16:35 | 0.68712 | 0.001512 | 69 | 454.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 574 | J.24.09.0187 | Y43 | Y43 | 2024-09-24 00:03 | 2024-09-24 03:58 | 0.097716 | 0.000416 | 19 | 234.7 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 575 | J.24.09.0188 | X54 | X54 | 2024-09-24 07:49 | 2024-09-24 12:48 | 0.032746 | 0.00011 | 5 | 298.9 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 576 | J.24.09.0189 | X52 | X52 | 2024-09-24 08:58 | 2024-09-24 11:47 | 0.003723 | 2.2e-05 | 1 | 169.9 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 577 | J.24.09.0190 | SW66 | SW66 | 2024-09-24 10:47 | 2024-09-24 13:42 | 0.019237 | 0.00011 | 5 | 175.6 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 578 | J.24.09.0192 | SW63 | SW63 | 2024-09-24 13:15 | 2024-09-24 13:55 | 0.013535 | 0.000351 | 16 | 38.6 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 579 | J.24.09.0197 | ASY_2692 | ASY_2692 | 2024-10-17 09:10 | 2024-10-17 12:23 | 0.084429 | 0.000438 | 20 | 192.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 580 | J.24.09.0198 | X54 | X54 | 2024-10-18 09:07 | 2024-10-18 13:53 | 0.025028 | 8.8e-05 | 4 | 285.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 581 | J.24.09.0200 | P45 | P45 | 2024-10-25 09:20 | 2024-10-25 14:22 | 0.22518 | 0.000745 | 34 | 302.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 582 | J.24.09.0202 | P45 | P45 | 2024-10-25 08:39 | 2024-10-25 16:10 | 0.007173 | 0.000898 | 82 | 4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 583 | J.24.09.0204 | ASY_2692 | ASY_2692 | 2024-10-22 09:04 | 2024-10-22 14:37 | 0.072796 | 0.000219 | 10 | 332.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 584 | J.24.09.0205 | SW64 | SW64 | 2024-09-25 19:32 | 2024-09-25 20:59 | 0.007661 | 8.8e-05 | 4 | 87.4 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 585 | J.24.09.0207 | X54 | X54 | 2024-09-25 21:34 | 2024-09-26 15:17 | 2.9675 | 0.003243 | 148 | 915 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 586 | J.24.09.0208 | X54 | X54 | 2024-09-25 21:41 | 2024-09-25 23:49 | 0.49144 | 0.003857 | 176 | 127.4 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 587 | J.24.09.0210 | SW66 | SW66 | 2024-09-26 08:17 | 2024-09-26 09:52 | 0.028885 | 0.000307 | 14 | 94.2 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 588 | J.24.09.0219 | X54 | X54 | 2024-09-26 16:30 | 2024-09-26 18:47 | 0.006035 | 4.4e-05 | 2 | 137.7 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 589 | J.24.09.0220 | S34 | S34 | 2024-09-26 18:28 | 2024-09-26 19:05 | 0.000813 | 2.2e-05 | 1 | 37.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 590 | J.24.09.0221 | ASY_2692 | ASY_2692 | 2024-10-29 09:17 | 2024-10-29 14:40 | 0.021223 | 6.6e-05 | 3 | 322.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 591 | J.24.09.0222 | ASY_2692 | ASY_2692 | 2024-10-29 09:20 | 2024-10-29 14:42 | 0.10578 | 0.000329 | 15 | 321.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 592 | J.24.09.0234 | U32 | U32 | 2024-09-29 14:41 | 2024-09-29 19:02 | 0.10282 | 0.000394 | 18 | 260.7 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 593 | J.24.09.0235 | KAI_7 | KAI_7 | 2024-10-21 09:15 | 2024-10-21 10:42 | 0.005742 | 6.6e-05 | 3 | 87.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 594 | J.24.09.0238 | KAI_7 | KAI_7 | 2024-10-18 08:40 | 2024-10-18 11:16 | 0.003433 | 2.2e-05 | 1 | 156.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 595 | J.24.09.0239 | ASY_2692 | ASY_2692 | 2024-04-11 09:07 | 2024-04-11 15:40 | 0.24084 | 0.000614 | 28 | 392.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 596 | J.24.10.0001 | KAI_6 | KAI_6 | 2024-01-10 08:55 | 2024-01-10 15:33 | 2.559 | 0.006443 | 294 | 397.2 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 597 | J.24.10.0004 | KKA_1432 | KKA_1432 | 2024-10-21 10:04 | 2024-10-21 14:33 | 0.01765 | 6.6e-05 | 3 | 268.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 598 | J.24.10.0009 | SB1152 | SB1152 | 2024-10-18 08:52 | 2024-10-18 11:09 | 0.003003 | 2.2e-05 | 1 | 137.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 599 | J.24.10.0013 | SW66 | SW66 | 2024-02-10 13:58 | 2024-02-10 15:14 | 0.031617 | 0.000416 | 19 | 75.9 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 600 | J.24.10.0021 | E80 | E80 | 2024-03-10 08:31 | 2024-03-10 17:38 | 0.27192 | 0.001293 | 59 | 210.3 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 601 | J.24.10.0024 | SW63 | SW63 | 2024-03-10 11:41 | 2024-03-10 12:44 | 0.001382 | 2.2e-05 | 1 | 63.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 602 | J.24.10.0026 | X54 | X54 | 2024-03-10 15:10 | 2024-03-10 16:18 | 0.007455 | 0.00011 | 5 | 68 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 603 | J.24.10.0029 | SW63 | SW63 | 2024-03-10 16:25 | 2024-03-10 16:56 | 0.064607 | 0.002082 | 95 | 31 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 604 | J.24.10.0033 | SB1142 | SB1142 | 2024-03-10 20:47 | 2024-04-10 00:09 | 0.11087 | 0.000548 | 25 | 202.4 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 605 | J.24.10.0034 | L52 | L52 | 2024-03-10 21:06 | 2024-03-10 23:10 | 0.062626 | 0.000504 | 23 | 124.3 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 606 | J.24.10.0042 | SW65 | SW65 | 2024-04-10 14:46 | 2024-04-10 15:01 | 0.000636 | 4.4e-05 | 2 | 14.5 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 607 | J.24.10.0044 | L52 | L52 | 2024-05-10 00:18 | 2024-05-10 11:06 | 0.32666 | 0.000504 | 23 | 648.1 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 608 | J.24.10.0047 | SB1062 | SB1062 | 2024-05-10 20:08 | 2024-05-10 21:35 | 0.022752 | 0.000263 | 12 | 86.5 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 609 | J.24.10.0050 | P45 | P45 | 2024-06-10 15:04 | 2024-06-10 15:45 | 0.21727 | 0.005347 | 488 | 20.3 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 610 | J.24.10.0053 | P45 | P45 | 2024-06-10 15:18 | 2024-06-10 18:25 | 0.65643 | 0.012513 | 571 | 52.5 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 611 | J.24.10.0056 | L52 | L52 | 2024-07-10 01:32 | 2024-07-10 12:58 | 0.3455 | 0.000504 | 23 | 685.5 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 612 | J.24.10.0059 | K19 | K19 | 2024-10-30 09:47 | 2024-10-30 14:54 | 0.033078 | 0.00011 | 10 | 150.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 613 | J.24.10.0060 | SW66 | SW66 | 2024-07-10 09:59 | 2024-07-10 10:05 | 0.00015 | 2.2e-05 | 1 | 6.9 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 614 | J.24.10.0062 | W21 | W21 | 2024-07-10 13:09 | 2024-07-10 13:19 | 0.000639 | 6.6e-05 | 3 | 9.7 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 615 | J.24.10.0064 | T43 | T43 | 2024-07-10 14:06 | 2024-07-10 15:56 | 0.004826 | 4.4e-05 | 2 | 110.1 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 616 | J.24.10.0066 | N44 | N44 | 2024-08-10 01:32 | 2024-08-10 07:57 | 0.075884 | 0.000197 | 9 | 384.8 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 617 | J.24.10.0069 | KAI_4 | KAI_4 | 2024-12-11 09:39 | 2024-12-11 15:00 | 0.39314 | 0.001227 | 56 | 320.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 618 | J.24.10.0075 | SW65 | SW65 | 2024-08-10 15:49 | 2024-08-10 17:09 | 0.02777 | 0.000351 | 16 | 79.2 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 619 | J.24.10.0077 | X54 | X54 | 2024-08-10 17:10 | 2024-08-10 18:49 | 0.010839 | 0.00011 | 5 | 98.9 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 620 | J.24.10.0080 | N34 | N34 | 2024-08-10 21:56 | 2024-08-10 22:42 | 0.059627 | 0.001293 | 59 | 46.1 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 621 | J.24.10.0083 | T42 | T42 | 2024-05-11 09:53 | 2024-05-11 12:43 | 0.089087 | 0.000526 | 24 | 169.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 622 | J.24.10.0084 | T42 | T42 | 2024-05-11 13:49 | 2024-05-11 15:08 | 0.03111 | 0.000394 | 18 | 78.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 623 | J.24.10.0088 | KAI_7 | KAI_7 | 2024-09-10 15:50 | 2024-09-10 15:59 | 0.001205 | 0.000131 | 6 | 9.2 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 624 | J.24.10.0091 | W23 | W23 | 2024-09-10 22:02 | 2024-09-10 22:06 | 0.0468 | 0.011461 | 523 | 4.1 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 625 | J.24.10.0092 | W22 | W22 | 2024-09-10 22:18 | 2024-09-10 22:20 | 0.007971 | 0.003046 | 139 | 2.6 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 626 | J.24.10.0093 | W21 | W21 | 2024-09-10 22:23 | 2024-09-10 22:26 | 0.016408 | 0.005895 | 269 | 2.8 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 627 | J.24.10.0096 | SW65 | SW65 | 2024-10-10 00:41 | 2024-10-10 03:14 | 0.050409 | 0.000329 | 15 | 153.4 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 628 | J.24.10.0099 | P35 | P35 | 2024-10-31 09:13 | 2024-10-31 15:19 | 0.41658 | 0.00114 | 52 | 365.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 629 | J.24.10.0100 | S34 | S34 | 2024-05-11 09:56 | 2024-05-11 13:52 | 0.077594 | 0.000329 | 15 | 236.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 630 | J.24.10.0104 | G33 | G33 | 2024-07-11 09:27 | 2024-07-11 16:07 | 0.008753 | 2.2e-05 | 1 | 399.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 631 | J.24.10.0106 | Y43 | Y43 | 2024-11-10 14:37 | 2024-11-10 15:26 | 0.00108 | 2.2e-05 | 1 | 49.3 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 632 | J.24.10.0107 | O76 | O76 | 2024-05-11 08:55 | 2024-05-11 17:08 | 0.021609 | 4.4e-05 | 2 | 493 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 633 | J.24.10.0108 | SW63 | SW63 | 2024-11-10 15:15 | 2024-11-10 15:37 | 0.000472 | 2.2e-05 | 1 | 21.5 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 634 | J.24.10.0109 | O76 | O76 | 2024-06-11 08:36 | 2024-06-11 18:13 | 0.02501 | 4.4e-05 | 2 | 570.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 635 | J.24.10.0110 | O76 | O76 | 2024-07-11 08:37 | 2024-07-11 15:51 | 0.019052 | 4.4e-05 | 2 | 434.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 636 | J.24.10.0111 | O76 | O76 | 2024-08-11 08:36 | 2024-08-11 13:35 | 0.013069 | 4.4e-05 | 2 | 298.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 637 | J.24.10.0114 | X57 | X57 | 2024-12-10 23:18 | 2024-10-13 00:58 | 0.28079 | 0.002805 | 128 | 100.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 638 | J.24.10.0116 | U92 | U92 | 2024-10-14 10:25 | 2024-10-14 20:39 | 0.013454 | 2.2e-05 | 1 | 613.9 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 639 | J.24.10.0118 | KKA_1432 | KKA_1432 | 2024-07-11 08:35 | 2024-07-11 17:30 | 0.035123 | 6.6e-05 | 3 | 534.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 640 | J.24.10.0124 | SW65 | SW65 | 2024-06-11 11:06 | 2024-06-11 15:33 | 0.099588 | 0.000373 | 17 | 267.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 641 | J.24.10.0125 | SW63 | SW63 | 2024-10-15 06:54 | 2024-10-15 09:26 | 0.009992 | 6.6e-05 | 3 | 152 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 642 | J.24.10.0127 | ASY_2762 | ASY_2762 | 2024-12-11 08:33 | 2024-12-11 10:21 | 0.002363 | 2.2e-05 | 1 | 107.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 643 | J.24.10.0129 | K15 | K15 | 2024-11-20 08:36 | 2024-11-20 16:22 | 1.6097 | 0.003506 | 160 | 459.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 644 | J.24.10.0131 | P35 | P35 | 2024-10-16 10:15 | 2024-10-16 11:02 | 0.001026 | 2.2e-05 | 1 | 46.8 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 645 | J.24.10.0146 | T42 | T42 | 2024-10-17 10:35 | 2024-10-17 10:53 | 0.000397 | 2.2e-05 | 1 | 18.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 646 | J.24.10.0147 | KAI_6 | KAI_6 | 2024-10-17 12:01 | 2024-10-17 12:47 | 0.02543 | 0.000548 | 25 | 46.4 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 647 | J.24.10.0149 | KAI_6 | KAI_6 | 2024-10-17 13:01 | 2024-10-17 17:49 | 0.075272 | 0.004865 | 222 | 15.5 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 648 | J.24.10.0151 | T43 | T43 | 2024-11-20 09:09 | 2024-11-20 15:25 | 0.070414 | 0.000197 | 10 | 321.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 649 | J.24.10.0155 | SB1142 | SB1142 | 2024-11-26 08:37 | 2024-11-26 18:05 | 0.37635 | 0.000679 | 31 | 554 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 650 | J.24.10.0156 | ASY_2772 | ASY_2772 | 2024-10-17 14:49 | 2024-10-17 16:18 | 0.001765 | 2.2e-05 | 2 | 40.3 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 651 | J.24.10.0160 | H31 | H31 | 2024-10-18 09:34 | 2024-10-18 13:33 | 0.015698 | 6.6e-05 | 3 | 238.8 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 652 | J.24.10.0161 | O76 | O76 | 2024-11-11 11:21 | 2024-11-11 15:01 | 0.009637 | 4.4e-05 | 2 | 219.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 653 | J.24.10.0162 | O76 | O76 | 2024-12-11 08:37 | 2024-12-11 15:18 | 0.017549 | 4.4e-05 | 2 | 400.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 654 | J.24.10.0163 | O76 | O76 | 2024-11-13 08:36 | 2024-11-13 15:23 | 0.017841 | 4.4e-05 | 2 | 407.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 655 | J.24.10.0165 | N34 | N34 | 2024-10-19 03:22 | 2024-10-19 04:27 | 1.4299 | 0.022243 | 1015 | 64.3 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 656 | J.24.10.0166 | N34 | N34 | 2024-10-19 03:22 | 2024-10-19 14:24 | 0.043483 | 6.6e-05 | 3 | 661.4 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 657 | J.24.10.0170 | SW64 | SW64 | 2024-10-20 07:19 | 2024-10-20 09:12 | 0.004946 | 4.4e-05 | 2 | 112.9 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 658 | J.24.10.0172 | P25 | P25 | 2024-10-21 07:44 | 2024-10-21 11:16 | 0.59735 | 0.003572 | 326 | 83.6 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 659 | J.24.10.0176 | N34 | N34 | 2024-10-21 12:19 | 2024-10-21 16:27 | 0.005448 | 2.2e-05 | 1 | 248.6 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 660 | J.24.10.0179 | G31 | G31 | 2024-11-14 09:38 | 2024-11-14 13:57 | 0.017071 | 6.6e-05 | 3 | 259.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 661 | J.24.10.0184 | X55 | X55 | 2024-10-22 04:09 | 2024-10-22 06:09 | 0.005276 | 4.4e-05 | 2 | 120.4 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 662 | J.24.10.0187 | KKA_1432 | KKA_1432 | 2024-10-22 09:41 | 2024-10-22 14:27 | 0.018803 | 6.6e-05 | 3 | 286 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 663 | J.24.10.0188 | K35 | K35 | 2024-11-18 10:00 | 2024-11-18 14:14 | 0.15613 | 0.000614 | 28 | 254.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 664 | J.24.10.0190 | T43 | T43 | 2024-10-22 11:31 | 2024-10-22 11:42 | 0.000236 | 2.2e-05 | 1 | 10.8 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 665 | J.24.10.0193 | L52 | L52 | 2024-10-22 14:01 | 2024-10-22 15:04 | 0.001367 | 2.2e-05 | 1 | 62.4 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 666 | J.24.10.0196 | X53 | X53 | 2024-10-22 15:35 | 2024-10-22 17:03 | 0.001926 | 2.2e-05 | 1 | 87.9 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 667 | J.24.10.0199 | SW63 | SW63 | 2024-10-22 19:15 | 2024-10-22 22:38 | 0.21285 | 0.00114 | 52 | 186.8 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 668 | J.24.10.0204 | SW66 | SW66 | 2024-10-23 10:56 | 2024-10-23 11:47 | 0.003312 | 6.6e-05 | 3 | 50.4 | Planned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 669 | J.24.10.0208 | SW65 | SW65 | 2024-10-23 13:57 | 2024-10-23 14:43 | 0.001996 | 4.4e-05 | 2 | 45.5 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 670 | J.24.10.0211 | SB1162 | SB1162 | 2024-10-23 14:37 | 2024-10-23 17:04 | 0.42971 | 0.002915 | 133 | 147.4 | Unplanned | Adverse Environment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 671 | J.24.10.0224 | X54 | X54 | 2024-10-23 23:25 | 2024-10-24 00:49 | 0.038718 | 0.00046 | 21 | 84.1 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 672 | J.24.10.0229 | O76 | O76 | 2024-11-18 10:26 | 2024-11-18 15:39 | 0.02054 | 6.6e-05 | 3 | 312.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 673 | J.24.10.0230 | O76 | O76 | 2024-11-19 08:42 | 2024-11-19 16:23 | 0.030325 | 6.6e-05 | 3 | 461.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 674 | J.24.10.0231 | O76 | O76 | 2024-11-20 09:02 | 2024-11-20 17:39 | 0.033974 | 6.6e-05 | 3 | 516.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 675 | J.24.10.0232 | O76 | O76 | 2024-11-21 08:51 | 2024-11-21 15:40 | 0.026882 | 6.6e-05 | 3 | 408.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 676 | J.24.10.0234 | W23 | W23 | 2024-10-25 07:38 | 2024-10-25 10:32 | 0.003803 | 2.2e-05 | 1 | 173.5 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 677 | J.24.10.0235 | U92 | U92 | 2024-10-25 09:09 | 2024-10-25 10:46 | 0.002137 | 2.2e-05 | 1 | 97.5 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 678 | J.24.10.0237 | SW64 | SW64 | 2024-05-11 08:07 | 2024-05-11 12:18 | 0.005506 | 2.2e-05 | 1 | 251.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 679 | J.24.10.0241 | O76 | O76 | 2024-11-27 09:04 | 2024-11-27 13:30 | 0.017454 | 6.6e-05 | 3 | 265.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 680 | J.24.10.0243 | N44 | N44 | 2024-10-25 14:18 | 2024-10-25 14:47 | 0.000649 | 2.2e-05 | 1 | 29.6 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 681 | J.24.10.0244 | U92 | U92 | 2024-11-20 09:03 | 2024-11-20 13:47 | 0.028808 | 0.00011 | 5 | 262.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 682 | J.24.10.0246 | P35 | P35 | 2024-11-20 10:32 | 2024-11-20 12:19 | 0.073098 | 0.000679 | 31 | 107.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 683 | J.24.10.0250 | K35 | K35 | 2024-10-26 08:51 | 2024-10-26 09:51 | 0.00528 | 8.8e-05 | 4 | 60.2 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 684 | J.24.10.0251 | X54 | X54 | 2024-10-26 16:43 | 2024-10-26 18:51 | 0.014012 | 0.00011 | 5 | 127.9 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 685 | J.24.10.0252 | X54 | X54 | 2024-10-26 19:11 | 2024-10-26 20:29 | 0.008605 | 0.00011 | 5 | 78.5 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 686 | J.24.10.0256 | X55 | X55 | 2024-10-27 07:08 | 2024-10-27 09:10 | 0.005308 | 4.4e-05 | 2 | 121.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 687 | J.24.10.0257 | X54 | X54 | 2024-10-27 08:47 | 2024-10-27 09:57 | 0.003047 | 4.4e-05 | 2 | 69.5 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 688 | J.24.10.0258 | X54 | X54 | 2024-10-27 08:56 | 2024-10-27 12:03 | 0.020579 | 0.00011 | 5 | 187.8 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 689 | J.24.10.0259 | X54 | X54 | 2024-10-27 09:57 | 2024-10-27 10:27 | 0.001973 | 6.6e-05 | 3 | 30 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 690 | J.24.10.0263 | P35 | P35 | 2024-10-27 18:00 | 2024-10-27 22:09 | 0.005459 | 2.2e-05 | 1 | 249.1 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 691 | J.24.10.0264 | P35 | P35 | 2024-10-27 18:09 | 2024-10-27 18:20 | 0.000242 | 2.2e-05 | 1 | 11.1 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 692 | J.24.10.0265 | P35 | P35 | 2024-10-27 18:20 | 2024-10-27 18:49 | 0.000638 | 2.2e-05 | 1 | 29.1 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 693 | J.24.10.0266 | P35 | P35 | 2024-10-27 19:04 | 2024-10-28 00:05 | 0.006607 | 2.2e-05 | 1 | 301.5 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 694 | J.24.10.0271 | SW63 | SW63 | 2024-10-28 12:57 | 2024-10-28 14:27 | 0.007886 | 8.8e-05 | 4 | 90 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 695 | J.24.10.0274 | P45 | P45 | 2024-10-28 13:20 | 2024-10-28 14:28 | 0.020914 | 0.000307 | 14 | 68.2 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 696 | J.24.10.0282 | KAI_6 | KAI_6 | 2024-11-28 12:07 | 2024-11-28 14:31 | 0.08793 | 0.000614 | 28 | 143.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 697 | J.24.10.0284 | W22 | W22 | 2024-02-12 09:04 | 2024-02-12 15:24 | 0.2248 | 0.000592 | 27 | 379.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 698 | J.24.10.0285 | Y23 | Y23 | 2024-11-20 08:33 | 2024-11-20 14:23 | 0.076777 | 0.000219 | 10 | 350.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 699 | J.24.10.0290 | SW66 | SW66 | 2024-10-30 05:40 | 2024-10-30 06:47 | 0.084715 | 0.001271 | 58 | 66.7 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 700 | J.24.10.0293 | SW64 | SW64 | 2024-10-30 07:51 | 2024-10-30 10:33 | 0.007138 | 4.4e-05 | 2 | 162.9 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 701 | J.24.10.0294 | X54 | X54 | 2024-11-18 09:26 | 2024-11-18 15:55 | 0.07665 | 0.000197 | 9 | 388.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 702 | J.24.10.0300 | G33 | G33 | 2024-10-30 12:21 | 2024-10-30 12:42 | 0.000456 | 2.2e-05 | 1 | 20.8 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 703 | J.24.10.0303 | X54 | X54 | 2024-10-31 05:25 | 2024-10-31 06:26 | 0.00133 | 2.2e-05 | 1 | 60.7 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 704 | J.24.10.0304 | W21 | W21 | 2024-11-21 09:07 | 2024-11-21 12:02 | 0.003827 | 2.2e-05 | 1 | 174.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 705 | J.24.10.0305 | W22 | W22 | 2024-11-21 09:12 | 2024-11-21 15:34 | 0.033498 | 8.8e-05 | 4 | 382.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 706 | J.24.10.0307 | U32 | U32 | 2024-11-26 09:05 | 2024-11-26 15:51 | 2.6523 | 0.006574 | 300 | 403.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 707 | J.24.10.0311 | H31 | H31 | 2024-10-31 16:44 | 2024-10-31 21:24 | 0.11035 | 0.000394 | 18 | 279.8 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 708 | J.24.11.0004 | N34 | N34 | 2024-01-11 07:29 | 2024-01-11 09:46 | 0.015006 | 0.00011 | 5 | 137 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 709 | J.24.11.0005 | P55 | P55 | 2024-01-11 08:37 | 2024-01-11 10:57 | 0.003074 | 2.2e-05 | 1 | 140.3 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 710 | J.24.11.0006 | KAI_7 | KAI_7 | 2024-11-25 09:04 | 2024-11-25 15:47 | 0.31779 | 0.000789 | 36 | 402.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 711 | J.24.11.0008 | X54 | X54 | 2024-01-11 09:05 | 2024-01-11 16:09 | 0.26847 | 0.003243 | 148 | 82.8 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 712 | J.24.11.0012 | U92 | U92 | 2024-01-11 13:52 | 2024-01-11 14:30 | 0.003321 | 8.8e-05 | 4 | 37.9 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 713 | J.24.11.0013 | SB1162 | SB1162 | 2024-01-11 18:13 | 2024-01-11 19:34 | 0.003524 | 4.4e-05 | 2 | 80.4 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 714 | J.24.11.0014 | U42 | U42 | 2024-01-11 19:38 | 2024-02-11 07:19 | 0.015363 | 2.2e-05 | 1 | 701.1 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 715 | J.24.11.0015 | SW66 | SW66 | 2024-02-11 07:15 | 2024-02-11 08:36 | 0.005289 | 6.6e-05 | 3 | 80.5 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 716 | J.24.11.0018 | KAI_6 | KAI_6 | 2024-02-11 17:32 | 2024-02-11 19:40 | 0.030183 | 0.000373 | 17 | 81 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 717 | J.24.11.0022 | KAI_6 | KAI_6 | 2024-02-11 20:30 | 2024-02-11 23:17 | 0.007327 | 4.4e-05 | 2 | 167.2 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 718 | J.24.11.0027 | P25 | P25 | 2024-02-11 22:24 | 2024-03-11 00:52 | 0.038867 | 0.000263 | 12 | 147.8 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 719 | J.24.11.0028 | SW65 | SW65 | 2024-02-11 21:34 | 2024-02-11 23:39 | 0.019155 | 0.000153 | 7 | 124.9 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 720 | J.24.11.0045 | X57 | X57 | 2024-03-11 09:58 | 2024-03-11 10:44 | 0.005084 | 0.00011 | 5 | 46.4 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 721 | J.24.11.0048 | W21 | W21 | 2024-03-11 14:28 | 2024-03-11 14:57 | 0.043236 | 0.00149 | 68 | 29 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 722 | J.24.11.0049 | KAI_5 | KAI_5 | 2024-03-11 20:34 | 2024-03-11 22:10 | 0.82065 | 0.008525 | 389 | 96.3 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 723 | J.24.11.0051 | KAI_7 | KAI_7 | 2024-04-11 06:54 | 2024-04-11 07:34 | 0.003531 | 8.8e-05 | 4 | 40.3 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 724 | J.24.11.0058 | G32 | G32 | 2024-09-12 09:40 | 2024-09-12 13:53 | 0.022186 | 8.8e-05 | 4 | 253.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 725 | J.24.11.0059 | ASY_2772 | ASY_2772 | 2024-09-12 09:14 | 2024-09-12 13:02 | 0.009989 | 4.4e-05 | 2 | 227.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 726 | J.24.11.0060 | P25 | P25 | 2024-04-11 11:26 | 2024-04-11 11:40 | 0.000973 | 6.6e-05 | 3 | 14.8 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 727 | J.24.11.0063 | T43 | T43 | 2024-05-11 07:37 | 2024-05-11 10:05 | 0.11426 | 0.000767 | 35 | 149 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 728 | J.24.11.0067 | E80 | E80 | 2024-05-11 10:00 | 2024-05-11 14:38 | 0.1094 | 0.000394 | 18 | 277.4 | Unplanned | Adverse Environment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 729 | J.24.11.0069 | K18 | K18 | 2024-11-28 22:03 | 2024-11-29 04:48 | 0.16872 | 0.000416 | 38 | 202.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 730 | J.24.11.0070 | W22 | W22 | 2024-05-11 18:32 | 2024-05-11 21:20 | 0.011055 | 6.6e-05 | 3 | 168.2 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 731 | J.24.11.0079 | H41 | H41 | 2024-06-11 22:33 | 2024-06-11 22:36 | 7.4e-05 | 2.2e-05 | 1 | 3.4 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 732 | J.24.11.0080 | X54 | X54 | 2024-07-11 06:49 | 2024-07-11 09:01 | 0.005788 | 4.4e-05 | 2 | 132.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 733 | J.24.11.0084 | G32 | G32 | 2024-12-12 09:13 | 2024-12-12 16:23 | 0.34874 | 0.000811 | 37 | 430.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 734 | J.24.11.0085 | U92 | U92 | 2024-07-11 11:45 | 2024-07-11 13:26 | 0.002218 | 2.2e-05 | 1 | 101.2 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 735 | J.24.11.0092 | X55 | X55 | 2024-08-11 06:38 | 2024-08-11 08:34 | 0.005091 | 4.4e-05 | 2 | 116.2 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 736 | J.24.11.0093 | ASY_2692 | ASY_2692 | 2024-08-11 07:10 | 2024-08-11 08:21 | 0.003115 | 4.4e-05 | 2 | 71.1 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 737 | J.24.11.0096 | U92 | U92 | 2024-11-27 09:33 | 2024-11-27 13:36 | 0.037281 | 0.000153 | 7 | 243 | Unplanned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 738 | J.24.11.0103 | ASY_2692 | ASY_2692 | 2024-09-11 06:09 | 2024-09-11 07:11 | 0.009391 | 0.000153 | 7 | 61.2 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 739 | J.24.11.0106 | X54 | X54 | 2024-09-11 16:09 | 2024-09-11 19:59 | 0.010065 | 4.4e-05 | 2 | 229.6 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 740 | J.24.11.0108 | P55 | P55 | 2024-09-11 20:01 | 2024-09-11 20:31 | 0.000664 | 2.2e-05 | 1 | 30.3 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 741 | J.24.11.0109 | P45 | P45 | 2024-10-11 01:51 | 2024-10-11 03:16 | 0.001872 | 2.2e-05 | 1 | 85.4 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 742 | J.24.11.0110 | L52 | L52 | 2024-10-11 09:25 | 2024-10-11 11:19 | 0.002508 | 2.2e-05 | 1 | 114.5 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 743 | J.24.11.0119 | E80 | E80 | 2024-04-12 09:06 | 2024-04-12 16:28 | 0.49394 | 0.001118 | 51 | 442 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 744 | J.24.11.0120 | P45 | P45 | 2024-11-11 10:01 | 2024-11-11 14:45 | 0.006229 | 2.2e-05 | 1 | 284.2 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 745 | J.24.11.0121 | N44 | N44 | 2024-11-21 08:07 | 2024-11-21 11:14 | 0.004092 | 2.2e-05 | 1 | 186.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 746 | J.24.11.0129 | X52 | X52 | 2024-11-11 14:27 | 2024-11-11 17:26 | 0.006525 | 4.4e-05 | 2 | 148.9 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 747 | J.24.11.0132 | G31 | G31 | 2024-11-11 16:15 | 2024-11-11 23:30 | 0.019063 | 4.4e-05 | 2 | 434.9 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 748 | J.24.11.0136 | X56 | X56 | 2024-12-19 11:05 | 2024-12-19 13:17 | 0.005769 | 4.4e-05 | 2 | 131.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 749 | J.24.11.0138 | H21 | H21 | 2024-12-11 10:05 | 2024-12-11 12:46 | 0.003529 | 2.2e-05 | 1 | 161.1 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 750 | J.24.11.0141 | H41 | H41 | 2024-12-11 11:33 | 2024-12-11 16:12 | 0.55848 | 0.00206 | 95 | 268.3 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 751 | J.24.11.0144 | K35 | K35 | 2024-12-18 08:17 | 2024-12-18 13:08 | 0.18502 | 0.000636 | 29 | 291.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 752 | J.24.11.0145 | P45 | P45 | 2024-12-11 14:24 | 2024-12-11 14:36 | 0.00027 | 2.2e-05 | 1 | 12.3 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 753 | J.24.11.0149 | U92 | U92 | 2024-05-12 09:55 | 2024-05-12 12:39 | 0.014434 | 8.8e-05 | 4 | 164.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 754 | J.24.11.0150 | H21 | H21 | 2024-11-13 09:29 | 2024-11-13 15:39 | 0.048674 | 0.000131 | 6 | 370.2 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 755 | J.24.11.0153 | SW66 | SW66 | 2024-12-19 08:53 | 2024-12-19 11:39 | 0.007249 | 4.4e-05 | 2 | 165.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 756 | J.24.11.0154 | P25 | P25 | 2024-11-13 13:30 | 2024-11-13 14:27 | 0.002462 | 4.4e-05 | 2 | 56.2 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 757 | J.24.11.0155 | T42 | T42 | 2024-05-12 09:36 | 2024-05-12 17:06 | 0.039472 | 8.8e-05 | 4 | 450.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 758 | J.24.11.0156 | ASY_2772 | ASY_2772 | 2024-11-21 23:18 | 2024-11-21 23:33 | 0.000519 | 0.000131 | 6 | 4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 759 | J.24.11.0157 | W21 | W21 | 2024-11-14 13:08 | 2024-11-14 14:51 | 0.008983 | 8.8e-05 | 4 | 102.5 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 760 | J.24.11.0161 | W21 | W21 | 2024-11-15 08:26 | 2024-11-15 10:16 | 0.068689 | 0.000855 | 39 | 80.4 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 761 | J.24.11.0164 | W21 | W21 | 2024-11-15 09:56 | 2024-11-15 10:15 | 0.015041 | 0.000811 | 37 | 18.6 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 762 | J.24.11.0165 | W22 | W22 | 2024-11-15 11:32 | 2024-11-15 12:29 | 0.023942 | 0.000416 | 19 | 57.5 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 763 | J.24.11.0168 | P35 | P35 | 2024-11-16 05:44 | 2024-11-16 06:49 | 0.026884 | 0.000416 | 19 | 64.6 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 764 | J.24.11.0173 | KAI_5 | KAI_5 | 2024-11-16 14:06 | 2024-11-16 15:05 | 0.002569 | 4.4e-05 | 2 | 58.6 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 765 | J.24.11.0176 | SW66 | SW66 | 2024-11-17 07:57 | 2024-11-17 09:00 | 0.00415 | 6.6e-05 | 3 | 63.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 766 | J.24.11.0181 | Y43 | Y43 | 2024-12-13 09:08 | 2024-12-13 15:48 | 0.1664 | 0.000416 | 19 | 399.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 767 | J.24.11.0182 | P45 | P45 | 2024-11-18 10:49 | 2024-11-18 11:00 | 0.000244 | 2.2e-05 | 1 | 11.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 768 | J.24.11.0183 | KAI_5 | KAI_5 | 2024-12-16 09:06 | 2024-12-16 10:33 | 0.005725 | 6.6e-05 | 3 | 87.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 769 | J.24.11.0188 | KAI_7 | KAI_7 | 2024-11-18 15:17 | 2024-11-18 17:44 | 0.11631 | 0.000789 | 36 | 147.4 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 770 | J.24.11.0192 | K36 | K36 | 2024-11-18 15:58 | 2024-11-18 16:53 | 0.004753 | 8.8e-05 | 4 | 54.2 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 771 | J.24.11.0194 | H31 | H31 | 2024-11-19 08:46 | 2024-11-19 09:46 | 0.002629 | 4.4e-05 | 2 | 60 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 772 | J.24.11.0195 | N44 | N44 | 2024-09-12 22:16 | 2024-10-12 01:51 | 0.20242 | 0.000942 | 43 | 214.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 773 | J.24.11.0196 | X54 | X54 | 2024-12-16 09:04 | 2024-12-16 12:19 | 0.012817 | 6.6e-05 | 3 | 195 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 774 | J.24.11.0199 | H41 | H41 | 2024-11-19 18:02 | 2024-11-19 19:14 | 0.011042 | 0.000153 | 7 | 72 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 775 | J.24.11.0201 | U92 | U92 | 2024-11-21 08:26 | 2024-11-21 13:53 | 0.014338 | 4.4e-05 | 2 | 327.1 | Planned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 776 | J.24.11.0202 | T42 | T42 | 2024-10-12 09:02 | 2024-10-12 16:20 | 0.28789 | 0.000657 | 30 | 437.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 777 | J.24.11.0203 | H31 | H31 | 2024-11-20 09:26 | 2024-11-20 09:37 | 0.000228 | 2.2e-05 | 1 | 10.4 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 778 | J.24.11.0205 | SW65 | SW65 | 2024-11-12 08:39 | 2024-11-12 11:22 | 0.021413 | 0.000131 | 6 | 162.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 779 | J.24.11.0206 | SW64 | SW64 | 2024-11-20 11:48 | 2024-11-20 12:41 | 0.005771 | 0.00011 | 5 | 52.7 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 780 | J.24.11.0207 | H31 | H31 | 2024-11-20 13:57 | 2024-11-20 15:05 | 0.019358 | 0.000285 | 13 | 68 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 781 | J.24.11.0213 | G33 | G33 | 2024-11-21 09:22 | 2024-11-21 16:59 | 0.050042 | 0.00011 | 5 | 456.7 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 782 | J.24.11.0214 | U32 | U32 | 2024-12-12 08:42 | 2024-12-12 12:09 | 0.56772 | 0.002739 | 125 | 207.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 783 | J.24.11.0215 | U42 | U42 | 2024-11-22 09:07 | 2024-11-22 10:11 | 0.015392 | 0.000241 | 11 | 63.9 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 784 | J.24.11.0216 | S35 | S35 | 2024-11-12 13:04 | 2024-11-12 15:41 | 0.044908 | 0.000285 | 13 | 157.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 785 | J.24.11.0217 | SW66 | SW66 | 2024-11-22 12:33 | 2024-11-22 13:28 | 0.002385 | 4.4e-05 | 2 | 54.4 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 786 | J.24.11.0221 | KAI_7 | KAI_7 | 2024-11-23 11:09 | 2024-11-23 12:16 | 0.001485 | 2.2e-05 | 1 | 67.8 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 787 | J.24.11.0229 | KKA_1432 | KKA_1432 | 2024-12-16 11:10 | 2024-12-16 16:30 | 0.021071 | 6.6e-05 | 3 | 320.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 788 | J.24.11.0230 | KKA_1432 | KKA_1432 | 2024-12-17 08:08 | 2024-12-17 17:54 | 0.03854 | 6.6e-05 | 3 | 586.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 789 | J.24.11.0231 | KKA_1432 | KKA_1432 | 2024-12-18 08:06 | 2024-12-18 13:57 | 0.023085 | 6.6e-05 | 3 | 351.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 790 | J.24.11.0234 | SB1142 | SB1142 | 2024-11-25 14:36 | 2024-11-25 18:50 | 0.011146 | 4.4e-05 | 2 | 254.3 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 791 | J.24.11.0235 | KAI_7 | KAI_7 | 2024-11-25 14:55 | 2024-11-25 15:47 | 0.3671 | 0.011637 | 531 | 31.5 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 792 | J.24.11.0240 | SW62 | SW62 | 2024-11-26 07:31 | 2024-11-26 08:42 | 0.006212 | 8.8e-05 | 4 | 70.9 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 793 | J.24.11.0243 | U32 | U32 | 2024-11-26 11:22 | 2024-11-26 12:55 | 0.00407 | 4.4e-05 | 2 | 92.9 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 794 | J.24.11.0252 | P25 | P25 | 2024-11-27 13:51 | 2024-11-27 14:20 | 0.002623 | 0.000285 | 13 | 9.2 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 795 | J.24.11.0257 | W21 | W21 | 2024-02-11 20:49 | 2024-03-11 14:53 | 2.5969 | 0.005895 | 269 | 440.5 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 796 | J.24.11.0258 | W21 | W21 | 2024-03-11 00:17 | 2024-03-11 00:19 | 0.006881 | 0.003441 | 157 | 2 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 797 | J.24.11.0259 | W21 | W21 | 2024-03-11 00:36 | 2024-03-11 00:38 | 0.006881 | 0.003441 | 157 | 2 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 798 | J.24.11.0264 | O76 | O76 | 2024-11-28 09:19 | 2024-11-28 10:12 | 0.001162 | 2.2e-05 | 1 | 53 | Unplanned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 799 | J.24.11.0272 | SW62 | SW62 | 2024-11-28 22:47 | 2024-11-29 00:01 | 0.006462 | 8.8e-05 | 4 | 73.7 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 800 | J.24.11.0274 | X57 | X57 | 2024-11-29 11:26 | 2024-11-29 13:40 | 0.12929 | 0.000964 | 44 | 134.1 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 801 | J.24.11.0276 | X57 | X57 | 2024-11-29 12:59 | 2024-11-29 13:37 | 0.044633 | 0.001183 | 54 | 37.7 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 802 | J.24.11.0278 | P25 | P25 | 2024-11-29 14:27 | 2024-11-29 15:08 | 0.001778 | 4.4e-05 | 2 | 40.6 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 803 | J.24.12.0003 | X55 | X55 | 2024-01-12 08:38 | 2024-01-12 11:58 | 0.029372 | 0.000614 | 28 | 47.9 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 804 | J.24.12.0005 | KAI_24 | KAI_24 | 2025-06-01 10:07 | 2025-06-01 15:33 | 0.014289 | 4.4e-05 | 2 | 326 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 805 | J.24.12.0008 | P45 | P45 | 2024-02-12 09:47 | 2024-02-12 10:02 | 0.00034 | 2.2e-05 | 1 | 15.5 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 806 | J.24.12.0012 | W22 | W22 | 2024-02-12 17:13 | 2024-02-12 18:32 | 0.024212 | 0.000307 | 14 | 78.9 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 807 | J.24.12.0013 | P55 | P55 | 2024-02-12 17:29 | 2024-02-12 17:31 | 3.8e-05 | 2.2e-05 | 1 | 1.8 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 808 | J.24.12.0014 | ASY_2762 | ASY_2762 | 2024-02-12 22:27 | 2024-03-12 00:06 | 1.5217 | 0.017159 | 783 | 88.7 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 809 | J.24.12.0015 | KAI_5 | KAI_5 | 2024-10-12 04:32 | 2024-10-12 05:36 | 0.004171 | 6.6e-05 | 3 | 63.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 810 | J.24.12.0020 | L53 | L53 | 2024-03-12 20:32 | 2024-03-12 21:22 | 0.007731 | 0.000153 | 7 | 50.4 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 811 | J.24.12.0022 | H41 | H41 | 2024-04-12 09:00 | 2024-04-12 10:52 | 0.004906 | 4.4e-05 | 2 | 111.9 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 812 | J.24.12.0024 | U42 | U42 | 2025-08-01 09:19 | 2025-08-01 14:49 | 0.12273 | 0.000373 | 17 | 329.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 813 | J.24.12.0028 | H31 | H31 | 2025-09-01 09:47 | 2025-09-01 11:52 | 0.003265 | 8.8e-05 | 4 | 37.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 814 | J.24.12.0029 | ASY_2712 | ASY_2712 | 2025-06-01 10:25 | 2025-06-01 15:52 | 0.064471 | 0.000197 | 9 | 326.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 815 | J.24.12.0030 | SW64 | SW64 | 2025-10-01 09:09 | 2025-10-01 16:33 | 0.16509 | 0.000373 | 17 | 443.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 816 | J.24.12.0032 | G32 | G32 | 2024-05-12 03:30 | 2024-05-12 08:53 | 0.028274 | 8.8e-05 | 4 | 322.6 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 817 | J.24.12.0037 | W21 | W21 | 2024-06-12 06:32 | 2024-06-12 07:45 | 0.006377 | 8.8e-05 | 4 | 72.8 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 818 | J.24.12.0039 | K37 | K37 | 2024-06-12 09:25 | 2024-06-12 10:36 | 0.3261 | 0.00458 | 209 | 71.2 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 819 | J.24.12.0044 | X55 | X55 | 2024-07-12 08:15 | 2024-07-12 09:11 | 0.003718 | 6.6e-05 | 3 | 56.6 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 820 | J.24.12.0045 | X52 | X52 | 2024-07-12 07:16 | 2024-07-12 09:35 | 0.006097 | 4.4e-05 | 2 | 139.1 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 821 | J.24.12.0047 | P55 | P55 | 2024-08-12 03:26 | 2024-08-12 04:49 | 0.001813 | 2.2e-05 | 1 | 82.7 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 822 | J.24.12.0048 | ASY_2762 | ASY_2762 | 2024-08-12 07:18 | 2024-08-12 09:01 | 0.002252 | 2.2e-05 | 1 | 102.8 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 823 | J.24.12.0051 | SW66 | SW66 | 2024-08-12 15:16 | 2024-08-12 15:47 | 0.20296 | 0.007802 | 356 | 26 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 824 | J.24.12.0053 | X52 | X52 | 2024-08-12 18:45 | 2024-08-12 20:45 | 0.007866 | 6.6e-05 | 3 | 119.7 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 825 | J.24.12.0061 | P25 | P25 | 2024-08-12 22:13 | 2024-09-12 12:07 | 0.21942 | 0.000263 | 12 | 834.4 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 826 | J.24.12.0065 | ASY_2712 | ASY_2712 | 2024-08-12 23:15 | 2024-09-12 01:37 | 1.0486 | 0.007407 | 338 | 141.6 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 827 | J.24.12.0066 | KAI_6 | KAI_6 | 2024-08-12 23:30 | 2024-09-12 00:05 | 0.53715 | 0.015274 | 697 | 35.2 | Unplanned | Human Error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 828 | J.24.12.0067 | P25 | P25 | 2024-08-12 22:19 | 2024-10-12 17:17 | 0.23222 | 0.000877 | 40 | 264.9 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 829 | J.24.12.0068 | H41 | H41 | 2024-08-12 22:09 | 2024-09-12 01:19 | 0.24499 | 0.001293 | 59 | 189.5 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 830 | J.24.12.0071 | X54 | X54 | 2024-08-12 21:44 | 2024-09-12 16:27 | 0.12297 | 0.00011 | 5 | 1122.3 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 831 | J.24.12.0072 | P35 | P35 | 2024-09-12 02:15 | 2024-09-12 16:47 | 2.1211 | 0.002433 | 111 | 872 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 832 | J.24.12.0073 | P35 | P35 | 2024-09-12 02:15 | 2024-09-12 02:47 | 0.30471 | 0.00973 | 444 | 31.3 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 833 | J.24.12.0075 | W23 | W23 | 2024-09-12 04:21 | 2024-09-12 05:24 | 0.010992 | 0.000175 | 8 | 62.7 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 834 | J.24.12.0076 | P35 | P35 | 2024-09-12 04:22 | 2024-09-12 14:05 | 0.089464 | 0.000153 | 7 | 583.2 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 835 | J.24.12.0081 | P45 | P45 | 2024-09-12 04:52 | 2024-09-12 10:58 | 0.88149 | 0.014683 | 670 | 60 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 836 | J.24.12.0083 | ASY_2762 | ASY_2762 | 2024-09-12 05:08 | 2024-09-12 11:01 | 0.015447 | 4.4e-05 | 2 | 352.5 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 837 | J.24.12.0086 | SW62 | SW62 | 2024-09-12 06:09 | 2024-09-12 10:25 | 0.050442 | 0.000197 | 9 | 255.8 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 838 | J.24.12.0091 | U42 | U42 | 2024-09-12 04:23 | 2024-09-12 07:14 | 0.082113 | 0.000482 | 22 | 170.3 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 839 | J.24.12.0092 | SB1062 | SB1062 | 2024-09-12 06:49 | 2024-09-12 09:04 | 0.0148 | 0.00011 | 5 | 135.1 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 840 | J.24.12.0095 | T41 | T41 | 2024-09-12 07:14 | 2024-09-12 16:07 | 0.023391 | 4.4e-05 | 2 | 533.7 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 841 | J.24.12.0097 | W21 | W21 | 2024-09-12 07:29 | 2024-09-12 13:58 | 0.017017 | 4.4e-05 | 2 | 388.3 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 842 | J.24.12.0102 | K36 | K36 | 2024-09-12 08:27 | 2024-09-12 10:00 | 0.010219 | 0.00011 | 5 | 93.3 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 843 | J.24.12.0106 | G33 | G33 | 2024-09-12 04:24 | 2024-09-12 10:49 | 0.11812 | 0.000307 | 14 | 385 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 844 | J.24.12.0108 | P35 | P35 | 2024-09-12 02:58 | 2024-09-12 10:59 | 0.32689 | 0.000679 | 31 | 481.2 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 845 | J.24.12.0109 | Y33 | Y33 | 2024-09-12 10:04 | 2024-09-12 10:20 | 0.001834 | 0.00011 | 5 | 16.7 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 846 | J.24.12.0113 | KAI_7 | KAI_7 | 2024-09-12 10:26 | 2024-09-12 15:08 | 0.024654 | 8.8e-05 | 4 | 281.3 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 847 | J.24.12.0120 | ASY_2762 | ASY_2762 | 2024-09-12 11:46 | 2024-09-12 11:58 | 0.000262 | 2.2e-05 | 1 | 12 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 848 | J.24.12.0121 | P55 | P55 | 2024-09-12 11:51 | 2024-09-12 12:20 | 0.000622 | 2.2e-05 | 1 | 28.4 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 849 | J.24.12.0123 | Y43 | Y43 | 2024-09-12 11:59 | 2024-09-12 13:23 | 0.003692 | 4.4e-05 | 2 | 84.2 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 850 | J.24.12.0125 | X54 | X54 | 2024-09-12 12:43 | 2024-09-12 15:31 | 0.022184 | 0.000131 | 6 | 168.7 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 851 | J.24.12.0126 | P55 | P55 | 2024-09-12 12:52 | 2024-09-12 14:09 | 0.022036 | 0.000285 | 13 | 77.4 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 852 | J.24.12.0129 | P25 | P25 | 2024-09-12 15:01 | 2024-09-12 15:20 | 0.000437 | 2.2e-05 | 1 | 20 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 853 | J.24.12.0131 | W23 | W23 | 2024-09-12 15:40 | 2024-09-12 16:23 | 0.002791 | 6.6e-05 | 3 | 42.5 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 854 | J.24.12.0135 | P25 | P25 | 2024-09-12 16:49 | 2024-09-12 18:15 | 0.007521 | 8.8e-05 | 4 | 85.8 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 855 | J.24.12.0136 | X54 | X54 | 2024-09-12 16:51 | 2024-09-12 17:44 | 0.002316 | 4.4e-05 | 2 | 52.9 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 856 | J.24.12.0137 | W21 | W21 | 2024-09-12 17:19 | 2024-09-12 20:49 | 0.004601 | 2.2e-05 | 1 | 210 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 857 | J.24.12.0138 | U92 | U92 | 2024-09-12 17:57 | 2024-10-12 01:41 | 0.071127 | 0.000153 | 7 | 463.7 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 858 | J.24.12.0142 | U92 | U92 | 2024-09-12 22:52 | 2024-10-12 01:41 | 0.018505 | 0.00011 | 5 | 168.9 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 859 | J.24.12.0144 | W21 | W21 | 2024-10-12 07:31 | 2024-10-12 10:41 | 0.004161 | 2.2e-05 | 1 | 189.9 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 860 | J.24.12.0148 | ASY_2762 | ASY_2762 | 2025-10-01 10:02 | 2025-10-01 15:01 | 0.045857 | 0.000153 | 7 | 298.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 861 | J.24.12.0150 | T41 | T41 | 2024-10-12 16:19 | 2024-10-12 17:20 | 0.002668 | 4.4e-05 | 2 | 60.9 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 862 | J.24.12.0151 | X52 | X52 | 2024-10-12 19:34 | 2024-10-12 21:16 | 0.013455 | 0.000131 | 6 | 102.3 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 863 | J.24.12.0154 | G33 | G33 | 2025-01-13 09:05 | 2025-01-13 14:42 | 0.066401 | 0.000197 | 9 | 336.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 864 | J.24.12.0155 | ASY_2692 | ASY_2692 | 2024-11-12 09:37 | 2024-11-12 09:45 | 0.003557 | 0.000438 | 20 | 8.1 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 865 | J.24.12.0162 | ASY_2692 | ASY_2692 | 2024-12-12 08:08 | 2024-12-12 09:32 | 0.001852 | 2.2e-05 | 1 | 84.5 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 866 | J.24.12.0163 | KAI_7 | KAI_7 | 2024-12-12 09:20 | 2024-12-12 09:29 | 0.000194 | 2.2e-05 | 1 | 8.9 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 867 | J.24.12.0170 | SB1062 | SB1062 | 2025-01-16 08:03 | 2025-01-16 16:08 | 0.063518 | 0.000131 | 6 | 483.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 868 | J.24.12.0175 | P45 | P45 | 2024-12-13 05:43 | 2024-12-13 12:31 | 0.15915 | 0.000394 | 18 | 403.5 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 869 | J.24.12.0177 | P55 | P55 | 2024-12-13 06:42 | 2024-12-13 08:21 | 0.002172 | 2.2e-05 | 1 | 99.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 870 | J.24.12.0178 | H41 | H41 | 2024-12-13 06:12 | 2024-12-13 07:23 | 0.001575 | 2.2e-05 | 1 | 71.9 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 871 | J.24.12.0179 | ASY_2762 | ASY_2762 | 2024-12-13 08:52 | 2024-12-13 08:55 | 0.037533 | 0.011374 | 519 | 3.3 | Unplanned | Human Error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 872 | J.24.12.0180 | U92 | U92 | 2024-12-13 09:02 | 2024-12-13 10:53 | 0.002423 | 2.2e-05 | 1 | 110.6 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 873 | J.24.12.0183 | X52 | X52 | 2024-12-13 14:35 | 2024-12-13 15:09 | 0.000733 | 2.2e-05 | 1 | 33.5 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 874 | J.24.12.0185 | H41 | H41 | 2024-12-13 15:31 | 2024-12-13 15:44 | 0.000298 | 2.2e-05 | 1 | 13.6 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 875 | J.24.12.0187 | SW66 | SW66 | 2024-12-13 21:09 | 2024-12-13 21:25 | 0.000348 | 2.2e-05 | 1 | 15.9 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 876 | J.24.12.0193 | SW65 | SW65 | 2024-12-14 13:10 | 2024-12-14 15:43 | 0.00335 | 2.2e-05 | 1 | 152.9 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 877 | J.24.12.0199 | U92 | U92 | 2024-12-15 08:50 | 2024-12-15 10:18 | 0.005759 | 6.6e-05 | 3 | 87.6 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 878 | J.24.12.0200 | P25 | P25 | 2024-12-15 10:58 | 2024-12-15 11:59 | 0.002657 | 4.4e-05 | 2 | 60.6 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 879 | J.24.12.0201 | K35 | K35 | 2024-12-15 23:19 | 2024-12-15 23:43 | 0.00206 | 8.8e-05 | 4 | 23.5 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 880 | J.24.12.0203 | SW66 | SW66 | 2024-12-16 06:02 | 2024-12-16 07:12 | 0.003085 | 4.4e-05 | 2 | 70.4 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 881 | J.24.12.0211 | L52 | L52 | 2024-12-16 08:59 | 2024-12-16 11:02 | 0.062282 | 0.000504 | 23 | 123.6 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 882 | J.24.12.0216 | U42 | U42 | 2024-12-16 13:42 | 2024-12-16 15:16 | 0.043259 | 0.00046 | 21 | 94 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 883 | J.24.12.0217 | H31 | H31 | 2024-12-16 17:46 | 2024-12-17 02:19 | 0.011248 | 2.2e-05 | 1 | 513.3 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 884 | J.24.12.0218 | H31 | H31 | 2024-12-16 18:00 | 2024-12-16 20:15 | 0.011851 | 8.8e-05 | 4 | 135.2 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 885 | J.24.12.0219 | H31 | H31 | 2024-12-16 17:47 | 2024-12-16 19:06 | 0.005196 | 6.6e-05 | 3 | 79 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 886 | J.24.12.0221 | P45 | P45 | 2024-12-16 18:47 | 2024-12-17 00:33 | 0.53024 | 0.002191 | 100 | 242 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 887 | J.24.12.0225 | X57 | X57 | 2024-12-17 07:03 | 2024-12-17 08:09 | 0.002877 | 4.4e-05 | 2 | 65.7 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 888 | J.24.12.0234 | U42 | U42 | 2025-01-14 09:39 | 2025-01-14 14:25 | 0.050158 | 0.000175 | 8 | 286.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 889 | J.24.12.0238 | SBK_42 | SBK_42 | 2025-01-21 09:16 | 2025-01-21 18:04 | 0.011484 | 2.2e-05 | 2 | 262 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 890 | J.24.12.0242 | X57 | X57 | 2025-08-01 08:15 | 2025-08-01 17:10 | 0.093779 | 0.000175 | 8 | 534.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 891 | J.24.12.0246 | SBK_82 | SBK_82 | 2025-01-23 09:00 | 2025-01-23 16:19 | 0.019236 | 4.4e-05 | 2 | 438.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 892 | J.24.12.0248 | H31 | H31 | 2024-12-19 07:20 | 2024-12-19 09:09 | 0.004807 | 4.4e-05 | 2 | 109.7 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 893 | J.24.12.0251 | ASY_2762 | ASY_2762 | 2025-01-20 08:29 | 2025-01-20 17:44 | 0.1095 | 0.000197 | 9 | 555.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 894 | J.24.12.0252 | ASY_2762 | ASY_2762 | 2025-01-21 08:04 | 2025-01-21 16:51 | 0.10405 | 0.000197 | 9 | 527.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 895 | J.24.12.0253 | ASY_2762 | ASY_2762 | 2025-01-22 08:12 | 2025-01-22 17:12 | 0.10642 | 0.000197 | 9 | 539.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 896 | J.24.12.0254 | P55 | P55 | 2024-12-19 11:53 | 2024-12-19 13:11 | 0.001704 | 2.2e-05 | 1 | 77.8 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 897 | J.24.12.0255 | ASY_2762 | ASY_2762 | 2025-01-20 07:07 | 2025-01-20 18:19 | 0.004343 | 4.4e-05 | 4 | 49.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 898 | J.24.12.0256 | ASY_2762 | ASY_2762 | 2025-01-21 07:13 | 2025-01-21 17:34 | 0.001828 | 4.4e-05 | 4 | 20.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 899 | J.24.12.0257 | ASY_2762 | ASY_2762 | 2025-01-22 07:42 | 2025-01-22 17:49 | 0.001918 | 4.4e-05 | 4 | 21.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 900 | J.24.12.0258 | G31 | G31 | 2025-01-23 09:41 | 2025-01-23 14:36 | 0.025855 | 8.8e-05 | 4 | 295 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 901 | J.24.12.0262 | KAI_5 | KAI_5 | 2025-01-22 09:11 | 2025-01-22 11:56 | 0.028948 | 0.000175 | 8 | 165.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 902 | J.24.12.0263 | KAI_5 | KAI_5 | 2025-01-22 13:07 | 2025-01-22 15:28 | 0.009294 | 6.6e-05 | 3 | 141.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 903 | J.24.12.0266 | X54 | X54 | 2024-12-20 23:08 | 2024-12-21 00:09 | 0.054808 | 0.000898 | 41 | 61 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 904 | J.24.12.0269 | SB1152 | SB1152 | 2024-12-21 00:11 | 2024-12-21 00:26 | 0.53694 | 0.035677 | 1628 | 15.1 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 905 | J.24.12.0270 | S34 | S34 | 2024-12-21 01:13 | 2024-12-21 01:23 | 0.2785 | 0.028817 | 1315 | 9.7 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 906 | J.24.12.0271 | SB1062 | SB1062 | 2024-12-21 00:11 | 2024-12-21 02:47 | 2.1627 | 0.036794 | 1679 | 58.8 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 907 | J.24.12.0273 | SB1152 | SB1152 | 2024-12-21 01:01 | 2024-12-21 01:02 | 0.082032 | 0.0593 | 2706 | 1.4 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 908 | J.24.12.0276 | SB1062 | SB1062 | 2024-12-21 01:56 | 2024-12-21 02:17 | 0.002656 | 0.000131 | 6 | 20.2 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 909 | J.24.12.0281 | SB1062 | SB1062 | 2024-12-21 00:11 | 2024-12-21 11:09 | 0.014417 | 2.2e-05 | 1 | 657.9 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 910 | J.24.12.0288 | Y43 | Y43 | 2024-12-22 06:49 | 2024-12-22 08:27 | 0.002149 | 2.2e-05 | 1 | 98.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 911 | J.24.12.0289 | P45 | P45 | 2024-12-22 08:39 | 2024-12-22 10:12 | 0.01218 | 0.000131 | 6 | 92.6 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 912 | J.24.12.0292 | X52 | X52 | 2024-12-23 05:52 | 2024-12-23 06:54 | 0.00136 | 2.2e-05 | 1 | 62.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 913 | J.24.12.0293 | X52 | X52 | 2024-12-23 11:25 | 2024-12-23 11:51 | 0.021217 | 0.000811 | 37 | 26.2 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 914 | J.24.12.0295 | X52 | X52 | 2024-12-23 17:59 | 2024-12-23 18:50 | 0.38463 | 0.010738 | 490 | 35.8 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 915 | J.24.12.0297 | X52 | X52 | 2024-12-23 18:36 | 2024-12-23 21:16 | 0.003507 | 2.2e-05 | 1 | 160.1 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 916 | J.24.12.0302 | P45 | P45 | 2024-12-24 16:18 | 2024-12-24 18:26 | 0.14078 | 0.001096 | 50 | 128.5 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 917 | J.24.12.0306 | KAI_7 | KAI_7 | 2024-12-25 06:48 | 2024-12-25 07:45 | 0.004988 | 8.8e-05 | 4 | 56.9 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 918 | J.24.12.0310 | P45 | P45 | 2024-12-26 10:41 | 2024-12-26 11:56 | 0.039282 | 0.000526 | 24 | 74.7 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 919 | J.24.12.0313 | H31 | H31 | 2024-12-26 11:24 | 2024-12-26 13:25 | 0.002648 | 2.2e-05 | 1 | 120.8 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 920 | J.24.12.0323 | P55 | P55 | 2024-12-27 08:29 | 2024-12-27 08:51 | 0.000496 | 2.2e-05 | 1 | 22.6 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 921 | J.24.12.0331 | ASY_2712 | ASY_2712 | 2024-12-29 00:44 | 2024-12-29 05:16 | 0.16672 | 0.007407 | 338 | 22.5 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 922 | J.24.12.0332 | ASY_2712 | ASY_2712 | 2024-12-29 05:12 | 2024-12-29 05:16 | 0.005869 | 0.001709 | 78 | 3.4 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 923 | J.24.12.0333 | G33 | G33 | 2024-12-29 12:25 | 2024-12-29 13:56 | 0.001995 | 2.2e-05 | 1 | 91 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 924 | J.24.12.0336 | G33 | G33 | 2024-12-29 18:58 | 2024-12-29 20:03 | 0.001428 | 2.2e-05 | 1 | 65.2 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 925 | J.24.12.0337 | SW63 | SW63 | 2024-12-30 08:44 | 2024-12-30 10:43 | 0.010424 | 8.8e-05 | 4 | 118.9 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 926 | J.24.12.0338 | SW66 | SW66 | 2024-12-30 09:42 | 2024-12-30 11:33 | 0.026866 | 0.000241 | 11 | 111.5 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 927 | J.24.12.0340 | G33 | G33 | 2024-12-30 11:42 | 2024-12-30 12:44 | 0.001354 | 2.2e-05 | 1 | 61.8 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 928 | J.24.12.0343 | SW66 | SW66 | 2024-12-31 08:21 | 2024-12-31 09:48 | 0.087313 | 0.001074 | 49 | 81.3 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 929 | J.24.12.0345 | W21 | W21 | 2024-12-31 09:40 | 2024-12-31 11:50 | 0.173 | 0.001337 | 61 | 129.4 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 930 | J.24.12.0347 | K35 | K35 | 2024-12-31 13:08 | 2024-12-31 14:45 | 0.008469 | 8.8e-05 | 4 | 96.6 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 931 | J.24.12.0348 | X57 | X57 | 2024-12-31 15:49 | 2024-12-31 17:57 | 0.002801 | 2.2e-05 | 1 | 127.8 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 932 | J.25.01.0001 | X54 | X54 | 2025-01-01 13:48 | 2025-01-01 19:27 | 0.007438 | 2.2e-05 | 1 | 339.4 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 933 | J.25.01.0002 | L51 | L51 | 2025-01-01 14:50 | 2025-01-01 15:51 | 0.002679 | 4.4e-05 | 2 | 61.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 934 | J.25.01.0005 | U82 | U82 | 2025-02-01 07:32 | 2025-02-01 08:20 | 0.010643 | 0.000219 | 10 | 48.6 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 935 | J.25.01.0006 | ASY_2692 | ASY_2692 | 2025-02-01 18:11 | 2025-02-01 19:28 | 0.003397 | 4.4e-05 | 2 | 77.5 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 936 | J.25.01.0007 | KAI_7 | KAI_7 | 2025-01-24 09:06 | 2025-01-24 11:36 | 0.019699 | 0.000131 | 6 | 149.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 937 | J.25.01.0009 | X53 | X53 | 2025-03-01 08:50 | 2025-03-01 11:24 | 0.013451 | 8.8e-05 | 4 | 153.5 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 938 | J.25.01.0010 | KAI_7 | KAI_7 | 2025-01-24 13:08 | 2025-01-24 15:40 | 0.006655 | 4.4e-05 | 2 | 151.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 939 | J.25.01.0011 | SB1162 | SB1162 | 2025-01-28 09:16 | 2025-01-28 12:30 | 0.004261 | 2.2e-05 | 1 | 194.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 940 | J.25.01.0014 | SW62 | SW62 | 2025-03-01 13:47 | 2025-03-01 15:10 | 0.01458 | 0.000175 | 8 | 83.2 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 941 | J.25.01.0023 | K33 | K33 | 2025-05-01 18:37 | 2025-05-01 22:14 | 0.028568 | 0.000131 | 6 | 217.3 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 942 | J.25.01.0029 | KAI_5 | KAI_5 | 2025-01-24 09:03 | 2025-01-24 14:48 | 0.064796 | 0.000197 | 9 | 328.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 943 | J.25.01.0030 | P45 | P45 | 2025-06-01 14:04 | 2025-06-01 14:35 | 0.000684 | 2.2e-05 | 1 | 31.2 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 944 | J.25.01.0031 | H41 | H41 | 2025-01-30 09:14 | 2025-01-30 15:35 | 0.058397 | 0.000153 | 7 | 380.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 945 | J.25.01.0034 | P35 | P35 | 2025-06-01 15:07 | 2025-06-01 15:23 | 0.00035 | 2.2e-05 | 1 | 16 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 946 | J.25.01.0035 | K15 | K15 | 2025-01-31 09:05 | 2025-01-31 15:31 | 0.66835 | 0.001731 | 79 | 386.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 947 | J.25.01.0036 | P55 | P55 | 2025-06-01 15:05 | 2025-06-01 16:33 | 0.005803 | 6.6e-05 | 3 | 88.3 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 948 | J.25.01.0039 | SW66 | SW66 | 2025-07-01 06:11 | 2025-07-01 07:07 | 0.052302 | 0.001074 | 49 | 48.7 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 949 | J.25.01.0054 | KAI_5 | KAI_5 | 2025-01-30 08:39 | 2025-01-30 11:02 | 0.009416 | 6.6e-05 | 3 | 143.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 950 | J.25.01.0055 | KAI_5 | KAI_5 | 2025-01-30 12:14 | 2025-01-30 14:28 | 0.005893 | 4.4e-05 | 2 | 134.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 951 | J.25.01.0056 | H21 | H21 | 2025-01-31 09:11 | 2025-01-31 11:54 | 0.010667 | 6.6e-05 | 3 | 162.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 952 | J.25.01.0057 | W23 | W23 | 2025-03-02 09:30 | 2025-03-02 14:12 | 0.006177 | 2.2e-05 | 1 | 281.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 953 | J.25.01.0060 | P25 | P25 | 2025-09-01 14:33 | 2025-09-01 15:40 | 0.002946 | 4.4e-05 | 2 | 67.2 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 954 | J.25.01.0062 | SB1142 | SB1142 | 2025-01-30 08:42 | 2025-01-30 12:24 | 0.10227 | 0.00046 | 21 | 222.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 955 | J.25.01.0064 | ASY_2692 | ASY_2692 | 2025-09-01 17:32 | 2025-09-01 18:36 | 0.002831 | 4.4e-05 | 2 | 64.6 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 956 | J.25.01.0067 | SB1062 | SB1062 | 2025-10-01 08:13 | 2025-10-01 09:50 | 0.010612 | 0.00011 | 5 | 96.9 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 957 | J.25.01.0068 | H31 | H31 | 2025-03-02 09:05 | 2025-03-02 15:34 | 0.31554 | 0.000811 | 37 | 389.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 958 | J.25.01.0070 | KAI_5 | KAI_5 | 2025-05-02 08:07 | 2025-05-02 15:54 | 0.26559 | 0.000614 | 28 | 432.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 959 | J.25.01.0072 | ASY_2772 | ASY_2772 | 2025-10-02 09:09 | 2025-10-02 11:41 | 0.019944 | 0.000131 | 6 | 151.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 960 | J.25.01.0073 | ASY_2772 | ASY_2772 | 2025-10-02 13:10 | 2025-10-02 15:46 | 0.010242 | 6.6e-05 | 3 | 155.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 961 | J.25.01.0074 | T41 | T41 | 2025-10-01 15:46 | 2025-10-01 20:45 | 0.013116 | 4.4e-05 | 2 | 299.3 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 962 | J.25.01.0076 | KAI_6 | KAI_6 | 2025-11-01 00:12 | 2025-11-01 13:43 | 3.3673 | 0.017488 | 798 | 192.6 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 963 | J.25.01.0081 | KAI_5 | KAI_5 | 2025-11-01 17:23 | 2025-11-01 18:00 | 0.002388 | 6.6e-05 | 3 | 36.3 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 964 | J.25.01.0084 | P45 | P45 | 2025-01-13 11:31 | 2025-01-13 12:56 | 0.009319 | 0.00011 | 5 | 85.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 965 | J.25.01.0085 | X54 | X54 | 2025-02-18 09:04 | 2025-02-18 16:37 | 0.77603 | 0.001775 | 81 | 437.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 966 | J.25.01.0088 | ASY_2772 | ASY_2772 | 2025-01-13 16:25 | 2025-01-13 17:49 | 0.014662 | 0.000175 | 8 | 83.6 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 967 | J.25.01.0089 | Y33 | Y33 | 2025-02-20 22:17 | 2025-02-21 02:07 | 1.0208 | 0.004427 | 202 | 230.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 968 | J.25.01.0091 | KAI_5 | KAI_5 | 2025-01-14 13:46 | 2025-01-14 14:01 | 0.008518 | 0.00057 | 26 | 15 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 969 | J.25.01.0092 | N44 | N44 | 2025-01-14 14:05 | 2025-01-14 14:42 | 0.001602 | 4.4e-05 | 2 | 36.6 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 970 | J.25.01.0093 | W23 | W23 | 2025-02-25 09:06 | 2025-02-25 14:48 | 0.082322 | 0.000241 | 11 | 341.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 971 | J.25.01.0094 | X54 | X54 | 2025-02-17 09:49 | 2025-02-17 15:11 | 0.063429 | 0.000197 | 9 | 321.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 972 | J.25.01.0096 | SW65 | SW65 | 2025-01-15 12:40 | 2025-01-15 17:51 | 0.006814 | 2.2e-05 | 1 | 311 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 973 | J.25.01.0097 | P35 | P35 | 2025-01-24 09:54 | 2025-01-24 11:42 | 0.007109 | 6.6e-05 | 3 | 108.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 974 | J.25.01.0098 | U42 | U42 | 2025-02-13 09:18 | 2025-02-13 11:21 | 0.008115 | 6.6e-05 | 3 | 123.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 975 | J.25.01.0100 | KKA_1432 | KKA_1432 | 2025-10-02 10:12 | 2025-10-02 17:59 | 0.030715 | 6.6e-05 | 3 | 467.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 976 | J.25.01.0101 | KKA_1432 | KKA_1432 | 2025-11-02 08:20 | 2025-11-02 20:00 | 0.046033 | 6.6e-05 | 3 | 700.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 977 | J.25.01.0102 | KKA_1432 | KKA_1432 | 2025-02-13 08:05 | 2025-02-13 15:59 | 0.031174 | 6.6e-05 | 3 | 474.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 978 | J.25.01.0103 | KKA_1432 | KKA_1432 | 2025-02-14 08:03 | 2025-02-14 14:03 | 0.023672 | 6.6e-05 | 3 | 360.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 979 | J.25.01.0105 | P35 | P35 | 2025-01-16 09:28 | 2025-01-16 09:51 | 0.000513 | 2.2e-05 | 1 | 23.4 | Unplanned | Human Error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 980 | J.25.01.0107 | P45 | P45 | 2025-01-16 10:31 | 2025-01-16 10:32 | 3.1e-05 | 2.2e-05 | 1 | 1.4 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 981 | J.25.01.0108 | U32 | U32 | 2025-12-02 07:19 | 2025-12-02 20:09 | 0.027648 | 0.000197 | 18 | 70.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 982 | J.25.01.0109 | U32 | U32 | 2025-12-02 08:25 | 2025-12-02 18:34 | 0.99903 | 0.001644 | 75 | 607.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 983 | J.25.01.0111 | KAI_7 | KAI_7 | 2025-01-17 07:07 | 2025-01-17 08:04 | 0.002479 | 4.4e-05 | 2 | 56.6 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 984 | J.25.01.0112 | SW65 | SW65 | 2025-01-17 10:57 | 2025-01-17 11:56 | 0.001295 | 2.2e-05 | 1 | 59.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 985 | J.25.01.0114 | Y43 | Y43 | 2025-02-19 08:20 | 2025-02-19 17:36 | 0.23679 | 0.000438 | 20 | 540.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 986 | J.25.01.0116 | U42 | U42 | 2025-01-18 16:16 | 2025-01-18 17:15 | 0.018091 | 0.000307 | 14 | 59 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 987 | J.25.01.0120 | P45 | P45 | 2025-01-20 07:51 | 2025-01-20 09:07 | 0.009612 | 0.000131 | 6 | 73.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 988 | J.25.01.0121 | X54 | X54 | 2025-02-24 09:10 | 2025-02-24 15:23 | 0.26164 | 0.000701 | 32 | 373.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 989 | J.25.01.0123 | W21 | W21 | 2025-01-21 00:55 | 2025-01-21 02:09 | 0.003217 | 4.4e-05 | 2 | 73.4 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 990 | J.25.01.0126 | P25 | P25 | 2025-01-21 12:20 | 2025-01-21 13:48 | 0.003848 | 4.4e-05 | 2 | 87.8 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 991 | J.25.01.0130 | H31 | H31 | 2025-02-27 09:03 | 2025-02-27 15:28 | 0.033729 | 8.8e-05 | 4 | 384.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 992 | J.25.01.0132 | SW66 | SW66 | 2025-02-14 08:44 | 2025-02-14 11:19 | 0.003384 | 2.2e-05 | 1 | 154.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 993 | J.25.01.0133 | X55 | X55 | 2025-02-18 09:20 | 2025-02-18 14:47 | 0.007162 | 2.2e-05 | 1 | 326.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 994 | J.25.01.0134 | H41 | H41 | 2025-01-30 03:02 | 2025-01-30 03:05 | 0.001268 | 0.000351 | 16 | 3.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 995 | J.25.01.0143 | SW66 | SW66 | 2025-01-23 09:03 | 2025-01-23 10:03 | 0.2221 | 0.003725 | 170 | 59.6 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 996 | J.25.01.0147 | ASY_2772 | ASY_2772 | 2025-01-24 11:44 | 2025-01-24 11:56 | 0.001836 | 0.000153 | 7 | 12 | Unplanned | Human Error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 997 | J.25.01.0150 | X54 | X54 | 2025-01-25 06:55 | 2025-01-25 17:23 | 0.2757 | 0.000701 | 32 | 393.1 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 998 | J.25.01.0151 | X55 | X55 | 2025-01-25 20:18 | 2025-01-25 21:34 | 0.009943 | 0.000131 | 6 | 75.6 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 999 | J.25.01.0155 | KAI_5 | KAI_5 | 2025-01-26 18:38 | 2025-01-26 19:10 | 0.54108 | 0.01648 | 752 | 32.8 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1000 | J.25.01.0156 | ASY_2692 | ASY_2692 | 2025-01-26 18:44 | 2025-01-26 19:34 | 0.83404 | 0.016765 | 2295 | 16.6 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1001 | J.25.01.0162 | P35 | P35 | 2025-01-26 19:56 | 2025-01-26 20:53 | 0.0087 | 0.000153 | 7 | 56.7 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1002 | J.25.01.0163 | SW66 | SW66 | 2025-01-27 07:15 | 2025-01-27 08:38 | 0.084508 | 0.001074 | 49 | 78.7 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1003 | J.25.01.0180 | SB1142 | SB1142 | 2025-01-28 07:46 | 2025-01-28 08:45 | 0.001306 | 2.2e-05 | 1 | 59.6 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1004 | J.25.01.0181 | T41 | T41 | 2025-01-28 07:56 | 2025-01-28 15:34 | 0.261 | 0.002301 | 105 | 113.4 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1005 | J.25.01.0184 | H41 | H41 | 2025-05-02 02:56 | 2025-05-02 02:58 | 0.000748 | 0.000351 | 16 | 2.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1006 | J.25.01.0185 | CUL_1222 | CUL_1222 | 2025-10-02 11:26 | 2025-10-02 11:57 | 0.002004 | 6.6e-05 | 3 | 30.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1007 | J.25.01.0192 | P35 | P35 | 2025-01-29 07:24 | 2025-01-29 08:10 | 0.001013 | 2.2e-05 | 1 | 46.2 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1008 | J.25.01.0193 | Y43 | Y43 | 2025-02-24 08:39 | 2025-02-24 16:44 | 0.21279 | 0.000438 | 20 | 485.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1009 | J.25.01.0196 | SW62 | SW62 | 2025-01-29 10:24 | 2025-01-29 12:14 | 0.012066 | 0.00011 | 5 | 110.1 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1010 | J.25.01.0197 | SW65 | SW65 | 2025-02-26 09:06 | 2025-02-26 14:06 | 0.10546 | 0.000351 | 16 | 300.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1011 | J.25.01.0202 | X54 | X54 | 2025-10-03 13:08 | 2025-10-03 15:36 | 0.025812 | 0.000175 | 8 | 147.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1012 | J.25.01.0209 | P55 | P55 | 2025-01-30 14:16 | 2025-01-30 14:53 | 0.000821 | 2.2e-05 | 1 | 37.5 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1013 | J.25.01.0210 | U92 | U92 | 2025-02-21 08:37 | 2025-02-21 15:47 | 0.64001 | 0.00149 | 68 | 429.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1014 | J.25.01.0213 | W23 | W23 | 2025-02-20 09:57 | 2025-02-20 12:55 | 0.062126 | 0.000351 | 16 | 177.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1015 | J.25.01.0215 | P45 | P45 | 2025-01-31 14:34 | 2025-01-31 15:21 | 0.003103 | 6.6e-05 | 3 | 47.2 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1016 | J.25.02.0004 | SW63 | SW63 | 2025-01-02 07:42 | 2025-01-02 07:55 | 0.000546 | 4.4e-05 | 2 | 12.5 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1017 | J.25.02.0009 | SW66 | SW66 | 2025-01-02 23:03 | 2025-01-02 23:05 | 0.00011 | 6.6e-05 | 3 | 1.7 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1018 | J.25.02.0010 | X52 | X52 | 2025-01-02 22:35 | 2025-02-02 00:13 | 0.007347 | 0.000175 | 8 | 41.9 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1019 | J.25.02.0011 | P35 | P35 | 2025-02-02 04:53 | 2025-02-02 07:18 | 0.003181 | 2.2e-05 | 1 | 145.2 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1020 | J.25.02.0012 | ASY_2692 | ASY_2692 | 2025-03-02 04:30 | 2025-03-02 06:31 | 0.65419 | 0.005413 | 247 | 120.9 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1021 | J.25.02.0014 | W23 | W23 | 2025-03-02 08:15 | 2025-03-02 10:04 | 0.007131 | 6.6e-05 | 3 | 108.5 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1022 | J.25.02.0017 | ASY_2762 | ASY_2762 | 2025-02-27 08:14 | 2025-02-27 16:41 | 0.63004 | 0.001271 | 58 | 495.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1023 | J.25.02.0020 | W23 | W23 | 2025-04-02 08:03 | 2025-04-02 09:13 | 0.003067 | 4.4e-05 | 2 | 70 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1024 | J.25.02.0023 | N34 | N34 | 2025-03-03 16:11 | 2025-03-03 17:28 | 0.040612 | 0.000526 | 24 | 77.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1025 | J.25.02.0024 | N34 | N34 | 2025-03-03 15:52 | 2025-03-03 17:28 | 0.1259 | 0.001315 | 60 | 95.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1026 | J.25.02.0026 | H41 | H41 | 2025-02-17 03:46 | 2025-02-17 03:50 | 0.001344 | 0.000351 | 16 | 3.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1027 | J.25.02.0030 | N34 | N34 | 2025-04-03 06:06 | 2025-04-03 17:37 | 21.6775 | 0.034099 | 1556 | 635.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1028 | J.25.02.0031 | P55 | P55 | 2025-04-02 12:44 | 2025-04-02 14:16 | 0.017097 | 0.000263 | 12 | 65 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1029 | J.25.02.0032 | N34 | N34 | 2025-05-03 06:06 | 2025-05-03 18:15 | 24.7167 | 0.034033 | 1553 | 726.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1030 | J.25.02.0035 | SW65 | SW65 | 2025-04-02 15:59 | 2025-04-02 16:03 | 0.053986 | 0.013061 | 596 | 4.1 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1031 | J.25.02.0040 | P35 | P35 | 2025-05-02 09:19 | 2025-05-02 15:13 | 0.007752 | 2.2e-05 | 1 | 353.7 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1032 | J.25.02.0043 | SB1152 | SB1152 | 2025-02-27 23:30 | 2025-02-28 01:38 | 0.36112 | 0.002827 | 129 | 127.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1033 | J.25.02.0044 | U42 | U42 | 2025-05-02 18:11 | 2025-05-02 18:14 | 0.00217 | 0.000964 | 44 | 2.3 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1034 | J.25.02.0045 | U42 | U42 | 2025-05-02 18:22 | 2025-05-02 19:19 | 0.04836 | 0.000855 | 39 | 56.6 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1035 | J.25.02.0048 | Y43 | Y43 | 2025-03-13 09:22 | 2025-03-13 15:55 | 0.16325 | 0.000416 | 19 | 392.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1036 | J.25.02.0051 | N34 | N34 | 2025-08-02 05:04 | 2025-08-02 15:09 | 3.6519 | 0.022309 | 1018 | 163.7 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1037 | J.25.02.0062 | SW63 | SW63 | 2025-09-02 12:28 | 2025-09-02 15:05 | 0.4856 | 0.007122 | 325 | 68.2 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1038 | J.25.02.0068 | U92 | U92 | 2025-09-02 17:50 | 2025-09-02 18:58 | 0.001493 | 2.2e-05 | 1 | 68.2 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1039 | J.25.02.0070 | P45 | P45 | 2025-09-02 18:27 | 2025-09-02 19:02 | 0.003809 | 0.00011 | 5 | 34.8 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1040 | J.25.02.0072 | SW66 | SW66 | 2025-03-17 10:09 | 2025-03-17 16:31 | 0.008353 | 2.2e-05 | 1 | 381.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1041 | J.25.02.0073 | W21 | W21 | 2025-12-03 09:10 | 2025-12-03 15:21 | 0.064987 | 0.000175 | 8 | 370.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1042 | J.25.02.0078 | P55 | P55 | 2025-10-02 17:24 | 2025-10-02 17:45 | 0.000932 | 4.4e-05 | 2 | 21.3 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1043 | J.25.02.0080 | L52 | L52 | 2025-12-03 09:47 | 2025-12-03 12:31 | 0.12519 | 0.000767 | 35 | 163.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1044 | J.25.02.0083 | P45 | P45 | 2025-03-20 09:40 | 2025-03-20 16:38 | 0.36672 | 0.000877 | 40 | 418.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1045 | J.25.02.0086 | Y43 | Y43 | 2025-03-18 08:38 | 2025-03-18 16:37 | 0.2101 | 0.000438 | 20 | 479.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1046 | J.25.02.0087 | Y43 | Y43 | 2025-03-19 08:33 | 2025-03-19 16:23 | 0.20604 | 0.000438 | 20 | 470.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1047 | J.25.02.0089 | P55 | P55 | 2025-12-02 10:13 | 2025-12-02 11:12 | 0.001289 | 2.2e-05 | 1 | 58.8 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1048 | J.25.02.0090 | KAI_5 | KAI_5 | 2025-12-02 12:48 | 2025-12-02 14:01 | 0.34929 | 0.004909 | 224 | 71.2 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1049 | J.25.02.0092 | KAI_5 | KAI_5 | 2025-12-02 14:40 | 2025-12-02 18:37 | 0.03935 | 0.001271 | 58 | 31 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1050 | J.25.02.0095 | KAI_1 | KAI_1 | 2025-03-03 09:07 | 2025-03-03 10:30 | 0.019676 | 0.000241 | 11 | 81.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1051 | J.25.02.0097 | ASY_2772 | ASY_2772 | 2025-10-03 08:37 | 2025-10-03 13:47 | 0.30502 | 0.000986 | 45 | 309.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1052 | J.25.02.0098 | Y23 | Y23 | 2025-03-26 08:36 | 2025-03-26 17:07 | 0.12333 | 0.000241 | 11 | 511.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1053 | J.25.02.0099 | T41 | T41 | 2025-03-25 09:32 | 2025-03-25 15:14 | 0.014995 | 4.4e-05 | 2 | 342.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1054 | J.25.02.0108 | P25 | P25 | 2025-03-24 09:46 | 2025-03-24 14:57 | 0.01364 | 4.4e-05 | 2 | 311.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1055 | J.25.02.0117 | E80 | E80 | 2025-02-15 20:08 | 2025-02-15 22:27 | 0.17858 | 0.001293 | 59 | 138.1 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1056 | J.25.02.0118 | E80 | E80 | 2025-02-15 22:27 | 2025-02-16 18:43 | 0.026642 | 2.2e-05 | 1 | 1215.7 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1057 | J.25.02.0122 | P25 | P25 | 2025-02-16 15:34 | 2025-02-16 15:56 | 0.00145 | 6.6e-05 | 3 | 22.1 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1058 | J.25.02.0124 | E80 | E80 | 2025-02-16 18:07 | 2025-02-16 18:23 | 0.015827 | 0.001008 | 46 | 15.7 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1059 | J.25.02.0127 | H41 | H41 | 2025-03-28 08:32 | 2025-03-28 15:36 | 0.87428 | 0.00206 | 94 | 424.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1060 | J.25.02.0128 | SW62 | SW62 | 2025-03-31 08:39 | 2025-03-31 11:29 | 0.02246 | 0.000131 | 6 | 170.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1061 | J.25.02.0131 | ASY_2762 | ASY_2762 | 2025-02-27 08:14 | 2025-02-27 16:12 | 1.4805 | 0.003134 | 143 | 472.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1062 | J.25.02.0139 | ASY_2772 | ASY_2772 | 2025-02-17 15:00 | 2025-02-17 17:25 | 0.05097 | 0.000351 | 16 | 145.4 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1063 | J.25.02.0140 | X54 | X54 | 2025-02-17 17:30 | 2025-02-17 18:27 | 0.21948 | 0.003879 | 177 | 56.6 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1064 | J.25.02.0142 | K35 | K35 | 2025-02-18 07:06 | 2025-02-18 07:58 | 0.004586 | 8.8e-05 | 4 | 52.3 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1065 | J.25.02.0152 | SW62 | SW62 | 2025-02-18 12:44 | 2025-02-18 13:46 | 0.002724 | 4.4e-05 | 2 | 62.2 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1066 | J.25.02.0153 | ASY_2772 | ASY_2772 | 2025-02-18 12:24 | 2025-02-18 14:13 | 0.007216 | 6.6e-05 | 3 | 109.8 | Unplanned | Human Error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1067 | J.25.02.0155 | H21 | H21 | 2025-02-19 08:31 | 2025-02-19 09:16 | 0.001971 | 4.4e-05 | 2 | 45 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1068 | J.25.02.0157 | KAI_6 | KAI_6 | 2025-03-26 09:13 | 2025-03-26 11:37 | 0.003156 | 2.2e-05 | 1 | 144 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1069 | J.25.02.0158 | SB1082 | SB1082 | 2025-03-26 12:19 | 2025-03-26 14:42 | 0.009407 | 6.6e-05 | 3 | 143.1 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1070 | J.25.02.0159 | W23 | W23 | 2025-02-19 10:40 | 2025-02-19 12:53 | 0.058073 | 0.000438 | 20 | 132.5 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1071 | J.25.02.0164 | KAI_7 | KAI_7 | 2025-03-31 09:15 | 2025-03-31 12:11 | 0.023082 | 0.000131 | 6 | 175.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1072 | J.25.02.0172 | T41 | T41 | 2025-02-19 23:23 | 2025-02-20 09:01 | 0.025349 | 4.4e-05 | 2 | 578.4 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1073 | J.25.02.0177 | Y23 | Y23 | 2025-02-20 21:31 | 2025-02-20 21:43 | 0.44601 | 0.038394 | 1752 | 11.6 | Unplanned | Human Error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1074 | J.25.02.0178 | Y23 | Y23 | 2025-02-20 22:17 | 2025-02-21 02:07 | 0.37379 | 0.001622 | 74 | 230.5 | Unplanned | Human Error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1075 | J.25.02.0179 | P25 | P25 | 2025-02-21 06:10 | 2025-02-21 07:58 | 0.021229 | 0.000197 | 9 | 107.6 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1076 | J.25.02.0180 | SW62 | SW62 | 2025-02-21 06:16 | 2025-02-21 07:36 | 0.007016 | 8.8e-05 | 4 | 80 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1077 | J.25.02.0183 | Y33 | Y33 | 2025-02-21 08:58 | 2025-02-21 09:50 | 0.027717 | 0.000526 | 24 | 52.7 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1078 | J.25.02.0184 | U32 | U32 | 2025-03-25 08:40 | 2025-03-25 16:12 | 1.9801 | 0.004383 | 200 | 451.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1079 | J.25.02.0187 | KKA_1432 | KKA_1432 | 2025-03-20 09:41 | 2025-03-20 17:02 | 0.028993 | 6.6e-05 | 3 | 441 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1080 | J.25.02.0188 | KKA_1432 | KKA_1432 | 2025-03-21 08:08 | 2025-03-21 14:10 | 0.023785 | 6.6e-05 | 3 | 361.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1081 | J.25.02.0189 | KAI_5 | KAI_5 | 2025-02-21 16:01 | 2025-02-21 17:55 | 0.010066 | 8.8e-05 | 4 | 114.8 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1082 | J.25.02.0191 | N34 | N34 | 2025-02-22 22:31 | 2025-02-23 00:16 | 0.002284 | 2.2e-05 | 1 | 104.2 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1083 | J.25.02.0200 | H41 | H41 | 2025-11-03 00:55 | 2025-11-03 01:00 | 0.001601 | 0.000351 | 16 | 4.6 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1084 | J.25.02.0202 | P55 | P55 | 2025-11-03 10:09 | 2025-11-03 12:09 | 0.007837 | 6.6e-05 | 3 | 119.2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1085 | J.25.02.0208 | L52 | L52 | 2025-02-24 20:55 | 2025-02-25 09:31 | 0.38092 | 0.000504 | 23 | 755.8 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1086 | J.25.02.0211 | U42 | U42 | 2025-02-25 07:56 | 2025-02-25 09:28 | 0.004033 | 4.4e-05 | 2 | 92 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1087 | J.25.02.0213 | SB1172 | SB1172 | 2025-02-25 10:28 | 2025-02-25 10:33 | 0.012381 | 0.002389 | 109 | 5.2 | Unplanned | Human Error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1088 | J.25.02.0221 | W21 | W21 | 2025-02-25 13:38 | 2025-02-25 14:35 | 0.002526 | 4.4e-05 | 2 | 57.6 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1089 | J.25.02.0222 | X53 | X53 | 2025-02-25 13:58 | 2025-02-25 14:17 | 0.001706 | 8.8e-05 | 4 | 19.5 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1090 | J.25.02.0223 | L51 | L51 | 2025-02-25 14:02 | 2025-02-25 14:20 | 0.000389 | 2.2e-05 | 1 | 17.8 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1091 | J.25.02.0229 | W21 | W21 | 2025-02-26 10:28 | 2025-02-26 14:53 | 0.034767 | 0.000131 | 6 | 264.4 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1092 | J.25.02.0234 | X52 | X52 | 2025-02-27 06:58 | 2025-02-27 07:56 | 0.012846 | 0.000219 | 10 | 58.6 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1093 | J.25.02.0236 | U32 | U32 | 2025-02-27 10:24 | 2025-02-27 12:59 | 0.25211 | 0.001622 | 74 | 155.5 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1094 | J.25.02.0240 | SB1042 | SB1042 | 2025-03-14 09:11 | 2025-03-14 09:52 | 0.005347 | 0.000131 | 6 | 40.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1095 | J.25.02.0241 | Y33 | Y33 | 2025-03-20 22:03 | 2025-03-21 05:05 | 1.8592 | 0.004427 | 202 | 420 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1096 | J.25.02.0242 | ASY_2762 | ASY_2762 | 2025-02-27 16:37 | 2025-02-27 19:31 | 0.13365 | 0.000767 | 35 | 174.3 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1097 | J.25.03.0001 | SW65 | SW65 | 2025-01-03 01:35 | 2025-01-03 04:10 | 0.19012 | 0.001227 | 56 | 154.9 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1098 | J.25.03.0005 | G31 | G31 | 2025-01-03 09:29 | 2025-01-03 11:45 | 0.008895 | 6.6e-05 | 3 | 135.3 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1099 | J.25.03.0008 | ASY_2762 | ASY_2762 | 2025-01-03 11:51 | 2025-01-03 12:41 | 0.001087 | 2.2e-05 | 1 | 49.6 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1100 | J.25.03.0012 | T42 | T42 | 2025-02-03 04:45 | 2025-02-03 06:59 | 0.005859 | 4.4e-05 | 2 | 133.7 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1101 | J.25.03.0016 | X52 | X52 | 2025-03-03 07:58 | 2025-03-03 09:08 | 0.003056 | 4.4e-05 | 2 | 69.7 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1102 | J.25.03.0019 | ASY_2712 | ASY_2712 | 2025-03-31 09:05 | 2025-03-31 13:33 | 0.005861 | 2.2e-05 | 1 | 267.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1103 | J.25.03.0021 | SW64 | SW64 | 2025-03-03 08:44 | 2025-03-03 10:56 | 0.017367 | 0.000131 | 6 | 132.1 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1104 | J.25.03.0022 | SW63 | SW63 | 2025-03-17 14:16 | 2025-03-17 15:55 | 0.008737 | 8.8e-05 | 4 | 99.7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1105 | J.25.03.0036 | P35 | P35 | 2025-03-03 14:00 | 2025-03-03 16:12 | 0.054913 | 0.000416 | 19 | 131.9 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1106 | J.25.03.0037 | P55 | P55 | 2025-03-27 10:04 | 2025-03-27 13:50 | 0.019814 | 8.8e-05 | 4 | 226 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1107 | J.25.03.0044 | P45 | P45 | 2025-04-03 07:29 | 2025-04-03 10:29 | 0.015761 | 8.8e-05 | 4 | 179.8 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1108 | J.25.03.0050 | X52 | X52 | 2025-05-03 05:48 | 2025-05-03 07:07 | 0.008678 | 0.00011 | 5 | 79.2 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1109 | J.25.03.0051 | Y23 | Y23 | 2025-05-03 06:24 | 2025-05-03 08:12 | 0.01183 | 0.00011 | 5 | 108 | Unplanned | Adverse Weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1110 | J.25.03.0059 | SW64 | SW64 | 2025-03-27 09:09 | 2025-03-27 11:37 | 0.045223 | 0.000307 | 14 | 147.4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1111 | J.25.03.0064 | P45 | P45 | 2025-05-03 16:30 | 2025-05-03 22:26 | 0.015637 | 4.4e-05 | 2 | 356.8 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1112 | J.25.03.0071 | ASY_2762 | ASY_2762 | 2025-06-03 10:17 | 2025-06-03 11:24 | 0.001451 | 2.2e-05 | 1 | 66.2 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1113 | J.25.03.0077 | S34 | S34 | 2025-03-26 09:12 | 2025-03-26 16:10 | 1.0822 | 0.002586 | 118 | 418.5 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1114 | J.25.03.0079 | G32 | G32 | 2025-06-03 17:07 | 2025-06-03 17:48 | 0.006335 | 0.000153 | 7 | 41.3 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1115 | J.25.03.0081 | SW66 | SW66 | 2025-07-03 08:33 | 2025-07-03 09:14 | 0.000898 | 2.2e-05 | 1 | 41 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1116 | J.25.03.0082 | T43 | T43 | 2025-07-03 09:34 | 2025-07-03 12:00 | 0.009635 | 6.6e-05 | 3 | 146.6 | Unplanned | Defective Equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1117 | J.25.03.0092 | X55 | X55 | 2025-09-03 09:27 | 2025-09-03 11:07 | 0.00877 | 8.8e-05 | 4 | 100.1 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1118 | J.25.03.0093 | ASY_2772 | ASY_2772 | 2025-09-03 14:17 | 2025-09-03 15:06 | 0.001078 | 2.2e-05 | 1 | 49.2 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1119 | J.25.03.0109 | KAI_7 | KAI_7 | 2025-10-03 15:55 | 2025-10-03 17:40 | 0.082363 | 0.000789 | 36 | 104.4 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1120 | J.25.03.0114 | X52 | X52 | 2025-11-03 08:44 | 2025-11-03 09:29 | 0.000988 | 2.2e-05 | 1 | 45.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1121 | J.25.03.0120 | X55 | X55 | 2025-11-03 20:43 | 2025-11-03 23:06 | 0.022384 | 0.000175 | 8 | 127.7 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1122 | J.25.03.0125 | Y43 | Y43 | 2025-03-26 08:38 | 2025-03-26 17:00 | 0.22036 | 0.000438 | 20 | 502.8 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1123 | J.25.03.0126 | Y43 | Y43 | 2025-03-31 09:05 | 2025-03-31 11:32 | 0.27381 | 0.00206 | 94 | 132.9 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1124 | J.25.03.0127 | Y43 | Y43 | 2025-03-31 11:52 | 2025-03-31 15:35 | 0.15101 | 0.000679 | 31 | 222.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1125 | J.25.03.0136 | W23 | W23 | 2025-03-13 06:26 | 2025-03-13 08:06 | 0.008767 | 8.8e-05 | 4 | 100 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1126 | J.25.03.0137 | ASY_2762 | ASY_2762 | 2025-03-13 09:23 | 2025-03-13 10:43 | 0.001755 | 2.2e-05 | 1 | 80.1 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1127 | J.25.03.0138 | U82 | U82 | 2025-03-13 09:37 | 2025-03-13 10:10 | 0.025574 | 0.000789 | 36 | 32.4 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1128 | J.25.03.0147 | H31 | H31 | 2025-03-31 14:01 | 2025-03-31 14:41 | 0.49723 | 0.023361 | 1066 | 21.3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1129 | J.25.03.0148 | W21 | W21 | 2025-03-31 13:01 | 2025-03-31 13:05 | 0.062243 | 0.020424 | 932 | 3 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1130 | J.25.03.0153 | ASY_2772 | ASY_2772 | 2025-03-13 22:44 | 2025-03-13 23:39 | 0.005988 | 0.00011 | 5 | 54.7 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1131 | J.25.03.0154 | L53 | L53 | 2025-03-14 09:04 | 2025-03-14 11:19 | 0.020722 | 0.000153 | 7 | 135.1 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1132 | J.25.03.0159 | X52 | X52 | 2025-03-14 13:49 | 2025-03-14 21:46 | 0.50872 | 0.005939 | 271 | 85.7 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1133 | J.25.03.0174 | SW65 | SW65 | 2025-03-17 12:15 | 2025-03-17 14:45 | 0.052817 | 0.000351 | 16 | 150.6 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1134 | J.25.03.0180 | KAI_4 | KAI_4 | 2025-03-17 21:45 | 2025-03-17 22:55 | 0.001547 | 2.2e-05 | 1 | 70.6 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1135 | J.25.03.0187 | W21 | W21 | 2025-03-18 19:35 | 2025-03-18 22:02 | 0.006447 | 4.4e-05 | 2 | 147.1 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1136 | J.25.03.0190 | ASY_2762 | ASY_2762 | 2025-03-19 10:56 | 2025-03-19 13:11 | 0.00593 | 4.4e-05 | 2 | 135.3 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1137 | J.25.03.0194 | P55 | P55 | 2025-03-19 13:45 | 2025-03-19 15:21 | 0.00423 | 4.4e-05 | 2 | 96.5 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1138 | J.25.03.0196 | W21 | W21 | 2025-03-19 14:53 | 2025-03-19 16:06 | 0.006405 | 8.8e-05 | 4 | 73.1 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1139 | J.25.03.0199 | W23 | W23 | 2025-03-19 16:01 | 2025-03-19 16:42 | 0.0009 | 2.2e-05 | 1 | 41.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1140 | J.25.03.0205 | X56 | X56 | 2025-03-20 04:01 | 2025-03-20 06:59 | 0.86493 | 0.005325 | 243 | 162.4 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1141 | J.25.03.0208 | X56 | X56 | 2025-03-20 06:17 | 2025-03-20 09:56 | 0.1342 | 0.000614 | 28 | 218.7 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1142 | J.25.03.0216 | P55 | P55 | 2025-03-20 16:42 | 2025-03-20 18:14 | 0.024154 | 0.000263 | 12 | 91.9 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1143 | J.25.03.0219 | SW66 | SW66 | 2025-03-20 23:38 | 2025-03-21 01:07 | 0.023505 | 0.000263 | 12 | 89.4 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1144 | J.25.03.0223 | SW64 | SW64 | 2025-03-21 11:38 | 2025-03-21 11:58 | 0.000877 | 4.4e-05 | 2 | 20 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1145 | J.25.03.0229 | P45 | P45 | 2025-03-22 14:16 | 2025-03-22 15:17 | 0.004019 | 6.6e-05 | 3 | 61.1 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1146 | J.25.03.0231 | X52 | X52 | 2025-03-22 18:56 | 2025-03-22 20:40 | 0.002272 | 2.2e-05 | 1 | 103.7 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1147 | J.25.03.0232 | P55 | P55 | 2025-03-23 20:29 | 2025-03-23 21:39 | 0.003076 | 4.4e-05 | 2 | 70.2 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1148 | J.25.03.0235 | CUL_1222 | CUL_1222 | 2025-03-24 07:59 | 2025-03-24 09:41 | 0.022502 | 0.000219 | 10 | 102.7 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1149 | J.25.03.0243 | U42 | U42 | 2025-03-25 09:47 | 2025-03-25 12:42 | 0.15755 | 0.000898 | 41 | 175.4 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1150 | J.25.03.0249 | X52 | X52 | 2025-03-26 08:51 | 2025-03-26 10:40 | 0.020125 | 0.000307 | 14 | 65.6 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1151 | J.25.03.0256 | P35 | P35 | 2025-03-27 18:44 | 2025-03-27 19:30 | 0.004025 | 8.8e-05 | 4 | 45.9 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1152 | J.25.03.0259 | K36 | K36 | 2025-03-28 11:00 | 2025-03-28 12:02 | 0.001359 | 2.2e-05 | 1 | 62 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1153 | J.25.03.0260 | K36 | K36 | 2025-03-28 16:28 | 2025-03-28 17:24 | 0.001237 | 2.2e-05 | 1 | 56.5 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1154 | J.25.03.0268 | X52 | X52 | 2025-03-30 09:00 | 2025-03-30 10:08 | 0.011901 | 0.000175 | 8 | 67.9 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1155 | J.25.03.0271 | W21 | W21 | 2025-03-30 23:04 | 2025-03-31 01:25 | 0.009258 | 6.6e-05 | 3 | 140.8 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1156 | J.25.03.0275 | X52 | X52 | 2025-03-31 09:34 | 2025-03-31 11:10 | 0.002111 | 2.2e-05 | 1 | 96.4 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1157 | J.25.03.0276 | L51 | L51 | 2025-03-31 08:19 | 2025-03-31 10:13 | 0.002493 | 2.2e-05 | 1 | 113.8 | Unplanned | Unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
MainPower NZ | 2025 |  | 1158 | J.25.03.0281 | P45 | P45 | 2025-03-31 13:47 | 2025-03-31 15:12 | 0.003752 | 4.4e-05 | 2 | 85.6 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 9 | 2024-04-01-0003 | Scotland St - 0006608257MLAAA | CB54-Scotland St | 2024-04-01 17:55 | 2024-04-01 18:51 | 0 | 0 | 1 | 56 | Unplanned | Defective equipment | EAM 1468427 ------------- 1/04/2024 6:03:03 pm Outage restored Blown 60A RW pole fuse, replaced with 60A HRC. Restored 1850. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 10 | 2024-04-02-0011 | Seymour St - 0001155309MLD42 | CB51-Seymour St | 2024-04-02 07:52 | 2024-04-02 10:01 | 0 | 0 | 1 | 128 | Unplanned | Defective equipment | EAM 1468429 Arcing trurip repaired . Letters left in mailboxes for customers | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 11 | 2024-04-02-0006 | East Coast - FUSE3879 | REC29-East Coast | 2024-04-02 08:30 | 2024-04-02 11:35 | 0.027085 | 0.0001472 | 4 | 736 | Planned | Planned interruption | Planned shutdown for maintenance issues. EAM 1440836 SAF 3952 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 12 | 2024-04-02-0007 | Howick Rd North - 0001175501ML09D | CB84-Howick Rd North | 2024-04-02 09:10 | 2024-04-02 10:07 | 0 | 0 | 1 | 57 | Unplanned | Defective equipment | 2/04/2024 9:12:28 am EAM 1468436 Blown 30A fuse replaced | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 13 | 2024-04-02-0015 | Redwood St Nth - 0001107365ML198 | CB1655-Redwood St Nth | 2024-04-02 09:42 | 2024-04-02 11:50 | 0 | 0 | 1 | 127 | Unplanned | Defective equipment | EAM 1468438 Trurip from pole JA1456 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 14 | 2024-04-02-0016 | Redwood St Nth - 0001107413MLA48 | CB1655-Redwood St Nth | 2024-04-02 09:57 | 2024-04-02 12:45 | 0 | 0 | 1 | 168 | Unplanned | Defective equipment | EAM 1468450 Faulty Trurip replaced from pole KB3226 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 15 | 2024-04-02-0013 | Seymour St - LVUG1488 | CB51-Seymour St | 2024-04-02 10:45 | 2024-04-02 12:16 | 0 | 0 | 1 | 91 | Unplanned | Defective equipment | EAM 1468449 Trurip has been replaced between poles DF5276 and DF5277. Failed span outside boundary and not chargeable to customer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 16 | 2024-04-02-0017 | Nelson St - 0001115346MLBAC | CB93-Nelson St | 2024-04-02 11:38 | 2024-04-02 13:15 | 0 | 0 | 1 | 97 | Unplanned | Defective equipment | EAM 1468459 Repair of faulty Trurip | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 17 | 2024-04-02-0009 | French Pass - REC160 | CB45-French Pass | 2024-04-02 12:29 | 2024-04-02 12:29 | 0 | 0 | 17 | 0 | Unplanned | Unknown | REC160 succesful auto reclose on phase OC. Cyclo 45 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 18 | 2024-04-02-0008 | Waihopai Valley - SUB3410JF | CB5493 Waihopai Valley | 2024-04-02 12:30 | 2024-04-02 14:10 | 0.0072864 | 7.36e-05 | 2 | 198 | Planned | Planned interruption | Planned shutdown to install new service fuse at Sub3410JF. EAM 1454192 SAF 4015 ------------- | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 19 | 2024-04-02-0014 | Seymour St - LVOH2203 | CB51-Seymour St | 2024-04-02 12:49 | 2024-04-02 13:46 | 0 | 0 | 1 | 57 | Unplanned | Defective equipment | EAM 1468462 MLL owned Trurip replaced between poles DF5272 and DF5273 ------ | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 20 | 2024-04-02-0010 | Industrial Estate - 0003350162ML4EB | CB1182-Industrial Estate | 2024-04-02 14:29 | 2024-04-02 16:55 | 0 | 0 | 1 | 146 | Unplanned | Defective equipment | EAM 1468472 found 3x blown 100A service fuses. Porcelain bases replaced with ABC and awaiting customer to engage electrician to check installation before relivening. Customer to call customer service when ready to liven. No reason for fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 21 | 2024-04-02-0018 | Hospital Rd West - 0001174381ML271 | CB47-Hospital Rd West | 2024-04-02 18:22 | 2024-04-02 20:32 | 0 | 0 | 1 | 130 | Unplanned | Defective equipment | No power EAM1468499 found burnt out fuse holder in Pillae box XA1207 Replaced burnt out holder and confirmed power restored 2/04/2024 8:30:41 pm Yellow phase also blown at pole DF2454 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 22 | 2024-04-02-0019 | Weld St - 0001161401ML7F8 | CB71-Weld St | 2024-04-02 18:34 | 2024-04-03 17:00 | 0 | 0 | 1 | 1347 | Unplanned | Defective equipment | Arcing service line EAM1468500 Called in by neigbhor Found arcing line between pole and house. No one home so fuse pulled and left for repair/ replacement tomorrow. Replaced with NS Contacted cust | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 23 | 2024-04-02-0020 | Parker St - 0001139033ML2F0 | CB1516-Parker St | 2024-04-02 19:48 | 2024-04-02 20:37 | 0 | 0 | 1 | 49 | Unplanned | Other cause | No power EAM1468501 found blown service fuse with no obvious cause. replaced fuse and confirmed power restored. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 24 | 2024-04-03-0023 | Craiglochart - REC1391 | REC1391-Craiglochart | 2024-04-03 00:20 | 2024-04-03 00:20 | 0 | 0 | 126 | 0 | Unplanned | Unknown | Successful reclose of REC 1391 Earth Fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 25 | 2024-04-03-0022 | French Pass - SUB336219 | CB45-French Pass | 2024-04-03 08:30 | 2024-04-03 10:45 | 0.078899 | 0.0005888 | 16 | 2144 | Planned | Planned interruption | Planned shutdown to install SL bracket. EAM 1444123 SAF 3959 ----------- | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 26 | 2024-04-03-0024 | Woodbourne - FUSE2084 | CB1178-Woodbourne | 2024-04-03 09:06 | 2024-04-03 12:13 | 0 | 0 | 3 | 561 | Planned | Planned interruption | 3/04/2024 9:09:07 am EAM 1464365 NAMS4021 ---- | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 27 | 2024-04-03-0025 | Grovetown - 0003340565MLDC1 | CB1465-Grovetown | 2024-04-03 11:11 | 2024-04-04 13:01 | 0 | 0 | 1 | 1550 | Unplanned | Adverse weather | Trurip is faulty and needs to be replaced. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 28 | 2024-04-03-0026 | Dry Hills - 0001113025MLE5F | CB1682-Dry Hills | 2024-04-03 12:36 | 2024-04-03 14:08 | 0 | 0 | 1 | 92 | Unplanned | Defective equipment | EAM 1468594 Burnt out LV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 29 | 2024-04-04-0027 | French Pass - REC160 | CB45-French Pass | 2024-04-03 23:51 | 2024-04-03 23:51 | 0 | 0 | 17 | 0 | Unplanned | Unknown | Successful reclose of REC 160 Phase OC | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 30 | 2024-04-04-0029 | Craiglochart - REC1391 | REC1391-Craiglochart | 2024-04-04 00:03 | 2024-04-04 00:04 | 0 | 0 | 126 | 0 | Unplanned | Unknown | Successful reclose of REC 1391 Earth Fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 31 | 2024-04-04-0028 | Old Renwick Rd - SUB360123 | CB66-Old Renwick Rd | 2024-04-04 08:40 | 2024-04-04 10:30 | 0.0040848 | 3.68e-05 | 1 | 111 | Planned | Planned interruption | Planned switching to upgrade Sub. EAM 1463161 SAF 3985 ---- | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 32 | 2024-04-04-0030 | Seymour St - LVOH400929 | CB51-Seymour St | 2024-04-04 09:27 | 2024-04-04 13:33 | 0 | 0 | 1 | 246 | Planned | Planned interruption | 4/04/2024 9:36:31 am EAM1461515 NAMS4028 ------- | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 33 | 2024-04-04-0031 | Old Renwick Rd - SUB360121 | CB66-Old Renwick Rd | 2024-04-04 10:47 | 2024-04-04 11:58 | 0.0026128 | 3.68e-05 | 1 | 71 | Planned | Planned interruption | Planned job to replace TX footer, Install Falcon Protection, reheatshrink service cable SUB360121 EAM 1463161 EAM 3985 ----- | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 34 | 2024-04-04-0039 | Taylor Pass - 0001176405MLA73 | CB1089-Taylor Pass | 2024-04-04 16:00 | 2024-04-04 19:01 | 0 | 0 | 1 | 181 | Unplanned | Defective equipment | Arcing trurim at POLE DF3187 Trurip changed - replaced two trurips connected as three phase with one 3ph NS service li | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 35 | 2024-04-04-0040 | Taylor Pass - 0001176417ML05B | CB1089-Taylor Pass | 2024-04-04 16:00 | 2024-04-04 19:01 | 0 | 0 | 1 | 181 | Unplanned | Defective equipment | Arcing trurim at POLE DF3187 Trurip changed - replaced two trurips connected as three phase with one 3ph NS service li | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 36 | 2024-04-04-0038 | Taylor Pass - 0001176401MLB79 | CB1089-Taylor Pass | 2024-04-04 16:01 | 2024-04-04 19:01 | 0 | 0 | 1 | 181 | Unplanned | Defective equipment | Arcing trurim at POLE DF3187 Trurip changed - replaced two trurips connected as three phase with one 3ph NS service li | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 37 | 2024-04-05-0041 | Woodbourne - 0000011022ML200 | CB1178-Woodbourne | 2024-04-05 00:50 | 2024-04-05 16:28 | 0 | 0 | 1 | 938 | Unplanned | Defective equipment | Pulled fuse on arcing service line, to be replaced in morning. EAM 1468913 -------- | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 38 | 2024-04-05-0042 | Grovetown - 0003350433ML5A3 | CB1465-Grovetown | 2024-04-05 10:55 | 2024-04-05 16:30 | 0 | 0 | 1 | 335 | Unplanned | Defective equipment | 5/04/2024 11:08:33 am EAM 1468939 - Went to site and confirmed that loop test readings were and basically at the switchboard / meter panel the red & white core | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 39 | 2024-04-05-0043 | Wairau Valley - REC87 | CB5399 Wairau Valley | 2024-04-05 12:12 | 2024-04-05 12:36 | 0.12718 | 0.0052992 | 144 | 3456 | Unplanned | Unknown | REC87 Tripped on Earth Fault. F3503 - NAMS EAM 1469178 Line to be patrolled on Saturday. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 40 | 2024-04-05-0044 | Old Renwick Rd - CB66 | CB66-Old Renwick Rd | 2024-04-05 13:25 | 2024-04-05 14:14 | 0.35184 | 0.0091264 | 248 | 9561 | Unplanned | Third party interference | 11kV CABLE STRIKE EAM1469223 NAMSF3504 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 41 | 2024-04-05-0050 | Waikawa - 0006615234MLB5B | CB109- Waikawa | 2024-04-05 19:13 | 2024-04-05 19:13 | 0 | 0 | 1 | 0 | Unplanned | Defective equipment | Part power EAM1469236 -------------Found tripped RCD causing issue. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 42 | 2024-04-06-0051 | Renwick Township - 0000052307ML86C | CB5482 Renwick Township | 2024-04-06 08:01 | 2024-04-06 15:49 | 0 | 0 | 1 | 468 | Unplanned | Defective equipment | EAM1469239 Found blown fuse with no obvious cause replaced fuse and confirmed power restored. Fault came back in later in day Found failed service | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 43 | 2024-04-06-0052 | Murphys Rd - 0001131557ML40F | CB68-Murphys Rd | 2024-04-06 08:38 | 2024-04-06 10:51 | 0 | 0 | 1 | 132 | Unplanned | Defective equipment | EAM1469237 arcing service line beyond repair. Replaced service line, relivened and confirmed power restored. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 44 | 2024-04-06-0053 | Riverlands - 0003350173ML203 | CB1181-Riverlands | 2024-04-06 10:40 | 2024-04-06 13:51 | 0 | 0 | 1 | 191 | Unplanned | Defective equipment | EAM1469238 found arcing service line beyond repair replaced service line with owner approval and relivened supply | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 45 | 2024-04-06-0054 | Omaka - 0001123447MLC07 | CB1088 - Omaka | 2024-04-06 11:04 | 2024-04-06 11:44 | 0 | 0 | 1 | 40 | Unplanned | Unknown | EAM1469240 found blown re wireable fuse with no obvious cause. Replaced fuse with an HRC and left a letter with the customer. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 46 | 2024-04-06-0055 | Okaramio - 0007705220MLAC8 | CB104 Okaramio | 2024-04-06 12:19 | 2024-04-06 13:17 | 0 | 0 | 1 | 58 | Unplanned | Unknown | EAM1469241 blown 30a service fuse on blue phase with no obvious cause replaced fuse and confiirmed power restored. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 47 | 2024-04-08-0057 | Murphys Rd - RMUS5182-B | CB68-Murphys Rd | 2024-04-08 07:08 | 2024-04-08 10:16 | 0.068816 | 0.000368 | 10 | 1870 | Planned | Planned interruption | Planned Work http://nams.mll.co.nz/Schedule/Edit/3473 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 48 | 2024-04-08-0056 | McLauchlan St - 0001130010MLFC5 | CB65 - McLauchlan St | 2024-04-08 08:30 | 2024-04-08 09:36 | 0 | 0 | 1 | 65 | Unplanned | Defective equipment | EAM 1469270 Blown 60amp HRC fuse replaced suspect overloading Fuse letter left with customer ------------ | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 49 | 2024-04-08-0058 | Wairau Valley - SUB341748 | CB5399 Wairau Valley | 2024-04-08 12:47 | 2024-04-08 14:03 | 0 | 0 | 1 | 75 | Planned | Planned interruption | Connect upgraded earths Planned Work http://nams.mll.co.nz/Schedule/Edit/3502 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 50 | 2024-04-08-0059 | Hospital Rd West - 0001174237ML848 | CB47-Hospital Rd West | 2024-04-08 18:08 | 2024-04-08 19:25 | 0 | 0 | 1 | 76 | Unplanned | Defective equipment | EAM1469480 found burnt out cutout. Replaced with new sicame fuse holder re-livened and confirmed power restored. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 51 | 2024-04-08-0060 | Hospital Rd East - 0001182489MLF3B | CB39-Hospital Rd East | 2024-04-08 22:23 | 2024-04-08 23:15 | 0 | 0 | 1 | 52 | Unplanned | Defective equipment | no power EAM1469481 fund burnt out fuse carrier replaced fuse carrier and relivened supply | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 52 | 2024-04-09-0061 | Richmond Brook - SUB353095 | CB1250-Richmond Brook | 2024-04-09 08:30 | 2024-04-09 17:10 | 0.63149 | 0.0012144 | 33 | 17160 | Planned | Planned interruption | Planned shutdown for TX replacement. EAM 1436991 SAF 3856 ------------- | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 53 | 2024-04-09-0062 | Ward - ABS880-B | REC31-Ward | 2024-04-09 08:30 | 2024-04-09 15:44 | 0.17568 | 0.0004048 | 11 | 4774 | Planned | Planned interruption | Replacement of spalling poles in Tachalls Rd EAM1422365 NAMS3848 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 54 | 2024-04-10-0065 | Ward - ABS880-B | REC31-Ward | 2024-04-10 08:30 | 2024-04-10 14:50 | 0.15382 | 0.0004048 | 11 | 4180 | Planned | Planned interruption | Replacement of spalling poles in Tachalls Rd EAM1422365 NAMS3848 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 55 | 2024-04-10-0064 | Wairau Valley - ENS7015-B | CB5399 Wairau Valley | 2024-04-10 10:45 | 2024-04-10 15:17 | 0.01001 | 3.68e-05 | 1 | 272 | Planned | Planned interruption | Connection of new spurline at 4263 SH63 EAM1447896 NAMS3951 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 56 | 2024-04-11-0066 | Pelorus - SUB335160 | CB5126-Pelorus | 2024-04-11 05:53 | 2024-04-11 08:42 | 0.068411 | 0.0004048 | 11 | 1859 | Unplanned | Adverse weather | EAM 1469745 NAMS3525 1 HV fuse out at SUB335160, No obvious cause found other than reported high winds. Fuses replaced and power confirmed restored. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 57 | 2024-04-11-0068 | Wairau Valley - FUSE2149 | CB5399 Wairau Valley | 2024-04-11 07:15 | 2024-04-11 07:33 | 0.0006624 | 3.68e-05 | 1 | 18 | Unplanned | Unknown | Found 1 HV fuse blown at Fuses 2149. No apparent cause. http://nams.mll.co.nz/Schedule/Edit/3524 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 58 | 2024-04-11-0067 | Wairau Valley - FUSE3786 | CB5399 Wairau Valley | 2024-04-11 07:21 | 2024-04-11 08:53 | 0.0068448 | 7.36e-05 | 2 | 186 | Unplanned | Unknown | EAM 1469744 -------------. Found 1 blown HV fuse 3786 and replaced all 3. Cause unknown. http://nams.mll.co.nz/Schedule/Edit/3524 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 59 | 2024-04-11-0069 | Renwick Township - 0000052437ML096 | CB5482 Renwick Township | 2024-04-11 08:11 | 2024-04-11 09:56 | 0 | 0 | 1 | 105 | Unplanned | Defective equipment | EAM 1469773 power restored due to blown fuse (old age) Deterioration ------------- | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 60 | 2024-04-11-0072 | Colemans Rd - LVUG1820 | CB1512-Colemans Rd | 2024-04-11 08:15 | 2024-04-11 11:58 | 0 | 0 | 2 | 444 | Planned | Planned interruption | Planned work to replace SFB 40 EAM 1459685 SAF 3972 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 61 | 2024-04-11-0070 | Ward - SUB352451 | REC31-Ward | 2024-04-11 08:57 | 2024-04-11 11:07 | 0 | 0 | 2 | 260 | Planned | Planned interruption | Replacement of x-arms in Wests Rd, Ward EAM1386414 NAMS2707 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 62 | 2024-04-11-0071 | Vintage Lane - 0002271553ML9EF | CB171-Vintage Lane | 2024-04-11 10:48 | 2024-04-11 11:03 | 0 | 0 | 1 | 15 | Unplanned | Defective equipment | Rreleased tension on service cable. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 63 | 2024-04-11-0074 | Seymour St - 0001163133ML6C0 | CB51-Seymour St | 2024-04-11 16:45 | 2024-04-11 18:18 | 0 | 0 | 1 | 93 | Unplanned | Defective equipment | Replacing faulty Trurip (Network section) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 64 | 2024-04-11-0075 | Seymour St - 0001163129MLEFC | CB51-Seymour St | 2024-04-11 16:45 | 2024-04-11 18:19 | 0 | 0 | 1 | 93 | Unplanned | Defective equipment | Replacing faulty Trurip (Network section) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 65 | 2024-04-11-0076 | Richmond Brook - 0005503245ML81D | CB1250-Richmond Brook | 2024-04-11 17:04 | 2024-04-11 18:24 | 0 | 0 | 1 | 81 | Unplanned | Defective equipment | EAM 1469903 Faulty oven, electrician repairing in morning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 66 | 2024-04-11-0077 | Sounds - REC97 | REC1170-Sounds | 2024-04-11 17:41 | 2024-04-11 17:41 | 0 | 0 | 177 | 0 | Unplanned | Adverse weather | 11kV REC97 auto reclosed on phase OC. Red 165A Yellow 161A Blue 11A | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 67 | 2024-04-11-0078 | Sounds - REC97 | REC1170-Sounds | 2024-04-11 19:14 | 2024-04-11 19:14 | 0 | 0 | 177 | 0 | Unplanned | Adverse weather | REC97 auto reclose on phase overcurrent. Red 135 Yellow 131 Blue 11 Cyclo244 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 68 | 2024-04-11-0079 | Sounds - REC97 | REC1170-Sounds | 2024-04-11 20:07 | 2024-04-11 20:07 | 0 | 0 | 177 | 0 | Unplanned | Adverse weather | REC97 Auto Reclose on Phase OC. Red 165 Yellow 163 Blue 11 Cyclo 245 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 69 | 2024-04-11-0081 | Havelock Canvastown - REC1403 | CB103 Havelock Canvastown | 2024-04-11 20:09 | 2024-04-15 13:10 | 1.1689 | 0.0012512 | 29 | 31765 | Unplanned | Vegetation | EAM 1469904 NAMS F3529 REC1403 tripped on phase OC Line isolated and earthed at 11kV Fuse3353.Patrol found line down between AE1435 &KJ1998. cut line off road and made safe. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 70 | 2024-04-11-0082 | Sounds - REC97 | REC1170-Sounds | 2024-04-11 21:16 | 2024-04-11 21:16 | 0 | 0 | 177 | 0 | Unplanned | Adverse weather | 11kV REC97 auto reclose on Phase OC. Red 13 Yellow 167 Blue 164 Cyclo 247 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 71 | 2024-04-12-0083 | Murphys Rd - RMUF5163 | CB68-Murphys Rd | 2024-04-12 00:29 | 2024-04-12 02:30 | 0.0089056 | 7.36e-05 | 2 | 242 | Planned | Planned interruption | Planned shutdown to upgrade fuse unit and tails. EAM 1446864 SAF 4073 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 72 | 2024-04-12-0085 | Wairau Valley - 0002278486MLC46 | CB5399 Wairau Valley | 2024-04-12 07:41 | 2024-04-12 08:43 | 0 | 0 | 1 | 61 | Unplanned | Other cause | Blown service fuse - suspect overloading. EAM 1469908 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 73 | 2024-04-12-0086 | Colemans Rd - LVUG1806 | CB1512-Colemans Rd | 2024-04-12 08:18 | 2024-04-12 08:37 | 0 | 0 | 3 | 60 | Unplanned | Defective equipment | http://nams.mll.co.nz/Schedule/Edit/3530 Found 2 blown LV fuses at Pos 5 DP and replaced. Suspect fault at central metering caused issue | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 74 | 2024-04-12-0088 | Wairau Valley - FUSE3632 | CB5399 Wairau Valley | 2024-04-12 08:26 | 2024-04-15 14:43 | 0.37514 | 0.0003312 | 9 | 10194 | Unplanned | Vegetation | EAM 1469910 http://nams.mll.co.nz/Schedule/Edit/3531 Condcutor down between poles KB4811 and AX1762 . Isolated at FUSE3918 and replaced blown fuse at FUSE3632.o investigate restoration of span. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 75 | 2024-04-12-0089 | Weld St - 0001162510MLAF4 | CB71-Weld St | 2024-04-12 08:55 | 2024-04-12 09:55 | 0 | 0 | 1 | 61 | Unplanned | Defective equipment | 12/04/2024 8:55:08 am EAM 1469913 - Tripped RCD Outage | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 76 | 2024-04-12-0090 | French Pass - 0008805218MLDA8 | CB45-French Pass | 2024-04-12 09:18 | 2024-04-12 14:54 | 0 | 0 | 1 | 337 | Unplanned | Adverse weather | EAM 1469915 12/04/2024 2:47:49 pm Jumper came out of overhead, wind related | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 77 | 2024-04-12-0091 | French Pass - REC1466 | CB45-French Pass | 2024-04-12 09:27 | 2024-04-15 16:31 | 0.31111 | 0.0013248 | 36 | 8454 | Unplanned | Adverse weather | Meter Box reported smoking REC 1466 Opened for safety reason. feeding Wharf Pole MA1276 1469935 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 78 | 2024-04-12-0092 | Richmond Brook - SUB353282 | CB1250-Richmond Brook | 2024-04-12 10:02 | 2024-04-17 17:00 | 0 | 0 | 1 | 7619 | Unplanned | Third party interference | http://nams.mll.co.nz/Schedule/Edit/3533Burnt out meter board fed from SUB 353282 1 Services isolated and TX Reliven | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 79 | 2024-04-12-0093 | Kaituna - SUB340403 | CB5448 Kaituna | 2024-04-12 11:26 | 2024-04-12 12:25 | 0.0043424 | 7.36e-05 | 2 | 118 | Unplanned | Adverse weather | EAM 1469964 http://nams.mll.co.nz/Schedule/Edit/3534 found 1x blown HT fuse at SUB340403 - no cause found. Replaced both fuses, 6A. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 80 | 2024-04-12-0094 | Okaramio - 0007705349ML26D | CB104 Okaramio | 2024-04-12 11:58 | 2024-04-12 13:52 | 0 | 0 | 1 | 113 | Unplanned | Adverse weather | Blown LV HRC fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 81 | 2024-04-12-0095 | Sounds - 0007709456ML39C | REC1170-Sounds | 2024-04-12 20:38 | 2024-04-13 10:24 | 0 | 0 | 1 | 827 | Unplanned | Defective equipment | EAM 1470041 Burnt fuse holder - replaced | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 82 | 2024-04-13-0096 | Seymour St - 0001163081MLDF3 | CB51-Seymour St | 2024-04-13 09:28 | 2024-04-13 10:22 | 0 | 0 | 1 | 54 | Unplanned | Other cause | 2024-04-12-0095 Blown service fuse - incorrectly loadedat 30A, confirmed should be 60A via ARC, u | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 83 | 2024-04-13-0098 | Howick Rd North - 0001124654ML40D | CB84-Howick Rd North | 2024-04-13 09:35 | 2024-04-13 13:04 | 0 | 0 | 1 | 209 | Unplanned | Defective equipment | EAM 1470045 Burnt cable crutch-repaired/tested | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 84 | 2024-04-13-0099 | Ngakuta - 0007709300ML519 | REC1562-Ngakuta | 2024-04-13 11:51 | 2024-04-13 14:23 | 0 | 0 | 1 | 151 | Unplanned | Defective equipment | 1470049 Blown rewireable fuse due to deterioration | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 85 | 2024-04-13-0101 | Redwood St Nth - LVUG165935 | CB1655-Redwood St Nth | 2024-04-13 19:30 | 2024-04-13 22:50 | 0 | 0 | 5 | 1005 | Unplanned | Defective equipment | 1470050 Replaced 100A Fuse base at pole JA4259 using WI15. Note - fuse feeds SFB131 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 86 | 2024-04-14-0102 | Grassmere - 0005506217ML7B0 | CB1253-Grassmere | 2024-04-14 16:10 | 2024-04-14 17:21 | 0 | 0 | 1 | 71 | Unplanned | Defective equipment | 1470055 'No Power - was fixing the oven and when they turned it on the whole power came out and might have blown the fuse advised to turn off main switch | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 87 | 2024-04-15-0103 | Wairau Valley - ABS15245-B | CB5399 Wairau Valley | 2024-04-15 08:30 | 2024-04-15 10:53 | 0.015787 | 0.0001104 | 3 | 429 | Planned | Planned interruption | Connection of upgraded earths at ABS15245 EAM1409277 NAMS3917 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 88 | 2024-04-15-0104 | Richmond Brook - ENS7001-B | CB1250-Richmond Brook | 2024-04-15 10:11 | 2024-04-15 16:05 | 0.33642 | 0.0046 | 125 | 9142 | Unplanned | Defective equipment | EAM 1470130 NAMS - F3543 Reports of tipped crossarm ENS 7001 opened for safety Isolated at Fuse 2931. Pole ET2512 burnt out on top and will require replacement. Pole replaced power restored | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 89 | 2024-04-15-0105 | Buller St - 0006607139MLCA2 | CB108-Buller St | 2024-04-15 15:31 | 2024-04-16 07:16 | 0 | 0 | 1 | 945 | Unplanned | Defective equipment | EAM 1470198 Loose connector, fuse holder and fuse replaced | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 90 | 2024-04-16-0106 | Redwood St Nth - 0001107150ML128 | CB1655-Redwood St Nth | 2024-04-16 06:56 | 2024-04-16 08:45 | 0 | 0 | 1 | 110 | Unplanned | Defective equipment | EAM 1470202 Burnt out fuse - Photos sent to get box replaced. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 91 | 2024-04-16-0107 | Old Renwick Rd - SUB360128 | CB66-Old Renwick Rd | 2024-04-16 08:30 | 2024-04-16 11:50 | 0.01472 | 7.36e-05 | 2 | 400 | Planned | Planned interruption | Correction of low 11kV spans between NK1835 and NK1840 in Old Renwick Rd EAM1462902 NAMS4031 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 92 | 2024-04-16-0108 | French Pass - SUB336011 | CB45-French Pass | 2024-04-16 08:39 | 2024-04-16 14:56 | 1.0405 | 0.00276 | 75 | 28275 | Planned | Planned interruption | Planned shutdown to replace pole and increase span height. EAM 1403924 SAF 3672 ------------- 16/04/2024 8:42:37 am HM assigned to outage. 16/04/2024 8:43:02 am | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 93 | 2024-04-16-0109 | Wairau Valley - 0002278056MLD05 | CB5399 Wairau Valley | 2024-04-16 08:49 | 2024-04-16 13:47 | 0.011003 | 3.68e-05 | 1 | 299 | Unplanned | Wildlife | EAM 1470214 NAMS F3554 Upon Arrival found blown an HV fuse and dead Magpie as cause for fault. Fuses replaced in holders, Power confirmed restored. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 94 | 2024-04-16-0110 | Okaramio - HVOH2732-S20739 | CB104 Okaramio | 2024-04-16 09:03 | 2024-04-16 11:47 | 0.32181 | 0.0019504 | 53 | 8745 | Planned | Planned interruption | SH6 Planned Tree Work http://nams.mll.co.nz/Schedule/Edit/3496 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 95 | 2024-04-16-0112 | Sounds - 0008811059ML72E | REC1170-Sounds | 2024-04-16 16:33 | 2024-04-16 20:33 | 0 | 0 | 1 | 241 | Unplanned | Adverse weather | EAM1470368 NAMSF3559 found blown LV Fuse B Phase at SUB325201. Did not have replacement 100A din fuse. A Cutout was wired into place using WI16, HV Fuses pulled to connect then reliven. Power confirmed restored 2024-04-16-0112 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 96 | 2024-04-17-0116 | Havelock Canvastown - ABS867-B | CB103 Havelock Canvastown | 2024-04-17 08:30 | 2024-04-17 15:02 | 1.6445 | 0.0041952 | 114 | 44688 | Planned | Planned interruption | Removal of vegetation between KB2448 and AP2348 - Wakamarina Rd EAM1464279 NAMS4052 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 97 | 2024-04-17-0114 | Craiglochart - FUSE4002 | REC1391-Craiglochart | 2024-04-17 09:00 | 2024-04-17 14:31 | 0.024288 | 7.36e-05 | 2 | 660 | Planned | Planned interruption | Planned shutdown to upgrade transformer. EAM 1464797 SAF 4023 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 98 | 2024-04-17-0113 | Havelock Canvastown - FUSE2278 | CB103 Havelock Canvastown | 2024-04-17 09:03 | 2024-04-17 11:40 | 0.017333 | 0.0001104 | 3 | 471 | Planned | Planned interruption | EAM 1470391 All 3 ICPs on site are off - Sub320260 http://nams.mll.co.nz/Schedule/Edit/3563 found blown fuse at 11kV FUSE2278 , carried out line patrol nothing obvious found. Fuses replaced and closed power confirmed restored 2024-04-17-0113 2.37 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 99 | 2024-04-17-0115 | Hutcheson St - 0001101551ML4AC | CB49-Hutcheson St | 2024-04-17 09:08 | 2024-04-17 09:38 | 0 | 0 | 1 | 30 | Unplanned | Defective equipment | EAM 1470392 internal issue | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 100 | 2024-04-17-0119 | French Pass - FUSE3592 | CB45-French Pass | 2024-04-17 09:25 | 2024-04-17 15:20 | 0.94325 | 0.0026496 | 72 | 25632 | Planned | Planned interruption | Okiwi Bay Planned Work http://nams.mll.co.nz/Schedule/Edit/3483 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 101 | 2024-04-17-0117 | Rai Valley - 0007714233ML5E4 | CB43-Rai Valley | 2024-04-17 14:40 | 2024-04-17 17:38 | 0.0065504 | 3.68e-05 | 1 | 178 | Unplanned | Adverse weather | EAM1470462 NAMSF3565 found blown HV fuses at Sub 335357, No obvious cause found Fuses replaced and power confirmed restored | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 102 | 2024-04-17-0118 | Hawkesbury Road - ABS1779-B | CB5457 Hawkesbury Road | 2024-04-17 15:04 | 2024-04-17 17:04 | 0.38294 | 0.0031648 | 86 | 10406 | Unplanned | Defective equipment | Replacement of damaged pole at 471 Tetley Brook Rd - EAM1470431 NAMSF3565 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 103 | 2024-04-17-0120 | Weld St - 0001162249ML3AF | CB71-Weld St | 2024-04-17 15:05 | 2024-04-17 17:51 | 0 | 0 | 1 | 166 | Unplanned | Defective equipment | Fault with phase conductor at mains entry repaired - EAM 1470470 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 104 | 2024-04-17-0121 | Hawkesbury Road - 0002271063MLB12 | CB5457 Hawkesbury Road | 2024-04-17 18:01 | 2024-04-17 20:04 | 0 | 0 | 1 | 123 | Unplanned | Defective equipment | Internal fault with solar inverter - EAM 1470525 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 105 | 2024-04-18-0123 | Wairau Valley - SUB341653 | CB5399 Wairau Valley | 2024-04-18 08:30 | 2024-04-18 11:00 | 0.14352 | 0.0009568 | 26 | 3900 | Planned | Planned interruption | Connection of new HV earths & fuse replacement at SUB341653 - EAM1227280 NAMS3908 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 106 | 2024-04-18-0124 | Sounds - REC1350 | REC1170-Sounds | 2024-04-18 08:46 | 2024-04-18 15:49 | 2.6616 | 0.020608 | 366 | 72326 | Planned | Planned interruption | Lochmara ENTEC Planned Work http://nams.mll.co.nz/Schedule/Edit/3457 18/04/2024 9:28:04 am | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 107 | 2024-04-18-0125 | French Pass - REC160 | CB45-French Pass | 2024-04-18 09:00 | 2024-04-18 15:43 | 0.25212 | 0.0006256 | 17 | 6851 | Planned | Planned interruption | Planned shutdown to replace pole. EAM 1423643 SAF 3927 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 108 | 2024-04-18-0126 | Koromiko - SUB331222 | CB55-Koromiko | 2024-04-18 16:30 | 2024-04-18 17:33 | 0.0023184 | 3.68e-05 | 1 | 63 | Unplanned | Wildlife | EAM1470863 NAMSF3570 Found 2 x blown HV Fuses at SUB321222 Line Patrol carried out nothing obvious found Fuses replaced power confirmed restored 2024-04-18-0126 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 109 | 2024-04-18-0127 | Dashwood - FUSE2483 | CB1252-Dashwood | 2024-04-18 18:26 | 2024-04-18 20:33 | 0.088798 | 0.0006992 | 19 | 2413 | Unplanned | Wildlife | 2 blown fuses at FUSE2483 replaced - no cause found, suspect wildlife - EAM 1470873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 110 | 2024-04-18-0128 | Hawkesbury Road - 0002271034MLED0 | CB5457 Hawkesbury Road | 2024-04-18 18:31 | 2024-04-18 19:54 | 0 | 0 | 1 | 83 | Unplanned | Defective equipment | Faulty service fuse carrier replaced - EAM 1470874 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 111 | 2024-04-18-0129 | Hospital Rd East - 0001182017MLF46 | CB39-Hospital Rd East | 2024-04-18 19:36 | 2024-04-18 19:51 | 0 | 0 | 1 | 14 | Unplanned | Defective equipment | Burnt off lead on LV service fuse repaired - EAM 1470872 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 112 | 2024-04-19-0130 | Riverlands - CB1181 | CB1181-Riverlands | 2024-04-19 06:21 | 2024-04-19 07:07 | 0.077869 | 0.0016928 | 46 | 2116 | Unplanned | Wildlife | CB1181 tripped and locked out on phase OC. Patrolled, no cause found. EAM1470875 F3572 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 113 | 2024-04-19-0131 | Grovetown - SUB370209 | CB1465-Grovetown | 2024-04-19 08:30 | 2024-04-19 09:27 | 0.0020976 | 3.68e-05 | 1 | 57 | Planned | Planned interruption | Connection of new earths at SUB370209 - EAM1307676 NAMS 4053 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 114 | 2024-04-19-0132 | Thomsons Ford Rd - SUB357120 | CB1509-Thomsons Ford Rd | 2024-04-19 08:48 | 2024-04-19 10:43 | 0 | 0 | 6 | 690 | Planned | Planned interruption | Planned shutdown to replace damaged SFB. EAM 1457248 SAF 3975 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 115 | 2024-04-19-0133 | Thomsons Ford Rd - SUB357151 | CB1509-Thomsons Ford Rd | 2024-04-19 09:05 | 2024-04-19 09:34 | 0.0032016 | 0.0001104 | 3 | 87 | Planned | Planned interruption | http://nams.mll.co.nz/Schedule/Edit/3506 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 116 | 2024-04-19-0134 | Thomsons Ford Rd - SUB357159 | CB1509-Thomsons Ford Rd | 2024-04-19 09:54 | 2024-04-19 10:17 | 0.0008464 | 3.68e-05 | 1 | 23 | Planned | Planned interruption | Planned Work http://nams.mll.co.nz/Schedule/Edit/3506 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 117 | 2024-04-19-0137 | Grovetown - SUB370293 | CB1465-Grovetown | 2024-04-19 10:00 | 2024-04-19 11:18 | 0.0086112 | 0.0001104 | 3 | 234 | Planned | Planned interruption | Connection of new earths at SUB370293 - EAM1307676 NAMS4053 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 118 | 2024-04-19-0135 | Grovetown - SUB370293 | CB1465-Grovetown | 2024-04-19 10:01 | 2024-04-19 10:47 | 0.004968 | 0.0001104 | 3 | 135 | Planned | Planned interruption | Planned http://nams.mll.co.nz/Schedule/Edit/3498 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 119 | 2024-04-19-0136 | Parker St - 0001137385MLA0E | CB1516-Parker St | 2024-04-19 10:49 | 2024-04-19 11:26 | 0 | 0 | 1 | 38 | Unplanned | Defective equipment | EAM 1470951 Blown fuse No oblivious cause | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 120 | 2024-04-19-0138 | Dry Hills - 0001108332MLD3A | CB1682-Dry Hills | 2024-04-19 12:18 | 2024-04-19 13:37 | 0 | 0 | 1 | 79 | Unplanned | Unknown | EAM 1470998Tripped RCD Internal | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 121 | 2024-04-20-0139 | Havelock Canvastown - 0007703109MLF0F | CB103 Havelock Canvastown | 2024-04-20 07:25 | 2024-04-20 09:59 | 0 | 0 | 1 | 154 | Unplanned | Defective equipment | Faulty dervice fuse base replaced - EAM 1471135 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 122 | 2024-04-20-0140 | Havelock Canvastown - 0007710373ML8C5 | CB103 Havelock Canvastown | 2024-04-20 16:36 | 2024-04-21 18:40 | 0 | 0 | 1 | 1564 | Unplanned | Adverse weather | Have sent email to Connections to let them know about status of ICP.Safetey Discon as building | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 123 | 2024-04-20-0141 | Linkwater West - 0007715029ML67F | REC1168-Linkwater West | 2024-04-20 18:01 | 2024-04-21 11:22 | 0 | 0 | 1 | 1040 | Unplanned | Defective equipment | EAM 1471161 Faulty Main switch on incoming side isolated at pole owner repairing it tomorrow | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 124 | 2024-04-20-0142 | Hospital Rd West - 0001177037ML0AF | CB47-Hospital Rd West | 2024-04-20 23:17 | 2024-04-21 00:14 | 0 | 0 | 1 | 57 | Unplanned | Defective equipment | Failed rewirable fuse replaced with an HRC - EAM 1471163 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 125 | 2024-04-21-0143 | Wairau Valley - FUSE2164 | CB5399 Wairau Valley | 2024-04-21 06:52 | 2024-04-21 09:39 | 0.018547 | 0.0001104 | 3 | 504 | Unplanned | Wildlife | NAMS F3576 2 x blown Fuses found at 11kV FUSE2164, Line patrol carried out no obvious cause found Fuses replaced in and holding 2024-04-21-0143 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 126 | 2024-04-22-0144 | Old Renwick Rd - 0002272049ML636 | CB66-Old Renwick Rd | 2024-04-22 03:59 | 2024-04-22 05:00 | 0 | 0 | 1 | 61 | Unplanned | Defective equipment | Internal fault with customer generator changeover - EAM 1471165 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 127 | 2024-04-22-0145 | Godfrey Road - SUB343217 | CB5367 Godfrey Road | 2024-04-22 08:30 | 2024-04-22 11:15 | 0 | 0 | 1 | 165 | Planned | Planned interruption | TX isolation for connection of new service at SUB343217 EAM1457803 NAMS3993 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 128 | 2024-04-22-0147 | Wairau Valley - 0002278498ML570 | CB5399 Wairau Valley | 2024-04-22 17:06 | 2024-04-22 20:14 | 0 | 0 | 1 | 186 | Unplanned | Third party interference | EAM1471366 Customer Called to report wire down ( OH from Pole to house ) reported via neighbour n | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 129 | 2024-04-23-0148 | Spring Creek - ABS327-B | CB187-Spring Creek | 2024-04-23 09:10 | 2024-04-23 13:53 | 0.26036 | 0.00092 | 25 | 7075 | Planned | Planned interruption | http://nams.mll.co.nz/Schedule/Edit/3462 Planned Work | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 130 | 2024-04-23-0149 | Rai Valley - SUB335034 | CB43-Rai Valley | 2024-04-23 13:04 | 2024-04-23 16:11 | 0.013763 | 7.36e-05 | 2 | 374 | Unplanned | Unknown | EAM 1471437 http://nams.mll.co.nz/Schedule/Edit/3585 Urgent replacement of SUB335034 at Rai Valley due to a serious oil leak. Found while completing earth testing. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 131 | 2024-04-24-0150 | Sounds - FUSE3036 | REC1170-Sounds | 2024-04-24 09:00 | 2024-04-24 16:15 | 1.3287 | 0.0030544 | 83 | 36105 | Planned | Planned interruption | Planned shutdown to replace 11kV Sectionalisers with Entec equipment EAM1414006 NAMS 3709.1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 132 | 2024-04-24-0151 | Taylor Pass - 0001177205MLDD5 | CB1089-Taylor Pass | 2024-04-24 11:01 | 2024-04-24 11:46 | 0 | 0 | 1 | 44 | Unplanned | Defective equipment | EAM 1471565 blown fuses suspect internal issue | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 133 | 2024-04-24-0152 | Parker St - 0001146553MLBDC | CB1516-Parker St | 2024-04-24 14:45 | 2024-04-24 16:18 | 0 | 0 | 1 | 92 | Unplanned | Defective equipment | EAM 1471651 Blown fuse replaced | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 134 | 2024-04-25-0153 | Koromiko - 0006608357ML3AE | CB55-Koromiko | 2024-04-25 16:39 | 2024-04-25 17:43 | 0 | 0 | 1 | 63 | Unplanned | Defective equipment | Part power EAM1471668 found burnt out 100a fuse holder. Replaced with sicame fuse holder using WI16. Installed fuse and confirmed all power restored | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 135 | 2024-04-26-0154 | Richmond Brook - 0005505585ML530 | CB1250-Richmond Brook | 2024-04-26 09:14 | 2024-04-26 13:22 | 0 | 0 | 1 | 249 | Unplanned | Adverse weather | EAM 1471683 Burnt out cable clutch, caused by UV damage | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 136 | 2024-04-26-0155 | Howick Rd North - FUSE2901 | CB84-Howick Rd North | 2024-04-26 10:04 | 2024-04-26 10:12 | 0.0094208 | 0.0011776 | 32 | 256 | Unplanned | Human error | SAF4065 - WO 1468519 Tap change at SUB3700QF to reduced voltage. Changed from Tap 2 to Tap 1. Voltage changed from 242v to 236v. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 137 | 2024-04-26-0156 | Rai Valley - CB5391 | CB43 - Rai Valley, CB45 - French Pass, CB5126 - Pelorus | 2024-04-26 21:19 | 2024-04-26 21:19 | 0 | 0 | 915 | 0 | Unplanned | Unknown | 33kV CB 5391 - LVY-RAI reclosed on EF - Cyclo 154 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 138 | 2024-04-27-0157 | Godfrey Road - RMUF1573 | CB5367 Godfrey Road | 2024-04-27 08:01 | 2024-04-27 10:21 | 0.014941 | 0.0001104 | 3 | 406 | Unplanned | Unknown | EAM1471759 http://nams.mll.co.nz/Schedule/Edit/3594 11kV RMUF1573 found in the OFF position, but trip flag did not indicate. Replaced fuses (10A) and relivened OK. no cause for fault found. Fuse replacement done | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 139 | 2024-04-27-0159 | Colemans Rd - 0001131384ML38B | CB1512-Colemans Rd | 2024-04-27 08:30 | 2024-04-27 10:07 | 0 | 0 | 1 | 96 | Unplanned | Defective equipment | part power EAM1471760 found a blown fuse in the meterboard. Replaced fuse and confirmed power restored | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 140 | 2024-04-27-0160 | Hawkesbury Road - 0000054325ML07C | CB5457 Hawkesbury Road | 2024-04-27 08:51 | 2024-04-27 10:38 | 0 | 0 | 1 | 107 | Unplanned | Defective equipment | no power EAM1471761 found a burnt out fuseholder, Swapped service to a spare fuseholder relivened and confirmed power restored | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 141 | 2024-04-27-0161 | Parker St - 0001146437MLC22 | CB1516-Parker St | 2024-04-27 17:30 | 2024-04-27 18:05 | 0 | 0 | 1 | 35 | Unplanned | Defective equipment | no power EAM1471762 found a burnt out fuse holder in pillar XA1377. Replaced fuse holder and fuse and confirmed power restored | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 142 | 2024-04-27-0162 | Havelock Canvastown - REC5247 | CB103 Havelock Canvastown | 2024-04-27 17:45 | 2024-04-27 17:45 | 0 | 0 | 98 | 0 | Unplanned | Unknown | 11kV REC5247 reclosed on phase OC (OC1+) - Cyclo 88 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 143 | 2024-04-27-0163 | Parker St - 0001138012ML240 | CB1516-Parker St | 2024-04-27 18:05 | 2024-04-27 19:02 | 0 | 0 | 1 | 57 | Unplanned | Unknown | No Power EAM1471763 t found a blown service fuse with no obvious cause. Replaced fuse and confirmed power restored. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 144 | 2024-04-28-0164 | Tuamarina - SUB356159 | CB188-Tuamarina | 2024-04-28 08:37 | 2024-05-01 07:02 | 0.11798 | 0.0001472 | 2 | 3206 | Unplanned | Vegetation | EAM 1471765 http://nams.mll.co.nz/Schedule/Edit/3595 Line down reported found neutral screen burnt thru between pole DF2022 and house. LV service fuses had not blown (Rewirables) and 1 TX fuse had. Replaced TX fuse. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 145 | 2024-04-28-0172 | Pelorus - FUSE2285 | CB5126-Pelorus | 2024-04-28 11:16 | 2024-04-28 15:11 | 0.0086848 | 3.68e-05 | 1 | 236 | Unplanned | Wildlife | EAM 1471766 found 2 blown HT fuses and a dead magpie at SUB335137. Replaced blown fuses, 3A. 2 fuses also blown at 11kV FUSE2285. replaced, 10A. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 146 | 2024-04-28-0173 | Rai Valley - CB5391 | CB43 - Rai Valley, CB45 - French Pass, CB5126 - Pelorus | 2024-04-28 12:00 | 2024-04-28 12:00 | 0 | 0 | 914 | 0 | Unplanned | Unknown | 33kV CB 5391 - LVY - RAI reclosed on EF. Cyclo 155. flickering power, and Elaine Bay generator had alarms which needed investigation following tripping (EAM 1471767) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 147 | 2024-04-28-0170 | Hutcheson St - 0001102525ML21B | CB49-Hutcheson St | 2024-04-28 13:04 | 2024-04-28 15:02 | 0 | 0 | 1 | 118 | Planned | Planned interruption | SAF 3637.1 WO 1193617 Replacement of DP15 Arthur St - SD1 - Removal of cable from LV Pos 5 DP15 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 148 | 2024-04-28-0171 | Hutcheson St - 0001102041ML9E4 | CB49-Hutcheson St | 2024-04-28 13:04 | 2024-04-28 15:02 | 0 | 0 | 1 | 118 | Planned | Planned interruption | SAF 3637.1 WO 1193617 Replacement of DP15 Arthur St - SD1 - Removal of cable from LV Pos 5 DP15 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 149 | 2024-04-28-0167 | Hutcheson St - 0001101551ML4AC | CB49-Hutcheson St | 2024-04-28 13:07 | 2024-04-28 15:00 | 0 | 0 | 1 | 113 | Planned | Planned interruption | SAF 3637.1 WO 1193617 Replacement of DP15 Arthur St - SD1 - Removal of cable from LV Pos 5 DP15 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 150 | 2024-04-28-0168 | Hutcheson St - 0001101547MLF8E | CB49-Hutcheson St | 2024-04-28 13:07 | 2024-04-28 15:00 | 0 | 0 | 1 | 113 | Planned | Planned interruption | SAF 3637.1 WO 1193617 Replacement of DP15 Arthur St - SD1 - Removal of cable from LV Pos 5 DP15 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 151 | 2024-04-28-0169 | Hutcheson St - 0001101543MLE84 | CB49-Hutcheson St | 2024-04-28 13:07 | 2024-04-28 15:00 | 0 | 0 | 1 | 113 | Planned | Planned interruption | SAF 3637.1 WO 1193617 Replacement of DP15 Arthur St - SD1 - Removal of cable from LV Pos 5 DP15 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 152 | 2024-04-29-0174 | Spring Creek - 0003315529ML82E | CB187-Spring Creek | 2024-04-29 05:09 | 2024-04-29 07:03 | 0 | 0 | 1 | 114 | Unplanned | Defective equipment | Part power EAM1471768 found burnt out aluminum tube connector. Replaced connecter using WI16 and confirmed power restored. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 153 | 2024-04-29-0175 | Richmond Brook - FUSE3075 | CB1250-Richmond Brook | 2024-04-29 08:53 | 2024-04-29 12:06 | 0.02841 | 0.0001472 | 4 | 772 | Planned | Planned interruption | Replacement of LV service arm at pole DF4150 - EAM1454333 NAMS3893 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 154 | 2024-04-29-0177 | Waikawa - ABS15332-B | CB109- Waikawa | 2024-04-29 08:58 | 2024-04-29 15:25 | 0.44035 | 0.0011408 | 31 | 11966 | Planned | Planned interruption | HV & LV mainteance between poles AX1785 and AK1146 - EAM1457898 NAMS4025 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 155 | 2024-04-29-0178 | Wairau Valley - FUSE3952 | CB5399 Wairau Valley | 2024-04-29 09:14 | 2024-04-29 13:57 | 0.072643 | 0.0002576 | 7 | 1974 | Planned | Planned interruption | SH63 Planned Work http://nams.mll.co.nz/Schedule/Edit/3589 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 156 | 2024-04-29-0179 | Waikawa - FUSE2251 | CB109- Waikawa | 2024-04-29 10:44 | 2024-04-29 13:11 | 0.21638 | 0.001472 | 40 | 5880 | Planned | Planned interruption | http://nams.mll.co.nz/Schedule/Edit/3450 Arapawa Island Planned Work | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 157 | 2024-04-29-0180 | Sounds - 0008811353ML6BC | REC1170-Sounds | 2024-04-29 11:49 | 2024-04-30 10:27 | 0 | 0 | 1 | 1358 | Unplanned | Defective equipment | EAM 1471817 Blown fuse on the sub main side. Replaced No oblivious reason - if its a fuse he will fix, otherwiseget all required details so we can prep and replace submain trurip | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 158 | 2024-04-29-0181 | Hutcheson St - 0001102525ML21B | CB49-Hutcheson St | 2024-04-29 16:31 | 2024-04-29 17:49 | 0 | 0 | 1 | 78 | Planned | Planned interruption | SAF 3637.1 WO 1193617 Replacement of DP15 Arthur St - SD1 - Part 2 - reconnection of cable to LV Pos 4 at DP22 Arthur St | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 159 | 2024-04-29-0182 | Hutcheson St - 0001102041ML9E4 | CB49-Hutcheson St | 2024-04-29 16:31 | 2024-04-29 17:49 | 0 | 0 | 1 | 78 | Planned | Planned interruption | SAF 3637.1 WO 1193617 Replacement of DP15 Arthur St - SD1 - Part 2 - reconnection of cable to LV Pos 4 at DP22 Arthur St | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 160 | 2024-04-30-0183 | Linkwater West - 0007709073MLF87 | REC1168-Linkwater West | 2024-04-30 08:59 | 2024-04-30 17:01 | 0 | 0 | 1 | 482 | Unplanned | Defective equipment | EAM 1471934 HRC fuse (MLL side) Fuse Letter given | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 161 | 2024-04-30-0184 | Sounds - SUB325407 | REC1170-Sounds | 2024-04-30 09:02 | 2024-04-30 12:19 | 0 | 0 | 2 | 394 | Planned | Planned interruption | Vegetation removal at 4214 Kenepuru Rd - EAM1405884 NAMS4079 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 162 | 2024-04-30-0185 | Waikawa - 0006630069ML8E2 | CB109- Waikawa | 2024-04-30 11:17 | 2024-04-30 15:00 | 0 | 0 | 1 | 223 | Unplanned | Defective equipment | EAM 1471946 Burnt out LV fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 163 | 2024-04-30-0187 | Sounds - SUB325201 | REC1170-Sounds | 2024-04-30 13:00 | 2024-04-30 13:14 | 0 | 0 | 13 | 182 | Planned | Planned interruption | EAM1471781 NAMSF3599 Outage to replace Temporary fuse at Krone switch | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 164 | 2024-04-30-0200 | Hutcheson St - 0001101551ML4AC | CB49-Hutcheson St | 2024-04-30 16:31 | 2024-04-30 19:48 | 0 | 0 | 1 | 197 | Planned | Planned interruption | Arthur St Planned Work http://nams.mll.co.nz/Application/Edit/3639 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 165 | 2024-04-30-0199 | Hutcheson St - 0001101543MLE84 | CB49-Hutcheson St | 2024-04-30 16:31 | 2024-04-30 19:48 | 0 | 0 | 1 | 197 | Planned | Planned interruption | Arthur St Planned Work http://nams.mll.co.nz/Application/Edit/3639 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 166 | 2024-04-30-0201 | Hutcheson St - 0001101547MLF8E | CB49-Hutcheson St | 2024-04-30 16:31 | 2024-04-30 19:47 | 0 | 0 | 1 | 197 | Planned | Planned interruption | Arthur St Planned Work http://nams.mll.co.nz/Application/Edit/3639 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 167 | 2024-04-30-0194 | East Coast, REC31 - Ward, REC1432 - Flaxbourne - CB5412 | REC29 - East Coast, REC31 - Ward, REC1432 - Flaxbourne | 2024-04-30 18:01 | 2024-04-30 19:34 | 0.47479 | 0.011629 | 316 | 12902 | Unplanned | Unknown | EAM 1472022 Phase OC tripping of REC 31 Causing 33kV tripping of 5412 and loss of Ward Sub relivened via SCADA Line patrol completed for REC 31 no cause found. Feeder relivened 1472022 http://nams.mll.co.nz/Schedule/Edit/3608 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 168 | 2024-04-30-0202 | McLauchlan St - 0001130010MLFC5 | CB65 - McLauchlan St | 2024-04-30 19:55 | 2024-04-30 21:01 | 0 | 0 | 1 | 65 | Unplanned | Other cause | EAM 1472023 Blown Blue phase fuse, 47A. ARC says it should be a 3ph 60A supply | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 169 | 2024-05-01-0003 | Scotland St - LVOH1954 | CB54-Scotland St | 2024-05-01 08:30 | 2024-05-01 14:50 | 0 | 0 | 1 | 380 | Planned | Planned interruption | Service outage in Market St, Picton for installation of new fuses - EAM1458149 NAMS4029 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 170 | 2024-05-01-0001 | Vintage Lane - FUSE2222 | CB171-Vintage Lane | 2024-05-01 08:31 | 2024-05-01 15:34 | 0.12424 | 0.0002944 | 8 | 3376 | Planned | Planned interruption | SAF 3851 WO 1433251 Replacement of poles 1 & 12 for the Tapp Tee project. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 171 | 2024-05-01-0002 | McLauchlan St - 0001130010MLFC5 | CB65 - McLauchlan St | 2024-05-01 09:02 | 2024-05-01 10:21 | 0 | 0 | 1 | 78 | Unplanned | Other cause | EAM 1472028 Blown Blue phase fuse, 47A.(the other 2 were 30amp) ARC says it should be a 3ph 60A supply?? | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 172 | 2024-05-01-0004 | Kaituna - REC5232 | CB5448 Kaituna | 2024-05-01 11:42 | 2024-05-01 12:33 | 0.12295 | 0.0026128 | 36 | 3341 | Unplanned | Third party interference | Digger Hit Earth Wire REC 5232 Opened for sefety http://nams.mll.co.nz/Schedule/Edit/3612 2024-05-01-0004 Transformer earth wire found hit TX Isolated 5232 closed and earth wire repaired before livening TX | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 173 | 2024-05-01-0005 | Redwood St Sth - 0001188405ML72F | CB1673-Redwood St Sth | 2024-05-01 11:49 | 2024-05-01 13:16 | 0 | 0 | 1 | 86 | Unplanned | Defective equipment | EAM 1472096 Blown fuse no cause identified | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 174 | 2024-05-01-0006 | Parker St - 0001146413ML07D | CB1516-Parker St | 2024-05-01 16:44 | 2024-05-01 17:40 | 0 | 0 | 1 | 57 | Unplanned | Unknown | EAM 1472220 Arrived onsite and property had power. Checked all connections whilst onsite. All okay. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 175 | 2024-05-01-0007 | Koromiko - 0006609759MLD94 | CB55-Koromiko | 2024-05-01 18:17 | 2024-05-01 20:15 | 0 | 0 | 1 | 119 | Unplanned | Defective equipment | EAM 1472222 Burnout Lv fuse, replaced. Power restored | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 176 | 2024-05-02-0010 | Hutcheson St - 0001101108MLEF4 | CB49-Hutcheson St | 2024-05-02 07:06 | 2024-05-02 08:11 | 0 | 0 | 1 | 64 | Planned | Planned interruption | Arthur St Planned Work http://nams.mll.co.nz/Schedule/Edit/3528 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 177 | 2024-05-02-0009 | Hutcheson St - 0001101107ML12A | CB49-Hutcheson St | 2024-05-02 07:07 | 2024-05-02 08:11 | 0 | 0 | 1 | 64 | Planned | Planned interruption | Arthur St Planned Work http://nams.mll.co.nz/Schedule/Edit/3528 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 178 | 2024-05-02-0008 | Pelorus - FUSE2503 | CB5126-Pelorus | 2024-05-02 08:30 | 2024-05-02 13:40 | 0.28428 | 0.00092 | 25 | 7725 | Planned | Planned interruption | TX upgrade at SUB335221 - EAM1458202 NAMS4044 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 179 | 2024-05-03-0011 | Godfrey Road - 0002270551ML8CA | CB5367 Godfrey Road | 2024-05-03 08:16 | 2024-05-03 09:27 | 0 | 0 | 1 | 71 | Unplanned | Defective equipment | EAM 1474207replaced burnt Fuse base using WI Power restored | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 180 | 2024-05-03-0012 | Weld St - LVOH8390 | CB71-Weld St | 2024-05-03 08:30 | 2024-05-03 11:44 | 0 | 0 | 9 | 1746 | Planned | Planned interruption | Re-Sag of LV conductors between DF5834 and DF5837 - EAM1454512 NAMS3956 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 181 | 2024-05-03-0013 | French Pass - 0008802287ML9F1 | CB45-French Pass | 2024-05-03 10:00 | 2024-05-03 14:24 | 0.0097152 | 3.68e-05 | 1 | 264 | Unplanned | Defective equipment | EAM 1474252 http://nams.mll.co.nz/Schedule/Edit/3615 NO POWER LV Phase burnt of TX Access permit to repair | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 182 | 2024-05-03-0014 | Taylor Pass - 0001179093ML17A | CB1089-Taylor Pass | 2024-05-03 19:51 | 2024-05-03 21:01 | 0 | 0 | 1 | 71 | Unplanned | Defective equipment | EAM 1474397 Faulty oven caused the pole fuse to blow. Advised to have it checked out and not to use it in the mean time. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 183 | 2024-05-05-0015 | Scotland St - 0006608165MLED4 | CB54-Scotland St | 2024-05-05 14:13 | 2024-05-05 15:30 | 0 | 0 | 1 | 78 | Unplanned | Defective equipment | EAM 1474403 Blown pole fuse due to deterioration. Replaced with HRC, | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 184 | 2024-05-05-0016 | Parker St - 0001146358ML30E | CB1516-Parker St | 2024-05-05 15:01 | 2024-05-05 17:15 | 0 | 0 | 1 | 135 | Unplanned | Third party interference | EAM 1474404 Damaged service cable by unknown vehicle. Repaired and livened at 1715. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 185 | 2024-05-06-0017 | Vintage Lane - FUSE2222 | CB171-Vintage Lane | 2024-05-06 08:30 | 2024-05-06 14:54 | 0.11305 | 0.0002944 | 8 | 3072 | Planned | Planned interruption | Planned shutdown to replace poles behind Woodbourne Sub for Tapp Tee project. EAM 1433251 SAF 3851 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 186 | 2024-05-06-0018 | Scotland St - 0006608233ML450 | CB54-Scotland St | 2024-05-06 10:20 | 2024-05-06 11:45 | 0 | 0 | 1 | 85 | Unplanned | Defective equipment | EAM 1475998 Internal fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 187 | 2024-05-07-0019 | Buller St - LVUG3978 | CB108-Buller St | 2024-05-07 09:00 | 2024-05-07 16:09 | 0 | 0 | 8 | 3432 | Planned | Planned interruption | NAMS4101 EAM1470080 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 188 | 2024-05-07-0020 | Thomsons Ford Rd - FUSE4177 | CB1509-Thomsons Ford Rd | 2024-05-07 09:03 | 2024-05-07 14:52 | 0.064032 | 0.000184 | 5 | 1740 | Planned | Planned interruption | Old Renwick Road Planned Work 1 http://nams.mll.co.nz/Schedule/Edit/3547 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 189 | 2024-05-07-0021 | McLauchlan St - FUSE2065 | CB65 - McLauchlan St | 2024-05-07 09:10 | 2024-05-07 14:56 | 0.089387 | 0.0002576 | 7 | 2429 | Planned | Planned interruption | Old Renwick Road Planned Work 2 http://nams.mll.co.nz/Schedule/Edit/3547 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 190 | 2024-05-07-0022 | Hutcheson St - 0001153264ML12D | CB49-Hutcheson St | 2024-05-07 09:14 | 2024-05-07 09:51 | 0 | 0 | 1 | 36 | Unplanned | Defective equipment | EAM 1476662 Blowen fuse Suspect overloading | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 191 | 2024-05-07-0023 | Koromiko - 0006608373MLFF1 | CB55-Koromiko | 2024-05-07 11:17 | 2024-05-07 11:53 | 0 | 0 | 1 | 36 | Unplanned | Unknown | EAM 1476695 Tripped RCD in house - Unable to check Shed Advised to get Electrictian if shed has no power | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 192 | 2024-05-07-0024 | Wairau Valley - SUB3414BR | CB5399 Wairau Valley | 2024-05-07 13:30 | 2024-05-07 15:01 | 0.0033856 | 3.68e-05 | 1 | 92 | Unplanned | Unknown | EAM 1476745 http://nams.mll.co.nz/Schedule/Edit/3621 1x blown fuse found at SUB3414BR. No cause found. All 3 fuses replaced, 6A | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 193 | 2024-05-07-0025 | Grassmere - 0005506393MLAF4 | CB1253-Grassmere | 2024-05-07 13:36 | 2024-05-07 14:37 | 0 | 0 | 1 | 61 | Unplanned | Defective equipment | EAM 1476744 Blown Pole fuse - No oblivious reason | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 194 | 2024-05-08-0026 | Craiglochart - REC1391 | REC1391-Craiglochart | 2024-05-08 01:24 | 2024-05-08 05:59 | 1.0154 | 0.0066976 | 126 | 27592 | Unplanned | Defective equipment | http://nams.mll.co.nz/Schedule/Edit/3622 EAM 1478707 REC tripped on Earth Fault. Unsuccesful trial close. Found cracked insulator on centre phase at pole BS2331 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 195 | 2024-05-08-0027 | Hospital Rd West - RMUS1565-B | CB47-Hospital Rd West | 2024-05-08 08:31 | 2024-05-08 19:29 | 0.48429 | 0.000736 | 20 | 13160 | Planned | Planned interruption | SAF4069.1 - WO 1439980 Upgrade of SUB3700CE from 750kVA to 1000kVA. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 196 | 2024-05-08-0028 | Hutcheson St - 0001153264ML12D | CB49-Hutcheson St | 2024-05-08 10:14 | 2024-05-08 11:00 | 0 | 0 | 1 | 46 | Unplanned | Defective equipment | EAM 1478761 Blown pole fuse replaced - caused by overloading (New heaters) customer in talks to get upgrade amps | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 197 | 2024-05-09-0029 | Rai Valley - CB5391 | CB43 - Rai Valley, CB45 - French Pass, CB5126 - Pelorus | 2024-05-09 03:12 | 2024-05-09 03:12 | 0.033672 | 0.033672 | 915 | 915 | Unplanned | Unknown | Auto Reclose on Earth fault. Cyclo 156. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 198 | 2024-05-09-0031 | Redwood St Nth - 0001107401ML060 | CB1655-Redwood St Nth | 2024-05-09 08:27 | 2024-05-09 09:58 | 0 | 0 | 1 | 91 | Planned | Planned interruption | 9/05/2024 8:36:41 am EAM1468503 NAMS4070 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 199 | 2024-05-09-0033 | Redwood St Nth - 0001107499MLD93 | CB1655-Redwood St Nth | 2024-05-09 08:27 | 2024-05-09 09:58 | 0 | 0 | 1 | 91 | Planned | Planned interruption | 9/05/2024 8:37:21 am EAM1468503 NAMS4070 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 200 | 2024-05-09-0034 | Redwood St Nth - 0001107413MLA48 | CB1655-Redwood St Nth | 2024-05-09 08:27 | 2024-05-09 09:58 | 0 | 0 | 1 | 91 | Planned | Planned interruption | 9/05/2024 8:37:13 am EAM1468503 NAMS4070 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 201 | 2024-05-09-0030 | Buller St - FUSE2216 | CB108-Buller St | 2024-05-09 08:30 | 2024-05-09 12:51 | 0.0096416 | 3.68e-05 | 1 | 262 | Unplanned | Vegetation | Tree on 11kV lines near Pole DF4767. 11kV fuses 2216 both blown. EAM 1479467 http://nams.mll.co.nz/Schedule/Edit/3626 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 202 | 2024-05-09-0035 | Howick Rd North - 0001175081ML0D2 | CB84-Howick Rd North | 2024-05-09 10:38 | 2024-05-09 11:20 | 0 | 0 | 1 | 43 | Planned | Planned interruption | Reconfiguration of LV service conductors in Karina Crescent - EAM1470775 NAMS4105 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 203 | 2024-05-09-0036 | Old Renwick Rd - LVOH99702 | CB66-Old Renwick Rd | 2024-05-09 13:02 | 2024-05-09 14:20 | 0 | 0 | 2 | 156 | Planned | Planned interruption | Planned shutdown to raise low span. EAM 1469615 NAMS 4100 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 204 | 2024-05-09-0037 | Hospital Rd West - 0001174440ML6D9 | CB47-Hospital Rd West | 2024-05-09 22:07 | 2024-05-09 23:04 | 0 | 0 | 1 | 56 | Unplanned | Defective equipment | EAM 1479706 Lights were flickering, now no power HRC fuse damaged, carrier appeared to be OK | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 205 | 2024-05-10-0038 | Richmond Brook - ABS1831-B | CB1250-Richmond Brook | 2024-05-10 08:33 | 2024-05-10 14:04 | 0.1093 | 0.0003312 | 9 | 2970 | Planned | Planned interruption | Planned shutdown to move Sub and replace hardware at second site EAM 1390324 SAF 2954 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 206 | 2024-05-10-0039 | Symons St - 0001104233ML3FB | CB50-Symons St | 2024-05-10 10:45 | 2024-05-10 11:33 | 0 | 0 | 1 | 47 | Unplanned | Defective equipment | EAM 1479839 is attending Submain issue Not on MLL side | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 207 | 2024-05-11-0040 | Craiglochart - FUSE3896 | REC1391-Craiglochart | 2024-05-11 19:29 | 2024-05-11 23:07 | 0.032089 | 0.0001472 | 4 | 872 | Unplanned | Third party interference | Broken cross arm at pole ZA3194 EAM 1479925 http://nams.mll.co.nz/Schedule/Edit/3631 Pole ZA3194. X-arm, insulators and braces replaced | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 208 | 2024-05-13-0047 | Dry Hills - 0001116959ML635 | CB1682-Dry Hills | 2024-05-13 08:05 | 2024-05-13 10:30 | 0 | 0 | 1 | 146 | Unplanned | Defective equipment | EAM 1479928 Burnt out cutout at SUB348554 replaced | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 209 | 2024-05-13-0042 | Kaituna - FUSE2105 | CB5448 Kaituna | 2024-05-13 08:36 | 2024-05-13 12:51 | 0.18768 | 0.000736 | 20 | 5100 | Planned | Planned interruption | Planned shutdown to remove burning vegetation. EAM 1455194 SAF 4095 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 210 | 2024-05-13-0045 | Wairau Valley - 0002278566MLFF8 | CB5399 Wairau Valley | 2024-05-13 09:39 | 2024-05-13 13:53 | 0 | 0 | 1 | 253 | Unplanned | Unknown | EAM 1479956 Replaced fuse on yellow phase. All had HRC fuses, unsure issue, but test fine at time of repair | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 211 | 2024-05-13-0044 | Taylor Pass - 0001195333MLC9B | CB1089-Taylor Pass | 2024-05-13 13:21 | 2024-05-13 15:29 | 0 | 0 | 1 | 129 | Unplanned | Unknown | EAM 1480083 Internal RCD - Oven | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 212 | 2024-05-14-0048 | Rapaura Rd - 0004421435ML31E | CB1077-Rapaura Rd | 2024-05-14 08:53 | 2024-05-14 10:56 | 0 | 0 | 1 | 122 | Unplanned | Other cause | EAM 1480155 HRC fuse blown - fuse letter issued. Suspect overloading - customer needs to get balace done on lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 213 | 2024-05-14-0049 | Jacksons Road - 0004421480MLCE3 | CB1179-Jacksons Road | 2024-05-14 16:51 | 2024-05-14 17:52 | 0 | 0 | 1 | 62 | Unplanned | Defective equipment | EAM 1480276 Outage ID 2024-05-14-0049 30 Amp HRC fuse replaced | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 214 | 2024-05-15-0054 | Parker St - 0001139265ML170 | CB1516-Parker St | 2024-05-15 12:54 | 2024-05-15 13:31 | 0 | 0 | 1 | 36 | Unplanned | Defective equipment | EAM 1480419 Burnt out pole fuse - no cause given | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 215 | 2024-05-15-0055 | Godfrey Road - 0002270477MLD14 | CB5367 Godfrey Road | 2024-05-15 15:29 | 2024-05-15 16:21 | 0.0018768 | 3.68e-05 | 1 | 51 | Unplanned | Wildlife | EAM 1480499 NAMS F3647 found dead possum below SUB343221 11kV Tx Fuses replaced (3A) and power confirmed restored 2024-05-15-0055 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 216 | 2024-05-16-0058 | Weld St - FUSE22237 | CB71-Weld St | 2024-05-16 08:57 | 2024-05-16 16:06 | 0 | 0 | 4 | 1716 | Planned | Planned interruption | Installation of new SFB42 Weld St - EAM1472232 NAMS4140 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 217 | 2024-05-17-0059 | Wairau Valley - 0002278130MLA7E | CB5399 Wairau Valley | 2024-05-17 09:10 | 2024-05-17 11:07 | 0 | 0 | 1 | 116 | Unplanned | Unknown | EAM 1480751 Blown 30amp pole fuse blue phase. 1amp on livening. No cause found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 218 | 2024-05-17-0060 | Vernon - SUB349053 | CB5184-Vernon | 2024-05-17 11:50 | 2024-05-17 13:35 | 0.012365 | 0.0001472 | 4 | 336 | Unplanned | Third party interference | Repairs to LV connections at Sub349053 after investigating AC fail alarm. Loose connection on stanger replaced. Voltages at TX still incorrect. Found upstream centre phase fuse blown at 11kV Fuses 2074 and replaced. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 219 | 2024-05-17-0061 | McLauchlan St - 0001128764ML171 | CB65 - McLauchlan St | 2024-05-17 12:43 | 2024-05-17 13:13 | 0 | 0 | 1 | 31 | Unplanned | Unknown | EAM 1480768 Outage restored by: MLL\jlanders Replaced blown 60A fuse 17/05/2024 1:13:30 pm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 220 | 2024-05-17-0062 | Dry Hills - LVUG302650 | CB1682-Dry Hills | 2024-05-17 13:38 | 2024-05-17 13:44 | 0 | 0 | 2 | 12 | Unplanned | Human error | EAM 1480770 NAMS F3652 SFB34 had un-connected Neutral to Neutral Bar | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 221 | 2024-05-17-0064 | Howick Rd North - 0001173429ML318 | CB84-Howick Rd North | 2024-05-17 20:09 | 2024-05-17 20:59 | 0 | 0 | 1 | 49 | Unplanned | Defective equipment | Repaired burnt off lead from service fuse. EAM 1480817 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 222 | 2024-05-18-0065 | Redwood St Nth - 0001108347ML528 | CB1655-Redwood St Nth | 2024-05-18 17:41 | 2024-05-18 18:21 | 0 | 0 | 1 | 41 | Unplanned | Defective equipment | Retailer Disconnect - EAM 1480822 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 223 | 2024-05-18-0066 | Wairau Valley - 0002278476MLC51 | CB5399 Wairau Valley | 2024-05-18 19:02 | 2024-05-18 20:16 | 0 | 0 | 1 | 74 | Unplanned | Defective equipment | Incorrect fuse insalled - 32A, should have been 63A EAM 1480823 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 224 | 2024-05-19-0067 | Hawkesbury Road - 0002271236ML452 | CB5457 Hawkesbury Road | 2024-05-19 08:44 | 2024-05-19 09:40 | 0 | 0 | 1 | 55 | Unplanned | Other cause | EAM 1480824 - Blown fuse, overload | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 225 | 2024-05-19-0068 | Rai Valley - 0007714005ML994 | CB43-Rai Valley | 2024-05-19 11:56 | 2024-05-19 14:14 | 0 | 0 | 1 | 137 | Unplanned | Unknown | EAM 1480825 - Blown fuse, suspect overload | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 226 | 2024-05-19-0069 | Rapaura Rd - 0004421435ML31E | CB1077-Rapaura Rd | 2024-05-19 18:12 | 2024-05-19 19:04 | 0 | 0 | 1 | 52 | Unplanned | Other cause | Blown service fuse - overload - EAM 1480155 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 227 | 2024-05-19-0071 | Hawkesbury Road - REC5436 | CB5457 Hawkesbury Road | 2024-05-19 22:10 | 2024-05-19 22:10 | 0 | 0 | 176 | 0 | Unplanned | Unknown | Circuit reclose - no cause found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 228 | 2024-05-20-0072 | Wairau Valley - ABS861-B | CB5399 Wairau Valley | 2024-05-20 08:04 | 2024-05-20 10:28 | 0.17892 | 0.0012512 | 34 | 4862 | Planned | Planned interruption | SAF 4123 - WO 1472075 HV shutdown for Liquid Action to pull out pump for service next to SUB3141SO. Steel pipe will be around 1m from HV line. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 229 | 2024-05-20-0073 | Parker St - 0001139594ML220 | CB1516-Parker St | 2024-05-20 08:46 | 2024-05-20 09:45 | 0 | 0 | 1 | 60 | Unplanned | Defective equipment | EAM 1480859 Blown fuse (Old porcelain changed to ABC type) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 230 | 2024-05-21-0075 | Koromiko - 0006632113ML56A | CB55-Koromiko | 2024-05-21 09:10 | 2024-05-21 15:31 | 0 | 0 | 1 | 381 | Unplanned | Third party interference | EAM 1481127 turned up to site, and found fuse pulled and no label on who has done this Customer service has no info of this being an retail disconnect (as customer has smart meter) Connections are contact retailer to see what action they want us to take | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 231 | 2024-05-21-0076 | Spring Creek - 0003315469ML38F | CB187-Spring Creek | 2024-05-21 16:23 | 2024-05-21 17:40 | 0 | 0 | 1 | 78 | Unplanned | Defective equipment | Lead burnt off service fuse holder - repaired - EAM 1481403 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 232 | 2024-05-21-0077 | Havelock Canvastown - 0007713005MLDF4 | CB103 Havelock Canvastown | 2024-05-21 17:15 | 2024-05-21 19:38 | 0 | 0 | 1 | 142 | Unplanned | Adverse weather | Blown service fuse due to conductor clashing - EAM 1481417 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 233 | 2024-05-22-0079 | Hawkesbury Road - SUB343019 | CB5457 Hawkesbury Road | 2024-05-22 09:00 | 2024-05-22 10:41 | 0.0074336 | 7.36e-05 | 2 | 202 | Unplanned | Unknown | Lines down TX outage to repair http://nams.mll.co.nz/Schedule/Edit/3663 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 234 | 2024-05-22-0078 | Sounds - ABS580-B | REC1170-Sounds | 2024-05-22 09:11 | 2024-05-22 16:43 | 1.181 | 0.0026128 | 71 | 32092 | Planned | Planned interruption | Endeavour Inlet Planned Work http://nams.mll.co.nz/Schedule/Edit/3569 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 235 | 2024-05-22-0080 | East Coast - 0005515257MLF14 | REC29-East Coast | 2024-05-22 11:28 | 2024-05-22 14:30 | 0 | 0 | 1 | 181 | Unplanned | Unknown | EAM 1481605 Internal fault No issue with MLL network Electrictian required | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 236 | 2024-05-23-0085 | Seaview - CB1251 | CB1251 - Seaview | 2024-05-23 05:12 | 2024-05-23 08:20 | 0.051225 | 0.0018032 | 49 | 1392 | Unplanned | Wildlife | 11kV CB1251 tripped and locked out on phase OC. Cyclo 67. Successfully relivened feeder after 15min. No power reported 2x blown fuses found at FUSE3737 and a dead swan on the ground 3 span from the fuses. All 3 fuses replaced | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 237 | 2024-05-23-0082 | Spring Creek - FUSE2182 | CB187-Spring Creek | 2024-05-23 05:30 | 2024-05-23 07:52 | 0.052256 | 0.000368 | 10 | 1420 | Unplanned | Unknown | EAM 1481703 1x 11kV fuse blown at FUSE2182. Line patrolled and nothing found. All 3 fuses replaced (20A). Confirmed power restored http://nams.mll.co.nz/Schedule/Edit/3665 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 238 | 2024-05-23-0086 | Vintage Lane - FUSE2222 | CB171-Vintage Lane | 2024-05-23 08:30 | 2024-05-23 16:55 | 0.14867 | 0.0002944 | 8 | 4040 | Planned | Planned interruption | Planned shut down to install OPGW from Jacksons to Tapp via Woodbourne. EAM 1433251 SAF 3808.1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 239 | 2024-05-23-0087 | Wairau Valley - FUSE3510 | CB5399 Wairau Valley | 2024-05-23 08:30 | 2024-05-23 14:27 | 0.026275 | 7.36e-05 | 2 | 714 | Planned | Planned interruption | Planned shutdown to install new pole & conductors under 110kV line at 3920 SH63. EAM 1435313 SAF 4067 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 240 | 2024-05-23-0088 | Hospital Rd West - 0001177077ML20A | CB47-Hospital Rd West | 2024-05-23 08:52 | 2024-05-23 09:23 | 0 | 0 | 1 | 31 | Unplanned | Other cause | EAM 1481716 Blown fuse - No letter left as incorrect fuse size used - ARC show 60amp, but on site is 30amp Correct fuse now used | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 241 | 2024-05-23-0089 | French Pass - FUSE2321 | CB45-French Pass | 2024-05-23 10:25 | 2024-05-23 16:36 | 0.027306 | 7.36e-05 | 2 | 742 | Planned | Planned interruption | D`Urville Island Planned Work http://nams.mll.co.nz/Schedule/Edit/3579 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 242 | 2024-05-24-0090 | Havelock Canvastown - LVOH7921 | CB103 Havelock Canvastown | 2024-05-24 08:30 | 2024-05-24 08:50 | 0 | 0 | 1 | 20 | Planned | Planned interruption | Planned shutdown to re-sag LV line. EAM 1469221 SAF 4078 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 243 | 2024-05-24-0091 | Colemans Rd - 0001130547MLF02 | CB1512-Colemans Rd | 2024-05-24 10:39 | 2024-05-24 11:02 | 0 | 0 | 1 | 24 | Unplanned | Unknown | EAM 1483602 Internal issue all power working apart from hot water. customer advised to get Electrictian | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 244 | 2024-05-26-0093 | Rai Valley - CB2032 | CB43 - Rai Valley, CB45 - French Pass, CB5126 - Pelorus | 2024-05-26 12:57 | 2024-05-26 12:57 | 0 | 0 | 914 | 0 | Unplanned | Unknown | 33kV CB2032 (BLN-LVY) reclosed on Earh fault and Phase OC inverse time (Yellow & Blue phases) Line patrolled but nothing found. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 245 | 2024-05-26-0092 | Renwick Township - 0000050354MLFE4 | CB5482 Renwick Township | 2024-05-26 14:08 | 2024-05-26 16:01 | 0 | 0 | 1 | 112 | Unplanned | Defective equipment | EAM 1484423 Burntout Lv fuse, replaced with new ABC fuse. Restored 1600. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 246 | 2024-05-27-0094 | Nelson St - LVOH3588-S14621 | CB93-Nelson St | 2024-05-27 08:30 | 2024-05-27 13:22 | 0 | 0 | 14 | 4088 | Planned | Planned interruption | Planned shutdown to replace pole JA2220. EAM 1430306 SAF4018 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 247 | 2024-05-27-0095 | Buller St - 0006606574MLCFD | CB108-Buller St | 2024-05-27 08:45 | 2024-05-27 12:54 | 0 | 0 | 1 | 189 | Unplanned | Other cause | EAM 1484434 Blue phase blown. Fuse replace - suspect overloading Fuse letter to be sent EAM 1484517 Customer has called to advise that they have blown another fuse - different one this time this time its the lights. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 248 | 2024-05-27-0096 | Richmond Brook - FUSE2479 | CB1250-Richmond Brook | 2024-05-27 09:30 | 2024-05-27 16:10 | 0.17664 | 0.0004416 | 12 | 4800 | Planned | Planned interruption | Planned work - Remove Spurline & Replace Stub Pole. EAM 1443498 SAF 3980 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 249 | 2024-05-29-0097 | Pelorus - FUSE2285 | CB5126-Pelorus | 2024-05-29 06:50 | 2024-05-29 08:48 | 0.0043792 | 3.68e-05 | 1 | 119 | Unplanned | Wildlife | Found 2 blown 11kV fuses at Fuse site 2285 No cause found - suspect bird Confirmed power restored with Customer EAM 1485004 http://nams.mll.co.nz/Schedule/Edit/3701 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 250 | 2024-05-29-0098 | Vintage Lane - FUSE2222 | CB171-Vintage Lane | 2024-05-29 08:30 | 2024-05-29 15:19 | 0.12011 | 0.0002944 | 8 | 3264 | Planned | Planned interruption | Planned shutdown for OPGW install at Woodbourne. EAM1433251 SAF 3811.1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 251 | 2024-05-29-0099 | Old Renwick Rd - 0002271599MLC91 | CB66-Old Renwick Rd | 2024-05-29 08:50 | 2024-05-29 09:50 | 0 | 0 | 1 | 59 | Unplanned | Defective equipment | EAM 1485025 internal 2 tripped circuit breakers (no issues on MLL network) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 252 | 2024-05-29-0100 | Richmond Brook - ABS610-B | CB1250-Richmond Brook | 2024-05-29 09:00 | 2024-05-29 15:06 | 0.6716 | 0.00184 | 50 | 18250 | Planned | Planned interruption | EAM1405831 NAMS4108 Arborist Permit & Access Permit being held on this outage | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 253 | 2024-05-29-0101 | Hutcheson St - 0001107234MLCD1 | CB49-Hutcheson St | 2024-05-29 11:22 | 2024-05-29 11:43 | 0 | 0 | 1 | 20 | Unplanned | Other cause | EAM 1485058 Blown fuse suspect overloading Fuse letter sent | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 254 | 2024-05-30-0102 | Parker St - XA2797-P5 | CB1516-Parker St | 2024-05-30 06:40 | 2024-05-30 07:51 | 0 | 0 | 25 | 772 | Unplanned | Defective equipment | Found Blown 160A fuse on blue phase at DB10 and replaced. Suspect faulty connection in fuse unit as still noisy when relivened EAM 1485290 http://nams.mll.co.nz/Schedule/Edit/3707 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 255 | 2024-05-30-0104 | Redwood St Sth - 0001177480ML3D6 | CB1673-Redwood St Sth | 2024-05-30 08:15 | 2024-05-30 09:20 | 0 | 0 | 1 | 64 | Unplanned | Unknown | Power restored . Replaced burnt out 32A fuse Red phase in XA4440. 0.5A on livening. EAM 1485293 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 256 | 2024-05-30-0105 | Wairau Valley - SUB3414TJ | CB5399 Wairau Valley | 2024-05-30 09:10 | 2024-05-30 14:54 | 0.037977 | 0.0001104 | 3 | 1032 | Planned | Planned interruption | Earth upgrade at SUB3414TJ - EAM1464904 NAMS4064 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 257 | 2024-05-30-0106 | Rapaura Rd - 0003330204MLBCF | CB1077-Rapaura Rd | 2024-05-30 11:01 | 2024-05-30 11:55 | 0 | 0 | 1 | 54 | Unplanned | Other cause | 1 HRC Fuse block, when tested showed 2.3 across all 3 phases Suspect Overloading (customer said issue happened when oven turned on) Electrictian to check for issues EAM 1485314 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 258 | 2024-05-30-0107 | Parker St - LVUG2588-S100 | CB1516-Parker St | 2024-05-30 13:07 | 2024-05-30 13:50 | 0 | 0 | 23 | 989 | Unplanned | Defective equipment | Shutdown to replace LV POS 5 DP10 after loose connection caused outage earlier in the day http://nams.mll.co.nz/Schedule/Edit/3707 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 259 | 2024-05-30-0108 | Industrial Estate - 0003350162ML4EB | CB1182-Industrial Estate | 2024-05-30 14:17 | 2024-05-30 16:45 | 0 | 0 | 1 | 148 | Unplanned | Unknown | EAM 1485379 2x blown 100A fuses. Person on site said an electrician had been and checked everything out. Turned off main switch, | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 260 | 2024-05-30-0109 | Koromiko - ABS747-B | CB55-Koromiko | 2024-05-30 15:02 | 2024-05-30 17:44 | 0.11327 | 0.0006992 | 19 | 3078 | Unplanned | Third party interference | Speeds Road Tractor Vs Pole Main line shutdown to change pole http://nams.mll.co.nz/Schedule/Edit/3710 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 261 | 2024-05-31-0110 | Rai Valley - 0007713589MLEA5 | CB43-Rai Valley | 2024-05-31 08:34 | 2024-05-31 14:55 | 0 | 0 | 1 | 381 | Unplanned | Other cause | 31/05/2024 8:41:59 am EAM 1485404 Replaced blown 30A pole fuse Red phase. 9A on livening. FUSE LETTER LEFT IN MAILBOX | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 262 | 2024-05-31-0112 | Scotland St - 0006611820MLC76 | CB54-Scotland St | 2024-05-31 17:02 | 2024-05-31 17:26 | 0 | 0 | 1 | 24 | Unplanned | Defective equipment | 31/05/2024 5:03:00 pm Customer electrician informed us it was not a MLL network issue. EAM 1485572 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 263 | 2024-05-31-0114 | Spring Creek - FUSE2182 | CB187-Spring Creek | 2024-05-31 20:35 | 2024-05-31 22:11 | 0.035328 | 0.000368 | 10 | 960 | Unplanned | Wildlife | Multiple no powers Wairau Bar Road Blown fuse 2182 red phase suspect bird. Line patrolled. http://nams.mll.co.nz/Schedule/Edit/3714 EAM 1485574 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 264 | 2024-05-31-0115 | Ngakuta - 0007716242MLFBC | REC1562-Ngakuta | 2024-05-31 23:22 | 2024-06-01 09:21 | 0 | 0 | 1 | 598 | Unplanned | Other cause | Blown 60A RW fuse due to overloading. Replaced with HRC, restored 0920. EAM 1485579 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 265 | 2024-05-31-0116 | Spring Creek - FUSE2182 | CB187-Spring Creek | 2024-05-31 23:38 | 2024-05-31 23:51 | 0.004784 | 0.000368 | 10 | 130 | Unplanned | Wildlife | 926 Wairau Bar Road called in again after fault earleir Still have part power FUSE 2182 Checked again, confirmed fuse 2182 fuse blown but not dropped out. 1485574 http://nams.mll.co.nz/Schedule/Edit/3715 ------------ | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 266 | 2024-06-01-0001 | Havelock Canvastown - SUB320212 | CB103 Havelock Canvastown | 2024-06-01 15:55 | 2024-06-02 11:23 | 0.042982 | 3.68e-05 | 1 | 1168 | Unplanned | Defective equipment | 2 Blown TX Fuses SUB 320212 - Suspect Wind TX Fuses blew on trial livening AP to remove LV TX Fuses blew on trial livening with LV removed - Faulty TX AP to replace TX 1485580 http://nams.mll.co.nz/Schedule/Edit/3716 Outage restored by: MLL\ | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 267 | 2024-06-01-0002 | French Pass - REC5024 | CB45-French Pass | 2024-06-01 16:31 | 2024-06-01 16:32 | 0 | 0 | 75 | 0 | Unplanned | Adverse weather | Succesful reclose of REC 5024 Phase OC Suspect high winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 268 | 2024-06-01-0003 | French Pass - REC5024 | CB45-French Pass | 2024-06-01 17:31 | 2024-06-01 18:03 | 0 | 0 | 75 | 0 | Unplanned | Adverse weather | 2 Successfule recloses of REC5024 - Suspect wind - Phase OC | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 269 | 2024-06-01-0005 | Richmond Brook - FUSE3409 | CB1250-Richmond Brook | 2024-06-01 20:13 | 2024-06-01 20:58 | 0.0049312 | 0.0001472 | 4 | 134 | Unplanned | Unknown | 2 Blown fuses 3409 Cause unknown. Line patrolled nothing found. 1485581 http://nams.mll.co.nz/Schedule/Edit/3717 2024-06-01-0005 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 270 | 2024-06-02-0007 | Flaxbourne - FUSE3479 | REC1432-Flaxbourne | 2024-06-02 08:49 | 2024-06-02 09:16 | 0.0041216 | 0.0001472 | 4 | 112 | Unplanned | Adverse weather | 2 Blown fuses 3479 line patrolled http://nams.mll.co.nz/Schedule/Edit/3718 suspect wind 1485582 original caller however modelling error does not show them fed from 3479 So outage removed and included in this | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 271 | 2024-06-03-0008 | Waikawa - 0006630013MLF2E | CB109- Waikawa | 2024-06-03 05:34 | 2024-06-03 10:35 | 0 | 0 | 1 | 302 | Unplanned | Defective equipment | Blown RW fuse (deterioration), replaced with new HRC. Restored 1035. EAM 1485583 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 272 | 2024-06-04-0011 | Woodbourne - CB1178 | CB1178-Woodbourne | 2024-06-04 08:30 | 2024-06-04 17:26 | 0.059174 | 0.0001104 | 3 | 1608 | Planned | Planned interruption | Planned shutdown to install new RMUS and LS1 at Woodbourne Sub. EAM 1397584 SAF 3937 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 273 | 2024-06-04-0012 | Waikawa - SUB330753 | CB109- Waikawa | 2024-06-04 09:34 | 2024-06-04 12:12 | 0.0058144 | 3.68e-05 | 1 | 158 | Planned | Planned interruption | Whekenui Bay Planned Work to alter service connection. http://nams.mll.co.nz/Schedule/Edit/3667 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 274 | 2024-06-04-0013 | Parker St - 0001144453ML198 | CB1516-Parker St | 2024-06-04 19:17 | 2024-06-04 20:59 | 0 | 0 | 1 | 102 | Unplanned | Defective equipment | Arcing Trurip, Temp repair made, tested @ 2 Meg Ohm Customer advised due to deterioration it is recommended to replace? 1485944 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 275 | 2024-06-05-0014 | Sounds - REC85 | REC1170-Sounds | 2024-06-05 08:30 | 2024-06-05 15:33 | 0.94955 | 0.0022448 | 61 | 25803 | Planned | Planned interruption | Planned shutdown to remove trees touching line in Crail Bay EAM 1436981 SAF 4110.1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 276 | 2024-06-05-0015 | Sounds - ABS580-B | REC1170-Sounds | 2024-06-05 09:02 | 2024-06-05 18:18 | 1.4553 | 0.0026128 | 71 | 39547 | Planned | Planned interruption | Planned Work EAM 1454939 SAF 4091 http://nams.mll.co.nz/Schedule/Edit/3573 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 277 | 2024-06-05-0016 | Richmond Brook - LVOH500129 | CB1250-Richmond Brook | 2024-06-05 09:36 | 2024-06-05 15:07 | 0 | 0 | 1 | 331 | Planned | Planned interruption | Planned shutdown to replace Chorus Pole. SAF 4164 . No EAM number. http://nams.mll.co.nz/Schedule/Edit/3668 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 278 | 2024-06-06-0022 | Omaka - 0001123523MLBF9 | CB1088 - Omaka | 2024-06-06 08:30 | 2024-06-06 14:40 | 0 | 0 | 1 | 370 | Planned | Planned interruption | Planned shutdown for Richardson Ave OHUG. SAF 3861 EAM 1412502 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 279 | 2024-06-06-0018 | Omaka - LVUG310355 | CB1088 - Omaka | 2024-06-06 08:30 | 2024-06-06 13:15 | 0 | 0 | 1 | 285 | Planned | Planned interruption | Planned shutdown for OHUG in Richardson Ave EAM 1412502 SAF 3861 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 280 | 2024-06-06-0017 | Seymour St - 0001166289ML2C0 | CB51-Seymour St | 2024-06-06 08:38 | 2024-06-06 11:43 | 0 | 0 | 1 | 186 | Unplanned | Defective equipment | Old rewirable fuse blown - replaced fuses EAM 1486238 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 281 | 2024-06-06-0023 | Omaka - 0001123527MLAF3 | CB1088 - Omaka | 2024-06-06 09:00 | 2024-06-06 11:30 | 0 | 0 | 1 | 150 | Planned | Planned interruption | Planned shutdown for Richardson Ave OHUG. SAF 3861 EAM 1412502 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 282 | 2024-06-06-0024 | Omaka - 0001123531ML1D1 | CB1088 - Omaka | 2024-06-06 09:00 | 2024-06-06 13:15 | 0 | 0 | 1 | 255 | Planned | Planned interruption | Planned shutdown for Richardson Ave OHUG. SAF 3861 EAM 1412502 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 283 | 2024-06-06-0019 | Seymour St - LVUG90098 | CB51-Seymour St | 2024-06-06 09:15 | 2024-06-06 09:30 | 0 | 0 | 1 | 15 | Unplanned | Defective equipment | Found potential fault at breakout on service cable and repaired while on site. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 284 | 2024-06-06-0020 | Seymour St - LVUG143359 | CB51-Seymour St | 2024-06-06 09:15 | 2024-06-06 09:30 | 0 | 0 | 1 | 15 | Unplanned | Defective equipment | Found potential fault at breakout on service cable and repaired while on site. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 285 | 2024-06-06-0025 | Omaka - 0001123536MLC1B | CB1088 - Omaka | 2024-06-06 09:30 | 2024-06-06 13:20 | 0 | 0 | 1 | 230 | Planned | Planned interruption | Planned shutdown for Richardson Ave OHUG. SAF 3861 EAM 1412502 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 286 | 2024-06-06-0026 | Omaka - 0001123539ML3C5 | CB1088 - Omaka | 2024-06-06 09:30 | 2024-06-06 13:20 | 0 | 0 | 1 | 230 | Planned | Planned interruption | Planned shutdown for Richardson Ave OHUG. SAF 3861 EAM 1412502 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 287 | 2024-06-06-0031 | Omaka - 0001123551MLE21 | CB1088 - Omaka | 2024-06-06 09:30 | 2024-06-06 15:00 | 0 | 0 | 1 | 330 | Planned | Planned interruption | Planned shutdown for Richardson Ave OHUG. SAF 3861 EAM 1412502 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 288 | 2024-06-06-0021 | Waikawa - LVOH1328 | CB109- Waikawa | 2024-06-06 10:42 | 2024-06-06 15:45 | 0 | 0 | 2 | 606 | Planned | Planned interruption | Replacement of Chorus Pole PT4110 in Sussex St, Picton SAF 4166 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 289 | 2024-06-06-0027 | Omaka - 0001123543ML409 | CB1088 - Omaka | 2024-06-06 13:00 | 2024-06-06 14:25 | 0 | 0 | 1 | 85 | Planned | Planned interruption | Planned shutdown for Richardson Ave OHUG. SAF 3861 EAM 1412502 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 290 | 2024-06-06-0028 | Omaka - 0001123555MLF2B | CB1088 - Omaka | 2024-06-06 13:00 | 2024-06-06 13:55 | 0 | 0 | 1 | 55 | Planned | Planned interruption | Planned shutdown for Richardson Ave OHUG. SAF 3861 EAM 1412502 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 291 | 2024-06-06-0029 | Omaka - 0001123575ML27E | CB1088 - Omaka | 2024-06-06 13:16 | 2024-06-06 15:25 | 0 | 0 | 1 | 129 | Planned | Planned interruption | Planned shutdown for Richardson Ave OHUG. SAF 3861 EAM 1412502 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 292 | 2024-06-06-0030 | Omaka - 0001123552ML2E1 | CB1088 - Omaka | 2024-06-06 13:16 | 2024-06-06 15:15 | 0 | 0 | 1 | 119 | Planned | Planned interruption | Planned shutdown for Richardson Ave OHUG. SAF 3861 EAM 1412502 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 293 | 2024-06-07-0032 | Hutcheson St - LVUG2271 | CB49-Hutcheson St | 2024-06-07 07:00 | 2024-06-07 07:46 | 0 | 0 | 4 | 184 | Planned | Planned interruption | Planned shutdown to reconnect cable in Andelec Box at DP95 Market St. EAM 1193617 SAF 4153.2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 294 | 2024-06-07-0033 | Hutcheson St - 0001101108MLEF4 | CB49-Hutcheson St | 2024-06-07 07:00 | 2024-06-07 07:46 | 0 | 0 | 1 | 46 | Planned | Planned interruption | Planned shutdown to reconnect cable in Andelec Box at DP95 Market St. EAM 1193617 SAF 4153.2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 295 | 2024-06-07-0034 | Hutcheson St - 0001101107ML12A | CB49-Hutcheson St | 2024-06-07 07:00 | 2024-06-07 07:46 | 0 | 0 | 1 | 46 | Planned | Planned interruption | Planned shutdown to reconnect cable in Andelec Box at DP95 Market St. EAM 1193617 SAF 4153.2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 296 | 2024-06-07-0035 | Hutcheson St - 0001101200MLFE3 | CB49-Hutcheson St | 2024-06-07 07:00 | 2024-06-07 07:46 | 0 | 0 | 1 | 46 | Planned | Planned interruption | Planned shutdown to reconnect cable in Andelec Box at DP95 Market St. EAM 1193617 SAF 4153.2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 297 | 2024-06-07-0036 | Hutcheson St - 0001101067ML7DE | CB49-Hutcheson St | 2024-06-07 07:00 | 2024-06-07 07:46 | 0 | 0 | 1 | 46 | Planned | Planned interruption | Planned shutdown to reconnect cable in Andelec Box at DP95 Market St. EAM 1193617 SAF 4153.2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 298 | 2024-06-07-0037 | Hutcheson St - 0001101289ML4F8 | CB49-Hutcheson St | 2024-06-07 07:00 | 2024-06-07 07:46 | 0 | 0 | 1 | 46 | Planned | Planned interruption | Planned shutdown to reconnect cable in Andelec Box at DP95 Market St. EAM 1193617 SAF 4153.2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 299 | 2024-06-07-0039 | Wairau Valley - 0002278438MLD6F | CB5399 Wairau Valley | 2024-06-07 08:39 | 2024-06-07 13:17 | 0 | 0 | 1 | 277 | Planned | Planned interruption | Replacement of LV arms and re-sag at poles KB9049 and AK2438 SAF 4137 EAM 1476640 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 300 | 2024-06-07-0040 | Old Renwick Rd - LVOH597-S23692 | CB66-Old Renwick Rd | 2024-06-07 08:58 | 2024-06-07 15:04 | 0 | 0 | 2 | 732 | Planned | Planned interruption | Replacement of OH service with UG for new ICP Planned Work http://nams.mll.co.nz/Schedule/Edit/3606 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 301 | 2024-06-07-0041 | Wairau Valley - RMUF1587 | CB5399 Wairau Valley | 2024-06-07 11:53 | 2024-06-07 12:09 | 0.0005888 | 3.68e-05 | 1 | 16 | Planned | Planned interruption | Shutdown of SUB3414VS to change tap from psotion 3 to position 2 to resolve high voltage issues. EAM 1486604 http://nams.mll.co.nz/Schedule/Edit/3725 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 302 | 2024-06-08-0042 | Parker St - 0001141400ML270 | CB1516-Parker St | 2024-06-08 09:45 | 2024-06-08 10:38 | 0 | 0 | 1 | 53 | Unplanned | Defective equipment | Retailer discon for vacant.Spoke to tenant who has been at property for 2 months but not signed up with a retailer - no power 1486661 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 303 | 2024-06-09-0043 | Renwick Township - 0000050250ML7EA | CB5482 Renwick Township | 2024-06-09 10:52 | 2024-06-09 14:16 | 0 | 0 | 1 | 204 | Unplanned | Defective equipment | Arcing line @ Tx342045 is smoking Discon @ 11:40 Livened @ 14:15 Trurip repair tested up poorly and was not safe to liven. Replaced trurip | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 304 | 2024-06-09-0044 | Grovetown - 0003342128MLF7E | CB1465-Grovetown | 2024-06-09 17:23 | 2024-06-09 18:21 | 0 | 0 | 1 | 58 | Unplanned | Other cause | No Power Blown HRC fuse due to be incorrectly loaded at 30A instead of 60A 9/06/2024 5:32:58 pm 1486697 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 305 | 2024-06-10-0045 | French Pass - REC5024 | CB45-French Pass | 2024-06-10 00:34 | 2024-06-10 00:35 | 0 | 0 | 75 | 0 | Unplanned | Adverse weather | REC5024 Auto Reclose on Phase OC. Cyclo 340. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 306 | 2024-06-10-0046 | Sounds - 0008812698ML862 | REC1170-Sounds | 2024-06-10 08:15 | 2024-06-10 09:50 | 0 | 0 | 1 | 94 | Unplanned | Unknown | Customer called back and advised that their power has come back on Have stood down faultmen EAM 1486701 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 307 | 2024-06-10-0048 | Ngakuta - LVOH3207 | REC1562-Ngakuta | 2024-06-10 09:09 | 2024-06-10 13:17 | 0 | 0 | 2 | 496 | Planned | Planned interruption | Planned replacement of LV arm on pole BS3931, installation of construction earths and removal of redundant span. SAF 4122 WO 1303468 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 308 | 2024-06-10-0047 | Waikawa - FUSE22374 | CB109- Waikawa | 2024-06-10 09:12 | 2024-06-10 14:20 | 0 | 0 | 12 | 3696 | Planned | Planned interruption | Planned shutdown to replace LV cross arms at 2 poles. EAM 1481402 SAF 4185 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 309 | 2024-06-10-0049 | Seymour St - 0001166157MLF1A | CB51-Seymour St | 2024-06-10 17:53 | 2024-06-10 18:31 | 0 | 0 | 1 | 38 | Unplanned | Defective equipment | Blown 60A rewireable fuse due to deterioration 1486814 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 310 | 2024-06-11-0050 | Hutcheson St - LVUG1229 | CB49-Hutcheson St | 2024-06-11 07:00 | 2024-06-11 08:16 | 0 | 0 | 2 | 150 | Planned | Planned interruption | Short shutdown of DP19 George St to unbolt cable from POS2 in preparation for installation into new DP19 George St. SAF4141 - WO 1453964 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 311 | 2024-06-11-0052 | Omaka - 0001123532MLD11 | CB1088 - Omaka | 2024-06-11 08:33 | 2024-06-11 14:30 | 0 | 0 | 1 | 357 | Planned | Planned interruption | Service conversion from OH to UG distribution EAM1412502 NAMS3863.2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 312 | 2024-06-11-0053 | Omaka - 0001123537ML05E | CB1088 - Omaka | 2024-06-11 08:33 | 2024-06-11 14:30 | 0 | 0 | 1 | 357 | Planned | Planned interruption | Service conversion from OH to UG distribution EAM1412502 NAMS3863.2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 313 | 2024-06-11-0054 | Omaka - 0001123540ML8C9 | CB1088 - Omaka | 2024-06-11 08:33 | 2024-06-11 14:30 | 0 | 0 | 1 | 357 | Planned | Planned interruption | Service conversion from OH to UG distribution EAM1412502 NAMS3863.2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 314 | 2024-06-11-0055 | Omaka - 0001123545ML586 | CB1088 - Omaka | 2024-06-11 08:33 | 2024-06-11 14:30 | 0 | 0 | 1 | 357 | Planned | Planned interruption | Service conversion from OH to UG distribution EAM1412502 NAMS3863.2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 315 | 2024-06-11-0056 | Omaka - 0001123544ML9C3 | CB1088 - Omaka | 2024-06-11 08:33 | 2024-06-11 14:30 | 0 | 0 | 1 | 357 | Planned | Planned interruption | Service conversion from OH to UG distribution EAM1412502 NAMS3863.2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 316 | 2024-06-11-0051 | Omaka - LVUG103111 | CB1088 - Omaka | 2024-06-11 09:29 | 2024-06-11 14:13 | 0 | 0 | 1 | 284 | Planned | Planned interruption | Service conversion from OH to UG distribution EAM1412502 NAMS3863.1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 317 | 2024-06-12-0057 | Hutcheson St - 0001161001MLBF9 | CB49-Hutcheson St | 2024-06-12 06:00 | 2024-06-13 14:30 | 0 | 0 | 1 | 1950 | Planned | Planned interruption | Service changeover at 78 Queen St for replacement of DP19 . LV Cable from Network to Florist had 2 faults that required repair EAM1193619 NAMS4142.1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 318 | 2024-06-12-0058 | Symons St - 0001109065MLA5B | CB50-Symons St | 2024-06-12 13:57 | 2024-06-12 14:23 | 0 | 0 | 1 | 25 | Unplanned | Defective equipment | Blue phase off - When doing test on yellow and Red only showing 32amp Cuddons to check Balance Fuse Letter issued EAM 1487012 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 319 | 2024-06-12-0059 | Parker St - 0001139061MLA7D | CB1516-Parker St | 2024-06-12 15:41 | 2024-06-12 16:31 | 0 | 0 | 1 | 50 | Unplanned | Defective equipment | Rewirable fuse burnt out (due to age). EAM 1487044 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 320 | 2024-06-12-0060 | Parker St - 0001139545ML327 | CB1516-Parker St | 2024-06-12 19:59 | 2024-06-12 21:07 | 0 | 0 | 1 | 68 | Unplanned | Defective equipment | internal fault RCD tripping, they are getting an electrician tomorrow W/O 1487055 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 321 | 2024-06-13-0061 | Alabama Rd - 0001184321MLFF2 | CB1667-Alabama Rd | 2024-06-13 07:24 | 2024-06-13 09:09 | 0 | 0 | 1 | 104 | Unplanned | Defective equipment | Replace 60A Pole fuse 11Amps on livening Cause overloading - Fuse letter sent out today EAM 1487057 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 322 | 2024-06-13-0062 | Jacksons Road - RMUS1398 | CB1179-Jacksons Road | 2024-06-13 08:00 | 2024-06-13 15:44 | 0.17075 | 0.000368 | 10 | 4640 | Planned | Planned interruption | Shutdown in Pak Lims Rd for OPGW installation EAM1433251 NAMS3812.1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 323 | 2024-06-13-0064 | Kaituna - FUSE2102 | CB5448 Kaituna | 2024-06-13 08:00 | 2024-06-13 16:22 | 0.022301 | 0.000184 | 3 | 606 | Planned | Planned interruption | Shutdown to Forest Estate and adjacent customers for OPGW installation EAM1433251 NAMS3812.1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 324 | 2024-06-13-0063 | Renwick Township - RMUF1325 | CB5482 Renwick Township | 2024-06-13 08:24 | 2024-06-13 16:01 | 0.21863 | 0.0004784 | 13 | 5941 | Planned | Planned interruption | Shutdown in Alma St North for OPGW installation EAM1433251 NAMS3812.1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 325 | 2024-06-13-0065 | Hutcheson St - 0001153264ML12D | CB49-Hutcheson St | 2024-06-13 11:46 | 2024-06-13 12:18 | 0 | 0 | 1 | 32 | Unplanned | Other cause | Blown fuse, (White ph) suspect overloading - customer has had an fuse letter prior EAM 1487105 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 326 | 2024-06-13-0066 | Spring Creek - 0003340510ML5D3 | CB187-Spring Creek | 2024-06-13 21:09 | 2024-06-13 22:33 | 0 | 0 | 1 | 83 | Unplanned | Defective equipment | no power W/O 1487118 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 327 | 2024-06-14-0067 | Sounds - SUB325423 | REC1170-Sounds | 2024-06-14 08:05 | 2024-06-15 10:53 | 0.11835 | 7.36e-05 | 2 | 3216 | Unplanned | Unknown | Found Red Phase REC5088 OPEN - no cause found EAM1487123 F3750 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 328 | 2024-06-15-0074 | Jacksons Road - FUSE3626 | CB1179-Jacksons Road | 2024-06-15 08:15 | 2024-06-15 09:30 | 0.025171 | 0.0003312 | 9 | 684 | Unplanned | Unknown | 1 x Pole fuse out at FUSE3626 Line patrolled - no cause found Power confirmed restored EAM 1487270 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 329 | 2024-06-15-0075 | Grovetown - CB1465 | CB1465-Grovetown | 2024-06-15 17:58 | 2024-06-15 20:02 | 0.62917 | 0.015566 | 423 | 17097 | Unplanned | Wildlife | Ph to Ph fault 2000A Line patrolled wire found down between Pole JA3122 & JA0535 Fell St Suspect Bird, although none found Isolation carried out and line reinstated Power restored | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 330 | 2024-06-16-0079 | Sounds - 0008814265MLEEF | REC1170-Sounds | 2024-06-16 08:23 | 2024-06-16 12:30 | 0.0091264 | 3.68e-05 | 1 | 248 | Unplanned | Lightning | Found 1 x blown fuse at SUB325633 Suspect Lightning as cause Power confirmed restored W/O 1487276 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 331 | 2024-06-16-0080 | Grovetown - 0003342285MLB39 | CB1465-Grovetown | 2024-06-16 08:44 | 2024-06-16 10:09 | 0 | 0 | 1 | 86 | Unplanned | Other cause | Net map has cable at three phase 60 amp, able has been parrelled up and only had a 30 amp in fuse carrier | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 332 | 2024-06-16-0081 | Sounds - 0008814397ML779 | REC1170-Sounds | 2024-06-16 09:43 | 2024-06-16 14:02 | 0.009568 | 3.68e-05 | 1 | 260 | Unplanned | Lightning | Suspect Lightning as cause Power confirmed restored EAM1487277 NAMSF3759 Found 1 x blown fuse at SUB325311 2024-06-016-0081 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 333 | 2024-06-16-0082 | Rai Valley - REC5167 | CB43-Rai Valley | 2024-06-16 12:48 | 2024-06-16 12:48 | 0.0038272 | 0.0038272 | 104 | 104 | Unplanned | Unknown | Sucessful Reclose of 11kV REC5167 - Carluke Outage | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 334 | 2024-06-16-0085 | Rai Valley - SUB335347 | CB43-Rai Valley | 2024-06-16 13:41 | 2024-06-16 16:00 | 0.0051152 | 3.68e-05 | 1 | 139 | Unplanned | Lightning | Found 3 x blown fuse at SUB335347 3A Suspect Lightning as cause Power confirmed restored | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 335 | 2024-06-16-0086 | Rai Valley - SUB335351 | CB43-Rai Valley | 2024-06-16 13:41 | 2024-06-16 16:18 | 0.017333 | 0.0001104 | 3 | 471 | Unplanned | Lightning | Found 2 x blown fuse at SUB335351 3A Suspect Lightning as cause Power confirmed restored | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 336 | 2024-06-16-0084 | Sounds - 0008812041MLD77 | REC1170-Sounds | 2024-06-16 13:53 | 2024-06-16 15:03 | 0.002576 | 3.68e-05 | 1 | 70 | Unplanned | Lightning | Found 1 x blown fuse at SUB3251CE Suspect Lightning as cause Power confirmed restored | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 337 | 2024-06-16-0087 | Rai Valley - SUB335353 | CB43-Rai Valley | 2024-06-16 16:30 | 2024-06-16 17:03 | 0.0024288 | 7.36e-05 | 2 | 66 | Unplanned | Lightning | Found 2 x blown fuse at SUB335353 3A Suspect Lightning as cause Power confirmed restored EAM1487279 NAMSF3765 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 338 | 2024-06-16-0088 | Sounds - 0008812609MLBC0 | REC1170-Sounds | 2024-06-16 18:42 | 2024-06-17 09:01 | 0.031611 | 3.68e-05 | 1 | 859 | Unplanned | Lightning | Found 1 x blown fuse at SUB3251CP 3A Suspect Lightning as cause Power confirmed restored Boat to be booked for 0810am | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 339 | 2024-06-17-0089 | Waikawa - 0008813266ML64F | CB109- Waikawa | 2024-06-17 08:13 | 2024-06-17 09:37 | 0.0030912 | 3.68e-05 | 1 | 84 | Unplanned | Lightning | Found 1 x blown fuse at SUB330233 3A Suspect Lightning as cause Power confirmed restored Found 1 x blown fuse at SUB330233 3A Suspect Lightning as cause | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 340 | 2024-06-17-0090 | Seymour St - 0001165221MLA2B | CB51-Seymour St | 2024-06-17 08:58 | 2024-06-17 10:05 | 0 | 0 | 1 | 67 | Unplanned | Unknown | Blown 30Amp pole fuse No cause given on txt EAM 1487293 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 341 | 2024-06-17-0091 | Sounds - 0008810590MLA35 | REC1170-Sounds | 2024-06-17 09:16 | 2024-06-17 09:56 | 0.001472 | 3.68e-05 | 1 | 40 | Unplanned | Lightning | Found 2 x blown fuse at SUB3251AG 10A Suspect Lightning as cause Power confirmed restored EAM 1487294 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 342 | 2024-06-17-0092 | Wairau Valley - 0002278567ML3BD | CB5399 Wairau Valley | 2024-06-17 09:32 | 2024-06-17 11:07 | 0 | 0 | 1 | 95 | Unplanned | Other cause | Blown 30A fuse white phase. 28A livening. Advised customer to get electrician to Ballance load. Fuse letter left EAM 1487296 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 343 | 2024-06-17-0093 | Scotland St - 0006610229ML98D | CB54-Scotland St | 2024-06-17 10:13 | 2024-06-17 10:56 | 0 | 0 | 1 | 43 | Unplanned | Defective equipment | Blown 60amp rewirable fuse - replaced and service restored Cause old age. EAM 1487298 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 344 | 2024-06-17-0094 | Wairau Valley - 0002278592MLEE5 | CB5399 Wairau Valley | 2024-06-17 11:01 | 2024-06-17 12:04 | 0 | 0 | 1 | 63 | Unplanned | Defective equipment | Internal Cable fault Have isolated 2 phases but have left the Blue phase working (so they have some power) Electrictian will call to get 3rd phase off, and then to get Reconnection done. Will close fault and work off EAM now. EAM 1487307 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 345 | 2024-06-17-0095 | Old Renwick Rd - 0003330346ML0EB | CB66-Old Renwick Rd | 2024-06-17 14:37 | 2024-06-17 15:31 | 0 | 0 | 1 | 54 | Unplanned | Defective equipment | Blown HRC fuse, replace, service given Overloading - Fuse Letter left in letterbox EAM 1487349 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 346 | 2024-06-17-0096 | Parker St - 0001128267ML8B4 | CB1516-Parker St | 2024-06-17 15:18 | 2024-06-17 16:00 | 0 | 0 | 1 | 41 | Unplanned | Unknown | Power to the smart meter Customer has been advised to contact retailer and to get Electrictian Internal Issue . EAM 1487384 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 347 | 2024-06-17-0097 | Sounds - 0008811155MLD34 | REC1170-Sounds | 2024-06-17 18:01 | 2024-06-17 20:33 | 0.0055568 | 3.68e-05 | 1 | 151 | Unplanned | Lightning | Found 2 x blown fuse at SUB325209 3A Suspect Lightning as cause Power confirmed restored W/O 1487392 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 348 | 2024-06-17-0098 | Seymour St - 0001166066MLDA3 | CB51-Seymour St | 2024-06-17 21:33 | 2024-06-17 22:39 | 0 | 0 | 1 | 65 | Unplanned | Defective equipment | Burnt out fuse carrierW/O 1487393 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 349 | 2024-06-18-0099 | Waikawa - 0006618520ML5DE | CB109- Waikawa | 2024-06-18 08:04 | 2024-06-18 09:39 | 0 | 0 | 1 | 95 | Unplanned | Unknown | Internal Issue RCD wont stay in, customer advised to get a Electrician EAM 1487414 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 350 | 2024-06-18-0105 | Murphys Rd - LVUG2589 | CB68-Murphys Rd | 2024-06-18 08:35 | 2024-06-18 14:32 | 0 | 0 | 8 | 2848 | Planned | Planned interruption | Replacement of LB173 Middle Renwick Rd EAM1413747 NAMS3457 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 351 | 2024-06-18-0100 | Havelock Canvastown - LVUG865 | CB103 Havelock Canvastown | 2024-06-18 08:43 | 2024-06-18 14:38 | 0 | 0 | 7 | 2478 | Planned | Planned interruption | Replacement of LVOH conductor with ABC next to the Havelock Fire Station Outage 1 of 2 due to modelling SAF3686 WO 1429394 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 352 | 2024-06-18-0101 | Havelock Canvastown - 0007702425ML5E1 | CB103 Havelock Canvastown | 2024-06-18 08:43 | 2024-06-18 14:37 | 0 | 0 | 1 | 354 | Planned | Planned interruption | Replacement of LVOH conductor with ABC next to the Havelock Fire Station Outage 2 of 2 due to modelling SAF3686 WO 1429394 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 353 | 2024-06-18-0102 | Sounds - SUB325213 | REC1170-Sounds | 2024-06-18 08:57 | 2024-06-18 10:38 | 0.00736 | 7.36e-05 | 2 | 200 | Unplanned | Adverse weather | Kenepuru Road SUB 325213 Blown 11kV Fuses - suspect lightning EAM 1487442 http://nams.mll.co.nz/Schedule/Edit/3776 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 354 | 2024-06-18-0104 | Parker St - 0001141269ML5D7 | CB1516-Parker St | 2024-06-18 09:23 | 2024-06-18 14:46 | 0 | 0 | 1 | 323 | Planned | Planned interruption | Replacement of condemned Pole JA4909 NAMS4168 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 355 | 2024-06-18-0106 | Sounds - 0008812201ML5D5 | REC1170-Sounds | 2024-06-18 11:30 | 2024-06-18 15:33 | 0.0089056 | 3.68e-05 | 1 | 242 | Unplanned | Lightning | Found 2 x blown fuse at SUB3251DC 6A Suspect Lightning as cause Power confirmed restored EAM 1487520 NAMS F3779 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 356 | 2024-06-18-0107 | Sounds - 0008812597ML4BF | REC1170-Sounds | 2024-06-18 12:12 | 2024-06-18 14:52 | 0.005888 | 3.68e-05 | 1 | 160 | Unplanned | Lightning | Found 1 x blown fuse at SUB3251EL 3A Suspect Lightning as cause Power confirmed restored EAM1487466 NAMSF3778 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 357 | 2024-06-18-0108 | Waikawa - SUB330209 | CB109- Waikawa | 2024-06-18 16:21 | 2024-06-19 15:15 | 0.0506 | 3.68e-05 | 1 | 1375 | Unplanned | Lightning | Found 1 x blown fuse at SUB330209 3A Suspect Lightning as cause Power confirmed restored EAM 1487733 Not attending tonight. Will make contact with customer tomorrow 19/06/2024 and see how urgent the fix is (is anyone attending freezers etc). | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 358 | 2024-06-18-0109 | McLauchlan St - 0001128521ML49C | CB65 - McLauchlan St | 2024-06-18 18:40 | 2024-06-18 19:30 | 0 | 0 | 1 | 50 | Unplanned | Unknown | Found 1 x blown 60A LV pole fuse. No cause found. Suspet overloading. EAM 1487735 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 359 | 2024-06-19-0111 | Sounds - REC1350 | REC1170-Sounds | 2024-06-19 08:15 | 2024-06-19 16:35 | 2.2641 | 0.024104 | 366 | 61526 | Planned | Planned interruption | Installation of new switches ENS7004 and ENS7021 in the Kenepuru SAF3870 - WO1393778 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 360 | 2024-06-19-0112 | Waikawa - SUB330131 | CB109- Waikawa | 2024-06-19 08:30 | 2024-06-19 12:12 | 0 | 0 | 8 | 1768 | Planned | Planned interruption | Replacement of LV x-arm on pole AX1752 in Port underwood Rd EAM1472589 NAMS4124 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 361 | 2024-06-19-0113 | Sounds - FUSE2370 | REC1170-Sounds | 2024-06-19 09:00 | 2024-06-19 15:35 | 0.26165 | 0.0006624 | 18 | 7110 | Planned | Planned interruption | Planned shutdown for arborist work on Forsyth Island. EAM 1457134 SAF 4130 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 362 | 2024-06-19-0114 | Wairau Valley - 0002278566MLFF8 | CB5399 Wairau Valley | 2024-06-19 17:37 | 2024-06-19 18:43 | 0 | 0 | 1 | 66 | Unplanned | Other cause | White phase blown on service due to overload. Service fuse letter left with customer. EAM 1487983 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 363 | 2024-06-19-0115 | Murphys Rd - 0001121440ML28D | CB68-Murphys Rd | 2024-06-19 21:21 | 2024-06-20 08:58 | 0 | 0 | 1 | 696 | Unplanned | Unknown | No issues with MLL network have advised customer to get Electrictian in EAM 1487985 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 364 | 2024-06-20-0116 | Vintage Lane - FUSE2222 | CB171-Vintage Lane | 2024-06-20 08:33 | 2024-06-20 15:33 | 0.12335 | 0.0002944 | 8 | 3352 | Planned | Planned interruption | Planned shutdown to install new 33kV cable up pole 12.3 EAM 1397584 SAF 3947.1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 365 | 2024-06-20-0117 | Wairau Valley - 0002278109ML3D7 | CB5399 Wairau Valley | 2024-06-20 10:29 | 2024-06-20 12:30 | 0 | 0 | 1 | 121 | Unplanned | Defective equipment | Rewirable fuse, no other details given. Suspect old age EAM 1488032 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 366 | 2024-06-20-0119 | Sounds - FUSE3036 | REC1170-Sounds | 2024-06-20 12:56 | 2024-06-20 14:19 | 0.24851 | 0.0030544 | 83 | 6753 | Unplanned | Defective equipment | Urgent shutdown to replace faulty LS Transformer at 11kV SEC150 - Kenepuru Heads EAM 1487992 SAF F3789 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 367 | 2024-06-21-0120 | Omaka - RMUF1482 | CB1088 - Omaka | 2024-06-21 08:30 | 2024-06-21 11:52 | 0.17841 | 0.0008832 | 24 | 4848 | Planned | Planned interruption | Planned work to replace 11kV conductor between POLE NZ2624 and AA1543 EAM 1469234 SAF 4093.1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 368 | 2024-06-21-0121 | Vintage Lane - FUSE2222 | CB171-Vintage Lane | 2024-06-21 08:30 | 2024-06-21 12:07 | 0.06359 | 0.0002944 | 8 | 1728 | Planned | Planned interruption | Planned shutdown to install new 33kV cable up pole 12.3 EAM 1397584 SAF 3947.2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 369 | 2024-06-22-0125 | Craiglochart - FUSE3718 | REC1391-Craiglochart | 2024-06-21 17:56 | 2024-06-22 12:07 | 0.040112 | 3.68e-05 | 1 | 1090 | Unplanned | Wildlife | 2 blown fuses found at 11kV FUSE3718. Line patrolled, nothing found. Suspect bird. EAM 1488486 http://nams.mll.co.nz/Schedule/Edit/3803 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 370 | 2024-06-21-0122 | Sounds - SUB325923 | REC1170-Sounds | 2024-06-21 21:40 | 2024-06-22 11:06 | 0.32627 | 0.0004048 | 11 | 8866 | Unplanned | Lightning | Found 1x blown HT fuse at SUB325923, suspect lightning. Replaced both fuses (10A) EAM 1488484 http://nams.mll.co.nz/Schedule/Edit/3802 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 371 | 2024-06-22-0123 | Sounds - SUB325003 | REC1170-Sounds | 2024-06-22 07:38 | 2024-06-22 09:52 | 0.0098624 | 7.36e-05 | 2 | 268 | Unplanned | Unknown | 1 blown HV fuse found at SUB325003 - No cause found. Replaced all 3 fuses (3A) EAM 1488485 http://nams.mll.co.nz/Schedule/Edit/3801 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 372 | 2024-06-22-0124 | Omaka - 0002270180ML5CC | CB1088 - Omaka | 2024-06-22 10:42 | 2024-06-22 11:46 | 0 | 0 | 1 | 64 | Unplanned | Unknown | Found blown fuse in SFB box. We have been here before for the other phase. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 373 | 2024-06-23-0126 | Havelock Canvastown - 0008802470ML22A | CB103 Havelock Canvastown | 2024-06-23 12:30 | 2024-06-23 14:50 | 0 | 0 | 1 | 140 | Unplanned | Defective equipment | found a blown 32A fuse in SFB box. Suspected overloading Fuse Letter sent EAM1488491 Replaced blown32A fuse. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 374 | 2024-06-23-0127 | Parker St - 0001138298MLF9C | CB1516-Parker St | 2024-06-23 13:04 | 2024-06-23 14:04 | 0 | 0 | 1 | 60 | Unplanned | Defective equipment | found a burnt out 30A rewirable pole fuse. Replaced with new ABC HRC fuse carrier. EAM 1488492 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 375 | 2024-06-23-0128 | Industrial Estate - CB1182 | CB1182-Industrial Estate | 2024-06-23 14:44 | 2024-06-23 15:23 | 0.090417 | 0.0023184 | 63 | 2457 | Unplanned | Unknown | 11kV CB1182 tripped on Phase OC. Line patrolled, nothing found and successfully relivened. EAM 1488493 http://nams.mll.co.nz/Schedule/Edit/3804 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 376 | 2024-06-24-0129 | Tuamarina - FUSE3926 | CB188-Tuamarina | 2024-06-24 05:18 | 2024-06-24 07:03 | 0.1932 | 0.00184 | 50 | 5250 | Unplanned | Unknown | Found a burnt out 30A rewirable pole fuse. Replaced with new ABC HRC fuse carrier. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 377 | 2024-06-24-0130 | Industrial Estate - 0003350162ML4EB | CB1182-Industrial Estate | 2024-06-24 07:27 | 2024-06-24 08:27 | 0 | 0 | 1 | 60 | Unplanned | Unknown | Blown pole fuse (100amp) Cause Unknown as unable to get access to site Customer to call me back to advise if power restored (15-20mins) Customer confirmed power restored 8.26am EAM 1488495 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 378 | 2024-06-24-0131 | Vintage Lane - FUSE2222 | CB171-Vintage Lane | 2024-06-24 08:30 | 2024-06-24 15:24 | 0.12159 | 0.0002944 | 8 | 3304 | Planned | Planned interruption | Planned shutdown to run 33kV cable up pole 11 on Woodbourne 33kV upgrade project. EAM 1397584 SAF 3950.1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 379 | 2024-06-24-0132 | Waikawa - SUB330205 | CB109- Waikawa | 2024-06-24 11:14 | 2024-06-24 14:12 | 0.0065504 | 3.68e-05 | 1 | 178 | Unplanned | Adverse weather | No power reported by customer in Green Bay . 1x blown HT fuse found, suspect lightning related. Replaced both fuses (3A) http://nams.mll.co.nz/Schedule/Edit/3808 EAM 1488606 Boat booked for 130pm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 380 | 2024-06-25-0133 | Waikawa - LVOH336 | CB109- Waikawa | 2024-06-25 08:30 | 2024-06-25 11:38 | 0 | 0 | 2 | 376 | Planned | Planned interruption | 25/06/2024 8:32:34 am EAM1479929 NAMS4146 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 381 | 2024-06-25-0134 | Renwick Township - LVOH2850 | CB5482 Renwick Township | 2024-06-25 08:30 | 2024-06-25 14:22 | 0 | 0 | 1 | 352 | Planned | Planned interruption | 25/06/2024 8:32:34 am EAM1479929 NAMS4146 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 382 | 2024-06-25-0135 | Renwick Township - 0000051494ML6A9 | CB5482 Renwick Township | 2024-06-25 08:30 | 2024-06-25 14:22 | 0 | 0 | 1 | 352 | Planned | Planned interruption | 25/06/2024 8:32:34 am EAM1479929 NAMS4146 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 383 | 2024-06-25-0136 | Renwick Township - 0000051498ML5B7 | CB5482 Renwick Township | 2024-06-25 08:30 | 2024-06-25 14:23 | 0 | 0 | 1 | 353 | Planned | Planned interruption | 25/06/2024 8:32:34 am EAM1479929 NAMS4146 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 384 | 2024-06-25-0137 | Hospital Rd West - SUB3700CG | CB47-Hospital Rd West | 2024-06-25 08:35 | 2024-06-25 14:30 | 0.24752 | 0.0006992 | 19 | 6726 | Unplanned | Defective equipment | Urgent repair of oil leak on SUB3700CG - Taylor Pass Rd EAM 1488488 http://nams.mll.co.nz/Schedule/Edit/3806 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 385 | 2024-06-25-0138 | Rai Valley - CB2032 | CB43 - Rai Valley, CB45 - French Pass, CB5126 - Pelorus | 2024-06-25 09:00 | 2024-06-25 09:00 | 0 | 0 | 914 | 0 | Unplanned | Unknown | Successful reclose of CB2032 Transpower | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 386 | 2024-06-25-0139 | Scotland St - 0006607086ML8CA | CB54-Scotland St | 2024-06-25 09:05 | 2024-06-25 13:00 | 0 | 0 | 1 | 235 | Planned | Planned interruption | Planned shutdown to replace stub pole. EAM 1481231 SAF 4181.1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 387 | 2024-06-25-0140 | Parker St - 0001138334MLD99 | CB1516-Parker St | 2024-06-25 20:23 | 2024-06-25 21:18 | 0 | 0 | 1 | 55 | Unplanned | Unknown | Blown 30A fuse, checked all connections and all good. 5A on livening. No cause found. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 388 | 2024-06-26-0141 | Grassmere - FUSE3291 | CB1253-Grassmere | 2024-06-26 06:53 | 2024-06-26 10:55 | 0.068374 | 0.0002944 | 8 | 1858 | Unplanned | Wildlife | 1 blown 11kV fuse at Fuse Site 3291. found dead swan approx 2 spans downstream. Opened 11kV ABS 15314 to avoid ferro issue when replacing fuses. EAM 1489078 SAF F3811 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 389 | 2024-06-26-0142 | Kaituna - CB5448 | CB5448 Kaituna | 2024-06-26 09:15 | 2024-06-26 11:49 | 0.45503 | 0.010267 | 279 | 12365 | Unplanned | Defective equipment | 11kV CB5448 Kaituna feeder tripped on earth fault. EAM 1489113 Line down between POLES KB9523 and JA3375 http://nams.mll.co.nz/Schedule/Edit/3810 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 390 | 2024-06-26-0143 | Flaxbourne - 0005507514ML5D2 | REC1432-Flaxbourne | 2024-06-26 09:27 | 2024-06-26 12:56 | 0 | 0 | 1 | 210 | Unplanned | Defective equipment | Cable crutch blown up - temp repairs to restore power Will revisit tomorrow 27/06/2024 to complete correctly EAM 1489113 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 391 | 2024-06-26-0144 | Wairau Valley - FUSE3593 | CB5399 Wairau Valley | 2024-06-26 10:01 | 2024-06-26 15:42 | 0.025098 | 7.36e-05 | 2 | 682 | Planned | Planned interruption | Planned work to OHUG 11kV under Transpower circuit. EAM 1435312 SAF 4048 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 392 | 2024-06-26-0145 | Renwick Township - 0000050207ML228 | CB5482 Renwick Township | 2024-06-26 13:41 | 2024-06-26 14:17 | 0 | 0 | 1 | 36 | Planned | Planned interruption | Planned shutdown to re position LV service. EAM 1480880 SAF 4202 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 393 | 2024-06-27-0146 | Parker St - ABS803-B | CB1516-Parker St | 2024-06-27 08:30 | 2024-06-27 14:28 | 0.17127 | 0.0004784 | 13 | 4654 | Planned | Planned interruption | Planned shutdown to replace pole NZ2100 & SUB370253 on Swamp Road. EAM 1464466 SAF 4083 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 394 | 2024-06-27-0147 | Hutcheson St - 0001107234MLCD1 | CB49-Hutcheson St | 2024-06-27 10:02 | 2024-06-27 10:31 | 0 | 0 | 1 | 30 | Unplanned | Other cause | Blown 30A HRC suspect overload 22A Red 21A White 6A Blue 27/06/2024 10:32:45 am EAM 1489345 - Blown 30A HRC suspect overload 22A Red 21A White 6A Blue Outage rest | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 395 | 2024-06-27-0148 | Havelock Canvastown - RMUS5129-B | CB103 Havelock Canvastown | 2024-06-27 10:15 | 2024-06-27 17:28 | 1.6452 | 0.0087216 | 237 | 44707 | Unplanned | Third party interference | Police reported van v pole near Blackball Culvert on SH6. found 11kV Pole KB0093 broken near top. 11kV off loaded for safety. EAM1489305 NAMSF3824 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 396 | 2024-06-27-0149 | Tuamarina - 0003315074MLA78 | CB188-Tuamarina | 2024-06-27 13:18 | 2024-06-27 17:50 | 0 | 0 | 1 | 272 | Unplanned | Defective equipment | Replaced a burntout Lv fuse, restrored 1749. White phase is reading at 379v - 3PH 60A OH supply EAM 1489447 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 397 | 2024-06-27-0150 | Nelson St - 0001116027ML9FA | CB93-Nelson St | 2024-06-27 17:20 | 2024-06-27 19:30 | 0 | 0 | 1 | 207 | Unplanned | Other cause | Blown 30A RW fuse due to overloading, replaced with 30A HRC fuse. . EAM 1489466 Blown 30A RW fuse due to overloading, | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 398 | 2024-06-27-0151 | Redwood St Sth - 0001186081ML7AE | CB1673-Redwood St Sth | 2024-06-27 17:41 | 2024-07-01 11:01 | 0 | 0 | 1 | 10624 | Unplanned | Defective equipment | Faulty mains entry box, due to possible burnt cable into the house, tenants to enage an electrician to replace the MEB and call MLL when this is completed. Electrician replaced the faulty MEB, and MLL relivened the supply | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 399 | 2024-06-27-0152 | Sounds - 0008812097ML1BA | REC1170-Sounds | 2024-06-27 18:12 | 2024-06-28 08:51 | 0 | 0 | 1 | 879 | Unplanned | Defective equipment | LV Pole Fuse blown due to overload Fuse Letter sent EAM 1489468 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 400 | 2024-06-27-0153 | Wairau Valley - 0002278566MLFF8 | CB5399 Wairau Valley | 2024-06-27 18:41 | 2024-06-27 20:58 | 0 | 0 | 1 | 137 | Unplanned | Other cause | Blown 30A due to overloading. Owner hasnt contacted an electrician yet to shed some load to the other phases. EAM 1489469 Blown 30A due to overloading | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 401 | 2024-06-28-0154 | Redwood St Sth - 0001183593MLFA3 | CB1673-Redwood St Sth | 2024-06-28 12:26 | 2024-06-28 13:15 | 0 | 0 | 1 | 50 | Unplanned | Unknown | Blown 30A fuse, unknown cause as minimal load on livening. Restored 1310 EAM 1489470 Blown 30A fuse, | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 402 | 2024-06-29-0155 | Koromiko - 0006632193ML020 | CB55-Koromiko | 2024-06-29 08:48 | 2024-06-29 10:56 | 0 | 0 | 1 | 127 | Unplanned | Defective equipment | Blown 30A pole fuse due to faulty freezer. Restored 1055. EAM 1489471 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 403 | 2024-07-01-0003 | Sounds - REC106 | REC1170-Sounds | 2024-06-29 09:06 | 2024-06-29 09:06 | 0 | 0 | 14 | 0 | Unplanned | Unknown | Succesful reclose of REC 106 Phase OC | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 404 | 2024-06-29-0157 | Hutcheson St - 0001161073MLE21 | CB49-Hutcheson St | 2024-06-29 18:26 | 2024-06-29 19:32 | 0 | 0 | 1 | 66 | Unplanned | Unknown | Blown Lv fuse in Linkbox Unknown cause Restored 1932 EAM 1489473 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 405 | 2024-06-29-0158 | Hawkesbury Road - 0002271064ML6D8 | CB5457 Hawkesbury Road | 2024-06-29 19:14 | 2024-06-29 20:27 | 0 | 0 | 1 | 72 | Unplanned | Unknown | Blown 30A fuse, unknown cause. Restored 2026. EAM 1489474 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 406 | 2024-06-30-0159 | Koromiko - 0006608534ML698 | CB55-Koromiko | 2024-06-30 17:09 | 2024-06-30 18:30 | 0 | 0 | 1 | 82 | Unplanned | Defective equipment | Blown pole fuse due to possible internal issue (oven). Restored 1830. EAM 1489475 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 407 | 2024-07-01-0001 | Wairau Valley - FUSE4041 | CB5399 Wairau Valley | 2024-07-01 08:30 | 2024-07-01 12:13 | 0.024619 | 0.0001104 | 3 | 669 | Planned | Planned interruption | Planned replacement of SWER iso sub for the Leatham EAM1469495 NAMS4085 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 408 | 2024-07-01-0002 | Rai Valley - SUB335353 | CB43-Rai Valley | 2024-07-01 08:42 | 2024-07-01 09:45 | 0.0046368 | 7.36e-05 | 2 | 126 | Unplanned | Unknown | Blown TX Fuse cause unknown. Replaced EAM 1489501 http://nams.mll.co.nz/Schedule/Edit/3826 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 409 | 2024-07-01-0004 | Murphys Rd - 0001121201MLA6B | CB68-Murphys Rd | 2024-07-01 10:28 | 2024-07-01 11:18 | 0 | 0 | 1 | 50 | Unplanned | Defective equipment | Blown pole fuse - cause unknown EAM 1489511 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 410 | 2024-07-01-0005 | Richmond Brook - 0005506001ML695 | CB1250-Richmond Brook | 2024-07-01 10:32 | 2024-07-01 12:04 | 0 | 0 | 1 | 92 | Unplanned | Defective equipment | Blown fuse - suspect faulty motor however took time to Upgraded fuse bases from Rewireable to HRC EAM1489514 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 411 | 2024-07-01-0006 | Rai Valley - ABS309-B | CB43-Rai Valley | 2024-07-01 10:44 | 2024-07-01 13:50 | 0.10447 | 0.0005888 | 16 | 2839 | Unplanned | Defective equipment | Replaced all 3 fused service restored again Power has gone off again Using same EAM 1489501 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 412 | 2024-07-01-0007 | French Pass - REC5024 | CB45-French Pass | 2024-07-01 13:24 | 2024-07-01 15:18 | 0 | 0 | 75 | 0 | Unplanned | Adverse weather | Multiple successful recloses of REC 5024 Saddle Hill Phase OC Suspect Wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 413 | 2024-07-01-0008 | Richmond Brook - 0005502405MLD1E | CB1250-Richmond Brook | 2024-07-01 13:51 | 2024-07-01 15:24 | 0 | 0 | 1 | 93 | Unplanned | Defective equipment | Blown 30A pole fuse due to faulty oven EAM 1489658 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 414 | 2024-07-01-0009 | Koromiko - 0006608385MLE69 | CB55-Koromiko | 2024-07-01 14:21 | 2024-07-01 15:30 | 0 | 0 | 1 | 69 | Unplanned | Defective equipment | Warn out fuse holder (old) replaced and service restored EAM 1489853 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 415 | 2024-07-01-0010 | Waikawa - REC74 | CB109- Waikawa | 2024-07-01 14:26 | 2024-07-01 14:26 | 0 | 0 | 46 | 0 | Unplanned | Adverse weather | Successful reclose of REC 74 Cause unknown suspect weather | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 416 | 2024-07-01-0011 | Sounds - REC97 | REC1170-Sounds | 2024-07-01 15:21 | 2024-07-01 15:21 | 0 | 0 | 177 | 0 | Unplanned | Adverse weather | Successful reclose of REC 97 Phase OC Suspect weather | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 417 | 2024-07-01-0013 | Causeway - CB1683 | CB1683 Causeway | 2024-07-01 15:41 | 2024-07-02 14:42 | 0.79837 | 0.00368 | 80 | 21695 | Unplanned | Defective equipment | Centre phase off insulator the 2 pole structure KB8484 / ZA2263 Phase off insulator at second site on Mahakipawa hill Pole MA2386. http://nams.mll.co.nz/Schedule/Edit/3831 EAM 1489908 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 418 | 2024-07-01-0018 | Linkwater West - REC1168 | CB1168 - Linkwater West | 2024-07-01 18:27 | 2024-07-01 18:38 | 0.065872 | 0.0065872 | 179 | 1790 | Unplanned | Unknown | Tripped on Phase OC when trying to use ABS 305 to refeed. Fault on 11kV Line going ove Mahaikipawa Hill. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 419 | 2024-07-02-0019 | Sounds - SUB3251DS | REC1170-Sounds | 2024-07-02 08:00 | 2024-07-02 13:43 | 0.10098 | 0.0002944 | 8 | 2744 | Planned | Planned interruption | Planned TX shutdown for vegetation removal and maintenance on LV conductors EAM1458167 NAMS4127 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 420 | 2024-07-02-0020 | Thomsons Ford Rd - RMUS1346 | CB1509-Thomsons Ford Rd | 2024-07-02 08:30 | 2024-07-02 16:26 | 0.070067 | 0.0001472 | 4 | 1904 | Planned | Planned interruption | Planned shutdown to install new RMUS and Transformers . EAM 1433815 SAF 4178 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 421 | 2024-07-02-0021 | French Pass - FUSE4040 | CB45-French Pass | 2024-07-02 09:56 | 2024-07-03 14:00 | 0.061934 | 3.68e-05 | 1 | 1683 | Unplanned | Adverse weather | AC Fail alarm at Bulwer radio site. found 11kV SWER line down between poles AE1876 & BE1685. Found 11kV SWER span down from AE1876 to BE1685 SWER line repaired Power confirmed restored | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 422 | 2024-07-03-0023 | Seymour St - 0001166217MLEBC | CB51-Seymour St | 2024-07-03 06:35 | 2024-07-03 07:59 | 0 | 0 | 1 | 84 | Unplanned | Other cause | Blown fuse - Incorrect fuse in - blown 30amp and ARC shows 60amp EAM 1490230 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 423 | 2024-07-03-0024 | Hutcheson St - 0001107234MLCD1 | CB49-Hutcheson St | 2024-07-03 10:20 | 2024-07-03 10:41 | 0 | 0 | 1 | 21 | Unplanned | Defective equipment | Service Fuse blown red phase EAM 1490355 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 424 | 2024-07-03-0027 | Koromiko - FUSE3587 | CB55-Koromiko | 2024-07-03 10:33 | 2024-07-03 12:02 | 0.019872 | 0.0002208 | 6 | 540 | Unplanned | Third party interference | had a tree make contact with 11kV Lines that a Fuse is blown . Found 2 x Blown Fuses at 11kV FUSE3587 Line patrol carried out to check for damage. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 425 | 2024-07-04-0028 | Craiglochart - RMUS5558 | REC1391-Craiglochart | 2024-07-04 08:30 | 2024-07-04 14:37 | 0.094539 | 0.0002576 | 7 | 2569 | Planned | Planned interruption | Planned shutdown to relocate 11kV line around new irrigation dam. EAM 1485405 SAF 4193 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 426 | 2024-07-04-0029 | Havelock Canvastown - LVUG136752 | CB103 Havelock Canvastown | 2024-07-04 09:17 | 2024-07-04 12:55 | 0 | 0 | 6 | 1302 | Planned | Planned interruption | Planned replacement of SFB XA0122http://nams.mll.co.nz/Application/Edit/4226 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 427 | 2024-07-04-0030 | Dry Hills - LVOH5803 | CB1682-Dry Hills | 2024-07-04 10:09 | 2024-07-04 11:00 | 0 | 0 | 1 | 51 | Planned | Planned interruption | Replacement of LV arm on pole NK1425 EAM1470474 NAMS4121 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 428 | 2024-07-04-0031 | Dashwood - 0005505020ML565 | CB1252-Dashwood | 2024-07-04 15:01 | 2024-07-04 16:00 | 0 | 0 | 1 | 59 | Unplanned | Defective equipment | Internal fault EAM 1491156 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 429 | 2024-07-04-0032 | Spring Creek - FUSE2182 | CB187-Spring Creek | 2024-07-04 17:42 | 2024-07-04 19:21 | 0.0368 | 0.000368 | 10 | 1000 | Unplanned | Wildlife | found dead swan near KB8085 and Blue phase fuse blown at 11kV Fuses 2182. Replaced all 3 with 30A Line to be inspected in daylight for any conductor damage.confirmed scorch marks but no conductor damage. EAM 1491182 F3843 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 430 | 2024-07-04-0033 | Seymour St - 0001166117MLDBF | CB51-Seymour St | 2024-07-04 21:17 | 2024-07-04 22:01 | 0 | 0 | 1 | 45 | Unplanned | Defective equipment | Blown 40A fuse @ meterboard 1491183 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 431 | 2024-07-05-0034 | Omaka - XB7856-P2 | CB1088 - Omaka | 2024-07-05 08:30 | 2024-07-05 10:47 | 0 | 0 | 2 | 274 | Planned | Planned interruption | Planned shutdown to connect re-laid cable between XA0661 and XA0659 due to boundary issues. EAM 1487078 SAF 4221 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 432 | 2024-07-05-0035 | Richmond Brook - SUB3532AA | CB1250-Richmond Brook | 2024-07-05 09:07 | 2024-07-05 11:48 | 0.0059616 | 3.68e-05 | 1 | 162 | Planned | Planned interruption | Planned shutdown for OHUG of LV service. EAM 1486809 SAF 4235 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 433 | 2024-07-05-0036 | Causeway - ABS15212-B | CB1683 Causeway | 2024-07-05 09:29 | 2024-07-05 10:54 | 0.0094944 | 0.0001104 | 3 | 258 | Unplanned | Defective equipment | Urgent shutdown to replace burnt faulty 11kV crossarm on pole KB8484/ZA2263 EAM 1489908 SAF F3835 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 434 | 2024-07-05-0037 | Parker St - 0001137261ML8BA | CB1516-Parker St | 2024-07-05 09:34 | 2024-07-05 09:47 | 0 | 0 | 1 | 13 | Unplanned | Defective equipment | Blown 30A HRC due to damaged heater lead EAM 1491224 Part power 2PH 30A OH supply | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 435 | 2024-07-06-0038 | Hawkesbury Road - 0002271286ML6E0 | CB5457 Hawkesbury Road | 2024-07-06 09:20 | 2024-07-06 12:10 | 0 | 0 | 1 | 171 | Unplanned | Defective equipment | Burnt fuse carrier, both replaced with PF100 EAM: 1491305 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 436 | 2024-07-06-0039 | Richmond Brook - 0005502571ML04D | CB1250-Richmond Brook | 2024-07-06 09:25 | 2024-07-06 10:47 | 0 | 0 | 1 | 82 | Unplanned | Defective equipment | Blown 60A HRC fuse. No cause found, suspect overload. Letter to be sent to customer. Unable to contact customer as requested, number incorrect 1491306 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 437 | 2024-07-06-0040 | Koromiko - 0006609110ML766 | CB55-Koromiko | 2024-07-06 11:39 | 2024-07-06 14:00 | 0 | 0 | 1 | 141 | Unplanned | Defective equipment | Burnt fuse carrier in Gyro. 1491307 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 438 | 2024-07-06-0041 | Weld St - 0001162409ML70C | CB71-Weld St | 2024-07-06 12:14 | 2024-07-06 13:00 | 0 | 0 | 1 | 46 | Unplanned | Defective equipment | Blown 30A HRC, suspect overload. Letter to be sent to customer 1491308 'Part Power | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 439 | 2024-07-07-0042 | East Coast - REC5274 | REC29-East Coast | 2024-07-07 07:42 | 2024-07-07 13:15 | 0.19607 | 0.0005888 | 16 | 5328 | Unplanned | Defective equipment | found 11kV REC5274 in Open position. Patrolling line to next downstream fuse 3528. Fuse had not blown but fault was beyond here. Replaced 10A Fuse with 6A. Fault found at pole AE1632 Sub 352552. 11kV Jumper broken from top of fuse repaired. 1491309 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 440 | 2024-07-07-0043 | Sounds - 0008814081MLF58 | REC1170-Sounds | 2024-07-07 11:52 | 2024-07-12 11:37 | 0 | 0 | 1 | 7186 | Unplanned | Defective equipment | Trurip burnt off pole. Service fuse pulled. Have arrange for faults to attend tomorrow 11/07/2024 to replace trurip customer award. 1491312 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 441 | 2024-07-07-0044 | Waikawa - 0006603227ML017 | CB109- Waikawa | 2024-07-07 13:11 | 2024-07-08 16:20 | 0 | 0 | 1 | 1630 | Unplanned | Defective equipment | Burnt neutral/earth at meterboard. Safety disc/tagged at pole. Customer to get Electrician to repair 1491313 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 442 | 2024-07-07-0045 | Hardings Rd - 0003350011ML472 | CB167-Hardings Rd | 2024-07-07 16:44 | 2024-07-07 18:16 | 0 | 0 | 1 | 92 | Unplanned | Defective equipment | Blown fuse at meterboard. Suspect internal fault 1491314 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 443 | 2024-07-07-0046 | Ngakuta - 0007715467MLB40 | REC1562-Ngakuta | 2024-07-07 18:23 | 2024-07-07 19:50 | 0 | 0 | 1 | 86 | Unplanned | Defective equipment | Blown 60A rewireable fuse due to deterioration 1491315 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 444 | 2024-07-08-0048 | Omaka - 0001123678MLE26 | CB1088 - Omaka | 2024-07-07 23:10 | 2024-07-08 08:10 | 0 | 0 | 1 | 539 | Unplanned | Defective equipment | Burnt 100A fuse base at meter board, replaced by Electrictian 1491317 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 445 | 2024-07-08-0049 | Ngakuta - XA0165-P4 | REC1562-Ngakuta | 2024-07-08 08:37 | 2024-07-08 11:31 | 0 | 0 | 10 | 1740 | Planned | Planned interruption | Planned shutdown to replace damaged SFB XA2352. EAM 1467400 SAF 4099 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 446 | 2024-07-08-0050 | Sounds - 0008811562MLB07 | REC1170-Sounds | 2024-07-08 10:38 | 2024-07-08 15:35 | 0 | 0 | 1 | 592 | Unplanned | Defective equipment | Internal issue - Issue at the Meterboard Line has been isolated at the meterboard, so MLL does not need to go back out to reliven Customer to Contact Meterboard Tech EAM 1491361 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 447 | 2024-07-08-0052 | Parker St - 0001146436ML067 | CB1516-Parker St | 2024-07-08 18:25 | 2024-07-08 19:29 | 0 | 0 | 1 | 64 | Unplanned | Defective equipment | Burnt fuse carrier 1491404 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 448 | 2024-07-09-0053 | Vintage Lane - CB171 | CB171-Vintage Lane | 2024-07-09 08:30 | 2024-07-09 17:01 | 0.16924 | 0.0003312 | 9 | 4599 | Planned | Planned interruption | Planned shutdown to complete 33kV line and cable work outside Woodbourne Sub for switchboard livening. Day 1 EAM 1397584 SAF 3977.1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 449 | 2024-07-09-0054 | Woodbourne - CB1178 | CB1178-Woodbourne | 2024-07-09 08:30 | 2024-07-09 17:00 | 0.056304 | 0.0001104 | 3 | 1530 | Planned | Planned interruption | Planned shutdown to complete 33kV line and cable work outside Woodbourne Sub for switchboard livening. Day 1 EAM 1397584 SAF 3977.1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 450 | 2024-07-10-0055 | Vintage Lane - CB171 | CB171-Vintage Lane | 2024-07-10 08:30 | 2024-07-10 18:07 | 0.19044 | 0.0054096 | 138 | 5175 | Planned | Planned interruption | Planned shutdown to complete 33kV line and cable work outside Woodbourne Sub for switchboard livening. Day 2 EAM 1397584 SAF 3977.2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 451 | 2024-07-10-0056 | Woodbourne - CB1178 | CB1178-Woodbourne | 2024-07-10 08:30 | 2024-07-10 18:21 | 0.065246 | 0.007544 | 202 | 1773 | Planned | Planned interruption | Planned shutdown to complete 33kV line and cable work outside Woodbourne Sub for switchboard livening. Day 2 EAM 1397584 SAF 3977.2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 452 | 2024-07-10-0057 | Sounds - FUSE2380 | REC1170-Sounds | 2024-07-10 08:30 | 2024-07-10 15:37 | 0 | 0 | 61 | 26047 | Planned | Planned interruption | Planned shutdown to remove vegetation between AX1245 & AA1998 EAM1436981 NAMS4223 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 453 | 2024-07-10-0058 | Sounds - 0008813589MLC29 | REC1170-Sounds | 2024-07-10 10:02 | 2024-07-10 13:30 | 0 | 0 | 1 | 209 | Unplanned | Defective equipment | EAM 1491628 on arrival found burnt out LV Service fuse at Pole HA2318 Fuse Base replaced and power confirmed restored | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 454 | 2024-07-10-0059 | Waikawa - FUSE2966 | CB109- Waikawa | 2024-07-10 10:38 | 2024-07-10 12:33 | 0.004232 | 3.68e-05 | 1 | 115 | Planned | Planned interruption | Planned shutdown to replace x-arm on pole PT5232. Work could not proceed due to ground conditions onsite. EAM1440291 NAMS3981 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 455 | 2024-07-10-0061 | Rapaura Rd - 0003330204MLBCF | CB1077-Rapaura Rd | 2024-07-10 15:48 | 2024-07-10 19:25 | 0 | 0 | 1 | 216 | Unplanned | Defective equipment | Blown fuse, appears to be issues with internal wiring EAM 1491757 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 456 | 2024-07-11-0066 | Vintage Lane - HVUG138822 | CB171-Vintage Lane | 2024-07-11 07:47 | 2024-07-11 07:53 | 0.02473 | 0.0041216 | 112 | 672 | Unplanned | Human error | Switching error during planned shutdown for Woodbourne 33kV switchroom upgrade. SAF 3977.3. 11kV RMUS 1527 opened before 11kV RMUS 1511 was closed | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 457 | 2024-07-11-0068 | Vintage Lane - CB171 | CB171-Vintage Lane | 2024-07-11 08:30 | 2024-07-11 16:58 | 0.16825 | 0.0003312 | 9 | 4572 | Planned | Planned interruption | Planned shutdown to complete 33kV line and cable work outside Woodbourne Sub for switchboard livening. Day 3 EAM 1397584 SAF 3977.3 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 458 | 2024-07-11-0069 | Woodbourne - CB1178 | CB1178-Woodbourne | 2024-07-11 08:30 | 2024-07-11 16:43 | 0.054427 | 0.0001104 | 3 | 1479 | Planned | Planned interruption | Planned shutdown to complete 33kV line and cable work outside Woodbourne Sub for switchboard livening. Day 3 EAM 1397584 SAF 3977.3 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 459 | 2024-07-11-0070 | Weld St - 0001162305MLB10 | CB71-Weld St | 2024-07-11 09:48 | 2024-07-11 11:12 | 0 | 0 | 1 | 85 | Unplanned | Defective equipment | Blown Pole fuse - replace 100amp Only showing 55amps but suspect Overloading Fuse Letter Sent EAM 1491785 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 460 | 2024-07-11-0071 | Hawkesbury Road - 0002271218MLA9C | CB5457 Hawkesbury Road | 2024-07-11 15:50 | 2024-07-11 18:30 | 0 | 0 | 1 | 161 | Unplanned | Unknown | Fuse at SFB XA5024 found blown, Fuse replaced and voltage on outgoing of fuses. No one at house and meterboard inside house. 3 PH 30Amp supply to house EAM1491987 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 461 | 2024-07-12-0072 | Vintage Lane - CB171 | CB171-Vintage Lane | 2024-07-12 08:30 | 2024-07-12 17:47 | 0.18448 | 0.0003312 | 9 | 5013 | Planned | Planned interruption | Planned shutdown to complete 33kV line and cable work outside Woodbourne Sub for switchboard livening. Day 4 EAM 1397584 SAF 3977.4 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 462 | 2024-07-12-0073 | Woodbourne - CB1178 | CB1178-Woodbourne | 2024-07-12 08:30 | 2024-07-12 17:44 | 0.061161 | 0.0001104 | 3 | 1662 | Planned | Planned interruption | Planned shutdown to complete 33kV line and cable work outside Woodbourne Sub for switchboard livening. Day 4 EAM 1397584 SAF 3977.4 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 463 | 2024-07-12-0074 | Ngakuta - 0007709565ML1A0 | REC1562-Ngakuta | 2024-07-12 08:42 | 2024-07-12 09:22 | 0 | 0 | 1 | 40 | Planned | Planned interruption | Resagging of LVOH across Queen Charlotte Drive outside 1508 EAM1476029 NAMS4133 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 464 | 2024-07-12-0075 | Weld St - 0001162305MLB10 | CB71-Weld St | 2024-07-12 09:41 | 2024-07-12 10:05 | 0 | 0 | 1 | 25 | Unplanned | Other cause | Blown fuse due to overloading, replaced fuse EAM 1492310 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 465 | 2024-07-12-0076 | Waikawa - REC74 | CB109- Waikawa | 2024-07-12 13:29 | 2024-07-13 10:33 | 0.99168 | 0.0037168 | 45 | 26948 | Unplanned | Defective equipment | REC74 has Tripped on PH OC A trial CLOSE was made 15min after Trip and REC74 tripped again. Line Patrol required carry out line patrol in chopper. EAM1492374 NAMS F3861 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 466 | 2024-07-12-0077 | Wairau Valley - 0002278567ML3BD | CB5399 Wairau Valley | 2024-07-12 18:42 | 2024-07-12 20:03 | 0 | 0 | 1 | 81 | Unplanned | Other cause | blown pole fuse due to overloading EAM 1492392 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 467 | 2024-07-12-0078 | Hutcheson St - 0001161073MLE21 | CB49-Hutcheson St | 2024-07-12 19:00 | 2024-07-12 20:12 | 0 | 0 | 1 | 73 | Unplanned | Defective equipment | No Power Burnt out fuse carrier - replaced EAM 1492393 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 468 | 2024-07-12-0079 | Richmond Brook - 0005502571ML04D | CB1250-Richmond Brook | 2024-07-12 20:42 | 2024-07-12 21:57 | 0 | 0 | 1 | 75 | Unplanned | Defective equipment | Fuse carrier burnt out, replaced EAM 1492394 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 469 | 2024-07-13-0080 | Old Renwick Rd - CB66 | CB66-Old Renwick Rd | 2024-07-13 13:16 | 2024-07-13 14:18 | 0.5796 | 0.0092 | 250 | 15750 | Unplanned | Unknown | heard a loud bang a couple of spans Line Patrol carried out Faultstaff watched Rene St whilst power was put back on. No obvious signs of faults CB in and holding. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 470 | 2024-07-13-0081 | Hawkesbury Road - 0002271064ML6D8 | CB5457 Hawkesbury Road | 2024-07-13 17:21 | 2024-07-13 18:33 | 0 | 0 | 1 | 73 | Unplanned | Other cause | Failed 30 AMP fuse, house drawing 38 Amp, owner looking maybe up grading house to a 60 Amp, also getting a Electrician up tomorrow., fuse letter required to be sent EAM 1492396 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 471 | 2024-07-13-0082 | Hutcheson St - 0001161073MLE21 | CB49-Hutcheson St | 2024-07-13 18:03 | 2024-07-13 18:39 | 0 | 0 | 1 | 37 | Unplanned | Defective equipment | Using same W/O as last night. Fuse Letter sent W/O 1492393 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 472 | 2024-07-14-0083 | Redwood St Nth - 0001106601MLBC7 | CB1655-Redwood St Nth | 2024-07-14 16:37 | 2024-07-14 17:49 | 0 | 0 | 1 | 73 | Unplanned | Defective equipment | Tripped RCD Internal fault W/O 1492398 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 473 | 2024-07-15-0084 | Thomsons Ford Rd - FUSE2570 | CB1509-Thomsons Ford Rd | 2024-07-15 08:35 | 2024-07-15 11:09 | 0.045337 | 0.0002944 | 8 | 1232 | Planned | Planned interruption | Re-sag of LV between AA2128 - AA2145. HV isolated due LV consuctor being No.8 EAM1480819 NAMS4187 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 474 | 2024-07-15-0085 | Godfrey Road - FUSE2123 | CB5367 Godfrey Road | 2024-07-15 08:38 | 2024-07-15 15:37 | 0.030765 | 7.36e-05 | 2 | 836 | Planned | Planned interruption | Line upgrade EAM1435926 NAMS4112 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 475 | 2024-07-16-0086 | Havelock Canvastown - REC5247 | CB103 Havelock Canvastown | 2024-07-16 08:30 | 2024-07-16 14:30 | 0.84743 | 0.0036432 | 99 | 23028 | Planned | Planned interruption | Planned shutdown to replace Sub320211 and TX fuses. SAF 4047 EAM 1464228 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 476 | 2024-07-16-0087 | Waikawa - SUB330061 | CB109- Waikawa | 2024-07-16 08:52 | 2024-07-16 11:43 | 0.33981 | 0.0019872 | 54 | 9234 | Planned | Planned interruption | Connection of new LV FUSE22443 at SUB330061 in Waikawa Rd http://nams.mll.co.nz/Schedule/Edit/3841 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 477 | 2024-07-16-0090 | Waikawa - 0006622032ML59F | CB109- Waikawa | 2024-07-16 08:52 | 2024-07-16 11:43 | 0.0062928 | 3.68e-05 | 1 | 171 | Planned | Planned interruption | due to model error, was missed in notification. Waikawa Road Planned Work http://nams.mll.co.nz/Schedule/Edit/3841. See 2024-07-16-0087 for main shutdown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 478 | 2024-07-16-0088 | Godfrey Road - FUSE2123 | CB5367 Godfrey Road | 2024-07-16 09:35 | 2024-07-16 16:37 | 0.030986 | 7.36e-05 | 2 | 842 | Planned | Planned interruption | Line upgrade EAM1435926 NAMS4112 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 479 | 2024-07-16-0089 | Omaka - 0001142875ML48E | CB1088 - Omaka | 2024-07-16 11:13 | 2024-07-16 12:54 | 0 | 0 | 1 | 101 | Unplanned | Defective equipment | Blown fuse in sfb Fuse letter left EAM 1492736 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 480 | 2024-07-17-0091 | Symons St - LVUG2271 | CB50-Symons St | 2024-07-17 05:30 | 2024-07-17 06:17 | 0 | 0 | 4 | 188 | Planned | Planned interruption | Shutdown of DP76 Market St for removal of cable from positions 3 and 5 for First Lane RMU and TX replacement. SAF4199 WO 1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 481 | 2024-07-17-0092 | Symons St - 0001101067ML7DE | CB50-Symons St | 2024-07-17 05:30 | 2024-07-17 06:17 | 0 | 0 | 1 | 47 | Planned | Planned interruption | Shutdown of DP76 Market St for removal of cable from positions 3 and 5 for First Lane RMU and TX replacement. SAF4199 WO 1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 482 | 2024-07-17-0093 | Symons St - 0001101289ML4F8 | CB50-Symons St | 2024-07-17 05:30 | 2024-07-17 06:17 | 0 | 0 | 1 | 47 | Planned | Planned interruption | Shutdown of DP76 Market St for removal of cable from positions 3 and 5 for First Lane RMU and TX replacement. SAF4199 WO 1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 483 | 2024-07-17-0094 | Symons St - 0001101200MLFE3 | CB50-Symons St | 2024-07-17 05:30 | 2024-07-17 06:17 | 0 | 0 | 1 | 47 | Planned | Planned interruption | Shutdown of DP76 Market St for removal of cable from positions 3 and 5 for First Lane RMU and TX replacement. SAF4199 WO 1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 484 | 2024-07-17-0095 | Godfrey Road - FUSE2123 | CB5367 Godfrey Road | 2024-07-17 08:46 | 2024-07-18 13:31 | 0.090712 | 0.0001104 | 2 | 2465 | Planned | Planned interruption | Line upgrade EAM1435926 NAMS4112.3 & NAMS4112.4 11kV Fuses at SUB343317 have been removed overnight. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 485 | 2024-07-17-0096 | Havelock Canvastown - REC1403 | CB103 Havelock Canvastown | 2024-07-17 09:16 | 2024-07-17 09:16 | 0 | 0 | 28 | 0 | Unplanned | Unknown | Successful reclose of REC 1403 Phase OC | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 486 | 2024-07-17-0097 | Waikawa - 0006617437ML2DD | CB109- Waikawa | 2024-07-17 18:15 | 2024-07-17 21:40 | 0 | 0 | 1 | 206 | Unplanned | Defective equipment | Replaced burnt out 63A fuse in Gyro box up ROW. EAM 1493123 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 487 | 2024-07-18-0102 | Symons St - LVUG2271 | CB50-Symons St | 2024-07-18 05:37 | 2024-07-18 07:11 | 0 | 0 | 4 | 376 | Planned | Planned interruption | Reconnection of LV cable to Pos 3 in DP76 Market St for First Lane RMU and TX replacement SAF 4199 WO 1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 488 | 2024-07-18-0103 | Symons St - 0001101067ML7DE | CB50-Symons St | 2024-07-18 05:37 | 2024-07-18 07:11 | 0 | 0 | 1 | 94 | Planned | Planned interruption | Reconnection of LV cable to Pos 3 in DP76 Market St for First Lane RMU and TX replacement SAF 4199 WO 1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 489 | 2024-07-18-0104 | Symons St - 0001101289ML4F8 | CB50-Symons St | 2024-07-18 05:37 | 2024-07-18 07:11 | 0 | 0 | 1 | 94 | Planned | Planned interruption | Reconnection of LV cable to Pos 3 in DP76 Market St for First Lane RMU and TX replacement SAF 4199 WO 1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 490 | 2024-07-18-0105 | Symons St - 0001101200MLFE3 | CB50-Symons St | 2024-07-18 05:37 | 2024-07-18 07:11 | 0 | 0 | 1 | 94 | Planned | Planned interruption | Reconnection of LV cable to Pos 3 in DP76 Market St for First Lane RMU and TX replacement SAF 4199 WO 1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 491 | 2024-07-18-0106 | Symons St - 0001101108MLEF4 | CB50-Symons St | 2024-07-18 05:37 | 2024-07-18 07:17 | 0 | 0 | 1 | 100 | Planned | Planned interruption | Reconnection of LV cable to Pos 3 in DP76 Market St for First Lane RMU and TX replacement SAF 4199 WO 1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 492 | 2024-07-18-0107 | Symons St - 0001101107ML12A | CB50-Symons St | 2024-07-18 05:37 | 2024-07-18 07:17 | 0 | 0 | 1 | 100 | Planned | Planned interruption | Reconnection of LV cable to Pos 3 in DP76 Market St for First Lane RMU and TX replacement SAF 4199 WO 1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 493 | 2024-07-18-0098 | Richmond Brook - RMUS5281 | CB1250-Richmond Brook | 2024-07-18 08:30 | 2024-07-18 15:11 | 1.579 | 0.0039376 | 107 | 42907 | Planned | Planned interruption | Planned shutdown to install a new transformer. EAM 1468533 SAF 4139 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 494 | 2024-07-18-0099 | Kaituna - FUSE2105 | CB5448 Kaituna | 2024-07-18 08:30 | 2024-07-18 12:57 | 0.19651 | 0.000736 | 20 | 5340 | Planned | Planned interruption | Planned shutdown to replace iron rail pole. EAM 1467347 SAF 4050 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 495 | 2024-07-18-0100 | Pelorus - 0007713181ML0B0 | CB5126-Pelorus | 2024-07-18 11:46 | 2024-07-18 18:13 | 0 | 0 | 1 | 388 | Unplanned | Defective equipment | Meter has shorted out due to moisture. 2 x blown pole fuses (60A porcelain). EAM 1493191 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 496 | 2024-07-18-0101 | Grassmere - REC28 | CB1253-Grassmere | 2024-07-18 13:12 | 2024-07-18 21:21 | 0.11114 | 0.0008832 | 24 | 3020 | Unplanned | Third party interference | Tree through 11kV. REC28 opened for safety - found tree on lines between poles DF1804 and PT2242. replaced broken pole PT2242 and replaced broken anchor at pole HA1842. Fuses replaced (20A) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 497 | 2024-07-19-0108 | Symons St - LVUG2271 | CB50-Symons St | 2024-07-19 05:31 | 2024-07-19 06:02 | 0 | 0 | 4 | 124 | Planned | Planned interruption | Disconnection of cable from LV Pos 4 at DP95 Market St for the First Lane RMU/TX replacement. SAF4199.1 WO 1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 498 | 2024-07-19-0109 | Symons St - 0001101067ML7DE | CB50-Symons St | 2024-07-19 05:31 | 2024-07-19 06:02 | 0 | 0 | 1 | 31 | Planned | Planned interruption | Disconnection of cable from LV Pos 4 at DP95 Market St for the First Lane RMU/TX replacement. SAF4199.1 WO 1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 499 | 2024-07-19-0110 | Symons St - 0001101289ML4F8 | CB50-Symons St | 2024-07-19 05:31 | 2024-07-19 06:02 | 0 | 0 | 1 | 31 | Planned | Planned interruption | Disconnection of cable from LV Pos 4 at DP95 Market St for the First Lane RMU/TX replacement. SAF4199.1 WO 1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 500 | 2024-07-19-0111 | Symons St - 0001101200MLFE3 | CB50-Symons St | 2024-07-19 05:31 | 2024-07-19 06:02 | 0 | 0 | 1 | 31 | Planned | Planned interruption | Disconnection of cable from LV Pos 4 at DP95 Market St for the First Lane RMU/TX replacement. SAF4199.1 WO 1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 501 | 2024-07-19-0112 | Symons St - 0001101108MLEF4 | CB50-Symons St | 2024-07-19 05:31 | 2024-07-19 06:06 | 0 | 0 | 1 | 35 | Planned | Planned interruption | Disconnection of cable from LV Pos 4 at DP95 Market St for the First Lane RMU/TX replacement. SAF4199.1 WO 1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 502 | 2024-07-19-0113 | Symons St - 0001101107ML12A | CB50-Symons St | 2024-07-19 05:31 | 2024-07-19 06:06 | 0 | 0 | 1 | 35 | Planned | Planned interruption | Disconnection of cable from LV Pos 4 at DP95 Market St for the First Lane RMU/TX replacement. SAF4199.1 WO 1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 503 | 2024-07-19-0114 | Symons St - 0001101014MLE43 | CB50-Symons St | 2024-07-19 05:45 | 2024-07-19 07:53 | 0 | 0 | 1 | 128 | Planned | Planned interruption | Changeover of the service from DP82/1 to the new DP First Lane SAF 4214.1 WO 1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 504 | 2024-07-19-0115 | Spring Creek - 0003340542MLD5E | CB187-Spring Creek | 2024-07-19 18:06 | 2024-07-19 19:26 | 0 | 0 | 1 | 80 | Unplanned | Other cause | Blown 30A fuse, should have been a 60A fuse. No charge and no letter required. EAM 1493530 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 505 | 2024-07-20-0116 | Okaramio - 0007705233MLCA5 | CB104 Okaramio | 2024-07-20 17:12 | 2024-07-20 17:55 | 0 | 0 | 1 | 43 | Unplanned | Other cause | Found a blown 30A fuse. These fuses were changed to a PF100 recently from a RW type and have probably been installed with 30A by mistake. ARC says it should be 2ph 60A supply. Will go back tomorrow and replace both fuses to 60A. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 506 | 2024-07-21-0117 | Omaka - 0001123301ML02F | CB1088 - Omaka | 2024-07-21 00:13 | 2024-07-21 13:51 | 0 | 0 | 1 | 818 | Unplanned | Third party interference | Pole KB2255 was destroyed by a vehicle accident. Service fuse removed at SFB66 and pole to be replaced in the morning. - pole replaced and services relivened | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 507 | 2024-07-21-0118 | Omaka - 0001123515MLD8E | CB1088 - Omaka | 2024-07-21 00:13 | 2024-07-21 13:51 | 0 | 0 | 1 | 818 | Unplanned | Third party interference | Pole KB2255 was destroyed by a vehicle accident. Service fuse removed at SFB66 and pole to be replaced in the morning. - pole replaced and services relivened | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 508 | 2024-07-21-0119 | Omaka - 0001123512ML044 | CB1088 - Omaka | 2024-07-21 00:13 | 2024-07-23 15:20 | 0 | 0 | 1 | 3787 | Unplanned | Third party interference | The Chrorus cabinet outside was destroyed by a vehicle accident. Service fuse removed at SFB66 will require inspection and livening once cabinet has been replaced | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 509 | 2024-07-21-0120 | Sounds - 0008811249ML784 | REC1170-Sounds | 2024-07-21 11:24 | 2024-07-22 14:02 | 0 | 0 | 1 | 1597 | Unplanned | Defective equipment | Service restored after fuse replaced - Internal issue caused fault EAM 1493535 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 510 | 2024-07-22-0121 | Symons St - LVUG2271 | CB50-Symons St | 2024-07-22 05:37 | 2024-07-22 06:17 | 0 | 0 | 4 | 160 | Planned | Planned interruption | Shutdown of DP76 and DP96 Market St to reconnect LV cable to Pos 4 at DP95 for First Lane RMU/TX replacement SAF4199.1 WO1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 511 | 2024-07-22-0122 | Symons St - 0001101067ML7DE | CB50-Symons St | 2024-07-22 05:37 | 2024-07-22 06:17 | 0 | 0 | 1 | 40 | Planned | Planned interruption | Shutdown of DP76 and DP96 Market St to reconnect LV cable to Pos 4 at DP95 for First Lane RMU/TX replacement SAF4199.1 WO1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 512 | 2024-07-22-0123 | Symons St - 0001101289ML4F8 | CB50-Symons St | 2024-07-22 05:37 | 2024-07-22 06:17 | 0 | 0 | 1 | 40 | Planned | Planned interruption | Shutdown of DP76 and DP96 Market St to reconnect LV cable to Pos 4 at DP95 for First Lane RMU/TX replacement SAF4199.1 WO1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 513 | 2024-07-22-0124 | Symons St - 0001101200MLFE3 | CB50-Symons St | 2024-07-22 05:37 | 2024-07-22 06:17 | 0 | 0 | 1 | 40 | Planned | Planned interruption | Shutdown of DP76 and DP96 Market St to reconnect LV cable to Pos 4 at DP95 for First Lane RMU/TX replacement SAF4199.1 WO1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 514 | 2024-07-22-0125 | Symons St - 0001101108MLEF4 | CB50-Symons St | 2024-07-22 05:37 | 2024-07-22 06:17 | 0 | 0 | 1 | 40 | Planned | Planned interruption | Shutdown of DP76 and DP96 Market St to reconnect LV cable to Pos 4 at DP95 for First Lane RMU/TX replacement SAF4199.1 WO1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 515 | 2024-07-22-0126 | Symons St - 0001101107ML12A | CB50-Symons St | 2024-07-22 05:37 | 2024-07-22 06:17 | 0 | 0 | 1 | 40 | Planned | Planned interruption | Shutdown of DP76 and DP96 Market St to reconnect LV cable to Pos 4 at DP95 for First Lane RMU/TX replacement SAF4199.1 WO1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 516 | 2024-07-22-0127 | Symons St - 0001101004ML4EE | CB50-Symons St | 2024-07-22 06:32 | 2024-07-22 08:14 | 0 | 0 | 1 | 102 | Planned | Planned interruption | Changeover of the LV service from DP82/1 to the new DP First Lane SAF 4215 WO1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 517 | 2024-07-22-0128 | Wairau Valley - ABS15159-B | CB5399 Wairau Valley | 2024-07-22 08:30 | 2024-07-22 11:23 | 0.28645 | 0.004784 | 130 | 7784 | Planned | Planned interruption | Planned shutdown to replace faulty 11kV ABS 15246 EAM 1470182 SAF 4098 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 518 | 2024-07-22-0129 | Hospital Rd East - 0001182000ML821 | CB39-Hospital Rd East | 2024-07-22 08:54 | 2024-07-22 10:35 | 0 | 0 | 1 | 101 | Unplanned | Other cause | blown pole fuse due to overloading Fuse letter left with customer (they were also advised verbally) EAM 1493560 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 519 | 2024-07-22-0130 | Old Renwick Rd - FUSE2045 | CB66-Old Renwick Rd | 2024-07-22 09:00 | 2024-07-22 14:30 | 0.024214 | 7.36e-05 | 2 | 658 | Planned | Planned interruption | Replacement of pole AE1841 (red tagged) EAM1471938 NAMS4126 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 520 | 2024-07-23-0131 | Symons St - 0001101012MLFCC | CB50-Symons St | 2024-07-23 06:45 | 2024-07-23 07:50 | 0 | 0 | 1 | 65 | Planned | Planned interruption | Changeover of the service to the 'Lifetime' building from DP82/1 to the new DP First Lane SAF 4216 WO 1413873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 521 | 2024-07-23-0132 | Godfrey Road - FUSE2123 | CB5367 Godfrey Road | 2024-07-23 08:35 | 2024-07-23 16:03 | 0.032973 | 7.36e-05 | 2 | 896 | Planned | Planned interruption | Planned Line rebuild at 530 New Renwick Rd EAM1435926 NAMS4112 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 522 | 2024-07-23-0133 | Kaituna - 0007706191ML5DC | CB5448 Kaituna | 2024-07-23 08:43 | 2024-07-23 10:32 | 0.004048 | 3.68e-05 | 1 | 110 | Unplanned | Wildlife | 2 Blown Fuses Fuse 2637 - Cattle rubbing on polehttp://nams.mll.co.nz/Schedule/Edit/3893 EAM 1493804 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 523 | 2024-07-23-0134 | Godfrey Road - 0002270569MLD26 | CB5367 Godfrey Road | 2024-07-23 08:56 | 2024-07-23 10:37 | 0 | 0 | 1 | 101 | Unplanned | Adverse weather | Blown fuse, suspect clashing of the lv. Been off for some time EAM 1493809 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 524 | 2024-07-23-0135 | Koromiko - 0006608561ML3DF | CB55-Koromiko | 2024-07-23 14:08 | 2024-07-23 16:35 | 0 | 0 | 1 | 148 | Unplanned | Defective equipment | Ran earth loop test with no faults found, internal fault, advised to contact electrician EAM 1493999 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 525 | 2024-07-24-0139 | Parker St - 0004450081ML7BE | CB1516-Parker St | 2024-07-24 06:41 | 2024-07-24 08:00 | 0 | 0 | 1 | 79 | Planned | Planned interruption | Planned shutdown to Replace DP 60, and remove Andelec DP 58 Grove Rd EAM 1481137 SAF 4171 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 526 | 2024-07-24-0140 | Parker St - LVUG633 | CB1516-Parker St | 2024-07-24 06:41 | 2024-07-24 08:50 | 0 | 0 | 1 | 129 | Planned | Planned interruption | Planned shutdown to Replace DP 60, and remove Andelec DP 58 Grove Rd EAM 1481137 SAF 4171 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 527 | 2024-07-24-0136 | Redwood St Nth - LVOH6210 | CB1655-Redwood St Nth | 2024-07-24 08:33 | 2024-07-24 12:13 | 0 | 0 | 5 | 1100 | Planned | Planned interruption | Planned shutdown to replace red tagged pole DF3262 EAM 1480750 SAF 4157 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 528 | 2024-07-24-0137 | Renwick Township - FUSE21731 | CB5482 Renwick Township | 2024-07-24 09:18 | 2024-07-24 16:01 | 0 | 0 | 2 | 806 | Planned | Planned interruption | Planned shutdown for LV OHUG work. EAM 1437118 SAF 3911 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 529 | 2024-07-24-0138 | Renwick Township - 0000051292ML120 | CB5482 Renwick Township | 2024-07-24 09:18 | 2024-07-24 16:01 | 0 | 0 | 1 | 403 | Planned | Planned interruption | Planned shutdown for LV OHUG work. EAM 1437118 SAF 3911 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 530 | 2024-07-24-0142 | French Pass - 0008802069MLAD7 | CB45-French Pass | 2024-07-24 10:30 | 2024-07-24 13:45 | 0 | 0 | 1 | 195 | Planned | Planned interruption | Replacement of red tagged pole JA2166 EAM1453766 SAF 4024 24/07/2024 2:03:37 pm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 531 | 2024-07-24-0141 | Thomsons Ford Rd - SUB360003 | CB1509-Thomsons Ford Rd | 2024-07-24 13:38 | 2024-07-24 15:02 | 0.003128 | 3.68e-05 | 1 | 85 | Planned | Planned interruption | Planned shutdown to resag HV lines using G&B techniques. EAM 1480820 SAF 4188 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 532 | 2024-07-24-0143 | Renwick Township - LVUG300080 | CB5482 Renwick Township | 2024-07-24 13:40 | 2024-07-29 20:30 | 0 | 0 | 1 | 7610 | Planned | Planned interruption | Planned shutdown for LV OHUG work. EAM 1437118 SAF 3911 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 533 | 2024-07-24-0144 | Thomsons Ford Rd - 0004421448ML918 | CB1509-Thomsons Ford Rd | 2024-07-24 16:37 | 2024-07-24 17:16 | 0 | 0 | 1 | 40 | Unplanned | Other cause | 2x blown 60A fuses. EAM 1494182 No power to shed, | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 534 | 2024-07-25-0149 | Parker St - 0001144340ML8F7 | CB1516-Parker St | 2024-07-25 06:30 | 2024-07-25 08:00 | 0 | 0 | 1 | 90 | Planned | Planned interruption | Planned shutdown to move service into new DP60 Grove Rd. EAM 1481137 SAF 4172 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 535 | 2024-07-25-0145 | Redwood St Nth - 0001104417ML9A2 | CB1655-Redwood St Nth | 2024-07-25 07:44 | 2024-07-25 09:00 | 0 | 0 | 1 | 76 | Unplanned | Other cause | Replaced blown 30A pole fuse, white phase at house. 22A on livening. Left Fuse letter with customer. EAM 1494189 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 536 | 2024-07-25-0146 | Ward - SUB352433 | REC31-Ward | 2024-07-25 08:30 | 2024-07-25 09:00 | 0.015456 | 0.0005152 | 14 | 420 | Planned | Planned interruption | Planned shutdown to replace HV cross arms in Carroll St EAM 1476689 SAF 4144 Job abandoned as school were unaware of outage. Retailer notification had been sent | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 537 | 2024-07-25-0147 | Buller St - LVOH292-S14644 | CB108-Buller St | 2024-07-25 08:47 | 2024-07-25 14:23 | 0 | 0 | 18 | 6048 | Planned | Planned interruption | LV arm replacement and pole patching at KB6611 and ET4857 EAM1481088 NAMS4175 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 538 | 2024-07-25-0148 | Redwood St Nth - 0001108426ML99F | CB1655-Redwood St Nth | 2024-07-25 09:57 | 2024-07-25 10:50 | 0 | 0 | 1 | 54 | Unplanned | Other cause | Blown 60amp fuse (White phase) suspect overloading, as balancing required over the other 2 phase showed 0 Fuse letter left EAM 1494221 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 539 | 2024-07-25-0150 | Weld St - 0001162421ML84D | CB71-Weld St | 2024-07-25 20:12 | 2024-07-26 10:01 | 0 | 0 | 1 | 829 | Unplanned | Defective equipment | Red phase 236V 0.66? White phase 238V EFL 0.64? House Main Earth 44 ? The meter had been changed on the 25th | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 540 | 2024-07-26-0151 | Wairau Valley - FUSE2545 | CB5399 Wairau Valley | 2024-07-26 08:30 | 2024-07-26 11:13 | 0.023846 | 0.0001472 | 4 | 648 | Planned | Planned interruption | Planned shutdown to replace missing hardware on poles AX1995 and AX1997. EAM 1485308 SAF 4189 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 541 | 2024-07-26-0152 | Waikawa - 0006602334MLEDE | CB109- Waikawa | 2024-07-26 08:51 | 2024-07-26 09:54 | 0 | 0 | 1 | 64 | Unplanned | Defective equipment | Replaced blown REW with HRC EAM 1494429 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 542 | 2024-07-26-0153 | Wairau Valley - SUB341775 | CB5399 Wairau Valley | 2024-07-26 12:09 | 2024-07-26 13:37 | 0.0065504 | 7.36e-05 | 2 | 178 | Planned | Planned interruption | 4334 SH63 - Planned Work - resag LV spans and install falcon protection http://nams.mll.co.nz/Schedule/Edit/3859 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 543 | 2024-07-26-0154 | Parker St - 0001146253ML4DE | CB1516-Parker St | 2024-07-26 13:27 | 2024-07-26 14:12 | 0 | 0 | 1 | 45 | Unplanned | Other cause | Blown fuse due to overloading, EAM 1494473 - Part power | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 544 | 2024-07-27-0157 | Renwick Township - 0000052595ML108 | CB5482 Renwick Township | 2024-07-27 09:20 | 2024-07-27 12:31 | 0 | 0 | 1 | 190 | Planned | Planned interruption | LV service OHYG http://nams.mll.co.nz/Schedule/Edit/3878 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 545 | 2024-07-27-0155 | Seymour St - SUB3700LR | CB51-Seymour St | 2024-07-27 10:39 | 2024-07-27 12:13 | 0.19349 | 0.0022816 | 62 | 5258 | Unplanned | Defective equipment | Broken LV jumper at POLE DF5274 TX Isolated to remove load and WI16 1494495 http://nams.mll.co.nz/Schedule/Edit/3920 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 546 | 2024-07-29-0158 | Old Renwick Rd - SUB362019 | CB66-Old Renwick Rd | 2024-07-29 08:00 | 2024-07-29 10:36 | 0.011482 | 7.36e-05 | 2 | 312 | Planned | Planned interruption | Isolation of SUB362019 to allow 3rd party to install a pump under lines EAM1492830 NAMS4277 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 547 | 2024-07-29-0162 | Wairau Valley - FUSE3952 | CB5399 Wairau Valley | 2024-07-29 08:37 | 2024-07-29 14:18 | 0.087841 | 0.0002576 | 7 | 2387 | Planned | Planned interruption | Replacement of x-arms at HA1559, ET1514, HA1560,HA1563 & HA1562 EAM1480135 NAMS4148 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 548 | 2024-07-29-0160 | Woodbourne - FUSE2640 | CB1178-Woodbourne | 2024-07-29 09:04 | 2024-07-29 10:14 | 0.005152 | 7.36e-05 | 2 | 140 | Unplanned | Wildlife | Found 2 x blown fuses at 11kV FUSE2460 - Dead magpie below Fuse. Installed dummy load to re liven SUB367019 Power confirmed restored EAM1494538 NAMSF3921 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 549 | 2024-07-29-0161 | Tuamarina - SUB356311 | CB188-Tuamarina | 2024-07-29 10:33 | 2024-07-29 13:48 | 0.014352 | 7.36e-05 | 2 | 390 | Unplanned | Unknown | Blown 11kV Fuse Cause unknown EAM 1494574 http://nams.mll.co.nz/Schedule/Edit/3927 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 550 | 2024-07-29-0163 | Symons St - 0001101223MLE76 | CB50-Symons St | 2024-07-29 12:45 | 2024-07-29 14:55 | 0 | 0 | 1 | 130 | Unplanned | Defective equipment | Blown fuse on customer board Fuse replaced Cause unknown fuse Letter to be sent EAM 1494627 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 551 | 2024-07-30-0164 | East Coast - SUB352760 | REC29-East Coast | 2024-07-30 09:37 | 2024-07-30 14:08 | 0.019872 | 7.36e-05 | 2 | 540 | Planned | Planned interruption | Silver Springs Road - Red tagged pole at 152 Silver Springs Rd Planned Work http://nams.mll.co.nz/Schedule/Edit/3873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 552 | 2024-07-30-0165 | Hospital Rd West - 0001102199MLFB6 | CB47-Hospital Rd West | 2024-07-30 13:34 | 2024-07-30 14:33 | 0 | 0 | 1 | 59 | Unplanned | Unknown | Blown 30amp fuse, 1.5amps - pdl fuse. No cause idemtified EAM 1495422 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 553 | 2024-07-30-0166 | Seymour St - 0001163165MLF47 | CB51-Seymour St | 2024-07-30 15:02 | 2024-07-30 16:08 | 0 | 0 | 1 | 65 | Unplanned | Unknown | Blown 32A fuse. Blew again upon relivening, main switch turned off, insulation test carried out, results low but suspect due to rain. Livened again without issue. Letter left EAM 1495500 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 554 | 2024-07-30-0167 | Spring Creek - 0003340369ML8D9 | CB187-Spring Creek | 2024-07-30 16:00 | 2024-07-30 16:49 | 0 | 0 | 1 | 48 | Unplanned | Unknown | blown pole fuse netural screen installed over a month ago Never had a problem prior - turned on stove and pop EAM 1495522 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 555 | 2024-07-30-0168 | Grassmere - REC1488 | CB1253-Grassmere | 2024-07-30 18:12 | 2024-07-30 18:12 | 0 | 0 | 10 | 0 | Unplanned | Adverse weather | 11kV REC1488 Auto Reclosed on POC. Cyclo190. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 556 | 2024-07-30-0169 | Hawkesbury Road - 0002271064ML6D8 | CB5457 Hawkesbury Road | 2024-07-30 18:23 | 2024-07-30 19:16 | 0 | 0 | 1 | 53 | Unplanned | Defective equipment | Blown 30A HRC due to overload, has been in contact with ML regarding upgrade 1495525 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 557 | 2024-07-30-0170 | Wairau Valley - 0000051368MLAA2 | CB5399 Wairau Valley | 2024-07-30 21:08 | 2024-07-30 21:52 | 0 | 0 | 1 | 44 | Unplanned | Defective equipment | Customer phoned back to cancel job 1495526 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 558 | 2024-07-31-0171 | Waikawa - SUB330023 | CB109- Waikawa | 2024-07-31 01:53 | 2024-07-31 11:40 | 0.47678 | 0.0041216 | 59 | 12956 | Unplanned | Adverse weather | Report of lines down found LV spans down from Pole KB7012 to PT4828 & PT4829. De-energised at Sub330023 and cut away using WI16 to make safe. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 559 | 2024-07-31-0172 | Hawkesbury Road - SUB343163 | CB5457 Hawkesbury Road | 2024-07-31 08:30 | 2024-07-31 09:20 | 0.0036064 | 7.36e-05 | 2 | 98 | Planned | Planned interruption | Planned shutdown to connect upgraded earths. EAM 1409921 SAF 4268 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 560 | 2024-07-31-0173 | Godfrey Road - SUB343279 | CB5367 Godfrey Road | 2024-07-31 10:03 | 2024-07-31 10:36 | 0.0011776 | 3.68e-05 | 1 | 32 | Planned | Planned interruption | Planned shutdown to upgrade transformer earths. EAM 1409921 SAF 4268 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 561 | 2024-07-31-0174 | Seymour St - 0001163165MLF47 | CB51-Seymour St | 2024-07-31 11:25 | 2024-07-31 12:48 | 0 | 0 | 1 | 83 | Unplanned | Defective equipment | Internal fault Left fuse letter with customer EAM 1495704 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 562 | 2024-07-31-0175 | Godfrey Road - SUB343271 | CB5367 Godfrey Road | 2024-07-31 12:30 | 2024-07-31 13:08 | 0.0013616 | 3.68e-05 | 1 | 37 | Planned | Planned interruption | Planned shutdown to connect upgraded earth. EAM 1409921 SAF 4268 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 563 | 2024-07-31-0176 | Vintage Lane - SUB342086 | CB171-Vintage Lane | 2024-07-31 14:16 | 2024-07-31 14:40 | 0.0017664 | 7.36e-05 | 2 | 48 | Planned | Planned interruption | Pak Lims Road Planned Work - Earth testing at SUB342086 http://nams.mll.co.nz/Schedule/Edit/3912 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 564 | 2024-07-31-0177 | Havelock Canvastown - REC1403 | CB103 Havelock Canvastown | 2024-07-31 15:10 | 2024-07-31 17:42 | 0.16221 | 0.0010672 | 29 | 4408 | Unplanned | Vegetation | Reports of trees on the 11kV Line Wakamarina AE 1427 REC1403 Opened for safety Access permit issued for tree removal. http://nams.mll.co.nz/Schedule/Edit/3933 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 565 | 2024-07-31-0178 | Grassmere - FUSE2451 | CB1253-Grassmere | 2024-07-31 15:47 | 2024-08-05 13:19 | 0.52329 | 0.000184 | 3 | 14220 | Unplanned | Defective equipment | 11kV Fuse 2451 Blown. Removed & Tagged with issuer earths applied to North East side of Fuse. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 566 | 2024-07-31-0179 | Renwick Township - 0000052428ML5E5 | CB5482 Renwick Township | 2024-07-31 18:17 | 2024-07-31 19:17 | 0 | 0 | 1 | 60 | Unplanned | Other cause | Replaced Service fuse (60A) Suspect overload Fuse letter to be sent EAM 1495777 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 567 | 2024-08-01-0001 | Spring Creek - LVOH4748 | CB187-Spring Creek | 2024-08-01 08:30 | 2024-08-01 14:59 | 0 | 0 | 4 | 1552 | Planned | Planned interruption | Planned work to replace pole and raise spans. EAM 1491756 SAF4272 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 568 | 2024-08-01-0002 | Spring Creek - 0003340547ML011 | CB187-Spring Creek | 2024-08-01 08:30 | 2024-08-01 14:58 | 0 | 0 | 1 | 388 | Planned | Planned interruption | Planned work to replace pole and raise spans. EAM 1491756 SAF4272 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 569 | 2024-08-01-0003 | Grovetown - SUB355384 | CB1465-Grovetown | 2024-08-01 08:36 | 2024-08-01 11:26 | 0.025024 | 0.0001472 | 4 | 680 | Planned | Planned interruption | Planned work to replace damaged SFB EAM 1464231 SAF 4046 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 570 | 2024-08-01-0004 | Linkwater West - SUB321030 | REC1168-Linkwater West | 2024-08-01 09:10 | 2024-08-01 14:33 | 0.011886 | 3.68e-05 | 1 | 323 | Planned | Planned interruption | Planned shutdown to upgrade Transformer. EAM 1484330 SAF 4174 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 571 | 2024-08-01-0005 | Seymour St - 0001163137ML7CA | CB51-Seymour St | 2024-08-01 10:46 | 2024-08-01 11:55 | 0 | 0 | 1 | 69 | Unplanned | Other cause | Replaced Service fuse Suspect overload Fuse letter left on another fault EAM 1495913 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 572 | 2024-08-01-0006 | Koromiko - SUB331009 | CB55-Koromiko | 2024-08-01 14:15 | 2024-08-01 15:21 | 0.021859 | 0.0003312 | 9 | 594 | Unplanned | Vegetation | Trees on LV Lines fed from SUB 331009 TX Isolated and permit issued for tree removal 1/08/2024 2:31:07 pm http://nams.mll.co.nz/Schedule/Edit/3939 1495984 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 573 | 2024-08-01-0007 | Grassmere - 0005506290MLF30 | CB1253-Grassmere | 2024-08-01 15:31 | 2024-08-01 17:06 | 0 | 0 | 1 | 94 | Unplanned | Defective equipment | Blown rewireable service fuse due to deterioration EAM 1496054 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 574 | 2024-08-02-0008 | Havelock Canvastown - RMUS1344-B | CB103 Havelock Canvastown | 2024-08-02 08:38 | 2024-08-02 11:18 | 0.15898 | 0.0009936 | 27 | 4320 | Planned | Planned interruption | Planned shutdown to replace SWER insulator and reconfigure jumpers. EAM 1479845 SAF4238 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 575 | 2024-08-02-0009 | Waihopai Valley - 0002272567MLDFD | CB5493 Waihopai Valley | 2024-08-02 09:43 | 2024-08-02 10:42 | 0 | 0 | 1 | 59 | Unplanned | Other cause | Blown fuse suspect overloading EAM 1496151 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 576 | 2024-08-02-0010 | Godfrey Road - SUB343326 | CB5367 Godfrey Road | 2024-08-02 10:08 | 2024-08-02 11:30 | 0 | 0 | 2 | 166 | Unplanned | Other cause | Blown 60amp fuse on transformer (distrubtion fuse) 2ph 60amp feeding 2 x 2ph 60amp properties overload EAM 1496162 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 577 | 2024-08-03-0011 | Old Renwick Rd - 0001132377MLDBC | CB66-Old Renwick Rd | 2024-08-03 18:50 | 2024-08-03 19:58 | 0 | 0 | 1 | 69 | Unplanned | Defective equipment | Blown 30A HRC service fuse, suspect overload. Letter to be sent 1496306 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 578 | 2024-08-04-0012 | Vernon - REC1576 | CB5184-Vernon | 2024-08-04 04:48 | 2024-08-04 05:08 | 0.027968 | 0.0013984 | 38 | 760 | Unplanned | Wildlife | EAM 1496307 Earth Fault trip at 11kV REC1576 Co-op drain 04:48 Red 3A Yellow 61A Blue 3A Earth 57A Cyclo 115 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 579 | 2024-08-05-0017 | Weld St - 0001162305MLB10 | CB71-Weld St | 2024-08-04 09:19 | 2024-08-05 07:37 | 0 | 0 | 1 | 1338 | Unplanned | Unknown | Blown 100A service fuse, no cause found EAM 1496308 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 580 | 2024-08-04-0013 | East Coast - 0005516198ML6C6 | REC29-East Coast | 2024-08-04 10:29 | 2024-08-04 14:06 | 0 | 0 | 1 | 217 | Unplanned | Unknown | Flickering power, patrolled area and checked connections. No cause found, investigations continuing - 1496309 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 581 | 2024-08-04-0014 | Flaxbourne - RMUF5301 | REC1432-Flaxbourne | 2024-08-04 13:03 | 2024-08-04 15:45 | 0.023699 | 0.0001472 | 4 | 644 | Unplanned | Wildlife | Found centre phase fuse blown at 11kV RMUF 5301. Nothing found on line patrol. Replacing all 3 with 16A http://nams.mll.co.nz/Schedule/Edit/3944 EAM 1496311 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 582 | 2024-08-04-0015 | Waikawa - 0006603149MLF7F | CB109- Waikawa | 2024-08-04 13:55 | 2024-08-04 14:40 | 0 | 0 | 1 | 45 | Unplanned | Defective equipment | 1496313 Blown rewireable service fuse due to deterioration - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 583 | 2024-08-04-0016 | Hawkesbury Road - 0002271149MLDD2 | CB5457 Hawkesbury Road | 2024-08-04 17:28 | 2024-08-04 18:45 | 0 | 0 | 1 | 78 | Unplanned | Defective equipment | 1496314 Blown 30A HRC, suspect overload - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 584 | 2024-08-05-0018 | Richmond Brook - SUB353085 | CB1250-Richmond Brook | 2024-08-05 08:35 | 2024-08-05 14:17 | 0.60411 | 0.0017664 | 48 | 16416 | Planned | Planned interruption | Various LV maintenance at POLES ET3611, KJ1324, NK1012, ET3630 and NK1010 SAF4169 WO 1480637 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 585 | 2024-08-05-0019 | Wairau Valley - 0002279061ML697 | CB5399 Wairau Valley | 2024-08-05 18:32 | 2024-08-05 21:02 | 0 | 0 | 1 | 151 | Unplanned | Defective equipment | 1496512 Blown service fuse due to water cylinder leak. Circuit isolated and tagged, owner to organise electrician to attend | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 586 | 2024-08-05-0020 | Parker St - 0001140525MLACE | CB1516-Parker St | 2024-08-05 19:34 | 2024-08-05 20:41 | 0 | 0 | 1 | 67 | Unplanned | Defective equipment | 1496513 Blown HRC service fuse due to overload. Letter to be sent - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 587 | 2024-08-06-0021 | Grassmere - 0005506290MLF30 | CB1253-Grassmere | 2024-08-06 08:02 | 2024-08-06 10:09 | 0 | 0 | 1 | 127 | Unplanned | Other cause | EAM 1496527 - Part power, SB checked Power restored replaced blown 30a pole fuse red phase | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 588 | 2024-08-06-0022 | Fifteen Valley - SUB348001 | CB5041-Fifteen Valley | 2024-08-06 08:30 | 2024-08-06 09:37 | 0.0024656 | 3.68e-05 | 1 | 67 | Planned | Planned interruption | Planned shutdown to connect upgraded earth grid to Sub348001 SAF 4269 EAM 1295693 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 589 | 2024-08-06-0023 | Seafair - RMUF1264 | CB5098-Seafair | 2024-08-06 08:30 | 2024-08-06 15:10 | 0.0736 | 0.000184 | 5 | 2000 | Planned | Planned interruption | Moving of SUB348003 to new Safelink switch EAM1413528 NAMS4174.4 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 590 | 2024-08-06-0024 | Grovetown - SUB370239 | CB1465-Grovetown | 2024-08-06 10:30 | 2024-08-06 11:21 | 0.0056304 | 0.0001104 | 3 | 153 | Planned | Planned interruption | Planned shutdown to connect upgraded earth grid to Sub 370239. SAF 4269 EAM 1295693 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 591 | 2024-08-06-0025 | Spring Creek - SUB356172 | CB187-Spring Creek | 2024-08-06 13:30 | 2024-08-06 14:27 | 0.0020608 | 3.68e-05 | 1 | 56 | Planned | Planned interruption | Planned shutdown to connect upgraded earths at Sub356172. SAF 4269 EAM 1295693 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 592 | 2024-08-06-0026 | Waikawa - 0006602286ML5ED | CB109- Waikawa | 2024-08-06 15:20 | 2024-08-06 15:40 | 0 | 0 | 1 | 21 | Unplanned | Other cause | EAM 1496703 - Part power, possibly internal issue.Tripped circuit breaker due to overloading FUSE LETT | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 593 | 2024-08-06-0027 | Seymour St - 0001163137ML7CA | CB51-Seymour St | 2024-08-06 16:54 | 2024-08-06 18:46 | 0 | 0 | 1 | 111 | Unplanned | Defective equipment | Internal fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 594 | 2024-08-07-0028 | Pelorus - 0007713040ML21E | CB5126-Pelorus | 2024-08-07 06:11 | 2024-08-07 07:23 | 0 | 0 | 1 | 71 | Unplanned | Defective equipment | Internal Fault - W/O 1496758 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 595 | 2024-08-07-0029 | Tuamarina - 0003313416MLCCC | CB188-Tuamarina | 2024-08-07 08:17 | 2024-08-07 13:01 | 0 | 0 | 1 | 284 | Unplanned | Defective equipment | replaced faulty trurip from Pole BS3518 to JA1637. MLL owned -- | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 596 | 2024-08-07-0030 | Howick Rd North - SUB3700QA | CB84-Howick Rd North | 2024-08-07 08:30 | 2024-08-07 12:03 | 0.17244 | 0.0008096 | 22 | 4686 | Planned | Planned interruption | Planned shutdown to replace 11kV cross arms and fuses at Sub3700QA. SAF 4150 EAM 1440653 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 597 | 2024-08-07-0031 | Nelson St - 0001115564ML07A | CB93-Nelson St | 2024-08-07 11:27 | 2024-08-07 12:21 | 0 | 0 | 1 | 53 | Unplanned | Defective equipment | 60amp pole fuse blown due to deterioration EAM 1496937 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 598 | 2024-08-07-0032 | Riverlands - 0003350181ML291 | CB1181-Riverlands | 2024-08-07 17:43 | 2024-08-07 19:04 | 0 | 0 | 1 | 80 | Unplanned | Defective equipment | Failed 30 Amp Hrc ,only drawing 5.2 amps, not letter was issued so one needs posting, EAM 1497051 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 599 | 2024-08-07-0033 | Sounds - ABS1729-B | REC1170-Sounds | 2024-08-07 20:53 | 2024-08-07 22:02 | 0.32248 | 0.0046736 | 127 | 8763 | Unplanned | Third party interference | Unplanned outage to remove netting wrapped abound 11kV at pole JA2720 EAM1497049 NAMS F3959 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 600 | 2024-08-08-0035 | Nelson St - 0001115564ML07A | CB93-Nelson St | 2024-08-08 10:05 | 2024-08-08 11:01 | 0 | 0 | 1 | 55 | Unplanned | Other cause | Blown service fuse, suspected internal fault that electrician was checking EAM 1497144 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 601 | 2024-08-08-0036 | Jacksons Road - 0003330595ML76F | CB1179-Jacksons Road | 2024-08-08 15:02 | 2024-08-08 20:33 | 0.0061456 | 7.36e-05 | 1 | 167 | Unplanned | Unknown | EAM 1497384 NAMSF3971 1 x fuse blown, no cause found Fuses replaced power confirmed restored | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 602 | 2024-08-08-0037 | Godfrey Road - 0002270426ML959 | CB5367 Godfrey Road | 2024-08-08 18:39 | 2024-08-08 21:19 | 0 | 0 | 1 | 160 | Unplanned | Defective equipment | Damaged LV cable repaired at SFB41 Morven Lane W/O 1497433 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 603 | 2024-08-09-0038 | Godfrey Road - LVUG1592-S3855 | CB5367 Godfrey Road | 2024-08-08 20:50 | 2024-08-08 20:52 | 0 | 0 | 6 | 12 | Unplanned | Unknown | EAM1497433 Replaced Blown fuse at LV Pos 4A at SUB343339 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 604 | 2024-08-09-0039 | Wairau Valley - SUB341907 | CB5399 Wairau Valley | 2024-08-09 09:00 | 2024-08-09 13:08 | 0.027379 | 0.0001104 | 3 | 744 | Planned | Planned interruption | Replacement of x-arms at pole AX1812 EAM1468934 NAMS4071 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 605 | 2024-08-09-0040 | Grovetown - 0003341413ML1B7 | CB1465-Grovetown | 2024-08-09 11:06 | 2024-08-09 11:35 | 0 | 0 | 1 | 29 | Planned | Planned interruption | Pull up low span between DF5999 - NK0730EAM1491419 NAMS4274 --- | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 606 | 2024-08-09-0041 | Colemans Rd - 0001131872ML11D | CB1512-Colemans Rd | 2024-08-09 11:32 | 2024-08-09 12:30 | 0 | 0 | 1 | 59 | Unplanned | Other cause | Replaced burnt out fuse carrier in SFB --EAM 1497571 - No power, 1PH 63A | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 607 | 2024-08-09-0042 | East Coast - FUSE2435 | REC29-East Coast | 2024-08-09 13:27 | 2024-08-09 14:42 | 0.002208 | 0.000368 | 7 | 60 | Unplanned | Unknown | EAM1497822 NAMSF3984 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 608 | 2024-08-09-0043 | Pelorus - 0007713025ML0A1 | CB5126-Pelorus | 2024-08-09 15:24 | 2024-08-09 17:52 | 0 | 0 | 1 | 148 | Unplanned | Third party interference | LV OH service hit . Service repaired and relivened | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 609 | 2024-08-09-0044 | Howick Rd North - 0001175041ML73D | CB84-Howick Rd North | 2024-08-09 22:19 | 2024-08-09 23:47 | 0 | 0 | 1 | 87 | Unplanned | Defective equipment | replaced Fuse carrier EAM 1497813 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 610 | 2024-08-09-0045 | Grovetown - LVUG1500 | CB1465-Grovetown | 2024-08-09 23:29 | 2024-08-10 01:05 | 0 | 0 | 2 | 194 | Unplanned | Defective equipment | At XA9049 Fuse carrier burnt out, replaced but had to isolate the SFB to do so Found burnt fuse base and connection at XB9049 Isolated power and repaired | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 611 | 2024-08-10-0046 | Grovetown - 0003342285MLB39 | CB1465-Grovetown | 2024-08-10 01:05 | 2024-08-10 09:47 | 0 | 0 | 1 | 522 | Unplanned | Defective equipment | Found burnt fuse base and connection at XB9049 - Isolated power and repaired W/O1497814 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 612 | 2024-08-10-0047 | Dry Hills - 0001116437MLF56 | CB1682-Dry Hills | 2024-08-10 09:21 | 2024-08-10 11:15 | 0 | 0 | 1 | 114 | Unplanned | Defective equipment | Failed fuse carrier in SFB XA0211, used W/I to replace EAM 1497815 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 613 | 2024-08-10-0048 | Nelson St - 0001147513ML8D9 | CB93-Nelson St | 2024-08-10 11:04 | 2024-08-10 11:45 | 0 | 0 | 1 | 41 | Unplanned | Defective equipment | Internal fault power to switch board,RCD tripped EAM 1497816 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 614 | 2024-08-10-0049 | French Pass - LV Box-SUB336113-P2 | CB45-French Pass | 2024-08-10 11:26 | 2024-08-10 15:55 | 0 | 0 | 14 | 3150 | Unplanned | Defective equipment | abnormal voltage readings at SFB190 (XA2980) Duncan Bay Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 615 | 2024-08-11-0051 | Hawkesbury Road - REC5436 | CB5457 Hawkesbury Road | 2024-08-11 06:18 | 2024-08-11 06:18 | 0 | 0 | 176 | 0 | Unplanned | Unknown | Successful reclose | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 616 | 2024-08-11-0050 | Colemans Rd - 0001130533MLB55 | CB1512-Colemans Rd | 2024-08-11 08:48 | 2024-08-11 09:50 | 0 | 0 | 1 | 61 | Unplanned | Defective equipment | Sub main had tripped EAM 1497821 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 617 | 2024-08-11-0053 | East Coast - FUSE4180 | REC29-East Coast | 2024-08-11 10:17 | 2024-08-11 13:43 | 0.022742 | 0.0001104 | 3 | 618 | Unplanned | Unknown | EAM1497822 NAMSF3984 Power off suspect fuse out at FUSE4180. Fuse found blown at FUSE4180, M | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 618 | 2024-08-11-0054 | Murphys Rd - 0001122345ML220 | CB68-Murphys Rd | 2024-08-11 15:24 | 2024-08-11 16:31 | 0 | 0 | 1 | 68 | Unplanned | Defective equipment | owners bought a surge Deverter causing blowing fuses out in SFB XA0263 EAM 1497823 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 619 | 2024-08-11-0055 | Parker St - 0001138070MLD35 | CB1516-Parker St | 2024-08-11 18:45 | 2024-08-11 19:38 | 0 | 0 | 1 | 52 | Unplanned | Defective equipment | Failed HRC , please post a letter, 2017 EAM 1497824 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 620 | 2024-08-12-0056 | McLauchlan St - FUSE2065 | CB65 - McLauchlan St | 2024-08-12 08:30 | 2024-08-12 14:44 | 0.096342 | 0.0002576 | 7 | 2618 | Planned | Planned interruption | Upgrade of 11kV line beyond FUSE2065 EAM1435924 NAMS4033 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 621 | 2024-08-12-0059 | Godfrey Road - ABS1984 | CB5367 Godfrey Road | 2024-08-12 08:44 | 2024-08-12 10:15 | 0.029808 | 0.0003312 | 9 | 810 | Planned | Planned interruption | Woodburne Planned Work http://nams.mll.co.nz/Schedule/Edit/3881 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 622 | 2024-08-12-0060 | Truckstop - 0003350268ML579 | CB5079-Truckstop | 2024-08-12 09:34 | 2024-08-12 11:14 | 0 | 0 | 1 | 100 | Unplanned | Other cause | Pole fuse blown, suspect overloading Letter left on site, but also emailed EAM 1497879 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 623 | 2024-08-12-0061 | Koromiko - 0006632381ML00F | CB55-Koromiko | 2024-08-12 14:17 | 2024-08-12 15:31 | 0 | 0 | 1 | 74 | Unplanned | Defective equipment | Power restored. Replaced blown 30A pole fuse. suspect internal fault. Left letter. EAM 1498025 -- | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 624 | 2024-08-12-0067 | East Coast, REC31 - Ward, REC1432 - Flaxbourne - CB5412 | REC29 - East Coast, REC31 - Ward, REC1432 - Flaxbourne | 2024-08-12 15:00 | 2024-08-12 19:37 | 0.31162 | 0.033046 | 314 | 8468 | Unplanned | Adverse weather | EAM1498043 NAMSF3987 Tripping of CB5412 Causing loss of supply to Ward Sub | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 625 | 2024-08-12-0069 | Buller St - CB108 | CB108 - Buller St | 2024-08-12 15:29 | 2024-08-12 15:30 | 0 | 0 | 265 | 0 | Unplanned | Adverse weather | Successful reclose CB108 Phase OC Suspect weather | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 626 | 2024-08-12-0070 | Waikawa - REC17 | CB109- Waikawa | 2024-08-12 15:53 | 2024-08-12 15:53 | 0.0033856 | 0.0033856 | 92 | 92 | Unplanned | Adverse weather | Successful reclose REC17 Phase OC Suspect high winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 627 | 2024-08-13-0077 | Grassmere - CB1253 | CB1253-Grassmere | 2024-08-12 17:37 | 2024-08-12 19:03 | 0.3592 | 0.004968 | 135 | 9761 | Unplanned | Adverse weather | Tripping of CB5412 Causing loss of supply to Ward Sub Further outage required to make repairs to 33kV Pole MA1154 taking off all customers in Ward Sub and CB1253 and CB1250 EAM1498043 NAMSF3987 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 628 | 2024-08-13-0078 | Richmond Brook - CB1250 | CB1250-Richmond Brook | 2024-08-12 17:37 | 2024-08-12 18:46 | 1.2924 | 0.018731 | 509 | 35121 | Unplanned | Adverse weather | Tripping of CB5412 Causing loss of supply to Ward Sub Further outage required to make repairs to 33kV Pole MA1154 taking off all customers in Ward Sub and CB1253 and CB1250 EAM1498043 NAMSF3987 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 629 | 2024-08-12-0073 | Tuamarina - 0003312169ML2EA | CB188-Tuamarina | 2024-08-12 19:08 | 2024-08-12 21:00 | 0 | 0 | 1 | 111 | Unplanned | Defective equipment | Failed fuse carrier, replaced using W/I EAM 1498062 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 630 | 2024-08-13-0079 | McLauchlan St - FUSE2065 | CB65 - McLauchlan St | 2024-08-13 08:30 | 2024-08-13 15:50 | 0.11309 | 0.0002576 | 7 | 3073 | Planned | Planned interruption | Upgrade of 11kV line beyond FUSE2065 EAM1435924 NAMS4034 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 631 | 2024-08-13-0080 | Kaituna - 0007705238ML271 | CB5448 Kaituna | 2024-08-13 08:49 | 2024-08-13 11:18 | 0 | 0 | 1 | 149 | Unplanned | Unknown | EAM 1498086 F3990 blown HV fuse at 11kV RMUF1234 (80A). Inspected 11kV cable terminations at Sub340410 and RMUF1234. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 632 | 2024-08-13-0081 | Waikawa - 0006602334MLEDE | CB109- Waikawa | 2024-08-13 11:30 | 2024-08-13 13:30 | 0 | 0 | 1 | 119 | Unplanned | Defective equipment | . Burnt fuse carrier EAM 1498127 13/08/2024 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 633 | 2024-08-14-0082 | Grassmere - FUSE3291 | CB1253-Grassmere | 2024-08-14 06:49 | 2024-08-14 08:57 | 0.03323 | 0.0002944 | 8 | 903 | Unplanned | Unknown | 2x blown fuses found at 11kV FUSE3291. Patrolled, no cause found. Replaced fuses (20A) EAM 1498197 http://nams.mll.co.nz/Schedule/Edit/3994 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 634 | 2024-08-14-0084 | Thomsons Ford Rd - SUB357150 | CB1509-Thomsons Ford Rd | 2024-08-14 09:56 | 2024-08-14 15:48 | 0.025907 | 7.36e-05 | 2 | 704 | Planned | Planned interruption | Upgrade SUB357150 from 3ph 50kVA to 3ph 150kVA SAF 4161 - WO 1480764 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 635 | 2024-08-14-0083 | Hospital Rd West - SUB3700CG | CB47-Hospital Rd West | 2024-08-14 10:02 | 2024-08-14 15:48 | 0.24262 | 0.0006992 | 19 | 6593 | Planned | Planned interruption | Replacement of leaking TX at SUB3700CG EAM1496420 NAMS4325 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 636 | 2024-08-15-0086 | Vintage Lane - CB171 | CB171-Vintage Lane | 2024-08-15 08:30 | 2024-08-15 18:03 | 0.18945 | 0.0003312 | 9 | 5148 | Planned | Planned interruption | Planned shutdown to remove pole 12.4 abandon old 33kV cable, test & connect new 33kV cable. Woodbourne upgrade project. EAM 1397584 SAF 4208 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 637 | 2024-08-15-0085 | Havelock Canvastown - FUSE2402 | CB103 Havelock Canvastown | 2024-08-15 09:29 | 2024-08-15 11:37 | 0.028042 | 0.0002208 | 6 | 762 | Planned | Planned interruption | Planned shutdown to replace pole. EAM 1495557 SAF 4312 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 638 | 2024-08-15-0087 | Spring Creek - SUB356191 | CB187-Spring Creek | 2024-08-15 12:21 | 2024-08-15 16:02 | 0.040664 | 0.000184 | 5 | 1105 | Planned | Planned interruption | Chaytors Road Planned Work http://nams.mll.co.nz/Schedule/Edit/3985 found broken bushing at SUB356191 and replaced transformer during shutdown. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 639 | 2024-08-15-0088 | Hutcheson St - 0001155325ML309 | CB49-Hutcheson St | 2024-08-15 16:46 | 2024-08-15 17:50 | 0 | 0 | 1 | 115 | Unplanned | Unknown | Replaced 2 x blown pole fuses. EAM 1498659 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 640 | 2024-08-15-0089 | Symons St - SUB3700HD-LV-POS8 | CB50-Symons St | 2024-08-15 21:19 | 2024-08-16 01:09 | 0 | 0 | 5 | 1150 | Planned | Planned interruption | Outage started early due to weather and businesses being closed earlier than expected. SAF 4288.1 EAM 1372354 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 641 | 2024-08-15-0090 | Symons St - SUB3700HD-LV-POS2 | CB50-Symons St | 2024-08-15 22:26 | 2024-08-16 01:27 | 0 | 0 | 4 | 724 | Planned | Planned interruption | Shutdown of customers in Wynen St to disconnect LV cable from LV pos 2SUB3700HD and LV Pos 4 DP19 Wynen St SAF 4288.1 EAM 1372354 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 642 | 2024-08-16-0091 | Havelock Canvastown - 0007702221ML2ED | CB103 Havelock Canvastown | 2024-08-16 07:37 | 2024-08-16 09:22 | 0 | 0 | 1 | 104 | Unplanned | Unknown | Pole fuse blown No reason given EAM 1498663 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 643 | 2024-08-16-0093 | Godfrey Road - ABS680-B | CB5367 Godfrey Road | 2024-08-16 08:30 | 2024-08-16 14:09 | 0.3493 | 0.0010304 | 28 | 9492 | Planned | Planned interruption | Planned shutdown to replace pole AK2152 and re-install fusesaver REC5265. EAM 1486971 SAF 4219 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 644 | 2024-08-16-0094 | Redwood St Nth - 0001108261ML0F6 | CB1655-Redwood St Nth | 2024-08-16 16:05 | 2024-08-16 17:01 | 0 | 0 | 1 | 55 | Unplanned | Defective equipment | Re-terminated load wire on pole fuse that had fallen out. EAM 1498814 ---- | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 645 | 2024-08-17-0095 | Tuamarina - 0003340233MLB44 | CB188-Tuamarina | 2024-08-17 17:35 | 2024-08-17 19:42 | 0 | 0 | 1 | 128 | Unplanned | Defective equipment | Replaced blown 60A pole fuse. Suspected cause faulty oven.? A | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 646 | 2024-08-18-0097 | Redwood St Sth - LVUG247 | CB1673-Redwood St Sth | 2024-08-18 18:22 | 2024-08-18 19:44 | 0 | 0 | 5 | 217 | Unplanned | Unknown | 2x distribution fuses found blown at pole DF3132. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 647 | 2024-08-19-0098 | Koromiko - 0006632141MLDE7 | CB55-Koromiko | 2024-08-19 07:45 | 2024-08-19 11:50 | 0 | 0 | 1 | 246 | Unplanned | Defective equipment | Burnt out crutch on service cable at TX pole EAM 1498829 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 648 | 2024-08-19-0099 | McLauchlan St - FUSE21943 | CB65 - McLauchlan St | 2024-08-19 08:30 | 2024-08-19 13:08 | 0 | 0 | 4 | 1112 | Planned | Planned interruption | Replacement of damaged SFB XA1875 EAM1445252 NAMS4080 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 649 | 2024-08-19-0100 | Murphys Rd - 0001131677MLA59 | CB68-Murphys Rd | 2024-08-19 09:52 | 2024-08-19 10:31 | 0 | 0 | 1 | 38 | Unplanned | Human error | Stripped fuse touching - workman ship prior Can confirm 2ph 30amp EAM 1498855 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 650 | 2024-08-19-0101 | Redwood St Nth - 0004421010MLF05 | CB1655-Redwood St Nth | 2024-08-19 16:38 | 2024-08-19 17:27 | 0 | 0 | 1 | 50 | Unplanned | Other cause | Staff attended and replaced blown 60A fuse. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 651 | 2024-08-20-0102 | Scotland St - RMUF5519 | CB54-Scotland St | 2024-08-20 08:00 | 2024-08-20 16:52 | 0.13675 | 0.0002576 | 7 | 3716 | Planned | Planned interruption | Upgrade of SUB332016 from 200VA to 500kVA. SAF 4252 EAM 1420778 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 652 | 2024-08-20-0104 | Hardings Rd - 0003350011ML472 | CB167-Hardings Rd | 2024-08-20 08:23 | 2024-08-20 14:49 | 0 | 0 | 1 | 385 | Unplanned | Other cause | Blown service fuse replaced EAM 1498974 - No power, has solar, woke up to notification saying he is on emergency battery back up | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 653 | 2024-08-20-0103 | Hawkesbury Road - ABS964-B | CB5457 Hawkesbury Road | 2024-08-20 08:30 | 2024-08-20 09:37 | 0.0097152 | 0.0001472 | 4 | 264 | Planned | Planned interruption | Connection of upgraded earths at ABS964 EAM1405836 NAMS4278 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 654 | 2024-08-20-0105 | Renwick Township - 0000050194ML20C | CB5482 Renwick Township | 2024-08-20 09:50 | 2024-08-20 10:27 | 0 | 0 | 1 | 37 | Unplanned | Defective equipment | Retail disconnect EAM 1499031 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 655 | 2024-08-20-0106 | Hawkesbury Road - ABS957-B | CB5457 Hawkesbury Road | 2024-08-20 11:30 | 2024-08-20 14:34 | 0.033672 | 0.000184 | 5 | 915 | Planned | Planned interruption | Connect new earths at ABS957 EAM1405836 NAMS4278 -- | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 656 | 2024-08-21-0107 | Murphys Rd - 0001177355MLCD9 | CB68-Murphys Rd | 2024-08-21 08:05 | 2024-08-21 09:51 | 0 | 0 | 1 | 106 | Unplanned | Defective equipment | Customer incorrectly had 2 fuses one in the gyro at 60amp and one in the meter box at 32amp Confirmed that the fuse in the meter box was not required and have remobved. EAM 1499275 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 657 | 2024-08-21-0110 | Woodbourne - ABS1731-B | CB1178-Woodbourne | 2024-08-21 08:06 | 2024-08-21 17:58 | 0.19607 | 0.0003312 | 9 | 5328 | Planned | Planned interruption | Planned shutdown to relocate 11kV cable due to new roundabout construction on SH6/Tancred Cres. EAM 1464206. SAF 4019 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 658 | 2024-08-21-0111 | Thomsons Ford Rd - RMUS1623-B | CB1509-Thomsons Ford Rd | 2024-08-21 08:30 | 2024-08-21 09:54 | 0.043277 | 0.0005152 | 14 | 1176 | Planned | Planned interruption | Connect upgraded earths at LA 20305 EAM1278045 NAMS4270 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 659 | 2024-08-21-0112 | Thomsons Ford Rd - SUB357128 | CB1509-Thomsons Ford Rd | 2024-08-21 10:30 | 2024-08-21 11:34 | 0.0023184 | 3.68e-05 | 1 | 63 | Planned | Planned interruption | Connectio of new earths at SUB357128 EAM1278045 NAMS4270 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 660 | 2024-08-21-0114 | Scotland St - 0004450143ML9D0 | CB54-Scotland St | 2024-08-21 10:30 | 2024-08-21 13:52 | 0.0074336 | 3.68e-05 | 1 | 202 | Planned | Planned interruption | Waikawa Road pothead project TX removal Planned Work http://nams.mll.co.nz/Application/Edit/4255 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 661 | 2024-08-21-0113 | Thomsons Ford Rd - SUB357152 | CB1509-Thomsons Ford Rd | 2024-08-21 13:00 | 2024-08-21 13:42 | 0.0015456 | 3.68e-05 | 1 | 42 | Planned | Planned interruption | Connection of new earths at SUB357152 EAM1278045 NAMS4270 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 662 | 2024-08-21-0115 | Thomsons Ford Rd - SUB357156 | CB1509-Thomsons Ford Rd | 2024-08-21 13:55 | 2024-08-21 14:46 | 0.0019136 | 3.68e-05 | 1 | 52 | Planned | Planned interruption | Connection of new earths at SUB357156 EAM1278045 NAMS4270 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 663 | 2024-08-21-0116 | Wairau Valley - 0002278045MLB68 | CB5399 Wairau Valley | 2024-08-21 19:47 | 2024-08-21 21:58 | 0 | 0 | 1 | 131 | Unplanned | Other cause | Blown 30A HRC fuse, caused by possilbe overloading. Will send them a 'blown fuse' letter. Restored 2120. EAM 1499575 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 664 | 2024-08-22-0120 | Dashwood - FUSE2484 | CB1252-Dashwood | 2024-08-22 08:46 | 2024-08-22 13:10 | 0 | 0 | 3 | 792 | Planned | Planned interruption | Planned shutdown for vegetation removal EAM1424440 NAMS4308 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 665 | 2024-08-22-0118 | Richmond Brook - SUB353025 | CB1250-Richmond Brook | 2024-08-22 08:47 | 2024-08-22 14:49 | 0.092993 | 0.0002576 | 7 | 2527 | Planned | Planned interruption | LV & HV maintenance works at AE1492, AE1494 and AE1495 EAM1449076 NAMS4183 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 666 | 2024-08-22-0119 | Richmond Brook - 0005502402ML0D4 | CB1250-Richmond Brook | 2024-08-22 08:51 | 2024-08-22 11:40 | 0 | 0 | 1 | 169 | Planned | Planned interruption | LV maintenance work on pole KB3237 EAM1480553 NAMS4163 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 667 | 2024-08-22-0121 | Wairau Valley - FUSE3632 | CB5399 Wairau Valley | 2024-08-22 09:00 | 2024-08-22 14:31 | 0.10963 | 0.0003312 | 9 | 2979 | Planned | Planned interruption | Planned shutdown to replace iron rail poles. EAM 1481026 SAF 4162 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 668 | 2024-08-22-0122 | Richmond Brook - 0005502415ML7B3 | CB1250-Richmond Brook | 2024-08-22 11:00 | 2024-08-22 11:40 | 0 | 0 | 1 | 40 | Planned | Planned interruption | LV maintenance work on pole KB3237 EAM1480553 NAMS4163 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 669 | 2024-08-22-0123 | Redwood St Nth - 0001108173ML9DD | CB1655-Redwood St Nth | 2024-08-22 19:04 | 2024-08-22 20:40 | 0 | 0 | 1 | 96 | Unplanned | Defective equipment | Loose jumper into RW fuse, retightened and replaced with HRC fuse. EAM 1499992 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 670 | 2024-08-22-0124 | Taylor Pass - 0001195345ML849 | CB1089-Taylor Pass | 2024-08-22 21:25 | 2024-08-22 23:01 | 0 | 0 | 1 | 96 | Unplanned | Defective equipment | Burnt out Lv fuse in SFB, replaced with new HRC fuse. EAM 1499993 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 671 | 2024-08-23-0126 | Sounds - 0008814103ML393 | REC1170-Sounds | 2024-08-23 08:05 | 2024-08-24 09:55 | 0 | 0 | 1 | 1550 | Unplanned | Defective equipment | Burntout mainswitch, isolated and replaced with new switch. EAM 1499998 - Part power, 3PH 30A supply. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 672 | 2024-08-23-0125 | Richmond Brook - LVOH4113 | CB1250-Richmond Brook | 2024-08-23 08:30 | 2024-08-23 11:03 | 0 | 0 | 10 | 1530 | Planned | Planned interruption | Planned shutdown to replace LV crossarm. EAM 1480553 SAF 4165 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 673 | 2024-08-26-0134 | Rai Valley - REC5167 | CB43-Rai Valley | 2024-08-25 00:12 | 2024-08-25 00:13 | 0 | 0 | 104 | 0 | Unplanned | Unknown | Successful reclose of REC 5167 Phase OC | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 674 | 2024-08-25-0128 | Okaramio - FUSE3612 | CB104 Okaramio | 2024-08-25 20:58 | 2024-08-25 22:53 | 0.0083904 | 7.36e-05 | 2 | 228 | Unplanned | Unknown | Blown fuse 3612 - Cause unknown http://nams.mll.co.nz/Schedule/Edit/4045 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 675 | 2024-08-25-0129 | Causeway - SUB320101 | CB1683 Causeway | 2024-08-25 21:02 | 2024-08-26 09:04 | 0.053065 | 7.36e-05 | 2 | 1442 | Unplanned | Adverse weather | Blown TX Fuse. Suspect Lightnng http://nams.mll.co.nz/Schedule/Edit/4046 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 676 | 2024-08-26-0130 | Sounds - FUSE2979 | REC1170-Sounds | 2024-08-26 08:12 | 2024-08-26 12:09 | 0.01737 | 7.36e-05 | 2 | 472 | Unplanned | Adverse weather | Blown TX Fuse and Blown inline fuse 2979 TX Fuse replaced. Inline fuse 2979 replaced No power 1500420 http://nams.mll.co.nz/Schedule/Edit/4047 Suspect lightning. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 677 | 2024-08-26-0131 | Waikawa - FUSE3611 | CB109- Waikawa | 2024-08-26 08:30 | 2024-08-26 15:13 | 0.21491 | 0.0011776 | 32 | 5840 | Planned | Planned interruption | Planned shutdown to upgrade transformer Sub330225. EAM 1429678 SAF 3994 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 678 | 2024-08-26-0132 | Hawkesbury Road - LVOH2946 | CB5457 Hawkesbury Road | 2024-08-26 08:30 | 2024-08-26 12:34 | 0 | 0 | 2 | 488 | Planned | Planned interruption | Planned shutdown to replace service pole. EAM 11481013 SAF 4376 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 679 | 2024-08-26-0133 | Hawkesbury Road - LVOH2951 | CB5457 Hawkesbury Road | 2024-08-26 08:35 | 2024-08-26 13:09 | 0 | 0 | 1 | 273 | Planned | Planned interruption | Planned shutdown to replace service pole. Anglesea St Planned Work http://nams.mll.co.nz/Schedule/Edit/4033 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 680 | 2024-08-27-0136 | Vintage Lane - FUSE2222 | CB171-Vintage Lane | 2024-08-27 08:35 | 2024-08-27 16:42 | 0.14367 | 0.0002944 | 8 | 3904 | Planned | Planned interruption | Woodbourne Sub Planned Work http://nams.mll.co.nz/Schedule/Edit/3894 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 681 | 2024-08-27-0137 | Richmond Brook - SUB353285 | CB1250-Richmond Brook | 2024-08-27 09:00 | 2024-08-27 14:41 | 0.44344 | 0.00368 | 100 | 12050 | Planned | Planned interruption | Upgrade SUB353285 to 100kVA SAF4220 - WO 1487103 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 682 | 2024-08-28-0138 | Richmond Brook - REC37 | CB1250-Richmond Brook | 2024-08-28 03:08 | 2024-08-28 03:08 | 0.0082064 | 0.0082064 | 223 | 223 | Unplanned | Wildlife | Successful auto reclose on REC37 Camerons Rd Earth Fault. Cyclo144. No fault current info. No fault seen on ENS7001 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 683 | 2024-08-28-0139 | Koromiko - LVOH3229 | CB55-Koromiko | 2024-08-28 08:30 | 2024-08-28 13:58 | 0 | 0 | 2 | 654 | Planned | Planned interruption | Planned shutdown to replace poles & conductor. EAM 1457364 SAF 4234 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 684 | 2024-08-28-0143 | Hawkesbury Road - SUB343019 | CB5457 Hawkesbury Road | 2024-08-28 12:14 | 2024-08-28 15:24 | 0.01391 | 7.36e-05 | 2 | 378 | Unplanned | Third party interference | Tractor vs LV lines fed from SUB343019 http://nams.mll.co.nz/Schedule/Edit/4057 1501374 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 685 | 2024-08-28-0141 | Pelorus - FUSE2281 | CB5126-Pelorus | 2024-08-28 12:42 | 2024-08-28 13:25 | 0.0063296 | 0.0001472 | 4 | 172 | Unplanned | Defective equipment | Urgent 11kV shutdown to replace broken preform at pole KB9683 near 161 Bulford Rd. EAM 1501366 FS F4056 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 686 | 2024-08-28-0142 | Koromiko - SUB331139 | CB55-Koromiko | 2024-08-28 13:19 | 2024-08-28 14:12 | 0.0076544 | 0.0001472 | 4 | 208 | Planned | Planned interruption | Planned shutdown to replace LV flyarm. EAM 1454203 SAF 4332 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 687 | 2024-08-28-0144 | Godfrey Road - SUB343331 | CB5367 Godfrey Road | 2024-08-28 14:57 | 2024-08-28 15:13 | 0 | 0 | 2 | 32 | Unplanned | Defective equipment | Reported broken earth at transformer. De energised Sub to make repairs. EAM1501437 NAMSF4059 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 688 | 2024-08-29-0145 | Waihopai Valley - ABS843-B | CB5493 Waihopai Valley | 2024-08-29 08:35 | 2024-08-29 14:37 | 0.37197 | 0.0010304 | 28 | 10108 | Planned | Planned interruption | Planned shutdown to replace bowing pole. EAM 1487336 SAF 4287 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 689 | 2024-08-29-0149 | Taylor Pass - LVOH4309 | CB1089-Taylor Pass | 2024-08-29 08:40 | 2024-08-29 14:30 | 0 | 0 | 4 | 1400 | Planned | Planned interruption | OHUG of LV services EAM1434930 NAMS4240 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 690 | 2024-08-29-0146 | Taylor Pass - LVOH4350 | CB1089-Taylor Pass | 2024-08-29 08:57 | 2024-08-29 09:14 | 0 | 0 | 1 | 16 | Unplanned | Defective equipment | Faulty connection while completing OHUG project at Pole DF248 and repaired. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 691 | 2024-08-29-0147 | Tuamarina - REC5262 | CB188-Tuamarina | 2024-08-29 15:19 | 2024-08-29 15:50 | 0.30117 | 0.0097152 | 264 | 8184 | Unplanned | Defective equipment | Urgent shutdown to return cross arm centre bolt back into position at Pole KB0301 Pembers Rd. EAM 1501654 F4062 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 692 | 2024-08-30-0150 | Godfrey Road - HVOH1061 | CB5367 Godfrey Road | 2024-08-30 08:30 | 2024-08-30 14:37 | 0.040406 | 0.0001104 | 3 | 1098 | Planned | Planned interruption | Planned shutdown to replace 11kV cross arms and install new ABS15432 EAM 1497878 SAF 4363 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 693 | 2024-08-30-0151 | Godfrey Road - SUB343078 | CB5367 Godfrey Road | 2024-08-30 08:30 | 2024-08-30 14:36 | 0.013469 | 3.68e-05 | 1 | 366 | Planned | Planned interruption | Planned shutdown to replace 11kV cross arms and install new ABS15432 EAM 1497878 SAF 4363 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 694 | 2024-08-30-0152 | Colemans Rd - 0001131457MLD0B | CB1512-Colemans Rd | 2024-08-30 08:36 | 2024-08-30 09:34 | 0 | 0 | 1 | 58 | Planned | Planned interruption | Replacement of SFB58 Colemans Rd - 3 outages due to modelling errors SAF4045 - WO 1464269 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 695 | 2024-08-30-0153 | Colemans Rd - 0001130459MLF30 | CB1512-Colemans Rd | 2024-08-30 08:36 | 2024-08-30 09:34 | 0 | 0 | 1 | 58 | Planned | Planned interruption | Replacement of SFB58 Colemans Rd - 3 outages due to modelling errors SAF4045 - WO 1464269 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 696 | 2024-08-30-0154 | Colemans Rd - 0001130987ML4E1 | CB1512-Colemans Rd | 2024-08-30 08:36 | 2024-08-30 09:34 | 0 | 0 | 1 | 58 | Planned | Planned interruption | Replacement of SFB58 Colemans Rd - 3 outages due to modelling errors SAF4045 - WO 1464269 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 697 | 2024-08-30-0156 | Wairau Valley - FUSE3246 | CB5399 Wairau Valley | 2024-08-30 09:20 | 2024-08-30 11:26 | 0.0046736 | 3.68e-05 | 1 | 127 | Unplanned | Unknown | EAM 1501665 - Part power, 3PH 200A, blue & white phase gone found 11kV Fuse 3246 one phase blown. No obvious cause. F4066 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 698 | 2024-08-30-0157 | Tuamarina - LVOH2723 | CB188-Tuamarina | 2024-08-30 11:01 | 2024-08-30 11:46 | 0 | 0 | 2 | 90 | Planned | Planned interruption | Rarangi Beach Road Planned Work http://nams.mll.co.nz/Schedule/Edit/4035 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 699 | 2024-08-30-0158 | Dashwood - FUSE2484 | CB1252-Dashwood | 2024-08-30 18:18 | 2024-08-30 20:15 | 0.013027 | 0.0001104 | 3 | 354 | Unplanned | Unknown | 1501728 found 1 HV fuse blown at Fuse site 2484. No apparent cause. Checked 3 phase supply at meter. F4069 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 700 | 2024-08-31-0159 | Redwood St Sth - 0001186077ML636 | CB1673-Redwood St Sth | 2024-08-31 11:54 | 2024-08-31 13:21 | 0 | 0 | 1 | 87 | Unplanned | Defective equipment | Blown rewireable fuse due to deterioration. Trurip had previous repair so Insulation test carried out as precaution. >999M ohm? 1501729 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 701 | 2024-08-31-0160 | French Pass - REC5005 | CB45-French Pass | 2024-08-31 17:26 | 2024-09-04 13:37 | 4.0347 | 0.042025 | 382 | 109640 | Unplanned | Lightning | EAM 1501730 F4070 REC 5005 tripped on earth fault. Found Blown TX Fuses at Sub336025 Twxt and Sub336201 blown by lightning and required replacement. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 702 | 2024-09-01-0016 | Okaramio - SUB320109 | CB104 Okaramio | 2024-08-31 19:01 | 2024-09-01 11:12 | 0.071465 | 7.36e-05 | 2 | 1942 | Unplanned | Lightning | EAM 1501756 F4083 SUB320109 - 3ph 15kVA - 3A Replaced blown TX fuses after lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 703 | 2024-08-31-0162 | French Pass - SUB336001 | CB45-French Pass | 2024-08-31 19:33 | 2024-09-02 15:49 | 0.19548 | 7.36e-05 | 2 | 5312 | Unplanned | Lightning | 1x blown fuse at SUB336001. Replaced fuses (3A), blew on livening (lightning damage). replaced TX 02/09. EAM 1501735 F4091 SUB336001 - 1ph 10kVA - 3A Upline FUSE2536 - 10A | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 704 | 2024-08-31-0163 | Okaramio - FUSE2233 | CB104 Okaramio | 2024-08-31 19:35 | 2024-09-01 10:50 | 0.067417 | 7.36e-05 | 2 | 1832 | Unplanned | Lightning | EAM 1501749 F4078 Found blown fuses at 2233 and Sub 320186 due to lightning. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 705 | 2024-08-31-0168 | Koromiko - SUB331015 | CB55-Koromiko | 2024-08-31 19:47 | 2024-09-02 13:07 | 0.091264 | 3.68e-05 | 1 | 2480 | Unplanned | Lightning | Transformer blown by lightning. TX replaced with a main line shutdown (2024-09-02-0034). EAM 1501740 F4077 & F4093 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 706 | 2024-08-31-0165 | Okaramio - SUB320121 | CB104 Okaramio | 2024-08-31 19:57 | 2024-09-01 11:11 | 0.033635 | 3.68e-05 | 1 | 914 | Unplanned | Lightning | Blown fuses at SUB320121 - Replaced fuses (3A). Confirmed power restored EAM 1501747 F4084 1/09/2024 9:03:49 amSUB320121 - 1ph 10kVA - 3 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 707 | 2024-08-31-0166 | Koromiko - SUB331142 | CB55-Koromiko | 2024-08-31 19:57 | 2024-09-01 10:23 | 0.095496 | 0.0001104 | 3 | 2595 | Unplanned | Lightning | 1x blown fuse at SUB331142 - lightning. Replaced both fuses (6A). Confirmed power restored EAM 1501736 http://nams.mll.co.nz/Schedule/Edit/4079 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 708 | 2024-08-31-0170 | Koromiko - SUB331016 | CB55-Koromiko | 2024-08-31 19:58 | 2024-09-02 11:59 | 0.088357 | 3.68e-05 | 1 | 2401 | Unplanned | Lightning | Transformer blown by lightning. TX replaced with a main line shutdown (2024-09-02-0034). SUB331016 - 1ph 15kVA - 3A F4085 & F4093 EAM 1501741 C | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 709 | 2024-08-31-0167 | Koromiko - SUB331024 | CB55-Koromiko | 2024-08-31 20:00 | 2024-09-01 09:41 | 0.060425 | 7.36e-05 | 2 | 1642 | Unplanned | Lightning | Found 2 blown TX fuses at Sub331024. Lightning in area. F4076 EAM 1501738 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 710 | 2024-08-31-0169 | Koromiko - SUB331011 | CB55-Koromiko | 2024-08-31 20:06 | 2024-09-01 09:03 | 0.20015 | 0.0002576 | 7 | 5439 | Unplanned | Lightning | Safety disc due to lightning strike. Customer to be informed to have electrician check premises prior to livening. TX Fuses open at Sub331011. Pole tagged DNO for the night due to weather | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 711 | 2024-08-31-0171 | Koromiko - 0006632400ML602 | CB55-Koromiko | 2024-08-31 20:26 | 2024-08-31 22:17 | 0 | 0 | 1 | 111 | Unplanned | Adverse weather | EAM 1501751 Property attended, no loss of supply. Customer concerned about safety due to lightning strike. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 712 | 2024-08-31-0172 | Okaramio - SUB320106 | CB104 Okaramio | 2024-08-31 20:28 | 2024-09-01 12:04 | 0.034481 | 3.68e-05 | 1 | 937 | Unplanned | Lightning | 1x blown fuse at SUB320106 - lightning. Replaced fuses (3A). COnfirmed power restored EAM 1501752 F4090 SUB320106 - 1ph 15kVA - 3A Upline FUSE3612 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 713 | 2024-08-31-0173 | Koromiko - FUSE3211 | CB55-Koromiko | 2024-08-31 21:07 | 2024-08-31 21:33 | 0.0038272 | 0.0001472 | 4 | 104 | Unplanned | Lightning | Found 1 HV fuse out at Fuse site 3211 and 1 blown fuse at Sub 331013. Lightning strike in area. F4071 EAM 1501733 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 714 | 2024-08-31-0174 | Koromiko - FUSE2206 | CB55-Koromiko | 2024-08-31 21:11 | 2024-09-01 14:11 | 0.11846 | 0.000184 | 5 | 3219 | Unplanned | Lightning | EAM 1501745 F4088 SUB331035 - 1ph 15kVA - 3A Found 2 blown fuses at 11kV Fuse2206, 2963 and TX 331035 due to lightening | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 715 | 2024-08-31-0177 | Okaramio - SUB320111 | CB104 Okaramio | 2024-08-31 21:59 | 2024-08-31 23:51 | 0.0082432 | 7.36e-05 | 2 | 224 | Unplanned | Lightning | found 1 blown TX fuse at Sub320111 and replaced. Lightning in area. F4074 EAM 1501734 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 716 | 2024-08-31-0176 | Havelock Canvastown - CB103 | CB103 Havelock Canvastown | 2024-08-31 22:51 | 2024-08-31 23:28 | 0.42611 | 0.020718 | 563 | 11579 | Unplanned | Lightning | CB103 Havelock tripped on earth fault (GFN). Lightning storm in area at the time. F4073 EAM 1051732 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 717 | 2024-09-02-0036 | Sounds - REC97 | REC1170-Sounds | 2024-08-31 23:11 | 2024-08-31 23:11 | 0.0065504 | 0.0065504 | 178 | 178 | Unplanned | Lightning | Succesful auto reclose on phase OC during lightning storm. Red 6A Yellow 121A Blue 8A Earth 119A Cyclo249 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 718 | 2024-09-01-0003 | French Pass - REC5024 | CB45-French Pass | 2024-09-01 03:13 | 2024-09-01 03:14 | 0 | 0 | 75 | 0 | Unplanned | Lightning | REC5024 Succesful reclose after phase overcurrent. Electrical storm passing through area. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 719 | 2024-09-01-0005 | Kaituna - FUSE3823 | CB5448 Kaituna | 2024-09-01 06:12 | 2024-09-01 09:32 | 0.4048 | 0.002024 | 55 | 11000 | Unplanned | Lightning | Blown TX fuses replaced EAM 1501746 F4075 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 720 | 2024-09-01-0004 | Koromiko - SUB331019 | CB55-Koromiko | 2024-09-01 07:33 | 2024-09-01 11:05 | 0.071061 | 0.0004048 | 11 | 1931 | Unplanned | Lightning | 1x blown fuse at SUB331019 - lightning. Replaced all 3 (10A). Confirmed power restored. EAM 1501739 http://nams.mll.co.nz/Schedule/Edit/4082 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 721 | 2024-09-01-0017 | Havelock Canvastown - 0007713005MLDF4 | CB103 Havelock Canvastown | 2024-09-01 07:35 | 2024-09-01 11:52 | 0 | 0 | 1 | 257 | Unplanned | Adverse weather | Blown TX fuses replaced - EAM 1501757 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 722 | 2024-09-01-0008 | Koromiko - SUB331017 | CB55-Koromiko | 2024-09-01 08:28 | 2024-09-02 12:40 | 0.062265 | 3.68e-05 | 1 | 1692 | Unplanned | Lightning | Found blown TX fuse after lightning storm. TX replaced under schedule F4093 (2024-09-02-0034) EAM 1501742 F4080 & F4093 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 723 | 2024-09-01-0022 | Rai Valley - SUB335313 | CB43-Rai Valley | 2024-09-01 08:30 | 2024-09-01 12:12 | 0.0081696 | 3.68e-05 | 1 | 222 | Unplanned | Lightning | All 3 fuses blown at SUB335313 - lightning. Replaced fuses (3A). Confirmed power restored EAM 1501743 F4089 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 724 | 2024-09-01-0010 | Okaramio - 0007705222MLA4D | CB104 Okaramio | 2024-09-01 08:39 | 2024-09-01 13:46 | 0 | 0 | 1 | 306 | Unplanned | Adverse weather | EAM 1501748 1/09/2024 10:06:00 am | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 725 | 2024-09-01-0018 | Okaramio - SUB320105 | CB104 Okaramio | 2024-09-01 09:03 | 2024-09-01 11:35 | 0.011187 | 7.36e-05 | 2 | 304 | Unplanned | Lightning | 1x blown fuse at SUB320105 - Lightning. Replaced fuses (3A). Confirmed power restored EAM1501758 F4086 SUB320105 - 3ph 15kVA - 3A | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 726 | 2024-09-01-0023 | Rai Valley - SUB335309 | CB43-Rai Valley | 2024-09-01 10:07 | 2024-09-01 11:19 | 0.0026864 | 3.68e-05 | 1 | 73 | Unplanned | Lightning | 1x blown fuse at SUB335309 - Lightning. Replaced fuses (3A) - Confirmed power restored EAM1501760 F4087 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 727 | 2024-09-01-0019 | Okaramio - SUB320151 | CB104 Okaramio | 2024-09-01 10:32 | 2024-09-01 10:55 | 0.0008832 | 3.68e-05 | 1 | 24 | Unplanned | Lightning | 2 blown fuses at SUB320151 - Replace fuses, 3A confirmed power restored EAM 1501759 F4081 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 728 | 2024-09-01-0020 | Koromiko - 0006632378MLE49 | CB55-Koromiko | 2024-09-01 10:55 | 2024-09-01 12:18 | 0 | 0 | 1 | 84 | Unplanned | Lightning | Property disc for safety after lightning strike. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 729 | 2024-09-01-0024 | Havelock Canvastown - LVUG160216 | CB103 Havelock Canvastown | 2024-09-01 12:28 | 2024-09-01 15:10 | 0 | 0 | 4 | 648 | Unplanned | Adverse weather | EAM 1501761 F4092 LV Line down beyond pole KB0119 due to clashing in strong winds. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 730 | 2024-09-01-0027 | Waikawa - 0006615516ML989 | CB109- Waikawa | 2024-09-01 19:03 | 2024-09-01 20:47 | 0 | 0 | 1 | 105 | Unplanned | Defective equipment | 1501762 ------------- Blown service fuseafter garage fire. Garage isolated and property relivened | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 731 | 2024-09-02-0028 | Richmond Brook - REC37 | CB1250-Richmond Brook | 2024-09-02 00:41 | 2024-09-02 00:42 | 0 | 0 | 223 | 0 | Unplanned | Wildlife | Succesful auto reclose on earth fault. Cyclo Red 5 Yellow 3 Blue 61 Earth 55 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 732 | 2024-09-02-0029 | Omaka - FUSE2406 | CB1088 - Omaka | 2024-09-02 08:17 | 2024-09-02 12:04 | 0.016707 | 7.36e-05 | 2 | 454 | Planned | Planned interruption | Planned shutdown to remove pump under 11kV lines. SAF 4383 EAM 1500015 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 733 | 2024-09-02-0039 | Symons St - RMUS1148-B | CB50-Symons St | 2024-09-02 09:28 | 2024-09-02 14:05 | 0.020387 | 7.36e-05 | 2 | 554 | Unplanned | Human error | Unplanned outage to EV chargers in Park Tce due to transposal of switch numbers on 11kV RMUS5677 and RMUS5695. See SAF4295.2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 734 | 2024-09-02-0040 | Nelson St - CB93 | CB93-Nelson St | 2024-09-02 09:30 | 2024-09-02 09:38 | 0.22522 | 0.028152 | 765 | 6120 | Unplanned | Human error | Unplanned outage on 11kV CB93 (Nelson St) due to transposal of switch numbers on 11kV RMUS5677 and RMUS5695. See SAF4295.2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 735 | 2024-09-02-0032 | Nelson St - 0001116051MLD28 | CB93-Nelson St | 2024-09-02 09:46 | 2024-09-02 10:55 | 0 | 0 | 1 | 69 | Unplanned | Unknown | EAM 1501799 - there is power to the meter, c/s to call customer to let them know | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 736 | 2024-09-02-0033 | Hutcheson St - 0001154485ML5B4 | CB49-Hutcheson St | 2024-09-02 10:01 | 2024-09-02 11:27 | 0 | 0 | 1 | 85 | Unplanned | Defective equipment | Loose neutral connection repaired | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 737 | 2024-09-02-0034 | Koromiko - ABS15084-B | CB55-Koromiko | 2024-09-02 10:02 | 2024-09-02 11:55 | 0.70277 | 0.0062192 | 169 | 19097 | Unplanned | Lightning | Replacement of SUB's 331015,331016 & 331017 - SH1 Koromiko. All 3 TX's damaged by lightning on EAM 1501742, EAM 1501741 & EAM 1501740 Related outages 2024-08-31-0168, 2024-08-31-0170 & 2024-09-01-0008 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 738 | 2024-09-02-0037 | Pelorus - SUB335153 | CB5126-Pelorus | 2024-09-02 10:45 | 2024-09-02 13:19 | 0.005704 | 3.68e-05 | 1 | 155 | Unplanned | Lightning | EAM 1501806 - No power, probably since the weekend F4095 Found blown TX fuse due to lightning in area SUB335153 - 1ph 15kVA - 3A | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 739 | 2024-09-03-0041 | Hutcheson St - RMUS1249 | CB49-Hutcheson St | 2024-09-03 09:09 | 2024-09-03 09:53 | 0.095532 | 0.0021712 | 59 | 2596 | Unplanned | Defective equipment | Urgent shutdown to remove faulty 11kV ABS783 on Beaver Rd. EAM1501825 F4096 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 740 | 2024-09-03-0043 | Sounds - SUB325080 | REC1170-Sounds | 2024-09-03 10:20 | 2024-09-03 13:17 | 0.013101 | 7.36e-05 | 2 | 356 | Unplanned | Lightning | Found blown TX fuse after lightening storm EAM 1501977 - No power F4098 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 741 | 2024-09-03-0044 | Rai Valley - SUB335347 | CB43-Rai Valley | 2024-09-03 13:41 | 2024-09-03 15:50 | 0.0047472 | 3.68e-05 | 1 | 129 | Unplanned | Lightning | EAM 1502095 F4099 2 phases out at Transformer ------------------- Found 1 blown 11kV TX fuse due to lightening in area over weekend | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 742 | 2024-09-03-0045 | Sounds - 0008811309MLC25 | REC1170-Sounds | 2024-09-03 15:03 | 2024-09-04 23:14 | 0 | 0 | 1 | 1930 | Unplanned | Third party interference | EAM 1502188 Replaced blown pole fuse. Fuse blew when replaced. On investigation found unsafe wiring that needs to be repaired by an electrician | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 743 | 2024-09-04-0046 | Wairau Valley - FUSE3855 | CB5399 Wairau Valley | 2024-09-04 08:30 | 2024-09-04 14:38 | 0.027085 | 7.36e-05 | 2 | 736 | Planned | Planned interruption | Replacement of all x-arms on pole HA1345 EAM1490038 NAMS4250 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 744 | 2024-09-04-0047 | Seaview - FUSE3912 | CB1251-Seaview | 2024-09-04 08:53 | 2024-09-04 13:57 | 0.011187 | 3.68e-05 | 1 | 304 | Planned | Planned interruption | Removal of redundant 11kV line at 192 Flemmings Rd EAM1494383 NAMS4304 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 745 | 2024-09-04-0048 | Thomsons Ford Rd - 0003330587MLD47 | CB1509-Thomsons Ford Rd | 2024-09-04 09:22 | 2024-09-04 11:20 | 0 | 0 | 1 | 117 | Unplanned | Other cause | Yellow fuse burnt out, EAM 1502345 - Pole fuse blown, 3PH 60A supply | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 746 | 2024-09-04-0049 | Hospital Rd East - 0001182105MLC6A | CB39-Hospital Rd East | 2024-09-04 18:23 | 2024-09-04 19:10 | 0 | 0 | 1 | 47 | Unplanned | Defective equipment | EAM 1502459 Failed rewirable fure replaced | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 747 | 2024-09-05-0054 | Wairau Valley - FUSE3041 | CB5399 Wairau Valley | 2024-09-05 07:20 | 2024-09-05 08:52 | 0.0068448 | 7.36e-05 | 2 | 186 | Unplanned | Unknown | Blown 11kV Fuse 3041 Cause unknown W/O 1502460 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 748 | 2024-09-05-0055 | Thomsons Ford Rd - RMUS1593 | CB1509-Thomsons Ford Rd | 2024-09-05 08:30 | 2024-09-05 14:31 | 0.25241 | 0.0006992 | 19 | 6859 | Planned | Planned interruption | Planned shutdown for spur line rebuild. EAM 1435933 SAF 4145 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 749 | 2024-09-05-0057 | Wairau Valley - RMUF1447 | CB5399 Wairau Valley | 2024-09-05 08:30 | 2024-09-05 10:23 | 0.0041584 | 3.68e-05 | 1 | 113 | Planned | Planned interruption | Install new fuse carrier in SUB3414GU for new connection EAM1486660 NAMS4264 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 750 | 2024-09-05-0056 | Spring Creek - ABS781 | CB187-Spring Creek | 2024-09-05 08:38 | 2024-09-05 11:05 | 0.010819 | 7.36e-05 | 2 | 294 | Planned | Planned interruption | Connection of new earths at 11kV REC5024 EAM1409777 NAMS4280.1 -- | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 751 | 2024-09-05-0058 | Thomsons Ford Rd - 0002270006ML80D | CB1509-Thomsons Ford Rd | 2024-09-05 19:24 | 2024-09-05 20:45 | 0 | 0 | 1 | 81 | Unplanned | Human error | Service fuse left out accidently by MLL inspector following planned shutdown W/O1502800 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 752 | 2024-09-06-0059 | Waihopai Valley - 0002272233MLBFD | CB5493 Waihopai Valley | 2024-09-06 08:11 | 2024-09-06 09:48 | 0 | 0 | 1 | 97 | Unplanned | Defective equipment | Faulty service cable. Repaired and charged to customer EAM 1502820 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 753 | 2024-09-06-0060 | Spring Creek - 0003315497ML003 | CB187-Spring Creek | 2024-09-06 08:30 | 2024-09-06 10:28 | 0 | 0 | 1 | 118 | Planned | Planned interruption | Replace broken/damaged LV pin insulators on pole KB4941. Pull up low span between KB4941 - KB4942. EAM1494803 NAMS4317 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 754 | 2024-09-06-0061 | Thomsons Ford Rd - HVOH2899-S4935 | CB1509-Thomsons Ford Rd | 2024-09-06 08:30 | 2024-09-06 14:54 | 0.070472 | 0.000184 | 5 | 1915 | Planned | Planned interruption | Spurline upgrade at 117 Bells Rd EAM1435933 NAMS4145 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 755 | 2024-09-06-0063 | Waihopai Valley - 0002272233MLBFD | CB5493 Waihopai Valley | 2024-09-06 10:28 | 2024-09-06 19:30 | 0 | 0 | 1 | 543 | Unplanned | Defective equipment | Faulty service cable - Repaired and customer charged EAM 1502820 - No power again ---- | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 756 | 2024-09-07-0064 | Hawkesbury Road - 0000051114ML6E6 | CB5457 Hawkesbury Road | 2024-09-07 01:14 | 2024-09-07 02:54 | 0 | 0 | 1 | 100 | Unplanned | Defective equipment | fault was in cable side of MLL distribution side supplin, hard tapped, re booted cable and re termed, two phase Truip across road Pole PT4161 Eam 1503121 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 757 | 2024-09-07-0065 | French Pass - REC5024 | CB45-French Pass | 2024-09-07 14:12 | 2024-09-07 14:12 | 0.00276 | 0.00276 | 75 | 75 | Unplanned | Adverse weather | 7/09/2024 2:42:43 pm Succesful Reclose 7/09/2024 2:43:25 pm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 758 | 2024-09-07-0066 | French Pass - REC5024 | CB45-French Pass | 2024-09-07 14:31 | 2024-09-07 14:31 | 0.00276 | 0.00276 | 75 | 75 | Unplanned | Adverse weather | Sucessful Reclose | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 759 | 2024-09-07-0067 | French Pass - REC5024 | CB45-French Pass | 2024-09-07 14:57 | 2024-09-07 14:57 | 0.00276 | 0.00276 | 75 | 75 | Unplanned | Adverse weather | Successful reclose | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 760 | 2024-09-07-0068 | French Pass - REC5024 | CB45-French Pass | 2024-09-07 15:53 | 2024-09-07 15:53 | 0.00276 | 0.00276 | 75 | 75 | Unplanned | Adverse weather | Successful reclose | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 761 | 2024-09-09-0072 | French Pass - REC107 | CB45-French Pass | 2024-09-07 16:42 | 2024-09-08 10:29 | 0.39302 | 0.000368 | 10 | 10680 | Unplanned | Defective equipment | REC107 Tripped but did not reclose. AR enabled no High Current Lockout on SCADA just Ph OC Attempt to CLOSE after 15min unsuccessful. will require line patrol. Patrol Carried out Sunday, found pole burnt down Pole MA2414 Lines disconnected | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 762 | 2024-09-07-0070 | French Pass - REC5024 | CB45-French Pass | 2024-09-07 18:26 | 2024-09-07 18:28 | 0.002392 | 0.002392 | 65 | 65 | Unplanned | Adverse weather | Successful reclose Outage | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 763 | 2024-09-09-0073 | French Pass - REC5024 | CB45-French Pass | 2024-09-07 19:37 | 2024-09-07 19:38 | 0 | 0 | 75 | 0 | Unplanned | Adverse weather | Outage restored Successful reclose | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 764 | 2024-09-07-0071 | Linkwater West - 0007709062ML96F | REC1168-Linkwater West | 2024-09-07 19:45 | 2024-09-07 23:25 | 0 | 0 | 1 | 220 | Unplanned | Defective equipment | two failed fuses ,40th happening over loading, please send a letter out pleas | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 765 | 2024-09-09-0074 | Spring Creek - 0003310562ML37F | CB187-Spring Creek | 2024-09-09 08:07 | 2024-09-09 10:30 | 0 | 0 | 1 | 144 | Unplanned | Defective equipment | Damaged cut out and faulty Netural connection EAM 1503141 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 766 | 2024-09-09-0077 | Nelson St - 0001114602MLCA6 | CB93-Nelson St | 2024-09-09 08:32 | 2024-09-09 10:01 | 0 | 0 | 1 | 88 | Unplanned | Defective equipment | Burnt out pole fuse replaced | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 767 | 2024-09-09-0076 | Hawkesbury Road - CB5457 | CB5457 Hawkesbury Road | 2024-09-09 09:00 | 2024-09-09 13:01 | 1.4811 | 0.0061456 | 167 | 40247 | Planned | Planned interruption | Anglesea St Planned Work - Replacement of HV and LV arms http://nams.mll.co.nz/Application/Edit/4207 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 768 | 2024-09-09-0078 | Wairau Valley - FUSE3667 | CB5399 Wairau Valley | 2024-09-09 09:22 | 2024-09-09 13:12 | 0.084272 | 0.000368 | 10 | 2290 | Planned | Planned interruption | Removal of SUB341572 EAM1496668 NAMS4326 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 769 | 2024-09-10-0081 | Howick Rd North - 0001123323MLDFF | CB84-Howick Rd North | 2024-09-09 12:22 | 2024-09-09 17:00 | 0 | 0 | 1 | 278 | Unplanned | Third party interference | Cable strike which turned power off to Carters. Cable repair made by MLL EAM1503245 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 770 | 2024-09-09-0079 | Hospital Rd East - 0001180054ML263 | CB39-Hospital Rd East | 2024-09-09 17:20 | 2024-09-09 18:19 | 0 | 0 | 1 | 60 | Unplanned | Defective equipment | Internal fault customers side | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 771 | 2024-09-09-0080 | Sounds - CB5582 | REC1168 - Linkwater West, REC1562 - Ngakuta, REC1170 - Sounds | 2024-09-09 18:31 | 2024-09-09 18:31 | 0.064179 | 0.064179 | 1744 | 1744 | Unplanned | Unknown | Successful reclose Red 28A Yellow 825A Blue 801A Outage restored | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 772 | 2024-09-10-0082 | Thomsons Ford Rd - HVOH2899 | CB1509-Thomsons Ford Rd | 2024-09-10 08:30 | 2024-09-10 14:53 | 0.070472 | 0.000184 | 5 | 1915 | Planned | Planned interruption | Planned shutdown for line re-build EAM 1435933 SAF 4145.2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 773 | 2024-09-10-0083 | Wairau Valley - FUSE3690 | CB5399 Wairau Valley | 2024-09-10 08:56 | 2024-09-10 10:36 | 0.096636 | 0.0009568 | 26 | 2626 | Unplanned | Wildlife | Multiple no powers reported and a dead duck found under the lines between poles HA1641 and HA1639. EAM 1503496 F412 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 774 | 2024-09-10-0084 | Rapaura Rd - SUB357018 | CB1077-Rapaura Rd | 2024-09-10 12:17 | 2024-09-10 13:25 | 0.0024656 | 3.68e-05 | 1 | 67 | Unplanned | Unknown | found 1 blown TX fuse at Sub357018. No apparent cause. Confirmed power restored at meterboard. EAM 1503689 F4131 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 775 | 2024-09-11-0085 | Renwick Township - 0000050102MLC64 | CB5482 Renwick Township | 2024-09-11 08:07 | 2024-09-11 10:15 | 0 | 0 | 1 | 128 | Planned | Planned interruption | replacing LV service arm EAM 1480870 SAF 4201 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 776 | 2024-09-11-0086 | Grassmere - SUB352014 | CB1253-Grassmere | 2024-09-11 08:36 | 2024-09-11 13:48 | 0.011445 | 3.68e-05 | 1 | 311 | Planned | Planned interruption | Planned shutdown to upgrade Sub352014 to 50kVa EAM 1491818 SAF 4262 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 777 | 2024-09-11-0087 | Renwick Township - LVOH200079 | CB5482 Renwick Township | 2024-09-11 09:08 | 2024-09-11 11:05 | 0 | 0 | 1 | 117 | Planned | Planned interruption | Planned shutdown. replacing LV cross arm. EAM 1481002 SAF 4203 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 778 | 2024-09-11-0088 | Renwick Township - 0000050518ML859 | CB5482 Renwick Township | 2024-09-11 09:08 | 2024-09-11 11:06 | 0 | 0 | 1 | 118 | Planned | Planned interruption | Planned shutdown. replacing LV cross arm. EAM 1481002 SAF 4203 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 779 | 2024-09-11-0089 | Renwick Township - LVOH1720 | CB5482 Renwick Township | 2024-09-11 10:38 | 2024-09-11 13:53 | 0 | 0 | 3 | 582 | Planned | Planned interruption | Planned shutdown to replace LV cross arms. EAM 1480870 SAF 4201 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 780 | 2024-09-11-0090 | Renwick Township - 0000050092MLA87 | CB5482 Renwick Township | 2024-09-11 10:38 | 2024-09-11 13:53 | 0 | 0 | 1 | 194 | Planned | Planned interruption | Planned shutdown to replace LV cross arms. EAM 1480870 SAF 4201 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 781 | 2024-09-11-0091 | Renwick Township - 0000050086ML120 | CB5482 Renwick Township | 2024-09-11 10:38 | 2024-09-11 13:53 | 0 | 0 | 1 | 194 | Planned | Planned interruption | Planned shutdown to replace LV cross arms. EAM 1480870 SAF 4201 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 782 | 2024-09-11-0092 | Kaituna - 0000050538ML50C | CB5448 Kaituna | 2024-09-11 11:31 | 2024-09-11 14:27 | 0 | 0 | 1 | 175 | Planned | Planned interruption | Planned shutdown to replace LV cross arms. EAM 1480870 SAF 4201 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 783 | 2024-09-11-0093 | East Coast - FUSE3733 | REC29-East Coast | 2024-09-11 13:58 | 2024-09-11 14:01 | 0.0002944 | 0.0001472 | 4 | 8 | Unplanned | Unknown | Short outage to change Fuse 3733 from a solid link to a 3amp to assist with intermittent fault. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 784 | 2024-09-11-0094 | Talleys - 0004450069MLF10 | CB172-Talleys | 2024-09-11 16:51 | 2024-09-12 17:30 | 0.054464 | 3.68e-05 | 1 | 1480 | Unplanned | Defective equipment | Faulty TX - ratio error on HV side of TX. TX replaced and relivened. Checked voltages and rotation OK. EAM 1504280 http://nams.mll.co.nz/Schedule/Edit/4135 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 785 | 2024-09-12-0095 | Wairau Valley - FUSE2163 | CB5399 Wairau Valley | 2024-09-12 08:30 | 2024-09-12 13:24 | 0.054096 | 0.000184 | 5 | 1470 | Planned | Planned interruption | Planned shutdown to replace 11kV crossarm & fuse arm. EAM 1495389 SAF 4321 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 786 | 2024-09-12-0097 | Renwick Township - 0000052557ML662 | CB5482 Renwick Township | 2024-09-12 08:31 | 2024-09-12 09:18 | 0 | 0 | 1 | 46 | Planned | Planned interruption | Re-heatshrinking of LV service cable SAF4195 - WO1480853 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 787 | 2024-09-12-0096 | Renwick Township - LVOH2809 | CB5482 Renwick Township | 2024-09-12 08:44 | 2024-09-12 10:18 | 0 | 0 | 2 | 188 | Planned | Planned interruption | Planned shutdown to replace iron rail pole. EAM 1481014 SAF 4210 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 788 | 2024-09-12-0098 | Buller St - 0006607109MLB5A | CB108-Buller St | 2024-09-12 09:02 | 2024-09-12 13:40 | 0 | 0 | 1 | 277 | Planned | Planned interruption | Kent Street Planned Work http://nams.mll.co.nz/Schedule/Edit/4018 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 789 | 2024-09-12-0099 | French Pass - FUSE2321 | CB45-French Pass | 2024-09-12 09:33 | 2024-09-12 13:13 | 0.016192 | 7.36e-05 | 2 | 440 | Unplanned | Defective equipment | Removal of burnt down SUB336718 and installation of earths at pole MA2414 http://nams.mll.co.nz/Schedule/Edit/4129 WO1503123 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 790 | 2024-09-12-0100 | Renwick Township - 0000052999MLE1A | CB5482 Renwick Township | 2024-09-12 10:24 | 2024-09-12 11:06 | 0 | 0 | 1 | 43 | Planned | Planned interruption | Re-heatshrinkng of LV service and replacement of rewirable fuses with HRC's. SAF 4195 WO1480853 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 791 | 2024-09-12-0101 | Renwick Township - 0000052489ML1BF | CB5482 Renwick Township | 2024-09-12 11:07 | 2024-09-12 11:56 | 0 | 0 | 1 | 49 | Planned | Planned interruption | Re-heatshrinkng of LV service and replacement of rewirable fuses with HRC's. SAF 4195 WO1480853 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 792 | 2024-09-12-0102 | Renwick Township - 0000052176MLB73 | CB5482 Renwick Township | 2024-09-12 12:13 | 2024-09-12 12:49 | 0 | 0 | 1 | 35 | Planned | Planned interruption | Re-heatshrinkng of LV service and replacement of rewirable fuses with HRC's. SAF 4195 WO1480853 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 793 | 2024-09-12-0104 | Okaramio - SUB320133 | CB104 Okaramio | 2024-09-12 15:45 | 2024-09-12 16:55 | 0.007728 | 0.0001104 | 3 | 210 | Unplanned | Third party interference | Flickering power reported by customer to gang working on Okaramio project. 1 fuse found dropped open at SUB320133. Closed fuse. Suspect caused by vibration from digger working around pole http://nams.mll.co.nz/Schedule/Edit/4140 EAM 1504509 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 794 | 2024-09-12-0103 | Murphys Rd - 0001122229ML7CA | CB68-Murphys Rd | 2024-09-12 16:26 | 2024-09-12 18:06 | 0 | 0 | 1 | 101 | Unplanned | Defective equipment | EAM 1504510 replaced burnt out pole fuse. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 795 | 2024-09-13-0111 | Spring Creek - LVOH4686 | CB187-Spring Creek | 2024-09-13 08:25 | 2024-09-13 11:30 | 0 | 0 | 1 | 185 | Planned | Planned interruption | Planned shutdown to replace red tagged pole. EAM 1493364 SAF 4283 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 796 | 2024-09-13-0112 | Spring Creek - LVOH4687 | CB187-Spring Creek | 2024-09-13 08:26 | 2024-09-13 11:30 | 0 | 0 | 1 | 185 | Planned | Planned interruption | Planned shutdown to replace red tagged pole. EAM 1493364 SAF 4283 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 797 | 2024-09-13-0106 | Spring Creek - SUB355017 | CB187-Spring Creek | 2024-09-13 08:30 | 2024-09-13 10:18 | 0.01575 | 0.0001472 | 4 | 428 | Planned | Planned interruption | Planned shutdown to replace LV cross arms. EAM 1495408 SAF 4318 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 798 | 2024-09-13-0107 | Waikawa - LVUG125195 | CB109- Waikawa | 2024-09-13 08:35 | 2024-09-13 09:53 | 0 | 0 | 10 | 780 | Planned | Planned interruption | Planned shutdown to replace damaged gyro box EAM 1467933 SAF 4316 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 799 | 2024-09-13-0114 | Sounds - SUB325619 | REC1170-Sounds | 2024-09-13 10:45 | 2024-09-13 12:25 | 0.0036432 | 3.68e-05 | 1 | 99 | Planned | Planned interruption | Shutdown of SUB325619 for connection of new service SAF4324 - WO 1476791 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 800 | 2024-09-13-0115 | Vintage Lane - SUB342084 | CB171-Vintage Lane | 2024-09-13 11:36 | 2024-09-13 12:06 | 0.0010672 | 3.68e-05 | 1 | 29 | Planned | Planned interruption | Connection of new earths at SUB342084 SAF4267 - EAM 1307679 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 801 | 2024-09-13-0116 | Vintage Lane - SUB342084 | CB171-Vintage Lane | 2024-09-13 13:31 | 2024-09-13 14:23 | 0.0019136 | 3.68e-05 | 1 | 52 | Planned | Planned interruption | Alma ST North Planned work http://nams.mll.co.nz/Schedule/Edit/3936 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 802 | 2024-09-15-0117 | Sounds - SUB326019 | REC1170-Sounds | 2024-09-15 06:36 | 2024-09-15 11:40 | 0.01115 | 3.68e-05 | 1 | 303 | Unplanned | Wildlife | Dead possum found on the TX bushings and the HV fuse blown. Removed possum and replaced fuse (3A) http://nams.mll.co.nz/Schedule/Edit/4141 EAM 1504727 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 803 | 2024-09-15-0118 | Grovetown - FUSE3763 | CB1465-Grovetown | 2024-09-15 22:04 | 2024-09-15 23:14 | 0.030912 | 0.0004416 | 12 | 840 | Unplanned | Wildlife | No power and swan in lines reported at 58 Steam Wharf Rd found 2 fuses blown at FUSE3761 and a dead swan on the ground in the span immediately past the fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 804 | 2024-09-16-0119 | Craiglochart - FUSE2199 | REC1391-Craiglochart | 2024-09-16 06:34 | 2024-09-16 08:27 | 0.012586 | 0.0001104 | 3 | 342 | Unplanned | Unknown | EAM 1504729 F4144 Found 2 blown 11kV fuses at 2199. Nothing found on patrol. Confirmed power restored with Customer. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 805 | 2024-09-16-0120 | Waikawa - FUSE2227 | CB109- Waikawa | 2024-09-16 08:34 | 2024-09-16 14:48 | 0.46795 | 0.0012512 | 34 | 12716 | Planned | Planned interruption | Planned shutdown to remove burning trees in Whangakoko Bay area. EAM 1422332 SAF 4311 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 806 | 2024-09-16-0121 | Wairau Valley - FUSE2692 | CB5399 Wairau Valley | 2024-09-16 08:36 | 2024-09-16 14:33 | 0.13174 | 0.000368 | 10 | 3580 | Planned | Planned interruption | Replacement of all arms on pole KB9564 and pulling up of LV spans EAM1476644 NAMS4138 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 807 | 2024-09-16-0122 | Wairau Valley - 0002278334ML173 | CB5399 Wairau Valley | 2024-09-16 12:16 | 2024-09-16 13:50 | 0 | 0 | 1 | 94 | Unplanned | Defective equipment | Hrc Pole fuse replaced No cause identifed Power restored Fuse letter sent EAM 1504829 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 808 | 2024-09-16-0123 | Okaramio - FUSE2265 | CB104 Okaramio | 2024-09-16 22:35 | 2024-09-17 00:57 | 0.11294 | 0.0008096 | 22 | 3069 | Unplanned | Unknown | 2 no powers reported from Leslies Rd. 2x blown fuses at FUSE2265. Line patrolled, no cause found. replaced fuses (20A) http://nams.mll.co.nz/Schedule/Edit/4145 EAM 1504894 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 809 | 2024-09-17-0125 | Taylor Pass - REC5559 | CB1089-Taylor Pass | 2024-09-16 23:59 | 2024-09-16 23:59 | 0.0013984 | 0.0013984 | 38 | 38 | Unplanned | Unknown | REC5559 (Meadowbank) reclosed on phase OC. Yellow phase fault inidicated. Cyclo 81 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 810 | 2024-09-17-0126 | Seaview - FUSE3133 | CB1251-Seaview | 2024-09-17 08:17 | 2024-09-17 10:26 | 0.004784 | 3.68e-05 | 1 | 130 | Unplanned | Wildlife | EAM 1504911 Blown Fuse 3133 Seaview - Dead bird found http://nams.mll.co.nz/Schedule/Edit/4146 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 811 | 2024-09-17-0127 | Okaramio - HVOH2732-S20732 | CB104 Okaramio | 2024-09-17 08:30 | 2024-09-17 14:16 | 0.67484 | 0.0019504 | 53 | 18338 | Planned | Planned interruption | Planned shutdown for Okaramio rebuild. Installing new ABS15416 & 15431. SD1 EAM1426402 SAF 4330.1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 812 | 2024-09-17-0128 | Redwood St Nth - 0001105455MLA22 | CB1655-Redwood St Nth | 2024-09-17 10:07 | 2024-09-17 11:29 | 0 | 0 | 1 | 81 | Unplanned | Defective equipment | Blown Pole fuse on the White Phase No Fuse letter given EAM 1504953 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 813 | 2024-09-17-0129 | Richmond Brook - FUSE4153 | CB1250-Richmond Brook | 2024-09-17 11:55 | 2024-09-17 13:50 | 0.0041952 | 3.68e-05 | 1 | 114 | Unplanned | Unknown | EAM 1505013 Blown 11kV Fuse 4153 http://nams.mll.co.nz/Schedule/Edit/4150 Cause unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 814 | 2024-09-18-0131 | Kaituna - REC1030 | CB5448 Kaituna | 2024-09-17 20:29 | 2024-09-17 20:30 | 0 | 0 | 25 | 0 | Unplanned | Unknown | Successful reclose REC1030 Phase OC Cause unknown. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 815 | 2024-09-18-0132 | Colemans Rd - LVUG1795 | CB1512-Colemans Rd | 2024-09-18 09:14 | 2024-09-18 11:28 | 0 | 0 | 14 | 1876 | Planned | Planned interruption | Replacement of SFB5 Clouston Gardens EAM1468504 NAMS4387 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 816 | 2024-09-18-0133 | Hutcheson St - 0001101223MLE76 | CB49-Hutcheson St | 2024-09-18 11:20 | 2024-09-18 12:35 | 0 | 0 | 1 | 76 | Unplanned | Defective equipment | Blown fuse - Customer advised that balancing needs to be done Fuse letter given in July for same thing EAM 1505230 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 817 | 2024-09-19-0143 | Seaview - FUSE3737 | CB1251-Seaview | 2024-09-19 08:31 | 2024-09-19 13:29 | 0.032899 | 0.0001104 | 3 | 894 | Planned | Planned interruption | Installation of SUB350093 in Reserve Rd SAF4237 - WO 1469912 Outage restored | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 818 | 2024-09-19-0144 | Sounds - LVOH1525 | REC1170-Sounds | 2024-09-19 09:01 | 2024-09-19 11:44 | 0 | 0 | 3 | 489 | Planned | Planned interruption | Replacement of red-tagged pole NK1107 in Double Cove SAF4222 - WO 1483204 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 819 | 2024-09-20-0159 | Rai Valley - CB5391 | CB43 - Rai Valley, CB45 - French Pass, CB5126 - Pelorus | 2024-09-20 01:57 | 2024-09-20 01:57 | 0 | 0 | 913 | 0 | Unplanned | Unknown | Successful reclose of CB5391 Earth Fault Cause unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 820 | 2024-09-20-0146 | Grassmere - FUSE3449 | CB1253-Grassmere | 2024-09-20 05:24 | 2024-09-20 08:57 | 0.039192 | 0.000184 | 5 | 1065 | Unplanned | Unknown | 2x blown fuses found at FUSE3449. Line patrolled, no cause found. Fuses replaced and confirmed power restored EAM 1505343 http://nams.mll.co.nz/Schedule/Edit/4172 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 821 | 2024-09-20-0147 | Rai Valley - FUSE2292 | CB43-Rai Valley | 2024-09-20 05:57 | 2024-09-20 10:32 | 0.26312 | 0.0009568 | 26 | 7150 | Unplanned | Wildlife | EAM 1505348 F4171 11kV Line down between AP1758 & DF1135 337 Ronga Rd Bird strike -- | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 822 | 2024-09-20-0148 | East Coast - 0005515125ML9CF | REC29-East Coast | 2024-09-20 06:44 | 2024-09-20 09:57 | 0 | 0 | 1 | 193 | Unplanned | Other cause | Burnt out cutout replaced EAM 1505344 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 823 | 2024-09-20-0153 | Hutcheson St - 0001101075MLDF6 | CB49-Hutcheson St | 2024-09-20 07:03 | 2024-09-20 08:12 | 0 | 0 | 1 | 69 | Planned | Planned interruption | LV shutdown to disconnect LV cable from Pos 2, D95 Market St SAF 4370 - EAM 1453961 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 824 | 2024-09-20-0157 | Hutcheson St - 0001101108MLEF4 | CB49-Hutcheson St | 2024-09-20 07:03 | 2024-09-20 08:04 | 0 | 0 | 1 | 60 | Planned | Planned interruption | LV shutdown to disconnect LV cable from Pos 2, D95 Market St SAF 4370 - EAM 1453961 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 825 | 2024-09-20-0158 | Hutcheson St - 0001101107ML12A | CB49-Hutcheson St | 2024-09-20 07:03 | 2024-09-20 08:12 | 0 | 0 | 1 | 69 | Planned | Planned interruption | LV shutdown to disconnect LV cable from Pos 2, D95 Market St SAF 4370 - EAM 1453961 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 826 | 2024-09-20-0152 | Hutcheson St - 0001101067ML7DE | CB49-Hutcheson St | 2024-09-20 07:03 | 2024-09-20 08:13 | 0 | 0 | 1 | 69 | Planned | Planned interruption | LV shutdown to disconnect LV cable from Pos 2, D95 Market St SAF 4370 - EAM 1453961 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 827 | 2024-09-20-0154 | Hutcheson St - 0001101588ML7BF | CB49-Hutcheson St | 2024-09-20 07:03 | 2024-09-20 08:13 | 0 | 0 | 1 | 69 | Planned | Planned interruption | LV shutdown to disconnect LV cable from Pos 2, D95 Market St SAF 4370 - EAM 1453961 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 828 | 2024-09-20-0155 | Hutcheson St - 0001101083MLC6E | CB49-Hutcheson St | 2024-09-20 07:04 | 2024-09-20 08:12 | 0 | 0 | 1 | 69 | Planned | Planned interruption | LV shutdown to disconnect LV cable from Pos 2, D95 Market St SAF 4370 - EAM 1453961 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 829 | 2024-09-20-0156 | Hutcheson St - 0001101079MLEE8 | CB49-Hutcheson St | 2024-09-20 07:13 | 2024-09-20 08:12 | 0 | 0 | 1 | 60 | Planned | Planned interruption | LV shutdown to disconnect LV cable from Pos 2, D95 Market St SAF 4370 - EAM 1453961 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 830 | 2024-09-20-0151 | Pelorus - FUSE2281 | CB5126-Pelorus | 2024-09-20 09:05 | 2024-09-20 12:11 | 0.027526 | 0.0001472 | 4 | 748 | Planned | Planned interruption | Planned shutdown to upgrade SUB335013 Bulford Rd EAM 1489855 SAF 4328 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 831 | 2024-09-20-0150 | Havelock Canvastown - 0007702041ML71A | CB103 Havelock Canvastown | 2024-09-20 09:05 | 2024-09-20 10:34 | 0 | 0 | 1 | 88 | Unplanned | Unknown | Blown pole fuse Cause unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 832 | 2024-09-20-0160 | Sounds - FUSE2363 | REC1170-Sounds | 2024-09-20 10:25 | 2024-09-20 14:57 | 0.060057 | 0.0002208 | 6 | 1632 | Unplanned | Defective equipment | Urgent shutdown to replace broken insulator at pole KB8248 EAM 1505263 SAF 4161 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 833 | 2024-09-20-0161 | Grovetown - SUB370270 | CB1465-Grovetown | 2024-09-20 16:20 | 2024-09-20 17:29 | 0.0025392 | 3.68e-05 | 1 | 69 | Unplanned | Unknown | Blown 11kV Fuse Sub 370270 Cause unknown EAM 1505414 Part power, lost 2 phases A http://nams.mll.co.nz/Schedule/Edit/4174 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 834 | 2024-09-20-0162 | Seymour St - 0001163161MLE4D | CB51-Seymour St | 2024-09-20 16:46 | 2024-09-20 18:00 | 0 | 0 | 1 | 74 | Unplanned | Defective equipment | Blown pole fuse caused by faulty oven. Electrician to investigate. Restored 1800. EAM 1505415 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 835 | 2024-09-23-0165 | Hutcheson St - 0001101067ML7DE | CB49-Hutcheson St | 2024-09-22 07:00 | 2024-09-22 15:22 | 0 | 0 | 1 | 501 | Planned | Planned interruption | Market Street Planned Work http://nams.mll.co.nz/Schedule/Edit/4121 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 836 | 2024-09-23-0166 | Hutcheson St - 0001101075MLDF6 | CB49-Hutcheson St | 2024-09-22 07:00 | 2024-09-22 15:21 | 0 | 0 | 1 | 501 | Planned | Planned interruption | Market Street Planned Work http://nams.mll.co.nz/Schedule/Edit/4121 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 837 | 2024-09-23-0167 | Hutcheson St - 0001101588ML7BF | CB49-Hutcheson St | 2024-09-22 07:00 | 2024-09-22 15:22 | 0 | 0 | 1 | 501 | Planned | Planned interruption | Market Street Planned Work http://nams.mll.co.nz/Schedule/Edit/4121 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 838 | 2024-09-23-0168 | Hutcheson St - 0001101083MLC6E | CB49-Hutcheson St | 2024-09-22 07:00 | 2024-09-22 15:22 | 0 | 0 | 1 | 501 | Planned | Planned interruption | Market Street Planned Work http://nams.mll.co.nz/Schedule/Edit/4121 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 839 | 2024-09-23-0169 | Hutcheson St - 0001101079MLEE8 | CB49-Hutcheson St | 2024-09-22 07:00 | 2024-09-22 15:22 | 0 | 0 | 1 | 501 | Planned | Planned interruption | Market Street Planned Work http://nams.mll.co.nz/Schedule/Edit/4121 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 840 | 2024-09-22-0163 | Kaituna - SUB340446 | CB5448 Kaituna | 2024-09-22 09:39 | 2024-09-22 10:15 | 0.001288 | 3.68e-05 | 1 | 35 | Unplanned | Unknown | TX Fuse found blown whilst driving past. Cause unknown Replaced | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 841 | 2024-09-22-0164 | Wairau Valley - 0002279047MLA4D | CB5399 Wairau Valley | 2024-09-22 12:00 | 2024-09-22 13:49 | 0 | 0 | 1 | 109 | Unplanned | Defective equipment | Loose connection into pole fuse. Repalced pole fuse with new ABC fuse. Power restored 1349. EAM 1505419 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 842 | 2024-09-23-0170 | Thomsons Ford Rd - SUB357119 | CB1509-Thomsons Ford Rd | 2024-09-23 06:53 | 2024-09-23 10:26 | 0.039192 | 0.000184 | 5 | 1065 | Unplanned | Defective equipment | Blown 11kV TX Fuse Twisted LV Wires found http://nams.mll.co.nz/Schedule/Edit/4176 EAM 1505420 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 843 | 2024-09-23-0173 | Okaramio - HVOH2732-S20732 | CB104 Okaramio | 2024-09-23 08:41 | 2024-09-23 14:22 | 0.1001 | 0.0002944 | 8 | 2720 | Planned | Planned interruption | Okaramio Stage 2 line rebuild - SD2 SAF 4330 - WO 1426402 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 844 | 2024-09-27-0186 | French Pass - 0008802134ML480 | CB45-French Pass | 2024-09-23 09:02 | 2024-09-27 14:24 | 0 | 0 | 1 | 6081 | Unplanned | Unknown | EAM1505437 Repairs made to neutal and service fuse power restored by | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 845 | 2024-09-23-0172 | McLauchlan St - 0001130117MLB0B | CB65 - McLauchlan St | 2024-09-23 09:09 | 2024-09-23 10:50 | 0 | 0 | 1 | 102 | Unplanned | Unknown | Blowen pole fuse, No oblivious reason Service restored EAM 1505424 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 846 | 2024-09-23-0174 | Tuamarina - 0003315013ML842 | CB188-Tuamarina | 2024-09-23 16:42 | 2024-09-23 18:23 | 0 | 0 | 1 | 101 | Unplanned | Defective equipment | Blown 30A pole fuse, unknown cause. Restored 1823. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 847 | 2024-09-23-0175 | Wairau Valley - FUSE4273 | CB5399 Wairau Valley | 2024-09-23 18:04 | 2024-09-23 20:31 | 0.011629 | 0.0001104 | 3 | 316 | Unplanned | Third party interference | LV Lines taken down by tractor http://nams.mll.co.nz/Schedule/Edit/4178 Fuse 4273 also blown LV Lines down between pole KB4848 and KB4838 Hit by tractor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 848 | 2024-09-24-0176 | Omaka - SUB362215 | CB1088 - Omaka | 2024-09-24 08:30 | 2024-09-24 10:54 | 0 | 0 | 4 | 576 | Planned | Planned interruption | Pull up low LV spans between BS1122 - JA1418. EAM1490092 NAMS4248 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 849 | 2024-09-24-0177 | Richmond Brook - REC37 | CB1250-Richmond Brook | 2024-09-24 10:07 | 2024-09-24 10:07 | 0.0082064 | 0.0082064 | 223 | 223 | Unplanned | Unknown | REC37 Maramar Rd succesful auto reclose on Phase OC. ENS7001 525A Red, 4A Yellow, 528A Blue, Earth 0A. P Fault indicators at Pole VA1403 (FI2728C) next pole past ABS406 were NOT flashing. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 850 | 2024-09-24-0178 | Wairau Valley - FUSE3781 | CB5399 Wairau Valley | 2024-09-24 12:33 | 2024-09-24 14:19 | 0.019504 | 0.000184 | 5 | 530 | Planned | Planned interruption | Centre Creek Road Planned Work http://nams.mll.co.nz/Schedule/Edit/3872 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 851 | 2024-09-24-0179 | Grovetown - FUSE2174 | CB1465-Grovetown | 2024-09-24 13:13 | 2024-09-24 15:20 | 0.042062 | 0.0003312 | 9 | 1143 | Unplanned | Adverse weather | Found dead Magpie at cable term pole at ABS15041 EAM 1505509 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 852 | 2024-09-25-0180 | Kaituna - HVOH2732-S17927 | CB5448 Kaituna | 2024-09-25 08:30 | 2024-09-25 14:40 | 0.10863 | 0.0002944 | 8 | 2952 | Planned | Planned interruption | Planned shutdown for Okaramio line rebuild. EAM 1426402 SAF 4330.6 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 853 | 2024-09-26-0181 | Wairau Valley - FUSE3952 | CB5399 Wairau Valley | 2024-09-26 08:30 | 2024-09-26 13:47 | 0.081659 | 0.0002576 | 7 | 2219 | Planned | Planned interruption | Planned shutdown to replace HV cross arms. EAM1480135 SAF 4401 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 854 | 2024-09-26-0182 | Kaituna - SUB340048 | CB5448 Kaituna | 2024-09-26 08:30 | 2024-09-26 10:51 | 0.010378 | 7.36e-05 | 2 | 282 | Planned | Planned interruption | Planned shutdown to replace stay. EAM 1502401 SAF 4395 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 855 | 2024-09-26-0184 | Scotland St - 0006608317ML10B | CB54-Scotland St | 2024-09-26 10:13 | 2024-09-26 14:55 | 0 | 0 | 1 | 281 | Planned | Planned interruption | York St Planned Work http://nams.mll.co.nz/Schedule/Edit/4147 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 856 | 2024-09-26-0183 | Scotland St - 0006608321ML77C | CB54-Scotland St | 2024-09-26 10:14 | 2024-09-26 14:55 | 0 | 0 | 1 | 281 | Planned | Planned interruption | York St Planned Work http://nams.mll.co.nz/Schedule/Edit/4147 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 857 | 2024-09-26-0185 | Howick Rd North - 0001174069ML9DC | CB84-Howick Rd North | 2024-09-26 12:45 | 2024-09-26 15:15 | 0 | 0 | 1 | 150 | Planned | Planned interruption | Planned LV Pole replacement EAM1497787 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 858 | 2024-09-23-0171 | French Pass - CB45 | CB45-French Pass | 2024-09-27 01:31 | 2024-09-27 11:19 | 4.8635 | 0.10764 | 585 | 132161 | Unplanned | Defective equipment | EAM1505686 F4186 CB Feeder at Rai Sub tripped 3 times on Earth fault over 20 minute period then locked out. Elaine Bay gens running in extended Island back to Okiwi bay REC5005. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 859 | 2024-09-27-0187 | Spring Creek - CB187 | CB187-Spring Creek | 2024-09-27 03:49 | 2024-09-27 04:48 | 0.3995 | 0.010157 | 276 | 10856 | Unplanned | Vegetation | EAM 1505687 F4187 CB187 Tripped on Phase OC Red Phase 2583A Yellow Phase 2570A No auto reclose on this feeder found tree down on Chaytors Rd near Sub355026. Confident the tree had made contact with 11kV lines but was now clear and been cut up. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 860 | 2024-09-27-0189 | Godfrey Road - ABS15311-B | CB5367 Godfrey Road | 2024-09-27 09:28 | 2024-09-27 12:57 | 0.0076544 | 3.68e-05 | 1 | 208 | Planned | Planned interruption | SH63 Planned Work http://nams.mll.co.nz/Schedule/Edit/3937 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 861 | 2024-09-27-0190 | Kaituna - 0007705051ML9D7 | CB5448 Kaituna | 2024-09-27 13:22 | 2024-09-27 15:24 | 0 | 0 | 1 | 122 | Unplanned | Unknown | Blown fuse on builders temp service EAM 1505765 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 862 | 2024-09-28-0195 | Redwood St Nth - 0001105343MLE02 | CB1655-Redwood St Nth | 2024-09-28 15:41 | 2024-09-28 16:41 | 0 | 0 | 1 | 61 | Unplanned | Defective equipment | Blown 30A HRC, suspect internal 1505802 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 863 | 2024-09-28-0192 | Richmond Brook - 0005502601ML613 | CB1250-Richmond Brook | 2024-09-28 20:01 | 2024-09-28 21:20 | 0 | 0 | 1 | 80 | Unplanned | Defective equipment | Burnt fuse carrier EAM 1505803 Flickering Power - pole fuse is sparking out on the road. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 864 | 2024-09-28-0193 | Richmond Brook - 0005505500MLD35 | CB1250-Richmond Brook | 2024-09-28 20:11 | 2024-09-28 21:40 | 0 | 0 | 1 | 89 | Unplanned | Other Cause | Internal fault, no loss of supply EAM 1505804 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 865 | 2024-09-30-0196 | Sounds - SUB325221 | REC1170-Sounds | 2024-09-30 07:58 | 2024-09-30 13:17 | 0.011702 | 3.68e-05 | 1 | 318 | Unplanned | Adverse weather | Found 1 blown TX fuse. Suspect lightening . EAM 1505819 F4195 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 866 | 2024-09-30-0197 | Wairau Valley - SUB3414GN | CB5399 Wairau Valley | 2024-09-30 08:30 | 2024-09-30 14:03 | 0.024509 | 7.36e-05 | 2 | 666 | Planned | Planned interruption | Planned shutdown to remove centre conductor. EAM 1463060 SAF 4076 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 867 | 2024-09-30-0198 | Dashwood - ABS15409-B | CB1252-Dashwood | 2024-09-30 08:38 | 2024-09-30 14:18 | 0.17517 | 0.0005152 | 14 | 4760 | Planned | Planned interruption | Taylor pass Road Planned Work http://nams.mll.co.nz/Schedule/Edit/4008 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 868 | 2024-09-30-0199 | Waikawa - SUB330101 | CB109- Waikawa | 2024-09-30 08:59 | 2024-09-30 11:42 | 0.053985 | 0.0003312 | 9 | 1467 | Planned | Planned interruption | Port Underwood Rd Planned Work http://nams.mll.co.nz/Schedule/Edit/3979 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 869 | 2024-09-30-0200 | Havelock Canvastown - LVUG160216 | CB103 Havelock Canvastown | 2024-09-30 09:15 | 2024-09-30 10:51 | 0 | 0 | 4 | 384 | Planned | Planned interruption | Planned shutdown to install spreader bars and repair LV lines due to clashing in wind. EAM 1505476 SAF 4429 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 870 | 2024-09-30-0201 | Buller St - 0006606574MLCFD | CB108-Buller St | 2024-09-30 12:52 | 2024-09-30 15:38 | 0 | 0 | 1 | 167 | Unplanned | Defective equipment | Blown fuse replaced EAM 1505961 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 871 | 2024-09-30-0202 | Wairau Valley - 0002279185ML423 | CB5399 Wairau Valley | 2024-09-30 16:10 | 2024-09-30 18:16 | 0 | 0 | 1 | 126 | Unplanned | Defective equipment | Burnt service fuse carrier replaced EAm 1506099 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 872 | 2024-10-01-0001 | Okaramio - ABS15426-B | CB104 Okaramio | 2024-10-01 08:30 | 2024-10-01 15:01 | 0.11511 | 0.0002944 | 8 | 3128 | Planned | Planned interruption | Planned shutdown to rebuild 11kV network at Okaramio EAM 1426402 SAF 4355 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 873 | 2024-10-01-0002 | Richmond Brook - SUB353163 | CB1250-Richmond Brook | 2024-10-01 11:19 | 2024-10-01 17:31 | 0.041069 | 0.0001104 | 3 | 1116 | Planned | Planned interruption | Replace IR pole NZ2307 with 9m TP pole. SAF 4447 EAM 1504562 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 874 | 2024-10-01-0003 | Scotland St - 0006607209ML859 | CB54-Scotland St | 2024-10-01 17:50 | 2024-10-02 16:38 | 0 | 0 | 1 | 1368 | Unplanned | Defective equipment | MLL has done a safety disconnection Before reconnection an COC will be required. Internal fault on red phase, blew fuse straight away. EAM 150637 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 875 | 2024-10-01-0007 | Weld St - SUB3700DT | CB71-Weld St | 2024-10-01 18:25 | 2024-10-01 20:14 | 0 | 0 | 114 | 12102 | Unplanned | Human error | GEN9 onsite in Maxwell Rd for replacement of RMU (SAF4389). Reports received for smoke coming from GEN. Gen 9 Shutdown, Replaced by Gen7 power restored. Cause of issue was curtains being left shut on GEN9 while running. http://nams.mll.co.nz/Schedule/Edit | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 876 | 2024-10-02-0008 | Weld St - 0001188597ML149 | CB71-Weld St | 2024-10-02 07:37 | 2024-10-02 08:09 | 0 | 0 | 1 | 32 | Unplanned | Defective equipment | burnt out pole fuse Old age EAM 1506396 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 877 | 2024-10-02-0009 | Richmond Brook - FUSE3409 | CB1250-Richmond Brook | 2024-10-02 08:08 | 2024-10-02 10:54 | 0.013322 | 0.0001472 | 4 | 362 | Unplanned | Unknown | 2 x Blown fuses found at 11kV FUSE3409 Line Patrol carried out nothing obvious found Fuses replaced and power confirmed restored EAM1506418 NAMS F4204 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 878 | 2024-10-02-0010 | Scotland St - LVOH307-S2844 | CB54-Scotland St | 2024-10-02 08:45 | 2024-10-02 13:16 | 0 | 0 | 7 | 1904 | Planned | Planned interruption | Market Street Planned Work - Replace pole PT5709 with new 9.5M Busck http://nams.mll.co.nz/Schedule/Edit/3868 EAM1484927 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 879 | 2024-10-02-0011 | Wairau Valley - FUSE3964 | CB5399 Wairau Valley | 2024-10-02 08:57 | 2024-10-02 10:47 | 0.004048 | 3.68e-05 | 1 | 110 | Planned | Planned interruption | Connection of upgraded earths at 11kV FUSE3964 EAM1409680 NAMS3909 2/10/2024 9:52:55 am | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 880 | 2024-10-02-0012 | Redwood St Nth - 0001106205ML6CC | CB1655-Redwood St Nth | 2024-10-02 10:50 | 2024-10-02 11:11 | 0 | 0 | 1 | 20 | Planned | Planned interruption | Outage created to reflect. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 881 | 2024-10-02-0014 | Waihopai Valley - 0000050558MLAFC | CB5493 Waihopai Valley | 2024-10-02 15:25 | 2024-10-02 15:56 | 0 | 0 | 1 | 31 | Unplanned | Defective equipment | Blown pole fuse due to lose wire in grinder | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 882 | 2024-10-02-0015 | Howick Rd North - 0001173228ML95B | CB84-Howick Rd North | 2024-10-02 21:18 | 2024-10-02 22:01 | 0 | 0 | 1 | 43 | Unplanned | Defective equipment | Burnt out outgoing lead, replaced fuse carrier EAM 1506707 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 883 | 2024-10-03-0017 | Richmond Brook - 0005505589ML62E | CB1250-Richmond Brook | 2024-10-03 14:06 | 2024-10-03 15:56 | 0 | 0 | 1 | 111 | Unplanned | Unknown | All 3 fuses blown. Have replaced, tested with meggar all going EAM 1506928 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 884 | 2024-10-04-0018 | Spring Creek - 0003340205MLD33 | CB187-Spring Creek | 2024-10-04 08:15 | 2024-10-04 11:46 | 0 | 0 | 1 | 211 | Planned | Planned interruption | Gouland Road Planned Work http://nams.mll.co.nz/Schedule/Edit/4023 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 885 | 2024-10-04-0019 | Spring Creek - LVOH200031-S100 | CB187-Spring Creek | 2024-10-04 08:22 | 2024-10-04 10:20 | 0 | 0 | 1 | 119 | Planned | Planned interruption | Gouland Road Planned Work http://nams.mll.co.nz/Schedule/Edit/4023 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 886 | 2024-10-04-0020 | Spring Creek - LVOH200030-S100 | CB187-Spring Creek | 2024-10-04 08:22 | 2024-10-04 10:20 | 0 | 0 | 1 | 119 | Planned | Planned interruption | Gouland Road Planned Work http://nams.mll.co.nz/Schedule/Edit/4023 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 887 | 2024-10-04-0021 | Woodbourne - 0000010367MLF49 | CB1178-Woodbourne | 2024-10-04 08:30 | 2024-10-04 11:14 | 0 | 0 | 1 | 164 | Planned | Planned interruption | Planned shutdown to replace red tagged pole. EAM 1446876 SAF 4327 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 888 | 2024-10-04-0022 | Waikawa - 0006624310MLE8C | CB109- Waikawa | 2024-10-04 10:22 | 2024-10-04 12:19 | 0 | 0 | 1 | 118 | Unplanned | Unknown | Blown 60A fuse, unknown cause EAM 1507071, Part power, 3PH 60A supply | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 889 | 2024-10-04-0023 | Taylor Pass - FUSE2035 | CB1089-Taylor Pass | 2024-10-04 11:50 | 2024-10-04 16:47 | 0 | 0 | 3 | 894 | Unplanned | Wildlife | F4216 Blown 11kV fuse 2035 at Iso Sub. Line not patrolled on North side. Fuse blew again on trial livening. found dead kingfisher hanging off juper and in contact with crossarm at pole PT2783 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 890 | 2024-10-04-0024 | Waihopai Valley - SUB3410DG | CB5493 Waihopai Valley | 2024-10-04 12:27 | 2024-10-04 13:53 | 0.006256 | 7.36e-05 | 2 | 170 | Planned | Planned interruption | Planned shutdown for mains alteration. EAM 1471090 SAF 4369 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 891 | 2024-10-04-0030 | Weld St - SUB3700DT | CB71-Weld St | 2024-10-04 16:00 | 2024-10-04 16:09 | 0 | 0 | 114 | 1026 | Planned | Planned interruption | Short shutdown at SUB3700DT to remove generator EAM1413529 NAMS4389 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 892 | 2024-10-04-0031 | Redwood St Sth - 0001183445MLA6A | CB1673-Redwood St Sth | 2024-10-04 23:52 | 2024-10-05 00:51 | 0 | 0 | 1 | 59 | Unplanned | Defective equipment | Failed 30-amp HRC , at time only drawing 1.5 amp and over phase 4 amps. letter needs to be sent. they have a pool the must get heated | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 893 | 2024-10-05-0033 | Taylor Pass - 0001194560MLFF5 | CB1089-Taylor Pass | 2024-10-05 11:30 | 2024-10-05 12:52 | 0 | 0 | 1 | 82 | Unplanned | Defective equipment | outgoing lead burnt off; Moved service to spare fuse carrier - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 894 | 2024-10-06-0034 | Sounds - 0008814326ML98E | REC1170-Sounds | 2024-10-06 18:23 | 2024-10-07 12:07 | 0 | 0 | 1 | 1065 | Unplanned | Third party interference | Link pulled in meterboard - suspect that they did not want the video camera catching them (place had been ransacked and internal wiring cut by Burglars) W/O1507202 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 895 | 2024-10-07-0035 | Ward - SUB352433 | REC31-Ward | 2024-10-07 08:30 | 2024-10-07 14:35 | 0.18753 | 0.0005152 | 14 | 5096 | Planned | Planned interruption | Carrol St Planned Work - Replace all x-arms on pole AK1569 & ER4144 http://nams.mll.co.nz/Schedule/Edit/4116 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 896 | 2024-10-07-0036 | Havelock Canvastown - LVOH7899 | CB103 Havelock Canvastown | 2024-10-07 09:00 | 2024-10-07 11:30 | 0 | 0 | 1 | 150 | Planned | Planned interruption | Planns shutdown for vegetation removal around pole KB4611 EAM1464532 NAMS4443 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 897 | 2024-10-07-0037 | Sounds - 0008813078ML57E | REC1170-Sounds | 2024-10-07 15:37 | 2024-10-08 13:50 | 0 | 0 | 1 | 1333 | Unplanned | Unknown | Blown 30amp Pole fuse EAM 1507320 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 898 | 2024-10-07-0038 | Seaview - 0005505350ML33B | CB1251-Seaview | 2024-10-07 16:06 | 2024-10-07 17:20 | 0.0027232 | 3.68e-05 | 1 | 74 | Unplanned | Wildlife | 2 x blown fuses found at Pole AP2473 (FUSE3133) Dead magpie found under pole Power confirmed restored EAM 1507336 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 899 | 2024-10-08-0039 | Taylor Pass - SUB3700DD-P2 | CB1089-Taylor Pass | 2024-10-08 06:32 | 2024-10-08 11:25 | 0 | 0 | 108 | 5242 | Unplanned | Defective equipment | Found scorched SFB14 Hope Drive due to flashover.Replaced SFB and terminations. W/O 1507339 http://nams.mll.co.nz/Schedule/Edit/4231 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 900 | 2024-10-08-0042 | Godfrey Road - LVUG1353 | CB5367 Godfrey Road | 2024-10-08 08:30 | 2024-10-08 14:22 | 0 | 0 | 9 | 3168 | Planned | Planned interruption | Planned shutdown to connect new LV cable for subdivision extn. EAM 1480175 SAF 4385 J | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 901 | 2024-10-08-0043 | Okaramio - HVOH2732-S17926 | CB104 Okaramio | 2024-10-08 08:49 | 2024-10-08 15:07 | 0.20866 | 0.000552 | 15 | 5670 | Planned | Planned interruption | Plannd shutdown for Okaramio rebuild stage 2. SAF 4356 - WO 1426402 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 902 | 2024-10-08-0044 | Richmond Brook - ABS1931-B | CB1250-Richmond Brook | 2024-10-08 11:04 | 2024-10-08 14:19 | 0.014278 | 7.36e-05 | 2 | 388 | Unplanned | Unknown | Blown fuse 3434 and blown LA Permit taken to remove the LA from the circuit EAM 1507408 http://nams.mll.co.nz/Schedule/Edit/4233 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 903 | 2024-10-08-0045 | Koromiko - 0006609345ML826 | CB55-Koromiko | 2024-10-08 19:47 | 2024-10-08 21:15 | 0 | 0 | 1 | 88 | Unplanned | Adverse weather | Combination of wind and slack service line caused the conductors to clash and break to neutral conductor. Repaired and rstored power at 2115. EAM 1507537 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 904 | 2024-10-09-0046 | Okaramio - FUSE3272 | CB104 Okaramio | 2024-10-09 07:04 | 2024-10-09 09:05 | 0.019872 | 0.0002944 | 8 | 540 | Unplanned | Wildlife | 1x blown fuse found at FUSE3272 and a dead duck under the 11kV lines. Fuses replaced (15A). EAM 1507552 F4239 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 905 | 2024-10-09-0047 | Sounds - SUB325995 | REC1170-Sounds | 2024-10-09 08:45 | 2024-10-09 09:50 | 0.004784 | 7.36e-05 | 2 | 130 | Planned | Planned interruption | Removal of redundant LVOH from SUB325995 in Nikau Bay SAF4445 EAM 1502162 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 906 | 2024-10-09-0048 | Waikawa - FUSE22090 | CB109- Waikawa | 2024-10-09 09:00 | 2024-10-09 12:04 | 0 | 0 | 24 | 4392 | Planned | Planned interruption | Planned shutdown to replace LV crossarms. EAM 1504938 SAF 4420 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 907 | 2024-10-09-0049 | Koromiko - SUB331129 | CB55-Koromiko | 2024-10-09 09:20 | 2024-10-09 11:20 | 0.0087584 | 7.36e-05 | 2 | 238 | Planned | Planned interruption | Planned shutdown to replace TX earths. EAM 1499714 SAF 4405 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 908 | 2024-10-09-0050 | Richmond Brook - 0005505760ML8C2 | CB1250-Richmond Brook | 2024-10-09 11:08 | 2024-10-09 15:30 | 0 | 0 | 1 | 262 | Unplanned | Defective equipment | Faulty service fuse holder replaced | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 909 | 2024-10-10-0051 | Waikawa - LVUG99385 | CB109- Waikawa | 2024-10-10 08:30 | 2024-10-10 14:00 | 0 | 0 | 16 | 5280 | Planned | Planned interruption | Planned shutdown to replace SFB EAM1502196 SAF4397 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 910 | 2024-10-10-0052 | Okaramio - HVOH2732-S17926 | CB104 Okaramio | 2024-10-10 08:38 | 2024-10-10 14:47 | 0.20424 | 0.000552 | 15 | 5550 | Planned | Planned interruption | Okaramio Planned Work http://nams.mll.co.nz/Schedule/Edit/4207 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 911 | 2024-10-10-0053 | Murphys Rd - LVUG1328 | CB68-Murphys Rd | 2024-10-10 08:47 | 2024-10-10 12:23 | 0 | 0 | 3 | 648 | Planned | Planned interruption | Planned shutdown to shift LV cable onto new SUB3700RD. EAM1465504 SAF 4362 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 912 | 2024-10-10-0055 | Waihopai Valley - SUB3410GF | CB5493 Waihopai Valley | 2024-10-10 12:56 | 2024-10-10 14:15 | 0.0029072 | 3.68e-05 | 1 | 79 | Unplanned | Unknown | Blown 11kV fuse at SUB3410GF Cause unknown 1508747 http://nams.mll.co.nz/Schedule/Edit/4250 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 913 | 2024-10-11-0056 | Murphys Rd - 0001121428MLF69 | CB68-Murphys Rd | 2024-10-11 14:56 | 2024-10-11 16:02 | 0 | 0 | 1 | 67 | Unplanned | Unknown | Blown pole fuse - Cause unknown EAM 1508933 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 914 | 2024-10-12-0057 | Sounds - 0008811180MLD39 | REC1170-Sounds | 2024-10-12 12:25 | 2024-10-12 17:30 | 0 | 0 | 1 | 306 | Unplanned | Third party interference | Service cable cut in half by excavator. Jointed cable back, completed the relevant tests and livened. Power restored 1730. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 915 | 2024-10-14-0059 | Tuamarina - LVOH2722 | CB188-Tuamarina | 2024-10-14 08:30 | 2024-10-14 14:15 | 0 | 0 | 2 | 690 | Planned | Planned interruption | Replacement of poles NZ2508 & NZ2509 NAMS4367 EAM1497931 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 916 | 2024-10-14-0058 | Godfrey Road - REC5183 | CB5367 Godfrey Road | 2024-10-14 08:31 | 2024-10-14 16:10 | 0.25337 | 0.000552 | 15 | 6885 | Planned | Planned interruption | Paynters Rd Line Rebuild - SD1 SAF4392 - WO 1436033 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 917 | 2024-10-14-0060 | Waikawa - 0006603539ML623 | CB109- Waikawa | 2024-10-14 09:09 | 2024-10-14 11:10 | 0 | 0 | 1 | 121 | Unplanned | Defective equipment | Blown pole fuse, after issue with Stove. EAM 1509002 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 918 | 2024-10-14-0061 | East Coast - 0005515281ML3D9 | REC29-East Coast | 2024-10-14 15:18 | 2024-10-14 17:50 | 0 | 0 | 1 | 153 | Unplanned | Defective equipment | Blown 30A RW fuse, replaced and restored 1750. EAM 1509155 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 919 | 2024-10-14-0062 | Renwick Township - FUSE22011 | CB5482 Renwick Township | 2024-10-14 15:34 | 2024-10-14 18:19 | 0 | 0 | 6 | 984 | Unplanned | Defective equipment | Blue phase lucy fuse burnt out at FUSE22011. Replaced using WI16 and relivened. COnfirmed voltage OK at 1 EAM 1509156 http://nams.mll.co.nz/Schedule/Edit/4274 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 920 | 2024-10-14-0064 | Hutcheson St - 0001101108MLEF4 | CB49-Hutcheson St | 2024-10-14 17:06 | 2024-10-14 20:05 | 0 | 0 | 1 | 179 | Planned | Planned interruption | LV shutdown for the replacement of DP95 Market St. Outage 1 of 2 due to modelling SAF 4393 EAM 1453954 O | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 921 | 2024-10-14-0065 | Hutcheson St - 0001101107ML12A | CB49-Hutcheson St | 2024-10-14 17:06 | 2024-10-14 20:05 | 0 | 0 | 1 | 179 | Planned | Planned interruption | LV shutdown for the replacement of DP95 Market St. Outage 2 of 2 due to modelling SAF 4393 EAM 1453954 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 922 | 2024-10-14-0063 | Grassmere - 0005506369ML872 | CB1253-Grassmere | 2024-10-14 18:16 | 2024-10-14 18:50 | 0 | 0 | 1 | 35 | Unplanned | Other cause | Blown 30A pole fuse, possible overloading but didnt check on how much current was flowing. Restored 1850. EAM 1509164 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 923 | 2024-10-15-0066 | Dry Hills - SUB348561 | CB1682-Dry Hills | 2024-10-15 07:17 | 2024-10-15 15:55 | 0.10282 | 0.0004416 | 6 | 2794 | Unplanned | Defective equipment | Loose / broken connection on LV fed from SUB 348561 - TX Shutdown to repair http://nams.mll.co.nz/Schedule/Edit/4275 TX Relivened however LV Line found down. TX Isolated again and permit taken to repair LV EAM 1509191 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 924 | 2024-10-15-0067 | Hospital Rd East - LVUG253 | CB39-Hospital Rd East | 2024-10-15 08:30 | 2024-10-15 14:14 | 0 | 0 | 18 | 3424 | Planned | Planned interruption | Planned shutdown for meterboard replacement in tee jointed area. SAF 4442 EAM 1502965 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 925 | 2024-10-15-0068 | Godfrey Road - REC5183 | CB5367 Godfrey Road | 2024-10-15 08:33 | 2024-10-15 17:43 | 0.3036 | 0.000552 | 15 | 8250 | Planned | Planned interruption | Paynters Rd rebuild SD2 SAF4392.2 EAM 1436033 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 926 | 2024-10-15-0069 | Okaramio - SUB320173 | CB104 Okaramio | 2024-10-15 09:29 | 2024-10-15 13:16 | 0.0083536 | 3.68e-05 | 1 | 227 | Planned | Planned interruption | Due to access main line can not be shutdown. Job changed to 1 TX only to carry out that portion of the work. SUB320173 EAM14679222 SAF4089 http://nams.mll.co.nz/Schedule/Edit/3680 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 927 | 2024-10-15-0071 | Tuamarina - LVOH3837 | CB188-Tuamarina | 2024-10-15 10:45 | 2024-10-15 11:13 | 0 | 0 | 1 | 28 | Planned | Planned interruption | pulling up of low spans between RM2860 (ET2497) - JA1558 & RM2860 (ET2497) - NK1959 NAMS4421 EAM1504831 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 928 | 2024-10-16-0076 | Richmond Brook - REC37 | CB1250-Richmond Brook | 2024-10-15 21:57 | 2024-10-15 21:58 | 0 | 0 | 224 | 0 | Unplanned | Unknown | Successful reclose of REC37 Phase OC Cause unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 929 | 2024-10-16-0075 | Seaview - ABS1950-B | CB1251-Seaview | 2024-10-16 08:32 | 2024-10-16 14:32 | 0.053139 | 0.0001472 | 4 | 1444 | Planned | Planned interruption | Seaview Solar Farm Planned Work http://nams.mll.co.nz/Schedule/Edit/4136 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 930 | 2024-10-16-0073 | McLauchlan St - LVUG146270 | CB65 - McLauchlan St | 2024-10-16 08:33 | 2024-10-16 09:01 | 0 | 0 | 1 | 27 | Unplanned | Defective equipment | found burning fuse base at SFB3 Waipuna. Has opened main switch replace fuse base using WI. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 931 | 2024-10-16-0074 | Grassmere - FUSE3293 | CB1253-Grassmere | 2024-10-16 08:35 | 2024-10-16 10:41 | 0.0093472 | 7.36e-05 | 2 | 254 | Unplanned | Wildlife | Bird Strike http://nams.mll.co.nz/Schedule/Edit/4280 EAM 1509283 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 932 | 2024-10-17-0077 | Okaramio - HVOH2732-S17927 | CB104 Okaramio | 2024-10-17 08:30 | 2024-10-17 13:56 | 0.53985 | 0.001656 | 45 | 14670 | Planned | Planned interruption | Planned shutdown (9) for 11kV rebuild at Okaramio EAM1426402 SAF4354.1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 933 | 2024-10-17-0078 | Godfrey Road - REC5183 | CB5367 Godfrey Road | 2024-10-17 08:30 | 2024-10-17 15:44 | 0.23902 | 0.000552 | 15 | 6495 | Planned | Planned interruption | Planned shutdown for Paynters Rd rebuild http://nams.mll.linesmarl.co.nz/Application/Edit/4392 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 934 | 2024-10-17-0080 | Godfrey Road - SUB343261 | CB5367 Godfrey Road | 2024-10-17 17:54 | 2024-10-17 20:27 | 0.028152 | 0.000184 | 5 | 765 | Unplanned | Adverse weather | LV Lines down TX Isolated and earth permit issued for repair. 1509537 http://nams.mll.co.nz/Schedule/Edit/4286 Conductors clashing | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 935 | 2024-10-17-0081 | Hospital Rd West - 0001174236ML40D | CB47-Hospital Rd West | 2024-10-17 19:45 | 2024-10-17 21:05 | 0 | 0 | 1 | 79 | Unplanned | Third party interference | SFB was hit by an unknown vhicle causing the service fuse to fall out. Allconnections were checked and fuse restored. Power back on 2100. EAM 1509538 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 936 | 2024-10-18-0084 | Dry Hills - 0001113093MLD62 | CB1682-Dry Hills | 2024-10-17 21:45 | 2024-10-17 22:15 | 0 | 0 | 1 | 30 | Unplanned | Defective equipment | Burnt out Lv fuse in SFB. Replaced with new fuse,EAM 1509588 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 937 | 2024-10-18-0082 | Seafair - RMUF1300 | CB5098-Seafair | 2024-10-18 08:18 | 2024-10-18 10:43 | 0.005336 | 3.68e-05 | 1 | 145 | Planned | Planned interruption | Planned shutdown to replace leaking sight glass on Sub348006 EAM 1505296 SAF 4455 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 938 | 2024-10-18-0085 | Koromiko - SUB331121 | CB55-Koromiko | 2024-10-18 12:22 | 2024-10-18 14:15 | 0.012475 | 0.0001104 | 3 | 339 | Planned | Planned interruption | Planned shutdown for tree cutting at 177 Speeds Rd EAM 1215891 SAF 4446 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 939 | 2024-10-18-0086 | Murphys Rd - 0001121307ML2E0 | CB68-Murphys Rd | 2024-10-18 17:33 | 2024-10-18 18:49 | 0 | 0 | 1 | 77 | Unplanned | Defective equipment | Blown pole fuse due to internal issue. Isolated oven and replaced fuse. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 940 | 2024-10-19-0087 | Alabama Rd - 0001190323ML116 | CB1667-Alabama Rd | 2024-10-19 12:21 | 2024-10-19 13:42 | 0 | 0 | 1 | 81 | Unplanned | Defective equipment | Found a burntout fuse in gyro box. Replaced fuse and restored at 1342. EAM 1509672 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 941 | 2024-10-21-0090 | Vintage Lane - SUB342090 | CB171-Vintage Lane | 2024-10-21 08:30 | 2024-10-21 09:22 | 0 | 0 | 1 | 52 | Planned | Planned interruption | Connection of upgraded earths at SUB342090 EAM 1315051 http://nams.mll.linesmarl.co.nz/Application/Edit/4400 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 942 | 2024-10-21-0088 | Wairau Valley - ABS861-B | CB5399 Wairau Valley | 2024-10-21 08:30 | 2024-10-21 11:46 | 0.24523 | 0.0012512 | 34 | 6664 | Planned | Planned interruption | Planned shutdown in Lanark Lane for Liquid Action to install a pump under the 11kV SAF4458 - WO 1506907 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 943 | 2024-10-21-0089 | Godfrey Road - REC5183 | CB5367 Godfrey Road | 2024-10-21 08:34 | 2024-10-21 14:30 | 0.19651 | 0.000552 | 15 | 5340 | Planned | Planned interruption | 11kV Line rebuild in Paynters Rd SAF4392 - WO1436033 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 944 | 2024-10-21-0091 | Vintage Lane - SUB342082 | CB171-Vintage Lane | 2024-10-21 09:30 | 2024-10-21 10:38 | 0 | 0 | 3 | 204 | Planned | Planned interruption | Connection of upgraded earths at SUB342082 http://nams.mll.linesmarl.co.nz/Application/Edit/4400 EAM 1315051 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 945 | 2024-10-21-0092 | Woodbourne - CB1178 | CB1178-Woodbourne | 2024-10-21 11:03 | 2024-10-21 16:24 | 0.035438 | 0.0001104 | 3 | 963 | Planned | Planned interruption | Planned outage on the 11kV outside Woodbourne Sub for the installation of a new ZSS TX in the switchyard issued NESS SAF4509 - WO 1422168 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 946 | 2024-10-21-0093 | Spring Creek - SUB356187 | CB187-Spring Creek | 2024-10-21 11:35 | 2024-10-21 13:03 | 0 | 0 | 4 | 348 | Planned | Planned interruption | COnnection of upgraded earths at SUB356187 EAM 1409276 http://nams.mll.linesmarl.co.nz/Application/Edit/4399 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 947 | 2024-10-21-0094 | Tuamarina - SUB356126 | CB188-Tuamarina | 2024-10-21 13:28 | 2024-10-21 14:21 | 0 | 0 | 1 | 54 | Planned | Planned interruption | COnnection of upgraded earths at SUB356126 EAM 1409276 http://nams.mll.linesmarl.co.nz/Application/Edit/4399 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 948 | 2024-10-21-0095 | Scotland St - 0006608337MLC5E | CB54-Scotland St | 2024-10-21 15:09 | 2024-10-21 16:56 | 0 | 0 | 1 | 107 | Unplanned | Defective equipment | Replaced burnt out LV Fuse cut out. EAM 150973 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 949 | 2024-10-21-0096 | Weld St - 0001162109ML209 | CB71-Weld St | 2024-10-21 15:49 | 2024-10-21 17:39 | 0 | 0 | 1 | 111 | Unplanned | Unknown | Blown ppole fuse, unknown cause, replaced and relivened. EAM 1509739 2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 950 | 2024-10-21-0097 | Thomsons Ford Rd - 0001132549MLFD9 | CB1509-Thomsons Ford Rd | 2024-10-21 18:10 | 2024-10-21 19:13 | 0 | 0 | 1 | 63 | Unplanned | Defective equipment | Checked all connections in SFB, all okay. Found a tripped RCD on the meterboard. Power restored | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 951 | 2024-10-22-0099 | Dry Hills - LVUG2115 | CB1682-Dry Hills | 2024-10-22 08:30 | 2024-10-22 14:22 | 0 | 0 | 10 | 3510 | Planned | Planned interruption | Replacement of XA2515 SFB 34 Dry Hills Rise EAM1505933 NAMS4466 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 952 | 2024-10-22-0098 | Okaramio - ABS15426-B | CB104 Okaramio | 2024-10-22 08:31 | 2024-10-22 14:49 | 0.09763 | 0.0002576 | 7 | 2653 | Planned | Planned interruption | Planned shutdown for 11kV line rebuild. EAM 1426402 SAF 4354.3 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 953 | 2024-10-22-0100 | Grovetown - FUSE3905 | CB1465-Grovetown | 2024-10-22 09:05 | 2024-10-22 10:40 | 0.010378 | 0.0001104 | 3 | 282 | Planned | Planned interruption | Planned shutdown to allow MDC to remove a pump under the lines at SUB361161. SAF4494 No EAM number | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 954 | 2024-10-23-0101 | Grovetown - 0003350998ML660 | CB1465-Grovetown | 2024-10-23 06:40 | 2024-10-23 07:47 | 0 | 0 | 1 | 68 | Unplanned | Defective equipment | Blue Connector on pole faulty - have sent pictures to Maintenance Moved service from Blue to Yellow phase (at pole KB9108 Sub370271) EAM 1510040 2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 955 | 2024-10-23-0102 | East Coast - FUSE3733 | REC29-East Coast | 2024-10-23 08:33 | 2024-10-23 12:14 | 0.032531 | 0.0001472 | 4 | 884 | Planned | Planned interruption | Planned shutdown to remove redundant HV and TX. EAM 1491513 SAF 4314 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 956 | 2024-10-23-0103 | Thomsons Ford Rd - 0001132549MLFD9 | CB1509-Thomsons Ford Rd | 2024-10-23 09:00 | 2024-10-23 11:32 | 0 | 0 | 1 | 152 | Unplanned | Defective equipment | Our side good,one power point in house when using vacuum cleaner tripped breaker. EAM 1510068 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 957 | 2024-10-23-0104 | Waikawa - SUB330101 | CB109- Waikawa | 2024-10-23 09:08 | 2024-10-23 14:00 | 0 | 0 | 9 | 2628 | Planned | Planned interruption | Relocation of pole PT1051 EAM1492820 NAMS4469 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 958 | 2024-10-23-0105 | Grovetown - 0003350449ML26F | CB1465-Grovetown | 2024-10-23 09:31 | 2024-10-23 11:31 | 0 | 0 | 1 | 120 | Unplanned | Defective equipment | Faulty connection on sub. Rplaced clamp and power restored EAM 1510081 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 959 | 2024-10-23-0106 | Waikawa - LVUG333930 | CB109- Waikawa | 2024-10-23 10:17 | 2024-10-23 13:57 | 0 | 0 | 2 | 442 | Planned | Planned interruption | Replacement of SFB XA9878 EAM1493903 NAMS4505 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 960 | 2024-10-24-0108 | Okaramio - ABS15426-B | CB104 Okaramio | 2024-10-24 08:30 | 2024-10-24 14:28 | 0.092221 | 0.0002576 | 7 | 2506 | Planned | Planned interruption | Planned shutdown for Okaramio Line Rebuild stage 2 - SD11 SAF4354 WO 1426402 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 961 | 2024-10-24-0111 | Godfrey Road - RMUS1113-B | CB5367 Godfrey Road | 2024-10-24 08:30 | 2024-10-24 17:49 | 0.43122 | 0.0007728 | 21 | 11718 | Planned | Planned interruption | Planned shutdown to lower 11kV cable under drive way for subdivision entrance. EAM1480175 SAF4464 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 962 | 2024-10-24-0107 | Weld St - ABS385-B | CB71-Weld St | 2024-10-24 08:30 | 2024-10-24 11:38 | 0.19018 | 0.0037904 | 64 | 5168 | Planned | Planned interruption | Planned shutdown to allow Electrician to replace meterboard in a tee jointed subdivision. SAF 4453 EAM 1501484 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 963 | 2024-10-24-0109 | Waikawa - LVOH1357 | CB109- Waikawa | 2024-10-24 08:38 | 2024-10-24 11:46 | 0 | 0 | 20 | 3760 | Planned | Planned interruption | Replacement of LV arms on pole PT5506 EAM1504927 NAMS4468 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 964 | 2024-10-24-0110 | Waikawa - LVOH2460 | CB109- Waikawa | 2024-10-24 08:38 | 2024-10-24 11:46 | 0 | 0 | 33 | 6204 | Planned | Planned interruption | Replacement of LV arms on pole PT5506 EAM1504927 NAMS4468 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 965 | 2024-10-24-0112 | Rapaura Rd - SUB357018 | CB1077-Rapaura Rd | 2024-10-24 11:37 | 2024-10-24 14:09 | 0.0055936 | 3.68e-05 | 1 | 152 | Planned | Planned interruption | Planned Work http://nams.mll.co.nz/Schedule/Edit/4252 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 966 | 2024-10-24-0113 | Symons St - 0001156667ML6CC | CB50-Symons St | 2024-10-24 12:05 | 2024-10-24 13:45 | 0 | 0 | 1 | 100 | Unplanned | Defective equipment | 2 failed 60amp fuses Suspect sparky at fault EAM 1510417 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 967 | 2024-10-24-0114 | Scotland St - 0006611583MLDA1 | CB54-Scotland St | 2024-10-24 15:14 | 2024-10-24 18:15 | 0 | 0 | 1 | 182 | Unplanned | Defective equipment | failed fuse, replaced EAM 1510560 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 968 | 2024-10-24-0115 | French Pass - REC5024 | CB45-French Pass | 2024-10-24 15:25 | 2024-10-24 15:26 | 0 | 0 | 75 | 0 | Unplanned | Adverse weather | Succesful auto reclose on REC5024 at Saddle Hill. Phase OC. Cyclo351 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 969 | 2024-10-24-0117 | French Pass - REC5024 | CB45-French Pass | 2024-10-24 23:14 | 2024-10-24 23:15 | 0 | 0 | 75 | 0 | Unplanned | Adverse weather | Successful Auto Reclose on REC5024. Phase OC Cyclo 352 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 970 | 2024-10-25-0118 | French Pass - REC5024 | CB45-French Pass | 2024-10-25 00:38 | 2024-10-25 00:38 | 0 | 0 | 75 | 0 | Unplanned | Adverse weather | Succesful auto reclose on REC5024 Phase OC Cyclo 353 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 971 | 2024-10-25-0119 | French Pass - REC5024 | CB45-French Pass | 2024-10-25 00:48 | 2024-10-25 00:49 | 0 | 0 | 75 | 0 | Unplanned | Adverse weather | Succesful auto reclose on REC5024 Phase OC Cyclo 354 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 972 | 2024-10-25-0120 | French Pass - REC5024 | CB45-French Pass | 2024-10-25 00:56 | 2024-10-25 00:57 | 0 | 0 | 75 | 0 | Unplanned | Adverse weather | Succesful auto reclose on REC5024 Phase OC Cyclo 355 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 973 | 2024-10-25-0121 | French Pass - REC5024 | CB45-French Pass | 2024-10-25 01:03 | 2024-10-25 01:04 | 0 | 0 | 75 | 0 | Unplanned | Adverse weather | Succesful auto reclose on REC5024 Phase OC Cyclo 356 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 974 | 2024-10-25-0122 | French Pass - REC5024 | CB45-French Pass | 2024-10-25 01:10 | 2024-10-25 01:10 | 0.00276 | 0.00276 | 75 | 75 | Unplanned | Adverse weather | Succesful auto reclose on REC5024 Phase OC Cyclo 357 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 975 | 2024-10-25-0123 | French Pass - REC5024 | CB45-French Pass | 2024-10-25 02:27 | 2024-10-25 02:27 | 0.00276 | 0.00276 | 75 | 75 | Unplanned | Adverse weather | Succesful auto reclose on REC5024 Phase OC Cyclo 358 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 976 | 2024-10-25-0125 | French Pass - REC5024 | CB45-French Pass | 2024-10-25 04:08 | 2024-10-25 04:09 | 0 | 0 | 75 | 0 | Unplanned | Adverse weather | Succesful Auto Reclose on phase OC. Cyclo 359 Storm conditions | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 977 | 2024-10-25-0126 | French Pass - REC5024 | CB45-French Pass | 2024-10-25 04:16 | 2024-10-25 04:16 | 0.00276 | 0.00276 | 75 | 75 | Unplanned | Adverse weather | Succesful Auto Reclose on phase OC. Cyclo 360 Storm conditions | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 978 | 2024-10-25-0127 | French Pass - REC5024 | CB45-French Pass | 2024-10-25 05:18 | 2024-10-25 05:18 | 0.00276 | 0.00276 | 75 | 75 | Unplanned | Adverse weather | Succesful Auto Reclose on phase OC. Cyclo 361 Storm conditions | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 979 | 2024-10-25-0128 | Symons St - RMUF1084 | CB50-Symons St | 2024-10-25 08:30 | 2024-10-25 14:51 | 0.042062 | 0.0001104 | 3 | 1143 | Planned | Planned interruption | Planned shutdown for RMU replacement outside Noel Leeming SAF 4417 EAM 1417791 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 980 | 2024-10-25-0129 | Dashwood - FUSE2483 | CB1252-Dashwood | 2024-10-25 08:38 | 2024-10-25 14:27 | 0.24402 | 0.0006992 | 19 | 6631 | Planned | Planned interruption | Various maintenance works in Dumgree Rd. SAF4282 WO 1491418 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 981 | 2024-10-25-0132 | Omaka - 0002270087ML102 | CB1088 - Omaka | 2024-10-25 08:38 | 2024-10-25 10:03 | 0 | 0 | 1 | 85 | Planned | Planned interruption | Planned shutdown to replace red tagged pole. EAM1487119 SAF4514 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 982 | 2024-10-25-0130 | Buller St - FUSE2213 | CB108-Buller St | 2024-10-25 10:29 | 2024-10-31 21:20 | 0.35405 | 0.0011408 | 31 | 9621 | Unplanned | Third party interference | 11kV Cable damaged while Contractors were removing bollards. isolated at fuse 2213 and Issuer Earths applied below fuses. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 983 | 2024-10-29-0139 | Howick Rd North - 0001173441MLEFC | CB84-Howick Rd North | 2024-10-26 11:48 | 2024-10-26 14:12 | 0 | 0 | 1 | 144 | Unplanned | Defective equipment | Blown 30A Rewireable fuse, conductors shorting at mains entry, repairs made. Holders need to be changed to IPC at some stage EAM 1510782 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 984 | 2024-10-26-0133 | Sounds - REC1350 | REC1170-Sounds | 2024-10-26 12:17 | 2024-10-29 14:09 | 14.9583 | 0.027526 | 748 | 406476 | Unplanned | Vegetation | EAM 1510783 NAMS F4308 Island Point Recloser opened on earth fault. No fault detected. Unable to connect to Kenepuru Generators due to comms issues. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 985 | 2024-10-26-0134 | Tuamarina - REC5262 | CB188-Tuamarina | 2024-10-26 18:13 | 2024-10-26 18:29 | 0.13542 | 0.011702 | 318 | 3680 | Unplanned | Third party interference | REC5262 opened for safety after CB188 Tripped at Spring Creek. Area was down one phase so back fed via REC5204 to restore customers. See EAM 1510784 & 2024-10-26-0135 for main outage. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 986 | 2024-10-26-0135 | Tuamarina - CB188 | CB188-Tuamarina | 2024-10-26 18:14 | 2024-10-30 12:04 | 0.54324 | 0.0088688 | 167 | 14762 | Unplanned | Adverse weather | CB 188 tripped on Phase OC RED 110 A Yellow 2402 A Blue 2313 A Neutral 5 A Cyclo 107 Milsoft 2024-10-26-0134 61.33 hrs ( Opened REC5262 as one phase showing no volts and backfed via REC5204) Patroll found missing a phase at SUB356121. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 987 | 2024-10-28-0138 | Wairau Valley - 0002278758ML19C | CB5399 Wairau Valley | 2024-10-28 08:52 | 2024-10-28 12:18 | 0 | 0 | 1 | 206 | Unplanned | Defective equipment | Burnt fuse carrier - Replaced EAM 1510785 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 988 | 2024-10-29-0140 | Ward - LVOH5627 | REC31-Ward | 2024-10-29 10:00 | 2024-10-29 11:30 | 0 | 0 | 3 | 270 | Planned | Planned interruption | Pole straightening at AE2316 EAM1504939 NAMS4430 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 989 | 2024-10-29-0144 | Waihopai Valley - FUSE4070 | CB5493 Waihopai Valley | 2024-10-29 13:28 | 2024-11-01 15:24 | 0.21679 | 0.0001472 | 4 | 5891 | Unplanned | Third party interference | Broken pole MA2070 due to suspected strike by tractor. Pole and TX replaced, LV serice reconnected EAM1510870 NAMS F4312 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 990 | 2024-10-29-0143 | Waihopai Valley - CB5493 | CB5493 Waihopai Valley | 2024-10-29 13:59 | 2024-10-29 14:17 | 0.15235 | 0.008464 | 230 | 4140 | Unplanned | Third party interference | CB5493 opened for safetyy due to broken pole MA2073 at SUB3410AV. http://nams.mll.co.nz/Schedule/Edit/4312 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 991 | 2024-10-29-0145 | Craiglochart - 0002272457ML301 | REC1391-Craiglochart | 2024-10-29 16:02 | 2024-10-29 18:14 | 0 | 0 | 1 | 131 | Unplanned | Defective equipment | Blown fuse on blue phase for service. no cause found EAM 1510950 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 992 | 2024-10-30-0146 | Spring Creek - CB187 | CB187-Spring Creek | 2024-10-30 05:40 | 2024-10-30 06:10 | 0.63104 | 0.027048 | 735 | 17148 | Unplanned | Unknown | 05:40 CB187 Tripped Red 2475 A Yel 2420 A Blu 69 A Power restored in sections from CB187 , REC5105, REC5204, REC5262 Line patrol carried out nothing obvious found EAM1510957 NAMS F4314 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 993 | 2024-10-30-0148 | Scotland St - 0006606605ML6E6 | CB54-Scotland St | 2024-10-30 08:37 | 2024-10-30 10:27 | 0 | 0 | 1 | 110 | Unplanned | Defective equipment | Burnt out fuse holder - Power restored EAM 1510983 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 994 | 2024-10-30-0150 | Grovetown - SUB361125 | CB1465-Grovetown | 2024-10-30 09:07 | 2024-10-30 10:37 | 0 | 0 | 3 | 270 | Planned | Planned interruption | Planned shutdown to replace LV cross arms EAM1505457 NAMS4457 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 995 | 2024-10-30-0149 | Seymour St - 0001166125MLAC2 | CB51-Seymour St | 2024-10-30 09:09 | 2024-10-30 09:52 | 0 | 0 | 1 | 44 | Unplanned | Defective equipment | Internal fuse caused issue EAM 1510991 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 996 | 2024-10-30-0151 | Redwood St Sth - CB1673 | CB1673-Redwood St Sth | 2024-10-30 09:42 | 2024-10-30 18:02 | 0.82549 | 0.026643 | 724 | 22432 | Unplanned | Defective equipment | EAM1511006 NAMSF4315 Report from member of public that Power box on fire. Fire service called. Power de-energized from CB1673 SFB15 Glenhill Drive burnt to ground. SFB15 Glenhill Drive isolated at SUB3700BF SFB15 to be replaced | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 997 | 2024-10-30-0156 | Hospital Rd East - 0001189383MLD48 | CB39-Hospital Rd East | 2024-10-30 13:25 | 2024-10-30 14:03 | 0 | 0 | 1 | 39 | Unplanned | Unknown | Customer has had part power since the feeder shutdown due to buring gyro in Glenhill Place Power confirmed OK when onsite | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 998 | 2024-10-30-0155 | Seymour St - 0001163257MLB39 | CB51-Seymour St | 2024-10-30 14:42 | 2024-10-30 16:04 | 0 | 0 | 1 | 83 | Unplanned | Defective equipment | Blown HRC fuse suspect overloading EAM 1511107 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 999 | 2024-10-30-0157 | Hospital Rd East - ABS492 | CB39-Hospital Rd East | 2024-10-30 17:52 | 2024-10-30 18:01 | 0 | 0 | 95 | 855 | Unplanned | Unknown | Related to Glenhill Drive outage during restoration 2024-10-30-0151 EAM1511006 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1000 | 2024-10-30-0159 | Pelorus - 0007713241ML45C | CB5126-Pelorus | 2024-10-30 21:32 | 2024-10-31 10:00 | 0 | 0 | 1 | 749 | Unplanned | Unknown | 2x LV fuses blown, power restored EAM 1511148 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1001 | 2024-10-30-0160 | Wairau Valley - REC87 | CB5399 Wairau Valley | 2024-10-30 21:49 | 2024-10-30 22:13 | 0.11272 | 0.0052992 | 144 | 3063 | Unplanned | Unknown | REC87 Tripped Phase OC. Close attempt after 15mins. Power restored. EAM1511149 NAMS F4319 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1002 | 2024-10-31-0161 | Richmond Brook - ABS1931-B | CB1250-Richmond Brook | 2024-10-31 09:02 | 2024-10-31 11:00 | 0.0086112 | 7.36e-05 | 2 | 234 | Planned | Planned interruption | Replace lightning arrestors LA3424 on pole ET4961 and straighten pole EAM1508577 NAMS4486 -- | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1003 | 2024-10-31-0162 | Sounds - 0008814153MLB9B | REC1170-Sounds | 2024-10-31 10:00 | 2024-11-06 13:23 | 0 | 0 | 1 | 10599 | Unplanned | Defective equipment | connection reconnected Have sent email see if t 2 LM available to assist Boat booked for 11am departure EAM 1511176 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1004 | 2024-10-31-0163 | Hutcheson St - 0001102525ML21B | CB49-Hutcheson St | 2024-10-31 10:00 | 2024-10-31 10:17 | 0 | 0 | 1 | 17 | Planned | Planned interruption | Planned shutdown to disconnect LV cable in Andelect Box for future DP22 Arthur St replacement project. EAM 300095 SAF 4532 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1005 | 2024-10-31-0164 | Hutcheson St - 0001102041ML9E4 | CB49-Hutcheson St | 2024-10-31 10:00 | 2024-10-31 10:17 | 0 | 0 | 1 | 17 | Planned | Planned interruption | Planned shutdown to disconnect LV cable in Andelect Box for future DP22 Arthur St replacement project. EAM 300095 SAF 4532 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1006 | 2024-10-31-0165 | Renwick Township - 0000050308ML4F2 | CB5482 Renwick Township | 2024-10-31 12:15 | 2024-10-31 12:40 | 0 | 0 | 1 | 25 | Unplanned | Third party interference | DP 40 damaged. disconnecting Services and re-tightening service cable connections in DP. EAM1511177 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1007 | 2024-10-31-0166 | Renwick Township - 0000050315ML104 | CB5482 Renwick Township | 2024-10-31 12:15 | 2024-10-31 12:40 | 0 | 0 | 1 | 25 | Unplanned | Third party interference | DP 40 damaged. disconnecting Services and re-tightening service cable connections in DP. EAM1511177 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1008 | 2024-10-31-0167 | Renwick Township - 0000050311ML00E | CB5482 Renwick Township | 2024-10-31 12:15 | 2024-10-31 12:40 | 0.00092 | 3.68e-05 | 1 | 25 | Unplanned | Third party interference | DP 40 damaged. disconnecting Services and re-tightening service cable connections in DP. EAM1511177 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1009 | 2024-10-31-0168 | Renwick Township - 0000050312MLCCE | CB5482 Renwick Township | 2024-10-31 12:15 | 2024-10-31 12:40 | 0 | 0 | 1 | 25 | Unplanned | Third party interference | DP 40 damaged. disconnecting Services and re-tightening service cable connections in DP. EAM1511177 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1010 | 2024-10-31-0169 | Renwick Township - 0000050309ML8B7 | CB5482 Renwick Township | 2024-10-31 12:15 | 2024-10-31 12:40 | 0 | 0 | 1 | 25 | Unplanned | Third party interference | DP 40 damaged.disconnecting Services and re-tightening service cable connections in DP. EAM1511177 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1011 | 2024-10-31-0170 | Renwick Township - 0000050002ML560 | CB5482 Renwick Township | 2024-10-31 12:15 | 2024-10-31 12:40 | 0 | 0 | 1 | 25 | Unplanned | Third party interference | DP 40 damaged disconnecting Services and re-tightening service cable connections in DP. EAM1511177 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1012 | 2024-10-31-0171 | McLauchlan St - 0001130429MLA6D | CB65 - McLauchlan St | 2024-10-31 16:18 | 2024-10-31 17:47 | 0 | 0 | 1 | 87 | Unplanned | Defective equipment | Burnt out fuse carrier replaced EAM 1511267 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1013 | 2024-10-31-0172 | Wairau Valley - FUSE3998 | CB5399 Wairau Valley | 2024-10-31 17:00 | 2024-10-31 17:54 | 0.0019872 | 3.68e-05 | 1 | 54 | Unplanned | Wildlife | Centre phase blown at FUSE3998 and a dead possum downline. Fuses replaced (50A) NAMS F4321 EAM1511149 Patrol carried out next day Found blown fuse at FUSE 3998 NAMS4321 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1014 | 2024-11-01-0001 | Godfrey Road - 0002271899ML999 | CB5367 Godfrey Road | 2024-11-01 09:10 | 2024-11-01 10:00 | 0 | 0 | 1 | 51 | Unplanned | Other cause | Blown red phase, replaced FUSE LETTER LEFT EAM 1511305 - PART POWER 3PH 30A, red phase gone | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1015 | 2024-11-02-0002 | Koromiko - FUSE2206 | CB55-Koromiko | 2024-11-02 07:31 | 2024-11-02 09:26 | 0.02116 | 0.000184 | 5 | 575 | Unplanned | Unknown | Found 1 x blown fuse at 11kV FUSE2206 carried out line patrol nothing obvious found Fuse found to be OK just loose in holder, retightened and closed Power confirmed restored | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1016 | 2024-11-02-0003 | Flaxbourne - FUSE3492 | REC1432-Flaxbourne | 2024-11-02 09:11 | 2024-11-02 12:30 | 0.014646 | 7.36e-05 | 2 | 398 | Unplanned | Wildlife | Found 2 x blown fuses at 11kV FUSE3492 line patroled nothing obvious found, near water suspect bird power confirmed restored W/O 1511368 NAMSF4334 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1017 | 2024-11-02-0004 | Rai Valley - 0007714177ML548 | CB43-Rai Valley | 2024-11-02 16:56 | 2024-11-02 19:44 | 0.0061824 | 3.68e-05 | 1 | 168 | Unplanned | Unknown | 3 x blown fuses found at FUSE 3141 Line patrol carried out no cause found W/O 1511369 NAMS F4335 EAM 1511369 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1018 | 2024-11-03-0005 | Spring Creek - FUSE2182 | CB187-Spring Creek | 2024-11-03 05:04 | 2024-11-03 06:15 | 0.026496 | 0.000368 | 10 | 720 | Unplanned | Wildlife | 1 x blown fuse at 11kV FUSE2182 Line patrol - no cause found Fuses replaced power confirmed restored EAM 1511370 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1019 | 2024-11-03-0006 | Woodbourne - ABS389-B | CB1178-Woodbourne | 2024-11-03 16:08 | 2024-11-03 18:01 | 0.71108 | 0.0062928 | 171 | 19323 | Unplanned | Defective equipment | found damaged insulator at Pole MA1628. Possibility of insulator failing at any time Network isolated and insulator replaced (Pole is outside 72 Caldwell Rd Woodbourne) EAM1511373 NAMS F4338 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1020 | 2024-11-04-0007 | Waikawa - 0006602538MLBC6 | CB109- Waikawa | 2024-11-04 16:49 | 2024-11-04 18:17 | 0 | 0 | 1 | 88 | Unplanned | Defective equipment | Installed new bolt and re attached Shangle W/O 1511374 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1021 | 2024-11-05-0013 | Waikawa - REC1 | CB109- Waikawa | 2024-11-05 08:25 | 2024-11-05 12:32 | 1.32 | 0.01196 | 325 | 35869 | Unplanned | Third party interference | 11kV lines between pole ZA3695 and ZA3697 hit by a forestry excavator moving under the lines. 1 phase came down and the middle phase suffered damage. Phase came into contact with lower circuit causing outages from REC1 and REC17. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1022 | 2024-11-05-0008 | Waikawa - REC17 | CB109- Waikawa | 2024-11-05 08:28 | 2024-11-05 12:23 | 0.78582 | 0.0033856 | 92 | 21354 | Unplanned | Third party interference | 11kV lines between pole ZA3695 and ZA3697 hit by a forestry excavator moving under the lines. 1 phase came down and the middle phase suffered damage. Phase came into contact with lower circuit causing outages from REC1 and REC17. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1023 | 2024-11-05-0011 | Nelson St - FUSE22439 | CB93-Nelson St | 2024-11-05 08:30 | 2024-11-05 11:04 | 0 | 0 | 7 | 1078 | Planned | Planned interruption | Replacement of SFB25C Goodman St EAM1471829 NAMS4501 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1024 | 2024-11-05-0019 | Kaituna - HVOH2738-S17904 | CB5448 Kaituna | 2024-11-05 08:31 | 2024-11-05 14:47 | 0.207 | 0.000552 | 15 | 5625 | Planned | Planned interruption | Okaramio Planned Work http://nams.mll.co.nz/Schedule/Edit/4214 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1025 | 2024-11-05-0010 | Grassmere - REC5092 | CB1253-Grassmere | 2024-11-05 08:39 | 2024-11-05 18:17 | 0.02127 | 3.68e-05 | 1 | 578 | Planned | Planned interruption | Planned shutdown for line rebuild to the start of the DSL network. SAF4423 - WO1433713 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1026 | 2024-11-05-0015 | Spring Creek - ABS781 | CB187-Spring Creek | 2024-11-05 08:45 | 2024-11-05 09:18 | 0.0024288 | 7.36e-05 | 2 | 66 | Planned | Planned interruption | EAM150000 NAMS4490 This outage was started then cancelled due to resource required at a fault. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1027 | 2024-11-05-0016 | Spring Creek - SUB356192 | CB187-Spring Creek | 2024-11-05 09:00 | 2024-11-05 09:11 | 0.002024 | 0.000184 | 5 | 55 | Planned | Planned interruption | EAM150000 NAMS4490 This outage was started then cancelled due to resource required at a fault. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1028 | 2024-11-05-0012 | Hospital Rd West - LVUG294 | CB47-Hospital Rd West | 2024-11-05 09:26 | 2024-11-05 12:55 | 0 | 0 | 8 | 1672 | Planned | Planned interruption | Replacement of burnt SFB at 205C Maxwell Rd EAM1468554 NAMSS4493 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1029 | 2024-11-05-0017 | Alabama Rd - 0001188233ML75E | CB1667-Alabama Rd | 2024-11-05 12:51 | 2024-11-06 14:12 | 0 | 0 | 1 | 1521 | Unplanned | Unknown | EAM 1511644 No access to property but no issues found on MLL network | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1030 | 2024-11-05-0018 | Scotland St - 0006610227MLA16 | CB54-Scotland St | 2024-11-05 14:00 | 2024-11-05 15:00 | 0 | 0 | 1 | 60 | Planned | Planned interruption | Re-heatshrinking of LV service cable at 5 Wairau Rd EAM1487334 NAMS4504 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1031 | 2024-11-05-0020 | Okaramio - REC5516 | CB104 Okaramio | 2024-11-05 14:46 | 2024-11-05 15:53 | 0.02219 | 0.0003312 | 9 | 603 | Planned | Planned interruption | Additional outage following Okaramio line rebuild works due to fuse saver being left open. http://nams.mll.co.nz/Schedule/Edit/4343 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1032 | 2024-11-05-0021 | Redwood St Nth - 0001106418ML53C | CB1655-Redwood St Nth | 2024-11-05 18:18 | 2024-11-05 19:38 | 0 | 0 | 1 | 80 | Unplanned | Defective equipment | Blown 32A HRC, no cause found, suspect internal EAM: 1511629 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1033 | 2024-11-06-0022 | Sounds - SUB326056 | REC1170-Sounds | 2024-11-06 08:28 | 2024-11-08 14:48 | 0.23994 | 7.36e-05 | 2 | 6520 | Unplanned | Defective equipment | Blown fuse at SUB326056 no obvious cause found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1034 | 2024-11-06-0024 | Richmond Brook - ABS15043-B | CB1250-Richmond Brook | 2024-11-06 08:30 | 2024-11-06 14:27 | 0.98532 | 0.00276 | 75 | 26775 | Planned | Planned interruption | Replace Pole ET2576 EAM1480733 NAMS4186 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1035 | 2024-11-06-0023 | Grassmere - REC5092 | CB1253-Grassmere | 2024-11-06 08:30 | 2024-11-06 18:05 | 0.02116 | 3.68e-05 | 1 | 575 | Planned | Planned interruption | Plannsed shutdown for line rebuild at Kaparu Rd - SD2 SAF 4427.1 EAM1433713 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1036 | 2024-11-06-0028 | Scotland St - 0006611101ML46F | CB54-Scotland St | 2024-11-06 09:04 | 2024-11-06 11:40 | 0 | 0 | 1 | 157 | Planned | Planned interruption | 64 Wellington Street Planned http://nams.mll.co.nz/Schedule/Edit/4301 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1037 | 2024-11-06-0029 | Scotland St - 0006611105ML565 | CB54-Scotland St | 2024-11-06 09:04 | 2024-11-06 11:41 | 0 | 0 | 1 | 157 | Planned | Planned interruption | 64 Wellington Street Planned http://nams.mll.co.nz/Schedule/Edit/4301 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1038 | 2024-11-06-0025 | Thomsons Ford Rd - FUSE21747 | CB1509-Thomsons Ford Rd | 2024-11-06 09:54 | 2024-11-06 13:31 | 0 | 0 | 6 | 1308 | Planned | Planned interruption | Road Planned Work http://nams.mll.co.nz/Schedule/Edit/4304 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1039 | 2024-11-06-0026 | Richmond Brook - LVOH4095 | CB1250-Richmond Brook | 2024-11-06 11:05 | 2024-11-06 13:29 | 0 | 0 | 6 | 864 | Planned | Planned interruption | Replacement of LV SASP at NK1319 EAM1480721 NAMS4190 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1040 | 2024-11-06-0030 | Godfrey Road - 0002271899ML999 | CB5367 Godfrey Road | 2024-11-06 14:20 | 2024-11-07 16:13 | 0 | 0 | 1 | 1554 | Unplanned | Other cause | Metering fault when changed 2 years ago causing shorts - inspector attended and fixed issue EAM 1511979 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1041 | 2024-11-07-0032 | Okaramio - HVOH2732-S17925 | CB104 Okaramio | 2024-11-07 08:30 | 2024-11-07 12:15 | 0.12365 | 0.000552 | 15 | 3360 | Planned | Planned interruption | Okaramio SD13 - Conductor install from poles 31 to 38 EAM1426402 NAMS4354 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1042 | 2024-11-07-0031 | Grovetown - SUB361123 | CB1465-Grovetown | 2024-11-07 08:34 | 2024-11-07 14:00 | 0 | 0 | 11 | 3586 | Planned | Planned interruption | Replace LV x-arm on pole JA0588 & JA0584 EAM1505870 NAMS4456 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1043 | 2024-11-07-0035 | Grassmere - ABS355-B | CB1253-Grassmere | 2024-11-07 08:40 | 2024-11-07 17:43 | 0.25977 | 0.0004784 | 13 | 7059 | Planned | Planned interruption | Kaparu Road Planned Work SD3 http://nams.mll.co.nz/Schedule/Edit/4298 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1044 | 2024-11-07-0033 | Grovetown - FUSE3905 | CB1465-Grovetown | 2024-11-07 08:55 | 2024-11-07 11:18 | 0.015677 | 0.0001104 | 3 | 426 | Planned | Planned interruption | Jones Road Planned Work - HV SD for pump installation under lines http://nams.mll.co.nz/Schedule/Edit/4345 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1045 | 2024-11-07-0034 | Renwick Township - LVUG795 | CB5482 Renwick Township | 2024-11-07 09:03 | 2024-11-07 13:42 | 0 | 0 | 5 | 1400 | Planned | Planned interruption | Planned Work http://nams.mll.co.nz/Schedule/Edit/4306 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1046 | 2024-11-07-0039 | Thomsons Ford Rd - ABS15039-B | CB1509-Thomsons Ford Rd | 2024-11-07 12:56 | 2024-11-07 14:05 | 0.03047 | 0.0004416 | 12 | 828 | Unplanned | Defective equipment | Shutdown to repair broken flicker on ABS15266 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1047 | 2024-11-07-0040 | Seymour St - 0001147629MLEB3 | CB51-Seymour St | 2024-11-07 15:44 | 2024-11-07 16:31 | 0 | 0 | 1 | 48 | Unplanned | Defective equipment | Blown fuse - Internal issue EAM 1512310 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1048 | 2024-11-07-0041 | Pelorus - 0007713241ML45C | CB5126-Pelorus | 2024-11-07 18:02 | 2024-11-07 19:30 | 0 | 0 | 1 | 89 | Unplanned | Adverse weather | Blown 60A HRC, suspect clashing 1512344 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1049 | 2024-11-08-0042 | Havelock Canvastown - FUSE3025 | CB103 Havelock Canvastown | 2024-11-08 09:05 | 2024-11-08 13:08 | 0.017811 | 7.36e-05 | 2 | 484 | Planned | Planned interruption | Kaiuma Bay Planned vegetation work http://nams.mll.co.nz/Application/Edit/4517 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1050 | 2024-11-08-0043 | Craiglochart - 0002272450MLECB | REC1391-Craiglochart | 2024-11-08 09:33 | 2024-11-08 11:55 | 0 | 0 | 1 | 142 | Unplanned | Defective equipment | Fuse blown due to internal issue. EAM 1512382 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1051 | 2024-11-08-0044 | Sounds - FUSE2373 | REC1170-Sounds | 2024-11-08 09:53 | 2024-11-08 14:48 | 0.065136 | 0.0002208 | 6 | 1770 | Unplanned | Defective equipment | Unplanned 11kV Shutdown to change faulty transformer ref outage 2024-11-06-0022 http://nams.mll.co.nz/Schedule/Edit/4347 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1052 | 2024-11-08-0045 | French Pass - REC1480 | CB45-French Pass | 2024-11-08 11:00 | 2024-11-08 16:28 | 2.1216 | 0.0064768 | 176 | 57653 | Unplanned | Vegetation | REC1480 tripped and locked out on phase OC. Patrol found a tree branch over the 11kV at pole JA0428. removed with pokey stick and line relivened. http://nams.mll.co.nz/Schedule/Edit/4354 EAM1512397 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1053 | 2024-11-08-0046 | French Pass - 0008805065MLDA9 | CB45-French Pass | 2024-11-08 18:44 | 2024-11-09 09:45 | 0 | 0 | 1 | 901 | Unplanned | Defective equipment | Blown service fuse, suspect internal fault. Letter to be sent 1512428 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1054 | 2024-11-09-0047 | Renwick Township - 0000051555ML407 | CB5482 Renwick Township | 2024-11-09 10:07 | 2024-11-09 11:55 | 0 | 0 | 1 | 109 | Unplanned | Defective equipment | Arcing trurip, temp repair made, customer works to send quote for replacement 1512430 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1055 | 2024-11-09-0048 | Pelorus - SUB335159 | CB5126-Pelorus | 2024-11-09 11:17 | 2024-11-09 18:13 | 0 | 0 | 2 | 619 | Unplanned | Vegetation | 1x blown HT fuse found at SUB335159. Found vegetation in LV to service. Broke jumpers to resore service to second ICP. Attended with bucket truck, removed vegetation and remade jumpers. EAM 1512431 http://nams.mll.co.nz/Schedule/Edit/4359 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1056 | 2024-11-10-0055 | French Pass - SUB336329 | CB45-French Pass | 2024-11-09 11:35 | 2024-11-10 10:45 | 0.1023 | 7.36e-05 | 2 | 2780 | Unplanned | Unknown | Power alarm from Saddle Hill Radio site. Attended and found 1x blown HV fuse at SUB336329, no cause found. Replaced fuses (3A). Confirmed alarm clear and voltage outgoing from TX. Delay in response due to weather and resourcing issues. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1057 | 2024-11-09-0051 | Vernon - FUSE2074 | CB5184-Vernon | 2024-11-09 11:46 | 2024-11-10 13:55 | 0.23081 | 0.0001472 | 4 | 6272 | Unplanned | Defective equipment | Power alarm for the MLL site at Jamies Knob. 1x fuse blown found at FUSE2074. Centre phase down at pole ET3516. Unable to repair at the time due to IR pole. Returned following day with tracked bucket and repaired wire and relivened. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1058 | 2024-11-09-0050 | Seaview - CB1251 | CB1251-Seaview | 2024-11-09 12:39 | 2024-11-11 16:32 | 0.21171 | 0.0018032 | 49 | 5753 | Unplanned | Vegetation | Large tree branch broke and fell through lines Reported by FENZ. Feeder opened for safey. Lines have been made safe, but tree removal and additional resoucre required to restore HV and LV. Pole replaced and restored 11/11. EAM 1512434 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1059 | 2024-11-09-0053 | Weld St - 0001162417MLE3A | CB71-Weld St | 2024-11-09 16:52 | 2024-11-09 18:05 | 0 | 0 | 1 | 73 | Unplanned | Adverse weather | 2x 30A HRC fuses blown. Suspect clashing, fuses through to main switch insulation tested as precaution, greater than 999M ohm 1512435 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1060 | 2024-11-09-0054 | French Pass - REC5024 | CB45-French Pass | 2024-11-09 18:05 | 2024-11-09 18:05 | 0.00276 | 0.00276 | 75 | 75 | Unplanned | Adverse weather | 11kV REC5024 reclosed on phase oc. Cyclo 363. Very windy at the time | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1061 | 2024-11-11-0056 | Waikawa - SUB330009 | CB109- Waikawa | 2024-11-11 01:53 | 2024-11-11 03:16 | 0.076433 | 0.0018768 | 51 | 2077 | Unplanned | Wildlife | 1 blown HT fuse found at SUB330009 and a dead possum, Replaced fuse (25A) http://nams.mll.co.nz/Schedule/Edit/4363 EAM 1512438 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1062 | 2024-11-11-0057 | Riverlands - ABS760-B | CB1181-Riverlands | 2024-11-11 08:36 | 2024-11-11 15:05 | 0.12884 | 0.0003312 | 9 | 3501 | Planned | Planned interruption | Replace pole & install new TX. EAM1496591 NAMS 4407 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1063 | 2024-11-11-0058 | Riverlands - SUB348509 | CB1181-Riverlands | 2024-11-11 08:36 | 2024-11-11 09:45 | 0 | 0 | 6 | 420 | Planned | Planned interruption | SUB348509 was re livened earlier than expected EAM1496591 NAMS 4407 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1064 | 2024-11-11-0059 | Godfrey Road - ABS15150-B | CB5367 Godfrey Road | 2024-11-11 08:38 | 2024-11-11 11:45 | 0.013763 | 7.36e-05 | 2 | 374 | Planned | Planned interruption | Planned shutdown for maintenance of 11kV RMUS5063-5148 EAM 1502359 SAF 4538 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1065 | 2024-11-11-0060 | Wairau Valley - FUSE4273 | CB5399 Wairau Valley | 2024-11-11 09:12 | 2024-11-11 16:59 | 0.051557 | 0.0001104 | 3 | 1401 | Planned | Planned interruption | Planned shutdown for transformer relocation . EAM 1495758 SAF 4531 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1066 | 2024-11-12-0063 | Hutcheson St - LVUG1077 | CB49-Hutcheson St | 2024-11-12 06:00 | 2024-11-12 06:49 | 0 | 0 | 2 | 98 | Planned | Planned interruption | Shutdown of Andelec box at DP36 Maxwell Rd for removal of cable from LV Pos1. Outage due to modelling SAF4520 - EAM 1507035 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1067 | 2024-11-12-0065 | Hutcheson St - 0001161005MLAF3 | CB49-Hutcheson St | 2024-11-12 06:00 | 2024-11-12 06:49 | 0 | 0 | 1 | 49 | Planned | Planned interruption | Shutdown of Andelec box at DP36 Maxwell Rd for removal of cable from LV Pos1. Outage due to modelling SAF4520 - EAM 1507035 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1068 | 2024-11-12-0066 | Hutcheson St - 0001161187ML638 | CB49-Hutcheson St | 2024-11-12 06:00 | 2024-11-12 06:49 | 0 | 0 | 1 | 49 | Planned | Planned interruption | Shutdown of Andelec box at DP36 Maxwell Rd for removal of cable from LV Pos1. Outage due to modelling SAF4520 - EAM 1507035 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1069 | 2024-11-12-0067 | Hutcheson St - 0001161017ML0DB | CB49-Hutcheson St | 2024-11-12 06:00 | 2024-11-12 06:49 | 0 | 0 | 1 | 49 | Planned | Planned interruption | Shutdown of Andelec box at DP36 Maxwell Rd for removal of cable from LV Pos1. Outage due to modelling SAF4520 - EAM 1507035 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1070 | 2024-11-12-0069 | Buller St - 0006607459ML657 | CB108-Buller St | 2024-11-12 07:40 | 2024-11-12 08:22 | 0 | 0 | 1 | 42 | Unplanned | Defective equipment | Not actually a line down, but a cable had come away from the pole Reattaching to pole EAM 1512925 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1071 | 2024-11-12-0070 | Okaramio - ABS15426-B | CB104 Okaramio | 2024-11-12 08:30 | 2024-11-12 13:43 | 0.25259 | 0.0008096 | 22 | 6864 | Planned | Planned interruption | Planned shutdown for Okaramio 11kV rebuild. Remove temp ABS and run conductor from pole 19 to 22 EAM1426402 SAF 4495 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1072 | 2024-11-12-0072 | Waikawa - FUSE2966 | CB109- Waikawa | 2024-11-12 09:00 | 2024-11-12 12:59 | 0.0087952 | 3.68e-05 | 1 | 239 | Planned | Planned interruption | Replace x-arm on pole PT5232 EAM1440291 NAMS4284 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1073 | 2024-11-12-0071 | Sounds - SUB325066 | REC1170-Sounds | 2024-11-12 09:03 | 2024-11-12 14:23 | 0.070877 | 0.0002208 | 6 | 1926 | Planned | Planned interruption | Planned Work - isolation of LV distribution for replacement of roof under lines http://nams.mll.co.nz/Schedule/Edit/4323 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1074 | 2024-11-12-0073 | Riverlands - 0004421216ML48D | CB1181-Riverlands | 2024-11-12 18:47 | 2024-11-12 20:30 | 0 | 0 | 1 | 104 | Unplanned | Unknown | Blown 30A RW pole fuse. Completed an insulation test on the cable, all ok. Repalced fuse with an HRC fuse, power restored 2030. EAM 1513981 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1075 | 2024-11-12-0074 | Koromiko - 0006610049MLC7A | CB55-Koromiko | 2024-11-12 19:14 | 2024-11-12 20:22 | 0 | 0 | 1 | 68 | Unplanned | Adverse weather | Service line pulled away from bargeboard due to wind. Re-attached and power never went off. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1076 | 2024-11-13-0080 | Hutcheson St - 0001161017ML0DB | CB49-Hutcheson St | 2024-11-13 06:09 | 2024-11-13 08:23 | 0 | 0 | 1 | 134 | Planned | Planned interruption | DP36 Maxwell Rd replacement - disconnection of cable from pos 6 http://nams.mll.co.nz/Schedule/Edit/4352 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1077 | 2024-11-13-0078 | Hutcheson St - 0001104071MLBDC | CB49-Hutcheson St | 2024-11-13 06:09 | 2024-11-13 08:25 | 0 | 0 | 1 | 136 | Planned | Planned interruption | DP36 Maxwell Rd replacement - disconnection of cable from pos 6 http://nams.mll.co.nz/Schedule/Edit/4352 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1078 | 2024-11-13-0077 | Hutcheson St - 0001161187ML638 | CB49-Hutcheson St | 2024-11-13 06:09 | 2024-11-13 08:23 | 0 | 0 | 1 | 134 | Planned | Planned interruption | DP36 Maxwell Rd replacement - disconnection of cable from pos 6 http://nams.mll.co.nz/Schedule/Edit/4352 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1079 | 2024-11-13-0079 | Hutcheson St - 0001104073MLB59 | CB49-Hutcheson St | 2024-11-13 06:10 | 2024-11-13 08:25 | 0 | 0 | 1 | 136 | Planned | Planned interruption | DP36 Maxwell Rd replacement - disconnection of cable from pos 6 http://nams.mll.co.nz/Schedule/Edit/4352 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1080 | 2024-11-13-0076 | Hutcheson St - 0001161005MLAF3 | CB49-Hutcheson St | 2024-11-13 06:10 | 2024-11-13 08:23 | 0 | 0 | 1 | 134 | Planned | Planned interruption | DP36 Maxwell Rd replacement - disconnection of cable from pos 6 http://nams.mll.co.nz/Schedule/Edit/4352 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1081 | 2024-11-13-0081 | Nelson St - RMUS5016-B | CB93-Nelson St | 2024-11-13 08:13 | 2024-11-13 17:35 | 2.5276 | 0.0044896 | 122 | 68686 | Planned | Planned interruption | Removal of SUB3700FH and replacement with new GM SUB3700RE in Budge St SAF4396 EAM 1469832 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1082 | 2024-11-13-0083 | Wairau Valley - FUSE2652 | CB5399 Wairau Valley | 2024-11-13 08:30 | 2024-11-13 15:38 | 0.14175 | 0.0003312 | 9 | 3852 | Planned | Planned interruption | Deviation of SWER line at Te-Rou http://nams.mll.linesmarl.co.nz/Application/Edit/4359 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1083 | 2024-11-13-0082 | French Pass - ENS7011-B | CB45-French Pass | 2024-11-13 08:32 | 2024-11-13 09:09 | 0.5258 | 0.013837 | 376 | 14288 | Unplanned | Defective equipment | Elaine Gen tripped when in island due to coolant alarm. found coolant hose split between heater and engine block. Repairs escalated to Maintenance team. Gen being run for planned work SAF4527 EAM1507442 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1084 | 2024-11-13-0084 | Spring Creek - FUSE2182 | CB187-Spring Creek | 2024-11-13 22:56 | 2024-11-14 07:19 | 0.1851 | 0.000368 | 10 | 5030 | Unplanned | Wildlife | 2 blown fuses 2182 Cause unknown Suspect bird All 3 replaced 30 amp 1516601 http://nams.mll.co.nz/Schedule/Edit/4386 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1085 | 2024-11-14-0085 | Hutcheson St - LVUG1077 | CB49-Hutcheson St | 2024-11-14 04:59 | 2024-11-14 07:25 | 0 | 0 | 2 | 292 | Planned | Planned interruption | Maxwell Road Planned Work - DP36 Maxwell Rd - Disconnect cable from LV Pos 5 http://nams.mll.co.nz/Application/Edit/4522 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1086 | 2024-11-14-0086 | Rai Valley - FUSE2291 | CB43-Rai Valley | 2024-11-14 06:51 | 2024-11-14 09:33 | 0.059984 | 0.000368 | 10 | 1630 | Unplanned | Unknown | blown fuse at 11kV FUSE2291 - no obvious cause found power confirmed restored EAM 1516620 http://nams.mll.co.nz/Schedule/Edit/4388 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1087 | 2024-11-14-0087 | Wairau Valley - FUSE2652 | CB5399 Wairau Valley | 2024-11-14 08:30 | 2024-11-14 13:50 | 0.10565 | 0.0003312 | 9 | 2871 | Planned | Planned interruption | Planned shutdown for SWER line rebuild at Te Rou EAM1435938 SAF4359 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1088 | 2024-11-14-0088 | Spring Creek - ABS1906-B | CB187-Spring Creek | 2024-11-14 08:37 | 2024-11-14 14:23 | 0.11459 | 0.0003312 | 9 | 3114 | Planned | Planned interruption | Maintenance works in Dicks Rd beyond ABS1906 http://nams.mll.linesmarl.co.nz/Application/Edit/4368 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1089 | 2024-11-14-0089 | Seaview - 0005505377ML3A4 | CB1251-Seaview | 2024-11-14 10:10 | 2024-11-14 17:31 | 0.016229 | 3.68e-05 | 1 | 441 | Planned | Planned interruption | Planned shutdown for repairs on 11kV switchboard. EAM 470070 SAF 4572 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1090 | 2024-11-14-0090 | Redwood St Sth - 0001189165MLC7A | CB1673-Redwood St Sth | 2024-11-14 10:58 | 2024-11-14 12:20 | 0 | 0 | 1 | 82 | Unplanned | Defective equipment | Internal Issue Power restored EAM 1518053 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1091 | 2024-11-14-0091 | East Coast, REC31 - Ward, REC1432 - Flaxbourne - CB1247 | REC29 - East Coast, REC31 - Ward, REC1432 - Flaxbourne | 2024-11-14 16:11 | 2024-11-14 17:01 | 1.4939 | 0.032347 | 879 | 40594 | Unplanned | Human error | T1 and T2 at Seddon tripped due to a the earth switch of CB576 being closed when relivening under SAF4572 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1092 | 2024-11-15-0118 | Alabama Rd - LVOH200072-S100 | CB1667-Alabama Rd | 2024-11-15 08:31 | 2024-11-15 11:14 | 0 | 0 | 2 | 326 | Planned | Planned interruption | Scott Street Planned Work http://nams.mll.co.nz/Schedule/Edit/4366 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1093 | 2024-11-15-0117 | Vernon - REC1576 | CB5184-Vernon | 2024-11-15 08:31 | 2024-11-15 08:31 | 0 | 0 | 38 | 0 | Unplanned | Unknown | Successful reclose of CB1576 Phase OC | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1094 | 2024-11-15-0119 | Sounds - FUSE2374 | REC1170-Sounds | 2024-11-15 10:04 | 2024-11-15 11:43 | 0.01093 | 0.0001104 | 3 | 297 | Planned | Planned interruption | Forysth Island Planned Work http://nams.mll.co.nz/Schedule/Edit/4364 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1095 | 2024-11-15-0120 | Murphys Rd - 0001122015ML92B | CB68-Murphys Rd | 2024-11-15 12:00 | 2024-11-15 12:01 | 0 | 0 | 1 | 2 | Unplanned | Other Cause | EAM 1518690 - Blown fuse in pillar box at Westwood development, supply comes from 23 Blackmore Place. 3PH 32A Blown fuse due to overloading | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1096 | 2024-11-15-0121 | Weld St - 0001187521MLB14 | CB71-Weld St | 2024-11-15 12:48 | 2024-11-15 13:42 | 0 | 0 | 1 | 53 | Unplanned | Other Cause | Internal issue caused by electrician EAM 1518771 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1097 | 2024-11-15-0122 | Grovetown - 0003341210MLB71 | CB1465-Grovetown | 2024-11-15 17:20 | 2024-11-15 19:07 | 0 | 0 | 1 | 107 | Unplanned | Unknown | ICP had been disconnected by their retailer. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1098 | 2024-11-16-0130 | Craiglochart - ABS810-B | REC1391-Craiglochart | 2024-11-16 06:07 | 2024-11-16 12:03 | 0.57643 | 0.0016192 | 44 | 15664 | Unplanned | Wildlife | Multiple no powers Waihopai Valley area Wire down POLE BS2319 http://nams.mll.co.nz/Schedule/Edit/4395 1518885 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1099 | 2024-11-16-0125 | Pelorus - 0007713241ML45C | CB5126-Pelorus | 2024-11-16 07:55 | 2024-11-16 10:18 | 0 | 0 | 1 | 143 | Unplanned | Adverse weather | 2x blown pole fuses, probably caused by conductor clashing. Restored 1018. EAM 1518886 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1100 | 2024-11-18-0133 | Tuamarina - CB188 | CB188-Tuamarina | 2024-11-16 20:35 | 2024-11-16 20:35 | 0 | 0 | 485 | 0 | Unplanned | Unknown | Successful Reclose CB188 Phase OC | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1101 | 2024-11-18-0134 | Hospital Rd East - 0001186337ML790 | CB39-Hospital Rd East | 2024-11-18 09:06 | 2024-11-18 10:13 | 0 | 0 | 1 | 67 | Unplanned | Defective equipment | Loose Connection - Power restored EAM 1518887 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1102 | 2024-11-18-0135 | Wairau Valley - FUSE2652 | CB5399 Wairau Valley | 2024-11-18 09:41 | 2024-11-18 17:15 | 0.15036 | 0.0003312 | 9 | 4086 | Planned | Planned interruption | Te Rou Northbank Planned Work http://nams.mll.co.nz/Application/Edit/4359 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1103 | 2024-11-19-0136 | Rai Valley - CB2032 | CB43 - Rai Valley, CB45 - French Pass, CB5126 - Pelorus | 2024-11-19 01:07 | 2024-11-19 01:07 | 0 | 0 | 919 | 0 | Unplanned | Unknown | Successful reclose of CB2032 Earth Fault trip | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1104 | 2024-11-19-0137 | Vintage Lane - CB171 | CB171-Vintage Lane | 2024-11-19 11:17 | 2024-11-22 11:56 | 0.33764 | 0.005704 | 138 | 9175 | Unplanned | Third party interference | Vintage Lane feeder tripped on Phase OC. due to 11kV cable strike EAM 1519295 Sub3680FS required to be isolated for work at cable term pole. http://nams.mll.co.nz/Schedule/Edit/4402 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1105 | 2024-11-20-0138 | Ngakuta - REC1562 | REC1562-Ngakuta | 2024-11-20 04:23 | 2024-11-20 04:23 | 0.016155 | 0.016155 | 439 | 439 | Unplanned | Wildlife | 11kV REC1562 tripped on Earth Fault (2 times) then stayed closed. Cyclo124 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1106 | 2024-11-20-0140 | Ngakuta - FUSE3999 | REC1562-Ngakuta | 2024-11-20 05:14 | 2024-11-20 10:40 | 1.9681 | 0.016155 | 439 | 53481 | Unplanned | Wildlife | 1519391 Found centre phase fuse blown at 11kV fuses3999 NAMS F4403 Possum located on pole BE1247 centre phase, hanging down to lower crossarm. Removed with Pokey stick and repaired damaged service neutral. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1107 | 2024-11-20-0143 | Sounds - SUB3251BA | REC1170-Sounds | 2024-11-20 09:55 | 2024-11-20 11:36 | 0 | 0 | 5 | 505 | Planned | Planned interruption | http://nams.mll.linesmarl.co.nz/Schedule/Edit/4228 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1108 | 2024-11-20-0144 | Nelson St - 0001145082MLD3E | CB93-Nelson St | 2024-11-20 15:54 | 2024-11-20 17:01 | 0 | 0 | 1 | 67 | Unplanned | Defective equipment | Burnt cutout EAM 1519572 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1109 | 2024-11-21-0145 | Grovetown - FUSE3905 | CB1465-Grovetown | 2024-11-21 08:46 | 2024-11-21 10:41 | 0.012696 | 0.0001104 | 3 | 345 | Planned | Planned interruption | HV shutdown to allow removal of flood pumps from under lines http://nams.mll.linesmarl.co.nz/Schedule/Edit/4346 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1110 | 2024-11-21-0146 | French Pass - ABS521-B | CB45-French Pass | 2024-11-21 09:00 | 2024-11-21 11:56 | 0.41451 | 0.0023552 | 64 | 11264 | Planned | Planned interruption | Planned shutdown to install spurline fuses and re-sag HVOH EAM1505626 SAF 4499 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1111 | 2024-11-21-0147 | Hospital Rd East - 0001186337ML790 | CB39-Hospital Rd East | 2024-11-21 17:42 | 2024-11-21 18:28 | 0 | 0 | 1 | 47 | Unplanned | Defective equipment | Broken service lead @ DF3111. Reconnected, 1519830 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1112 | 2024-11-21-0148 | Thomsons Ford Rd - RMUF1616 | CB1509-Thomsons Ford Rd | 2024-11-21 19:15 | 2024-11-21 21:09 | 0.075145 | 0.0008464 | 23 | 2042 | Unplanned | Wildlife | 1519832 Found Magpie caught in 11kV jumpers at SUB357152 and blown TX fuse. Also 11kV Fuses3444 2 blown and 11kV RMUF1616 2 fuses blown. http://nams.mll.co.nz/Schedule/Edit/4407 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1113 | 2024-11-22-0149 | Pelorus - 0007713241ML45C | CB5126-Pelorus | 2024-11-22 08:30 | 2024-11-22 11:31 | 0 | 0 | 1 | 180 | Unplanned | Wildlife | Blown 60amp fuse . Thinks there are 2 possibilities why the consistent fault at above address. 1. The stay wire on the Iron Rail is being banged by horses and cattle. When they rub the stay wire - this clashes the lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1114 | 2024-11-25-0150 | Sounds - REC5319 | REC1170-Sounds | 2024-11-25 08:38 | 2024-11-25 14:04 | 0.31192 | 0.0009568 | 26 | 8476 | Planned | Planned interruption | Planned shutdown to replace pole VA2441. EAM 1422065 SAF 4026 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1115 | 2024-11-25-0151 | Godfrey Road - ABS387-B | CB5367 Godfrey Road | 2024-11-25 18:28 | 2024-11-26 15:23 | 0.20902 | 0.012438 | 334 | 5680 | Unplanned | Third party interference | Car V Pole KB8505. Broken in 3 places. http://nams.mll.co.nz/Schedule/Edit/4411 EAM 1519909 Pole replaced on same day but 2 customers left off overnight as Transformer not installed yet. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1116 | 2024-11-26-0153 | Richmond Brook - REC37 | CB1250-Richmond Brook | 2024-11-26 02:11 | 2024-11-26 02:12 | 0 | 0 | 224 | 0 | Unplanned | Wildlife | Succesful auto reclose at 11kV REC37 Camerons Rd. Earth fault Cyclo148. ENS7011 saw Red 10A Yellow 7 A Blue 50A Earth 40A | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1117 | 2024-11-26-0155 | Waikawa - FUSE2257 | CB109- Waikawa | 2024-11-26 08:34 | 2024-11-26 13:14 | 0.16486 | 0.0005888 | 16 | 4480 | Planned | Planned interruption | BS2816 - Replace hardware/cross-arms SAF 4087 - WO 1327167 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1118 | 2024-11-26-0154 | Sounds - FUSE2381 | REC1170-Sounds | 2024-11-26 09:02 | 2024-11-26 15:03 | 0.19872 | 0.000552 | 15 | 5400 | Planned | Planned interruption | Vegetation works around 11kV in Elie Bay SAF4530 WO1445557 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1119 | 2024-11-26-0156 | Sounds - HVOH305-S13258 | REC1170-Sounds | 2024-11-26 09:28 | 2024-11-26 10:40 | 0.38684 | 0.0052992 | 144 | 10512 | Planned | Planned interruption | Lochmara Planned Work - Commisioning of SEC5639 http://nams.mll.co.nz/Schedule/Edit/4382 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1120 | 2024-11-26-0157 | Koromiko - 0006609037MLEFD | CB55-Koromiko | 2024-11-26 12:18 | 2024-11-26 13:56 | 0 | 0 | 1 | 97 | Planned | Planned interruption | Replace 4x service fuses & connectors on pole BS2382. http://nams.mll.co.nz/Application/Edit/4498 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1121 | 2024-11-26-0158 | Koromiko - 0006609033MLFF7 | CB55-Koromiko | 2024-11-26 12:18 | 2024-11-26 13:56 | 0 | 0 | 1 | 97 | Planned | Planned interruption | Replace 4x service fuses & connectors on pole BS2382. http://nams.mll.co.nz/Application/Edit/4498 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1122 | 2024-11-26-0159 | Koromiko - 0006609045MLB25 | CB55-Koromiko | 2024-11-26 12:18 | 2024-11-26 13:56 | 0 | 0 | 1 | 97 | Planned | Planned interruption | Replace 4x service fuses & connectors on pole BS2382. http://nams.mll.co.nz/Application/Edit/4498 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1123 | 2024-11-26-0160 | Koromiko - 0006609049ML83B | CB55-Koromiko | 2024-11-26 12:18 | 2024-11-26 13:56 | 0 | 0 | 1 | 97 | Planned | Planned interruption | Replace 4x service fuses & connectors on pole BS2382. http://nams.mll.co.nz/Application/Edit/4498 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1124 | 2024-11-26-0161 | Waikawa - 0006630032MLE3E | CB109- Waikawa | 2024-11-26 14:56 | 2024-11-26 18:26 | 0 | 0 | 1 | 210 | Unplanned | Defective equipment | Internal issue - Mains switch in off position EAM 1520119 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1125 | 2024-11-27-0162 | Ward - FUSE3492 | REC31-Ward | 2024-11-27 08:30 | 2024-11-27 14:38 | 0 | 0 | 2 | 736 | Planned | Planned interruption | Planned shutdown to straighten & relocate 11kV poles. EAM 1370004 SAF2450 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1126 | 2024-11-27-0163 | Murphys Rd - 0001120637ML1BD | CB68-Murphys Rd | 2024-11-27 09:12 | 2024-11-27 10:31 | 0 | 0 | 1 | 78 | Unplanned | Defective equipment | Burnt out fuse at the bottom of service box box - Burnt inside box. replaced EAM 1520234 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1127 | 2024-11-27-0164 | Nelson St - LVOH3659 | CB93-Nelson St | 2024-11-27 09:29 | 2024-11-27 13:22 | 0 | 0 | 3 | 699 | Planned | Planned interruption | Replace Pole JA3057 http://nams.mll.linesmarl.co.nz/Schedule/Edit/4406 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1128 | 2024-11-27-0165 | Murphys Rd - 0001120637ML1BD | CB68-Murphys Rd | 2024-11-27 12:12 | 2024-11-27 13:01 | 0 | 0 | 1 | 49 | Unplanned | Defective equipment | Blown fuse holder - related to first fault this morning Blown fuse again, Confirmed on ARC via ICP customer is 2ph 63amp EAM 1520234 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1129 | 2024-11-28-0168 | Jacksons Rd - CB1179 | CB1179 - Jacksons Rd | 2024-11-28 04:14 | 2024-11-28 04:33 | 0.070619 | 0.0037168 | 101 | 1919 | Unplanned | Unknown | Trip to Lockout on Phase OC at 04:14AM Manual reclose after 15min Closed successfully, Line patrolled with nothing found 2024-11-28-0167 EAM1520428 NAMSF4420 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1130 | 2024-11-28-0169 | Howick Rd North - FUSE2057 | CB84-Howick Rd North | 2024-11-28 08:30 | 2024-11-28 15:40 | 0.11077 | 0.0002576 | 7 | 3010 | Planned | Planned interruption | Install of new SUB3700RG http://nams.mll.linesmarl.co.nz/Schedule/Edit/4385 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1131 | 2024-11-28-0170 | Redwood St Nth - LVOH6192 | CB1655-Redwood St Nth | 2024-11-28 08:30 | 2024-11-28 09:51 | 0 | 0 | 2 | 162 | Planned | Planned interruption | Replacement of service fuses at re-heatshrinking at POLE DF2622 http://nams.mll.linesmarl.co.nz/Schedule/Edit/4399 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1132 | 2024-11-28-0171 | Howick Rd North - 0001185093MLF66 | CB84-Howick Rd North | 2024-11-28 11:12 | 2024-11-28 12:10 | 0 | 0 | 1 | 57 | Unplanned | Defective equipment | 100Amp burntout (Cutout required) EAM 1520511 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1133 | 2024-11-28-0172 | Wairau Valley - 0004420147ML263 | CB5399 Wairau Valley | 2024-11-28 13:18 | 2024-11-28 15:24 | 0 | 0 | 1 | 126 | Unplanned | Defective equipment | Burnt out pole fuse caused by burnt connector (old age) EAM 1520539 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1134 | 2024-11-28-0173 | Waihopai Valley - FUSE4070 | CB5493 Waihopai Valley | 2024-11-28 13:26 | 2024-11-28 15:07 | 0.014867 | 0.0001472 | 4 | 404 | Unplanned | Defective equipment | Loose bolt on x arm retightened Pole DF3205 EAM1520418 F4423 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1135 | 2024-11-28-0174 | Craiglochart - 0002272537ML5F5 | REC1391-Craiglochart | 2024-11-28 15:43 | 2024-11-28 19:14 | 0 | 0 | 1 | 212 | Unplanned | Vegetation | Service line damaged by fallen tree. Removed, repaired and relivened EAM 1520575 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1136 | 2024-11-28-0175 | Vintage Lane - 0007703244ML1F2 | CB171-Vintage Lane | 2024-11-28 17:52 | 2024-11-28 19:34 | 0 | 0 | 1 | 103 | Unplanned | Defective equipment | Blown service fuse replaced due to overloading W/O 1520580 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1137 | 2024-11-29-0178 | Symons St - LVUG178 | CB50-Symons St | 2024-11-29 07:35 | 2024-11-29 09:47 | 0 | 0 | 18 | 2376 | Unplanned | Unknown | NZI fuse (feeding cable B) at SUB3700JX has been replaced power restored Maintenance required on NZI fuses EAM 152058141 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1138 | 2024-11-29-0177 | Hawkesbury Road - XA0583-P1 | CB5457 Hawkesbury Road | 2024-11-29 08:38 | 2024-11-29 12:27 | 0 | 0 | 16 | 3664 | Planned | Planned interruption | Kowhai Drive Planned Work http://nams.mll.co.nz/Schedule/Edit/4368 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1139 | 2024-11-29-0179 | Wairau Valley - 0002279129MLF22 | CB5399 Wairau Valley | 2024-11-29 11:42 | 2024-11-29 13:16 | 0 | 0 | 1 | 94 | Planned | Planned interruption | 3951 SH63 Planned Work http://nams.mll.co.nz/Schedule/Edit/4393 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1140 | 2024-11-29-0180 | Symons St - RMUS5611-B | CB50-Symons St | 2024-11-29 12:26 | 2024-11-29 17:32 | 0.22216 | 0.0015088 | 41 | 6037 | Unplanned | Defective equipment | Park View Lane Fault Box of fire SFB 11 Park View Lane RMUS5611 Opened for safety http://nams.mll.co.nz/Schedule/Edit/4427 repairs made SFB11 replaced power restored. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1141 | 2024-11-29-0181 | Buller St - 0006607529MLA0E | CB108-Buller St | 2024-11-29 21:42 | 2024-11-29 23:08 | 0 | 0 | 1 | 87 | Unplanned | Defective equipment | failed fuse carrier, replaced with new fuse base EAM 1520747 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1142 | 2024-11-30-0182 | Koromiko - 0006608581ML965 | CB55-Koromiko | 2024-11-30 07:05 | 2024-11-30 09:11 | 0 | 0 | 1 | 127 | Unplanned | Defective equipment | fuse carrier burnt out , installed new fuse carrier EAM 1520748 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1143 | 2024-12-02-0002 | Kaituna - FUSE2105 | CB5448 Kaituna | 2024-12-02 08:33 | 2024-12-02 11:07 | 0.11334 | 0.000736 | 20 | 3080 | Planned | Planned interruption | Maintenance works at pole AE1728 SAF4473 - EAM1507070 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1144 | 2024-12-02-0003 | Waikawa - REC58 | CB109- Waikawa | 2024-12-02 09:05 | 2024-12-02 13:53 | 0.26496 | 0.00092 | 25 | 7200 | Planned | Planned interruption | Erire Bay Planned Work http://nams.mll.co.nz/Schedule/Edit/4400 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1145 | 2024-12-02-0004 | East Coast - ABS273-B | REC29-East Coast | 2024-12-02 09:17 | 2024-12-02 12:14 | 0.090675 | 0.0005152 | 14 | 2464 | Planned | Planned interruption | Clarence Valley Planned Work http://nams.mll.co.nz/Schedule/Edit/4405 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1146 | 2024-12-02-0008 | Grovetown - 0004421264ML155 | CB1465-Grovetown | 2024-12-02 09:37 | 2024-12-02 10:31 | 0 | 0 | 1 | 54 | Unplanned | Defective equipment | Burnt out fuse base replaced on red phase at TX pole. Advised electrician of outcome. EAM 1520780. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1147 | 2024-12-02-0006 | Pelorus - 0007713039ML912 | CB5126-Pelorus | 2024-12-02 09:46 | 2024-12-02 12:05 | 0 | 0 | 1 | 140 | Unplanned | Adverse weather | Replaced 2x blown 100A fuses. Suspect related to a lightning strike earlier in the year. EAM 1520779 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1148 | 2024-12-02-0010 | Rai Valley - FUSE3947 | CB43-Rai Valley | 2024-12-02 10:00 | 2024-12-02 14:42 | 0.04151 | 0.0001472 | 4 | 1128 | Planned | Planned interruption | Planned shutdown for vegetation removal http://nams.mll.linesmarl.co.nz/Schedule/Edit/4369 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1149 | 2024-12-02-0007 | Thomsons Ford Rd - 0004421448ML918 | CB1509-Thomsons Ford Rd | 2024-12-02 10:47 | 2024-12-02 10:58 | 0 | 0 | 1 | 11 | Unplanned | Unknown | Fault at property. Pole fuse replaced power restored | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1150 | 2024-12-02-0011 | Thomsons Ford Rd - 0003330211MLC2D | CB1509-Thomsons Ford Rd | 2024-12-02 13:07 | 2024-12-02 13:08 | 0 | 0 | 1 | 0 | Unplanned | Defective equipment | checked power OK and found that there is an internal issue so has told customer to call an electrcian. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1151 | 2024-12-03-0012 | Thomsons Ford Rd - SUB357109 | CB1509-Thomsons Ford Rd | 2024-12-03 08:15 | 2024-12-03 15:24 | 0.01575 | 3.68e-05 | 1 | 428 | Planned | Planned interruption | Conversion of SUB357109 to a single pole EAM 1505882 SAF4562 Outage 1 of 2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1152 | 2024-12-03-0014 | French Pass - SUB336206 | CB45-French Pass | 2024-12-03 08:30 | 2024-12-03 15:48 | 0.0003312 | 7.36e-05 | 1 | 9 | Planned | Planned interruption | Planned shutdown for tree removal under 11kV lines in McLarens Bay. Elaine Bay Gen running for Customers beyond ABS15341 SAF 4527 EAM 1507442 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1153 | 2024-12-03-0013 | Thomsons Ford Rd - SUB357108 | CB1509-Thomsons Ford Rd | 2024-12-03 08:32 | 2024-12-03 15:00 | 0.014278 | 3.68e-05 | 1 | 388 | Planned | Planned interruption | Conversion of SUB357109 to a single pole. Outage for this sub to increase clearance for live work EAM 1505882 SAF4562 Outage 2 of 2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1154 | 2024-12-04-0015 | Spring Creek - HVOH3163-S15560 | CB187-Spring Creek | 2024-12-04 08:30 | 2024-12-04 13:34 | 0.11187 | 0.000368 | 10 | 3040 | Planned | Planned interruption | Planned shutdown for maintenance at 2 sites in Marshlands. SAF 4490 EAM 1500000 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1155 | 2024-12-04-0016 | Sounds - ABS578-B | REC1170-Sounds | 2024-12-04 09:00 | 2024-12-04 12:10 | 0.3496 | 0.00184 | 50 | 9500 | Planned | Planned interruption | Planned shutdown to replace 11kV fuse and other maintenance work in area. EAM 1487287 http://nams.mll.linesmarl.co.nz/Schedule/Edit/4416 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1156 | 2024-12-04-0017 | Koromiko - 0006609341ML92C | CB55-Koromiko | 2024-12-04 10:51 | 2024-12-04 12:05 | 0 | 0 | 1 | 75 | Planned | Planned interruption | Planned Work http://nams.mll.co.nz/Schedule/Edit/4418 4/12/2024 12:10:10 pm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1157 | 2024-12-04-0018 | Taylor Pass - FUSE2035 | CB1089-Taylor Pass | 2024-12-04 14:50 | 2024-12-04 16:22 | 0.010267 | 0.0001104 | 3 | 279 | Unplanned | Defective equipment | JA1049 main pin on polymer strain drifting out. Maxwell Pass Road http://nams.mll.co.nz/Schedule/Edit/4454 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1158 | 2024-12-05-0019 | Grovetown - FUSE2177 | CB1465-Grovetown | 2024-12-05 04:02 | 2024-12-05 07:40 | 0.11283 | 0.0005152 | 14 | 3066 | Unplanned | Vegetation | Tree branch found in 11kV at pole JA0523 at 57 Staces Rd. Line isolated and removed under AP. EAM: 1521355 http://nams.mll.co.nz/Schedule/Edit/4457 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1159 | 2024-12-05-0020 | Richmond Brook - ENS7001-B | CB1250-Richmond Brook | 2024-12-05 08:30 | 2024-12-05 15:29 | 1.6711 | 0.0053728 | 127 | 45410 | Planned | Planned interruption | Planned shutdown for maintenance work at 3 sites. SAF 4117 EAM1456375 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1160 | 2024-12-05-0021 | Godfrey Road - SUB343247 | CB5367 Godfrey Road | 2024-12-05 08:30 | 2024-12-05 10:31 | 0.0044528 | 3.68e-05 | 1 | 121 | Planned | Planned interruption | Line re-sags beyond pole MA1488 in Wrekin Rd http://nams.mll.linesmarl.co.nz/Schedule/Edit/4419 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1161 | 2024-12-05-0022 | Nelson St - 0004450077ML626 | CB93-Nelson St | 2024-12-05 09:08 | 2024-12-05 10:30 | 0 | 0 | 1 | 82 | Unplanned | Defective equipment | Blown 200A service fuse, suspect internal. EAM 1521464 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1162 | 2024-12-05-0023 | Tuamarina - 0003310481MLC01 | CB188-Tuamarina | 2024-12-05 11:53 | 2024-12-05 13:26 | 0 | 0 | 1 | 93 | Unplanned | Unknown | Unable to locat any issues - customer advised that its mainly happening at night. Customer advised to ring immediately - so we can be on site to witness issue. EAM 1521491 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1163 | 2024-12-05-0024 | Godfrey Road - FUSE3001 | CB5367 Godfrey Road | 2024-12-05 12:30 | 2024-12-05 14:41 | 0.038566 | 0.0002944 | 8 | 1048 | Planned | Planned interruption | Planned shutdown for HV re-sag. EAM 1509225 SAF 4526.2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1164 | 2024-12-05-0025 | Rai Valley - 0007713326MLF62 | CB43-Rai Valley | 2024-12-05 13:37 | 2024-12-05 15:43 | 0 | 0 | 1 | 126 | Unplanned | Defective equipment | Blown fuse - suspect internal issue. EAM 1521505 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1165 | 2024-12-05-0026 | Sounds - HVOH305-S13259 | REC1170-Sounds | 2024-12-05 14:31 | 2024-12-05 16:37 | 0.6677 | 0.0052992 | 144 | 18144 | Unplanned | Third party interference | 11kV SEC5639 opened for a fire at pole VA2130 as requested by FENZ. On arrival, found fire extinguished and no network damage, however fire had burnt upto pole. EAM 1521517 http://nams.mll.co.nz/Schedule/Edit/4459 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1166 | 2024-12-05-0027 | Parker St - 0001137257MLECD | CB1516-Parker St | 2024-12-05 21:33 | 2024-12-05 22:00 | 0 | 0 | 1 | 28 | Unplanned | Defective equipment | Retailer disconnect EAM 1521545 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1167 | 2024-12-05-0028 | Omaka - CB1088 | CB1088 - Omaka | 2024-12-05 23:16 | 2024-12-06 13:53 | 1.3537 | 0.018878 | 513 | 36785 | Unplanned | Third party interference | Omaka Feeder tripped on phase OC and FENZ reported a vehicle accident on the cnr of New Renwick and Bells Rd. Found pole KB2251 destroyed and vehicle had fled the scene. Site isolated | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1168 | 2024-12-06-0029 | Koromiko - FUSE4006 | CB55-Koromiko | 2024-12-06 05:40 | 2024-12-06 07:59 | 0.094833 | 0.000736 | 20 | 2577 | Unplanned | Unknown | 2x fuses found blown at FUSE4006. Line patrolled, nothing found. Replaced fuses (30A) EAM 1521547 - http://nams.mll.co.nz/Schedule/Edit/4462 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1169 | 2024-12-06-0030 | Thomsons Ford Rd - ABS15425-B | CB1509-Thomsons Ford Rd | 2024-12-06 08:30 | 2024-12-06 14:19 | 0.038419 | 0.0001104 | 3 | 1044 | Planned | Planned interruption | Planned shutdown to shift 11kV Cable. EAM 1519345 SAF 4604 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1170 | 2024-12-06-0031 | Dashwood - SUB351072 | CB1252-Dashwood | 2024-12-06 08:44 | 2024-12-06 11:26 | 0.0059616 | 3.68e-05 | 1 | 162 | Planned | Planned interruption | Planned shutdown to upgrade LV service fuse. EAM 1519345 SAF 4604 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1171 | 2024-12-06-0032 | Ward - FUSE3492 | REC31-Ward | 2024-12-06 08:51 | 2024-12-06 13:58 | 0.022522 | 7.36e-05 | 2 | 612 | Planned | Planned interruption | Planned work to relocate & straighten poles. EAM 1370004 SAF 4448 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1172 | 2024-12-06-0034 | Dashwood - SUB350083 | CB1252-Dashwood | 2024-12-06 09:55 | 2024-12-06 11:53 | 0.0043424 | 3.68e-05 | 1 | 118 | Planned | Planned interruption | Planned shutdown for Transformer inspection. SAF 4573 EAM 1420367 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1173 | 2024-12-06-0033 | Ngakuta - SUB321105 | REC1562-Ngakuta | 2024-12-06 11:36 | 2024-12-06 12:47 | 0 | 0 | 2 | 144 | Planned | Planned interruption | Queen Charlotte Dve Planned Work http://nams.mll.co.nz/Schedule/Edit/4433 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1174 | 2024-12-06-0035 | Old Renwick Rd - 0003330346ML0EB | CB66-Old Renwick Rd | 2024-12-06 14:27 | 2024-12-06 15:39 | 0 | 0 | 1 | 72 | Unplanned | Defective equipment | Blown service fuse, no cause found EAM 1521707 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1175 | 2024-12-06-0036 | Rai Valley - CB5391 | CB43 - Rai Valley, CB45 - French Pass, CB5126 - Pelorus | 2024-12-06 23:45 | 2024-12-06 23:45 | 0 | 0 | 918 | 0 | Unplanned | Unknown | CB5391 (LVY-RAI) reclosed on EF. Cyclo 164 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1176 | 2024-12-07-0037 | Old Renwick Rd - 0004421460ML659 | CB66-Old Renwick Rd | 2024-12-07 12:07 | 2024-12-07 13:31 | 0 | 0 | 1 | 83 | Unplanned | Defective equipment | Fault had been restored previous day, 1ph pump in shed not working but all 3 phases live. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1177 | 2024-12-09-0045 | French Pass - FUSE4100 | CB45-French Pass | 2024-12-08 12:08 | 2024-12-09 16:06 | 0.32303 | 0.00276 | 75 | 8778 | Unplanned | Defective equipment | Bumping AC fail alarms for Saddle Hill radio site. Broken jumper found on the top of 11kV FUSE4100. Isolated main line and repaired connection. EAM 1521911 http://nams.mll.co.nz/Schedule/Edit/4467 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1178 | 2024-12-08-0040 | Kaituna - FUSE2111 | CB5448 Kaituna | 2024-12-08 16:28 | 2024-12-08 17:56 | 0.022411 | 0.0002576 | 7 | 609 | Unplanned | Defective equipment | 1x fuse open at 11kV FUSE2111 feeding Lamberts Rd. Line patrolled, nothing found. Replaced fuse (10A). on inspection, found fuse had fallen open W/O1521767 http://nams.mll.co.nz/Schedule/Edit/4463 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1179 | 2024-12-08-0039 | Craiglochart - 0002272549ML333 | REC1391-Craiglochart | 2024-12-08 17:06 | 2024-12-08 18:30 | 0 | 0 | 1 | 83 | Unplanned | Adverse weather | Blown fuse due to clashing condcutors. Open conductors, happens all the time ,1 failed 60-amp fuse EAM 1521768 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1180 | 2024-12-09-0046 | French Pass - REC5024 | CB45-French Pass | 2024-12-08 20:28 | 2024-12-08 20:28 | 0.0026496 | 0.0026496 | 72 | 72 | Unplanned | Unknown | REC5024 reclosed on phase oc. Trip 1 of 3. Strong winds at the time | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1181 | 2024-12-09-0047 | French Pass - REC5024 | CB45-French Pass | 2024-12-08 20:59 | 2024-12-08 21:00 | 0 | 0 | 72 | 0 | Unplanned | Unknown | REC5024 reclosed on phase oc. Trip 2 of 3. Strong winds at the time | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1182 | 2024-12-09-0048 | French Pass - REC5024 | CB45-French Pass | 2024-12-08 21:28 | 2024-12-08 21:28 | 0.0026496 | 0.0026496 | 72 | 72 | Unplanned | Unknown | REC5024 reclosed on phase oc. Trip 3 of 3. Strong winds at the time | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1183 | 2024-12-09-0041 | Grassmere - FUSE3449 | CB1253-Grassmere | 2024-12-09 05:39 | 2024-12-11 12:39 | 0.20729 | 0.000184 | 5 | 5633 | Unplanned | Defective equipment | Pole HA1816 failed and fell, causing damage to 2 downline private LV poles also. TX pole was replaced, and service to properties at SUB35220 converted to UG in conjunction with customer. W/O 1521770 http://nams.mll.co.nz/Schedule/Edit/4472 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1184 | 2024-12-09-0043 | Grassmere - REC28 | CB1253-Grassmere | 2024-12-09 06:33 | 2024-12-09 07:55 | 0.057334 | 0.0006992 | 19 | 1558 | Unplanned | Defective equipment | REC28 opened for safety following a lines down in Clifford Rd (2024-12-09-0041). http://nams.mll.co.nz/Schedule/Edit/4464 1521770 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1185 | 2024-12-09-0044 | Waikawa - FUSE4007 | CB109- Waikawa | 2024-12-09 08:54 | 2024-12-09 14:39 | 0.41775 | 0.0012144 | 33 | 11352 | Planned | Planned interruption | TX replacements in Curious Cove (Kiwi Ranch) http://nams.mll.linesmarl.co.nz/Schedule/Edit/4436 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1186 | 2024-12-09-0049 | Hawkesbury Road - SUB342003 | CB5457 Hawkesbury Road | 2024-12-09 16:40 | 2024-12-09 19:55 | 0.3641 | 0.0018768 | 51 | 9894 | Unplanned | Unknown | Found 1x TX fuse blown at SUB342003. On trial livening, fuse base exploded. Isolated HV and replaced all 3 TX fuse bases. See 2024-12-09-0052 and 2024-12-09-0053 fhttp://nams.mll.co.nz/Schedule/Edit/4473 EAM 1522070 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1187 | 2024-12-09-0052 | Waihopai Valley - RMUS5485 | CB5493 Waihopai Valley | 2024-12-09 18:53 | 2024-12-09 19:54 | 0.049385 | 0.0008096 | 22 | 1342 | Unplanned | Defective equipment | Outage for the replacement of broken TX fuse at SUB342003 in Anglesea St http://nams.mll.co.nz/Schedule/Edit/4473 EAM 1522070 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1188 | 2024-12-09-0053 | Hawkesbury Road - ABS15399-B | CB5457 Hawkesbury Road | 2024-12-09 18:54 | 2024-12-09 19:55 | 0.2604 | 0.0042688 | 116 | 7076 | Unplanned | Defective equipment | Outage for the replacement of broken TX fuse at SUB342003 in Anglesea St http://nams.mll.co.nz/Schedule/Edit/4473 EAM 1522070 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1189 | 2024-12-10-0054 | Sounds - HVOH305-S13258 | REC1170-Sounds | 2024-12-10 08:30 | 2024-12-10 12:23 | 1.2347 | 0.0052992 | 144 | 33552 | Planned | Planned interruption | Planned shutdown for TX replacement and pole replacement. EAM 1482743 SAF 4225 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1190 | 2024-12-10-0055 | Murphys Rd - 0001121041ML2C9 | CB68-Murphys Rd | 2024-12-10 10:08 | 2024-12-10 14:21 | 0 | 0 | 1 | 253 | Unplanned | Unknown | No fault found service tested 400v no one home CS updated EAM 1522193 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1191 | 2024-12-10-0056 | Waikawa - REC5191 | CB109- Waikawa | 2024-12-10 14:25 | 2024-12-10 15:31 | 2.6075 | 0.047987 | 1255 | 70857 | Unplanned | Third party interference | Car vs Pole near 289 Waikawa Rd REC 5191 Opened for safety Field staff confirmed pole OK and OK to liven Repairs to pole conducted later 1522298 http://nams.mll.co.nz/Schedule/Edit/4481 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1192 | 2024-12-10-0058 | Dashwood - 0005504360ML563 | CB1252-Dashwood | 2024-12-10 14:57 | 2024-12-10 17:50 | 0 | 0 | 1 | 173 | Unplanned | Unknown | Found a blown 100A fuse, replaced with 30A as per ARC. Restored 1750. EAM 1522310 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1193 | 2024-12-10-0059 | Waikawa - SUB330063 | CB109- Waikawa | 2024-12-10 15:20 | 2024-12-10 15:51 | 0.055899 | 0.0018032 | 49 | 1519 | Unplanned | Third party interference | Part of car vs pole PT5783 LV Wires clashing causing TX Fuses to blow. 1522298 http://nams.mll.co.nz/Schedule/Edit/4481 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1194 | 2024-12-10-0060 | Waikawa - LVOH130 | CB109- Waikawa | 2024-12-10 18:27 | 2024-12-11 10:40 | 0 | 0 | 21 | 6814 | Unplanned | Third party interference | Repairs to pole PT5783 after car vs pole EAM 1522298 http://nams.mll.co.nz/Schedule/Edit/4481 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1195 | 2024-12-11-0061 | Waikawa - 0006621342ML121 | CB109- Waikawa | 2024-12-11 06:02 | 2024-12-11 11:31 | 0 | 0 | 1 | 329 | Unplanned | Third party interference | Follow up fault from car vs pole pole. LV Configuration issues due to incorrect GIS data EAM 1522298 11/12/2024 7:19:58 am EAM 1522298 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1196 | 2024-12-11-0062 | Waikawa - 0006621439ML5AA | CB109- Waikawa | 2024-12-11 07:37 | 2024-12-11 11:31 | 0 | 0 | 1 | 233 | Unplanned | Third party interference | EAM 1522298 Follow up fault from car vs pole pole. LV Configuration issues due to incorrect GIS data | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1197 | 2024-12-11-0063 | Linkwater West - 0007709005MLB55 | REC1168-Linkwater West | 2024-12-11 08:25 | 2024-12-11 10:41 | 0 | 0 | 1 | 136 | Unplanned | Unknown | Yellow phase blown - cause unknow, fuse letter left on site EAM 1522490 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1198 | 2024-12-11-0064 | Havelock Canvastown - REC1475 | CB103 Havelock Canvastown | 2024-12-11 09:02 | 2024-12-11 13:12 | 0.2484 | 0.0009936 | 27 | 6750 | Planned | Planned interruption | Planned outage Whatanihi http://nams.mll.co.nz/Schedule/Edit/4439 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1199 | 2024-12-12-0071 | Craiglochart - LVOH8027 | REC1391-Craiglochart | 2024-12-11 09:30 | 2024-12-11 15:30 | 0 | 0 | 2 | 720 | Planned | Planned interruption | Waihoapi valley rd Planned Work http://nams.mll.co.nz/Schedule/Edit/4468 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1200 | 2024-12-11-0065 | Thomsons Ford Rd - 0004421366ML8D4 | CB1509-Thomsons Ford Rd | 2024-12-11 09:31 | 2024-12-11 13:52 | 0 | 0 | 1 | 260 | Unplanned | Defective equipment | Retail disconnect Faultman has discussed with customer EAM 1522516 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1201 | 2024-12-11-0066 | Sounds - REC85 | REC1170-Sounds | 2024-12-11 09:56 | 2024-12-11 13:58 | 0.53213 | 0.002208 | 60 | 14460 | Planned | Planned interruption | Crail Bay Planned Work http://nams.mll.co.nz/Schedule/Edit/4440 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1202 | 2024-12-11-0067 | Redwood St Nth - 0001190281ML088 | CB1655-Redwood St Nth | 2024-12-11 18:10 | 2024-12-11 21:00 | 0 | 0 | 1 | 170 | Unplanned | Defective equipment | Owner had been disconnected by their retailer. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1203 | 2024-12-12-0068 | East Coast - SUB352645 | REC29-East Coast | 2024-12-12 07:12 | 2024-12-12 09:41 | 0.0054464 | 3.68e-05 | 1 | 148 | Unplanned | Unknown | Blown 11kV Fuse SUB 352642 - http://nams.mll.co.nz/Schedule/Edit/4491 EAM 1522607 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1204 | 2024-12-12-0069 | Grovetown - SUB370291 | CB1465-Grovetown | 2024-12-12 08:30 | 2024-12-12 14:29 | 0.026422 | 7.36e-05 | 2 | 718 | Planned | Planned interruption | Replacement of pole and conductor re-sags http://nams.mll.linesmarl.co.nz/Schedule/Edit/4442 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1205 | 2024-12-12-0070 | Rai Valley - ABS216-B | CB43-Rai Valley | 2024-12-12 09:52 | 2024-12-12 12:51 | 0.21616 | 0.0012144 | 33 | 5874 | Unplanned | Unknown | Urgent shutdown to replace damaged POLE KB4455 http://nams.mll.co.nz/Schedule/Edit/4487 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1206 | 2024-12-13-0072 | Craiglochart - 0002272537ML5F5 | REC1391-Craiglochart | 2024-12-13 08:17 | 2024-12-13 11:41 | 0 | 0 | 1 | 205 | Unplanned | Unknown | Blown pole fuse, no cause found EAM 1522964 - Red phase gone | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1207 | 2024-12-13-0073 | Tuamarina - ABS15195-B | CB188-Tuamarina | 2024-12-13 08:30 | 2024-12-13 13:38 | 0.067785 | 0.0002208 | 6 | 1842 | Planned | Planned interruption | Planned shutdown to replace HV cross arms. EAM 1502762 SAF 4398 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1208 | 2024-12-13-0075 | Symons St - LVUG2728 | CB50-Symons St | 2024-12-13 08:30 | 2024-12-13 12:12 | 0 | 0 | 2 | 444 | Planned | Planned interruption | Planned shutdown to shift SFB 50 Seymour St EAM 1520132 SAF 4635 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1209 | 2024-12-13-0074 | Taylor Pass - 0002270022ML452 | CB1089-Taylor Pass | 2024-12-13 08:45 | 2024-12-13 10:55 | 0 | 0 | 1 | 130 | Planned | Planned interruption | Work completed using live procedures no TX Shutdown required Taylor Pass Road Planned Work http://nams.mll.co.nz/Schedule/Edit/4483 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1210 | 2024-12-13-0077 | East Coast - 0005507421ML661 | REC29-East Coast | 2024-12-13 12:30 | 2024-12-13 16:37 | 0 | 0 | 1 | 247 | Unplanned | Defective equipment | Blown pole fuse, possibly caused by trees clashing with the line, Corey advised that she should get her trees trimmed EAM 1523018 - Part power, 2PH 60A - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1211 | 2024-12-14-0083 | Tuamarina - CB187 | CB188-Tuamarina | 2024-12-14 15:21 | 2024-12-14 19:12 | 0.80397 | 0.0087216 | 184 | 21847 | Unplanned | Adverse weather | Lines down CB 187 Opened for safety ABR Scheme operated http://nams.mll.co.nz/Schedule/Edit/4495 1523103 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1212 | 2024-12-14-0080 | Renwick Township - 0000052195MLD09 | CB5482 Renwick Township | 2024-12-14 15:43 | 2024-12-14 16:59 | 0 | 0 | 1 | 76 | Unplanned | Defective equipment | Burntout Lv pole fuse, replaced with ABC fuse. EAM 1523104 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1213 | 2024-12-14-0089 | Renwick Township - 0000051322MLA96 | CB5482 Renwick Township | 2024-12-14 18:32 | 2024-12-14 20:25 | 0 | 0 | 1 | 113 | Unplanned | Defective equipment | Burnt out Lv fuse, replaced with an ABC fuse. EAM 1523105 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1214 | 2024-12-15-0091 | Grassmere - FUSE3196 | CB1253-Grassmere | 2024-12-15 08:20 | 2024-12-15 10:19 | 0.0090528 | 0.0001104 | 3 | 246 | Unplanned | Adverse weather | Blown fuse at fuse 3196 Cause unknown Replaced at 20amp 2024-12-15-0091 1523107 http://nams.mll.co.nz/Schedule/Edit/4499 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1215 | 2024-12-15-0092 | Spring Creek - 0003310207MLEC2 | CB187-Spring Creek | 2024-12-15 15:48 | 2024-12-15 16:55 | 0 | 0 | 1 | 67 | Unplanned | Defective equipment | Burntout Lv fuse, replaced with an ABC fuse. EAM 1523110 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1216 | 2024-12-16-0093 | Weld St - LVUG203 | CB71-Weld St | 2024-12-16 09:01 | 2024-12-16 11:05 | 0 | 0 | 15 | 1860 | Planned | Planned interruption | Newbourne Crescent Planned Work http://nams.mll.co.nz/Schedule/Edit/4449 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1217 | 2024-12-16-0094 | French Pass - FUSE4100 | CB45-French Pass | 2024-12-16 09:55 | 2024-12-16 16:29 | 0.043497 | 0.0001104 | 3 | 1182 | Planned | Planned interruption | Saddle Hill Planned Work http://nams.mll.co.nz/Schedule/Edit/4448 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1218 | 2024-12-16-0095 | Old Renwick Rd - CB66 | CB66-Old Renwick Rd | 2024-12-16 11:39 | 2024-12-16 12:14 | 0.32329 | 0.0092368 | 251 | 8785 | Unplanned | Unknown | CB66 tripped on EF. AR disabled at the time for live line works on feeder. Line patrolled, nothing found. Successfully relivened. Cyclo 71 http://nams.mll.co.nz/Schedule/Edit/4503 EAM 1523160 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1219 | 2024-12-16-0096 | Craiglochart - REC1345 | REC1391-Craiglochart | 2024-12-16 11:57 | 2024-12-16 12:15 | 0.010488 | 0.000552 | 15 | 285 | Unplanned | Adverse weather | Tripping of REC 1345 Trial close after 15 mins and stayed closed. Cause unknow suspect lightning http://nams.mll.co.nz/Schedule/Edit/4504 1523161 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1220 | 2024-12-16-0097 | Rapaura Rd - FUSE2591 | CB1077-Rapaura Rd | 2024-12-16 15:03 | 2024-12-16 16:49 | 0.035438 | 0.0003312 | 9 | 963 | Unplanned | Wildlife | Blown FUSE 2591 - suspect bird http://nams.mll.co.nz/Schedule/Edit/4516 EAM 1523172 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1221 | 2024-12-16-0099 | Havelock Canvastown - FUSE3637 | CB103 Havelock Canvastown | 2024-12-16 16:58 | 2024-12-16 17:35 | 0.006808 | 0.000184 | 5 | 185 | Unplanned | Adverse weather | Takorika Radio Hut Called in By MLL power alarm. Found fuse 3637 blown, suspect weather related. Replaced fuse (10A) 1523188 http://nams.mll.linesmarl.co.nz/Schedule/Edit/4519 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1222 | 2024-12-17-0120 | Sounds - SUB326017 | REC1170-Sounds | 2024-12-16 17:48 | 2024-12-17 11:19 | 0.039008 | 0.0001104 | 3 | 1060 | Unplanned | Lightning | Sub326017 1 Phase 15 3A SWER Blown TX Fuse Suspect lightning 1523189 http://nams.mll.co.nz/Schedule/Edit/4529 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1223 | 2024-12-16-0102 | Rai Valley - FUSE2292 | CB43-Rai Valley | 2024-12-16 19:03 | 2024-12-16 19:56 | 0.050269 | 0.0009568 | 26 | 1366 | Unplanned | Adverse weather | Blown Fuse 2292 Ronga Road Suspect Lightning 1523190 http://nams.mll.co.nz/Schedule/Edit/4520 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1224 | 2024-12-16-0103 | Craiglochart - REC1345 | REC1391-Craiglochart | 2024-12-16 20:27 | 2024-12-17 05:29 | 0.29863 | 0.001104 | 15 | 8115 | Unplanned | Adverse weather | Phase OC Tripping of REC 1345 Lightning event Feeder left off overnight for safety 1523191 http://nams.mll.co.nz/Schedule/Edit/4521 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1225 | 2024-12-16-0104 | Godfrey Road - REC5265 | CB5367 Godfrey Road | 2024-12-16 20:53 | 2024-12-17 07:25 | 0.20255 | 0.0006624 | 9 | 5504 | Unplanned | Lightning | Multiple no powers Brancott Road Lightning event http://nams.mll.co.nz/Schedule/Edit/4522 1523192 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1226 | 2024-12-16-0105 | Vernon - SUB349026 | CB5184-Vernon | 2024-12-16 21:02 | 2024-12-17 07:49 | 0.071429 | 0.0001104 | 3 | 1941 | Unplanned | Lightning | Replaced blown 11kV TX fuses at SUB349026. Blown due to lightning EAM 1523195 http://nams.mll.linesmarl.co.nz/Schedule/Edit/4526 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1227 | 2024-12-16-0106 | Pelorus - SUB335147 | CB5126-Pelorus | 2024-12-16 21:09 | 2024-12-17 06:41 | 0.02105 | 3.68e-05 | 1 | 572 | Unplanned | Lightning | Blown TX Fuse SUB 335147 Lightning 1523193 http://nams.mll.co.nz/Schedule/Edit/4523 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1228 | 2024-12-17-0111 | Wairau Valley - SUB3414BI | CB5399 Wairau Valley | 2024-12-16 21:13 | 2024-12-17 09:21 | 0.080371 | 0.0001104 | 3 | 2184 | Unplanned | Lightning | http://nams.mll.co.nz/Schedule/Edit/4525 Found 1 TX fuse blown and replaced all 3. Lightning in area. EAM 1523196 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1229 | 2024-12-17-0108 | Godfrey Road - SUB343055 | CB5367 Godfrey Road | 2024-12-17 06:31 | 2024-12-17 07:06 | 0.002576 | 7.36e-05 | 2 | 70 | Unplanned | Lightning | Blown TX Fuse Lightning http://nams.mll.co.nz/Schedule/Edit/4524 1523194 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1230 | 2024-12-17-0109 | Godfrey Road - SUB343081 | CB5367 Godfrey Road | 2024-12-17 07:58 | 2024-12-17 08:23 | 0.0017664 | 7.36e-05 | 2 | 48 | Unplanned | Lightning | TX fuse found blown while travelling down New Renwick Rd. Sub343081 Lightning in area. Replaced all 3 fuses. EAM 1523203 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1231 | 2024-12-17-0110 | Wairau Valley - SUB3414SQ | CB5399 Wairau Valley | 2024-12-17 08:24 | 2024-12-17 09:58 | 0.003496 | 3.68e-05 | 1 | 95 | Unplanned | Lightning | Found 1 blown TX fuse and replaced all 3 EAM 1523209 http://nams.mll.co.nz/Schedule/Edit/4528 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1232 | 2024-12-17-0112 | Wairau Valley - ENS7015-B | CB5399 Wairau Valley | 2024-12-17 08:30 | 2024-12-17 09:22 | 0.0019136 | 3.68e-05 | 1 | 52 | Planned | Planned interruption | Shutdown http://nams.mll.linesmarl.co.nz/Schedule/Edit/4452 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1233 | 2024-12-17-0113 | Wairau Valley - FUSE3814 | CB5399 Wairau Valley | 2024-12-17 08:30 | 2024-12-17 16:01 | 0.04979 | 0.0001104 | 3 | 1353 | Planned | Planned interruption | Planned shutdown for spur-line upgrade http://nams.mll.linesmarl.co.nz/Schedule/Edit/4452 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1234 | 2024-12-17-0118 | Wairau Valley - SUB3414BQ | CB5399 Wairau Valley | 2024-12-17 09:25 | 2024-12-17 11:07 | 0.0037904 | 3.68e-05 | 1 | 103 | Unplanned | Lightning | TX fuses blown and replaced. Lightning in area. EAM 1523216 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1235 | 2024-12-17-0119 | Richmond Brook - SUB353460 | CB1250-Richmond Brook | 2024-12-17 11:05 | 2024-12-17 11:19 | 0.001104 | 7.36e-05 | 2 | 30 | Unplanned | Lightning | EAM 1523257 TX fuse blown at SUB353460 Lightning in area. http://nams.mll.co.nz/Schedule/Edit/4536 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1236 | 2024-12-17-0121 | Craiglochart - SUB341129 | REC1391-Craiglochart | 2024-12-17 11:41 | 2024-12-17 11:44 | 0.0002208 | 7.36e-05 | 2 | 6 | Unplanned | Lightning | SUB341129 1 Phase 50kVa SWER 6A Lightning EAM 1523213 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1237 | 2024-12-17-0122 | Craiglochart - SUB341133 | REC1391-Craiglochart | 2024-12-17 11:51 | 2024-12-17 12:01 | 0.0003312 | 3.68e-05 | 1 | 9 | Unplanned | Lightning | Blown 11kV Fuse SUB 341133 Lightning EAM 1523463 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1238 | 2024-12-17-0123 | Wairau Valley - ENS7015-B | CB5399 Wairau Valley | 2024-12-17 15:21 | 2024-12-17 16:00 | 0.0014352 | 3.68e-05 | 1 | 39 | Planned | Planned interruption | Shutdown of Kea Solar Farm for live work at 1746 SH63 http://nams.mll.linesmarl.co.nz/Schedule/Edit/4452 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1239 | 2024-12-17-0124 | Godfrey Road - SUB343055 | CB5367 Godfrey Road | 2024-12-17 17:35 | 2024-12-17 19:09 | 0.0069184 | 7.36e-05 | 2 | 188 | Unplanned | Lightning | found 1 TX fuse had blown but not dropped out. Replaced all 3. Lightning in area last night http://nams.mll.co.nz/Schedule/Edit/4546 EAM1523704 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1240 | 2024-12-17-0125 | Sounds - 0008813393ML213 | REC1170-Sounds | 2024-12-17 21:00 | 2024-12-18 01:50 | 0 | 0 | 1 | 291 | Unplanned | Defective equipment | Trurip arcing at pole by house. Repair made. Awaiting details from crew to pass on for possible replacement quote 1523705 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1241 | 2024-12-18-0126 | Vernon - SUB349029 | CB5184-Vernon | 2024-12-18 07:30 | 2024-12-18 08:54 | 0.003128 | 3.68e-05 | 1 | 85 | Unplanned | Lightning | EAM 1523706 http://nams.mll.co.nz/Schedule/Edit/4547 Found TX fuse burnt in half. Replaced both. Lightning in area recently | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1242 | 2024-12-18-0127 | Kaituna - ABS535-B | CB5448 Kaituna | 2024-12-18 08:30 | 2024-12-18 13:41 | 0.32524 | 0.0019872 | 54 | 8838 | Planned | Planned interruption | Various maintenance tasks beyond ABS535 - Onamalutu http://nams.mll.linesmarl.co.nz/Application/Edit/4422 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1243 | 2024-12-18-0128 | Vernon - SUB349031 | CB5184-Vernon | 2024-12-18 09:01 | 2024-12-18 09:22 | 0.0008096 | 3.68e-05 | 1 | 22 | Unplanned | Lightning | TX fuses blown on arrival. Was working on another fault on the same property but a different Sub Lightning in area recently. EAM1523706 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1244 | 2024-12-18-0129 | Pelorus - SUB335153 | CB5126-Pelorus | 2024-12-18 10:00 | 2024-12-18 11:55 | 0.004232 | 3.68e-05 | 1 | 115 | Unplanned | Lightning | Found 1 blown TX fuse and replaced both. Lightning in area recently. http://nams.mll.co.nz/Schedule/Edit/4549 EAM 1523795 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1245 | 2024-12-18-0130 | East Coast - 0005516255MLD71 | REC29-East Coast | 2024-12-18 11:46 | 2024-12-18 16:25 | 0 | 0 | 1 | 280 | Unplanned | Defective equipment | Faulty LV fuse holder replaced. EAM 1523819 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1246 | 2024-12-18-0131 | East Coast - REC24 | REC29-East Coast | 2024-12-18 12:22 | 2024-12-18 15:25 | 0.053875 | 0.0002944 | 8 | 1464 | Planned | Planned interruption | Planned urgent shutdown to install line fault indicators to locate intermitent fault. EAM 1504281 http://nams.mll.co.nz/Schedule/Edit/4518 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1247 | 2024-12-18-0132 | Wairau Valley - SUB341590 | CB5399 Wairau Valley | 2024-12-18 12:55 | 2024-12-18 14:35 | 0 | 0 | 1 | 100 | Planned | Planned interruption | Planned shutdown to remove redundant LV service at SUB341590 http://nams.mll.linesmarl.co.nz/Schedule/Edit/4453 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1248 | 2024-12-18-0133 | Koromiko - LVOH200070-S100 | CB55-Koromiko | 2024-12-18 15:20 | 2024-12-18 18:01 | 0 | 0 | 1 | 160 | Unplanned | Third party interference | 1ph NS conductor replaced EAM 1523889 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1249 | 2024-12-19-0134 | Thomsons Ford Rd - ABS1847-B | CB1509-Thomsons Ford Rd | 2024-12-19 08:30 | 2024-12-19 13:55 | 0.25116 | 0.0007728 | 21 | 6825 | Planned | Planned interruption | Replacement of pole KB9426 and fuse arm at SUB357152 - http://nams.mll.linesmarl.co.nz/Schedule/Edit/4470 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1250 | 2024-12-19-0135 | Hawkesbury Road - ABS287-B | CB5457 Hawkesbury Road | 2024-12-19 08:40 | 2024-12-19 13:57 | 0.18606 | 0.0005888 | 16 | 5056 | Planned | Planned interruption | Planned shutdown to replace pole PT1997. EAM 1509337 SAF 4554 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1251 | 2024-12-19-0137 | Craiglochart - SUB341123 | REC1391-Craiglochart | 2024-12-19 10:19 | 2024-12-19 12:09 | 0.0040848 | 3.68e-05 | 1 | 111 | Unplanned | Lightning | Original fault logged under wrong ICP.Found blown TX fuse and replaced. Lightning in area recently. http://nams.mll.co.nz/Schedule/Edit/4555 EAM 1524016 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1252 | 2024-12-19-0138 | Parker St - 0001137061ML2BD | CB1516-Parker St | 2024-12-19 19:58 | 2024-12-19 21:09 | 0 | 0 | 1 | 71 | Unplanned | Defective equipment | Burnt jumper - replaced 1524131 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1253 | 2024-12-19-0139 | Hawkesbury Road - LVOH7423-S22382 | CB5457 Hawkesbury Road | 2024-12-19 20:08 | 2024-12-19 22:59 | 0.010966 | 7.36e-05 | 2 | 298 | Unplanned | Defective equipment | LV line down between poles JA3806 & JA3810. Isolated at SUB343019 a EAM 1524132 http://nams.mll.co.nz/Schedule/Edi | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1254 | 2024-12-20-0140 | Omaka - LVOH5494 | CB1088 - Omaka | 2024-12-20 08:42 | 2024-12-20 09:34 | 0 | 0 | 2 | 104 | Planned | Planned interruption | Planned shutdown to pull up low span accross Bells Rd. EAM 1519045 SAF 4609 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1255 | 2024-12-20-0142 | Waikawa - LVOH242-S8275 | CB109- Waikawa | 2024-12-20 08:48 | 2024-12-20 09:56 | 0 | 0 | 1 | 68 | Planned | Planned interruption | East Bay Planned Work http://nams.mll.co.nz/Application/Edit/4496 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1256 | 2024-12-20-0144 | Waikawa - CB2052 | CB187 - Spring Creek, CB188 - Tuamarina, CB1077 - Rapaura Rd, CB1465 - Grovetown, CB54 - Scotland St, CB55 - Koromiko, CB108 - Buller St, CB109 - Waikawa | 2024-12-20 09:52 | 2024-12-20 09:52 | 0 | 0 | 3317 | 0 | Unplanned | Unknown | Auto reclose on 33kV CB2052 BLN-SCK-TUA -2 at Transpower GXP. Earth fault red phase zone 2. DM patrolling line. EAM1524149 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1257 | 2024-12-21-0145 | Sounds - SUB326058 | REC1170-Sounds | 2024-12-21 16:51 | 2024-12-22 09:10 | 0.072054 | 7.36e-05 | 2 | 1958 | Unplanned | Wildlife | TX fuse blown and dead bird at the base of the pole. Confirmed power restored at meter board. EAM 1524183 http://nams.mll.co.nz/Schedule/Edit/4560 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1258 | 2024-12-21-0146 | Godfrey Road - 0002270406ML40C | CB5367 Godfrey Road | 2024-12-21 20:43 | 2024-12-21 21:26 | 0 | 0 | 1 | 43 | Unplanned | Defective equipment | Internal fault EAM: 1524184 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1259 | 2024-12-22-0148 | Colemans Rd - 0001133160ML17C | CB1512-Colemans Rd | 2024-12-22 17:08 | 2024-12-22 18:30 | 0 | 0 | 1 | 82 | Unplanned | Third party interference | Gyro appears to have been hit by vehicle, no damage to box, broken fuse holder. Replaced EAM 1524185 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1260 | 2024-12-23-0151 | Ngakuta - 0007716440ML93F | REC1562-Ngakuta | 2024-12-23 15:21 | 2024-12-23 17:46 | 0 | 0 | 1 | 145 | Unplanned | Defective equipment | burnt out service fuse carier at SUB321167 and replaced using WI. Confirmed power restored at boat shed. EAM 1524563 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1261 | 2024-12-23-0152 | Rai Valley - SUB335036 | CB43-Rai Valley | 2024-12-23 16:01 | 2024-12-23 16:13 | 0.0004416 | 3.68e-05 | 1 | 12 | Unplanned | Adverse weather | Blown TX Fuse feed to pump suspect lightning EAM 1524561 http://nams.mll.co.nz/Schedule/Edit/4566 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1262 | 2024-12-23-0153 | Richmond Brook - REC36 | CB1250-Richmond Brook | 2024-12-23 19:38 | 2024-12-24 14:15 | 1.2827 | 0.001288 | 35 | 34857 | Unplanned | Lightning | Mainline patrolled and sectionalized along the way then relivened. Found blown fuses at SUB353530, SUB353540, SUB353525 All fuses replaced and power restored. EAM1524565 http://nams.mll.co.nz/Schedule/Edit/4567 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1263 | 2024-12-24-0154 | East Coast - ABS273-B | REC29-East Coast | 2024-12-24 09:32 | 2024-12-24 10:23 | 0.02679 | 0.0005152 | 14 | 728 | Unplanned | Unknown | Clarence Fault Shutdown to by pass REC24 to assist in fault finding. http://nams.mll.co.nz/Schedule/Edit/4564 1504281 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1264 | 2024-12-24-0155 | East Coast - FUSE4180 | REC29-East Coast | 2024-12-24 17:11 | 2024-12-24 18:12 | 0.0068448 | 0.0001104 | 3 | 186 | Unplanned | Lightning | SUB352750 blown fuse Line patrol carried out on south side of river 3 x SUBs Fuse4180 Blown north side of river Fuse 4180 replaced Fuse replaced at SUB352750 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1265 | 2024-12-25-0157 | Parker St - 0001140577ML243 | CB1516-Parker St | 2024-12-25 09:40 | 2024-12-25 10:55 | 0 | 0 | 1 | 75 | Unplanned | Defective equipment | Burnt cutout | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1266 | 2024-12-26-0159 | Rai Valley - CB5391 | CB43 - Rai Valley, CB45 - French Pass, CB5126 - Pelorus | 2024-12-26 09:06 | 2024-12-26 09:06 | 0 | 0 | 917 | 0 | Unplanned | Unknown | Successful reclose Earth Fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1267 | 2024-12-26-0160 | Waikawa - 0006617118ML553 | CB109- Waikawa | 2024-12-26 19:43 | 2024-12-26 20:35 | 0 | 0 | 1 | 51 | Unplanned | Vegetation | Tree on service line. Cut away EAM: 1524615 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1268 | 2024-12-26-0161 | Riverlands - 0001116523MLDF5 | CB1181-Riverlands | 2024-12-26 20:23 | 2024-12-27 09:40 | 0 | 0 | 1 | 797 | Unplanned | Unknown | Job attended, no one on site, no problem found. Customer called and voicemail left, customer has not returned call EAM 1524616 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1269 | 2024-12-27-0162 | Flaxbourne - FUSE3891 | REC1432-Flaxbourne | 2024-12-27 12:21 | 2024-12-27 15:15 | 0.012806 | 7.36e-05 | 2 | 348 | Unplanned | Adverse weather | Non consistent voltage found at LV side of Tx Checked FUSE3891 found blown fuses, carried out line patrol no obvious cause Replaced Fuses at FUSE3891 LV voltage confirmed restored EAM1524619 NAMSF4569 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1270 | 2024-12-28-0163 | East Coast - FUSE4180 | REC29-East Coast | 2024-12-28 08:40 | 2024-12-28 18:59 | 0.06267 | 0.0001104 | 3 | 1703 | Unplanned | Human error | EAM1524623 NAMSF4570 Found blown fuse at SUB352750 and also blown fuse at FUSE4180 FUSE4180 replaced at 6 Amp, SUB352750 replaced b | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1271 | 2024-12-28-0164 | Murphys Rd - 0001121321MLE3A | CB68-Murphys Rd | 2024-12-28 08:46 | 2024-12-28 10:21 | 0 | 0 | 1 | 96 | Unplanned | Unknown | No supply loss, meter board cover fallen off | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1272 | 2024-12-28-0165 | Dashwood - 0005504412MLFB9 | CB1252-Dashwood | 2024-12-28 09:27 | 2024-12-28 10:09 | 0 | 0 | 1 | 42 | Unplanned | Defective equipment | Customer phoned back to cancel | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1273 | 2024-12-28-0166 | East Coast - REC33 | REC29-East Coast | 2024-12-28 11:22 | 2024-12-28 17:43 | 0.35089 | 0.0051888 | 66 | 9535 | Unplanned | Defective equipment | http://nams.mll.linesmarl.co.nz/Schedule/Edit/4570 e 2024-12-28-0163 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1274 | 2024-12-29-0168 | Jacksons Rd - CB1179 | CB1179 - Jacksons Rd | 2024-12-29 06:58 | 2024-12-29 07:15 | 0.06256 | 0.00368 | 100 | 1700 | Unplanned | Unknown | Trip to Lockout on PH OC Manual reclose after 15mins, Circuit restored Line patrol to be carried out | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1275 | 2024-12-29-0169 | Pelorus - 0007713205ML7F3 | CB5126-Pelorus | 2024-12-29 11:24 | 2024-12-29 13:54 | 0 | 0 | 1 | 150 | Unplanned | Defective equipment | Blown 60A HRC, suspect internal fault EAM 1524624 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1276 | 2024-12-29-0170 | Grassmere - 0005506245MLF3D | CB1253-Grassmere | 2024-12-29 14:09 | 2024-12-29 20:20 | 0 | 0 | 1 | 372 | Unplanned | Vegetation | Willow tree through service line (outside customer boundary). Broken LV arm and 3ph supply EAM1524625 -- | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1277 | 2024-12-30-0171 | Craiglochart - REC1391 | REC1391-Craiglochart | 2024-12-30 01:12 | 2024-12-30 04:57 | 0.58125 | 0.0046368 | 126 | 15795 | Unplanned | Wildlife | Line patrol carried out Possum found and removed at pole BS2327 Power restored EAM1524626 NAMSF4572 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1278 | 2024-12-30-0172 | Koromiko - SUB331017 | CB55-Koromiko | 2024-12-30 09:43 | 2024-12-30 11:29 | 0.0039008 | 3.68e-05 | 1 | 106 | Unplanned | Third party interference | digger has touched lines and blown pole fuse 2x 11kV fuses replaced power confirmed restored EAM1524627 NAMSF4573 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1279 | 2024-12-30-0173 | East Coast - SUB352750 | REC29-East Coast | 2024-12-30 13:10 | 2024-12-31 17:10 | 0.065577 | 0.0001104 | 3 | 1782 | Unplanned | Defective equipment | TX at SUB352750 replaced due to ongoing faults. FUSE4029 opened during replacement for proximity to crane.. EAM 1524630 http://nams.mll.co.nz/Schedule/Edit/4586 -- | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1280 | 2024-12-30-0174 | Richmond Brook - 0005505423ML5A4 | CB1250-Richmond Brook | 2024-12-30 14:57 | 2024-12-30 17:06 | 0.004784 | 3.68e-05 | 1 | 130 | Unplanned | Lightning | Found blown Tx fuses, probable lightning as cause, Replaced fuses power confirmed restored http://nams.mll.linesmarl.co.nz/Schedule/Edit/4575 EAM1524631 NAMSF4575 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1281 | 2024-12-30-0175 | Taylor Pass - 0001191030ML5D8 | CB1089-Taylor Pass | 2024-12-30 15:58 | 2024-12-30 17:49 | 0 | 0 | 1 | 110 | Unplanned | Defective equipment | EAM 1524632 Internal issue Safety Disc due to damaged mains cable. COC to be provided prior to livening | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1282 | 2024-12-30-0190 | Craiglochart - FUSE3896 | REC1391-Craiglochart | 2024-12-30 16:08 | 2025-01-01 12:17 | 0.34246 | 0.000184 | 4 | 9306 | Unplanned | Lightning | SUB's 341321 and 341323 both failed during lightning. Both TX's replaced and relivened. TEAM 1524633 http://nams.mll.co.nz/Schedule/Edit/4577 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1283 | 2024-12-30-0188 | Craiglochart - SUB341311 | REC1391-Craiglochart | 2024-12-30 16:21 | 2024-12-30 20:37 | 0.018842 | 7.36e-05 | 2 | 512 | Unplanned | Lightning | Found 2 blown HV fuses, LV checks out OK , lightning probable cause Fuses replaced Power restored http://nams.mll.linesmarl.co.nz/Schedule/Edit/4576 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1284 | 2024-12-30-0181 | Pelorus - REC5152 | CB5126-Pelorus | 2024-12-30 16:48 | 2024-12-30 18:58 | 0.31273 | 0.0028704 | 72 | 8498 | Unplanned | Lightning | Fenz F4119193 as a burning TX following lightning strike REC5152 opened for safety Blown fuse at SUB335155 , but no evidence of fire Fuses replaced and power confirmed restored http://nams.mll.linesmarl.co.nz/Schedule/Edit/4574 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1285 | 2024-12-30-0185 | Havelock Canvastown - REC1469 | CB103 Havelock Canvastown | 2024-12-30 17:27 | 2024-12-30 17:28 | 0.0008096 | 0.0008096 | 22 | 22 | Unplanned | Human error | Operator error open REC1469 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1286 | 2024-12-30-0184 | Pelorus - 0007713191MLA1D | CB5126-Pelorus | 2024-12-30 17:40 | 2024-12-30 19:19 | 0.0036432 | 3.68e-05 | 1 | 99 | Unplanned | Lightning | 2 x blown fuses found, lightning cause, LV looks OK Fuses repalced power confirmed restored http://nams.mll.linesmarl.co.nz/Schedule/Edit/4578 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1287 | 2024-12-30-0186 | Rai Valley - SUB335325 | CB43-Rai Valley | 2024-12-30 17:40 | 2024-12-30 19:42 | 0.013579 | 0.0001104 | 3 | 369 | Unplanned | Lightning | Found 2 x blown fuses SUB335325 - lightning Power confirmed restored http://nams.mll.linesmarl.co.nz/Schedule/Edit/4579 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1288 | 2024-12-30-0187 | Rai Valley - 0007714289ML5C7 | CB43-Rai Valley | 2024-12-30 19:27 | 2024-12-30 20:03 | 0.0013616 | 3.68e-05 | 1 | 37 | Unplanned | Lightning | Found 2 x blown fuses SUB335313 - Lightning Power confirmed restored http://nams.mll.linesmarl.co.nz/Schedule/Edit/4580 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1289 | 2024-12-30-0189 | Wairau Valley - FUSE4107 | CB5399 Wairau Valley | 2024-12-30 19:54 | 2024-12-31 17:01 | 0.046625 | 3.68e-05 | 1 | 1267 | Unplanned | Unknown | TX at SUB341560 failed as a result of lightning. Replaced TX and relivened. Fault also caused FUSE4107 to blow. EAM: 1524644 http://nams.mll.co.nz/Schedule/Edit/4584 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1290 | 2024-12-30-0191 | Craiglochart - SUB341310 | REC1391-Craiglochart | 2024-12-30 20:29 | 2024-12-30 20:45 | 0.0005888 | 3.68e-05 | 1 | 16 | Unplanned | Lightning | Found 2 blown HV fuses, LV checks out OK , lightning probable cause Fuses replaced Power restored http://nams.mll.linesmarl.co.nz/Schedule/Edit/4581 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1291 | 2024-12-30-0192 | Pelorus - SUB335119 | CB5126-Pelorus | 2024-12-30 21:06 | 2024-12-31 09:45 | 0.055862 | 7.36e-05 | 2 | 1518 | Unplanned | Lightning | 2x blown HV fuses found at SUB335119 as a result of lightning. Replaced fuses (3A) and confirmed power restored. EAM 1524645 http://nams.mll.co.nz/Schedule/Edit/4585 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1292 | 2024-12-31-0193 | Kaituna - SUB340007 | CB5448 Kaituna | 2024-12-31 04:32 | 2024-12-31 08:45 | 0.018694 | 7.36e-05 | 2 | 508 | Unplanned | Lightning | 1x blown HV fuse found at SUB340007 from lightning. Replaced fuses (3A) EAM 1524647 http://nams.mll.co.nz/Schedule/Edit/4583 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1293 | 2024-12-31-0194 | Sounds - 0008812409ML1C7 | REC1170-Sounds | 2024-12-31 08:51 | 2024-12-31 13:30 | 0 | 0 | 1 | 280 | Unplanned | Defective equipment | DM and NS attended and repaired faulty trurip. To be referred to customer works to price replacement. EAM 1524650 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1294 | 2024-12-31-0195 | Pelorus - SUB335153 | CB5126-Pelorus | 2024-12-31 08:53 | 2024-12-31 10:40 | 0.0039376 | 3.68e-05 | 1 | 107 | Unplanned | Lightning | 1x blown HV fuse found at SUB335153 following lightning. Replaced fuses (3A) and confirmed power restored EAM 1524649 http://nams.mll.co.nz/Schedule/Edit/4589 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1295 | 2024-12-31-0198 | Craiglochart - SUB341309 | REC1391-Craiglochart | 2024-12-31 09:15 | 2025-01-01 14:26 | 0.064437 | 3.68e-05 | 1 | 1751 | Unplanned | Lightning | SUB341309 failed as a result of lightning. Replaced TX following day and relivened. Delayed restoration due to lack of resource EAM 1524651 http://nams.mll.co.nz/Schedule/Edit/4587 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1296 | 2024-12-31-0196 | Craiglochart - 0002273225ML17F | REC1391-Craiglochart | 2024-12-31 09:45 | 2024-12-31 09:46 | 0 | 0 | 1 | 1 | Unplanned | Defective equipment | All connections were re-tightened. Suspect related to faults on REC1391 and lightning issues over previous nights. EAM1524653 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1297 | 2024-12-31-0197 | Pelorus - SUB335122 | CB5126-Pelorus | 2024-12-31 09:53 | 2024-12-31 10:11 | 0.0006256 | 3.68e-05 | 1 | 17 | Unplanned | Lightning | spotted 3x blown fuses at SUB335122 following lightning. Replaced fuses (3A) http://nams.mll.co.nz/Schedule/Edit/4588 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1298 | 2024-12-31-0199 | Wairau Valley - REC1697 | CB5399 Wairau Valley | 2024-12-31 10:21 | 2024-12-31 10:22 | 0 | 0 | 20 | 0 | Unplanned | Lightning | REC1697 reclosed while fault finding for fault at SUB341560. http://nams.mll.co.nz/Schedule/Edit/4584 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1299 | 2024-12-31-0200 | Grovetown - SUB361134 | CB1465-Grovetown | 2024-12-31 12:03 | 2024-12-31 13:46 | 0.0075808 | 7.36e-05 | 2 | 206 | Unplanned | Lightning | 1x HV fuse found blown at SUB361134, suspect lightning related. Replaced fuses (6A) . EAM1524652 http://nams.mll.co.nz/Schedule/Edit/4590 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1300 | 2024-12-31-0201 | Sounds - 0008813017ML550 | REC1170-Sounds | 2024-12-31 17:09 | 2025-01-01 16:12 | 0 | 0 | 1 | 1382 | Unplanned | Vegetation | Faulty trurip where vegetation has been rubbing. made repair, tagged and relivened. To be referred to Customer Works to price replacement. EAM1524654 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1301 | 2025-01-01-0001 | Parker St - 0001137437ML73B | CB1516-Parker St | 2025-01-01 11:30 | 2025-01-01 18:00 | 0 | 0 | 1 | 390 | Unplanned | Other Cause | Sparking lines found trees had been rubbing against service. Line has been disconnected and lowered to allow trees to be cut. returned and replaced trurip with NS and relivened. EAM 1524656 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1302 | 2025-01-03-0003 | Ward - 0005507109MLC25 | REC31-Ward | 2025-01-03 06:59 | 2025-01-03 10:50 | 0 | 0 | 1 | 232 | Unplanned | Adverse weather | 7/18 Cu service line on the deck, suspect wind from a couple of weeks ago repaired and restored at 1050. EAM 1524659 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1303 | 2025-01-03-0005 | Kaituna - SUB340051 | CB5448 Kaituna | 2025-01-03 16:24 | 2025-01-03 17:51 | 0.0032016 | 3.68e-05 | 1 | 87 | Unplanned | Lightning | 2x blown HV fuses at SUB340051 due to lightning. Replaced both fuses (3A) http://nams.mll.co.nz/Schedule/Edit/4592 EAM 1524662 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1304 | 2025-01-04-0007 | Richmond Brook - SUB353530 | CB1250-Richmond Brook | 2025-01-04 13:12 | 2025-01-04 15:34 | 0.010525 | 7.36e-05 | 2 | 286 | Unplanned | Lightning | TX fuse blown at SUB353530, suspect as a result of lightning. Replaced fuse (3A). EAM 1524663 http://nams.mll.co.nz/Schedule/Edit/4593 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1305 | 2025-01-04-0008 | Weld St - 0001172375ML6AC | CB71-Weld St | 2025-01-04 18:16 | 2025-01-04 19:10 | 0 | 0 | 1 | 54 | Unplanned | Unknown | Blown 30A pole fuse on white phase, unknown cause. Restored 1910. WO 1524664 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1306 | 2025-01-05-0009 | Koromiko - FUSE2957 | CB55-Koromiko | 2025-01-05 07:31 | 2025-01-05 08:50 | 0.017664 | 0.0002208 | 6 | 480 | Unplanned | Unknown | Centre and Road side fuses blown at FUSE2957. Line patrolled, nothing found. Replaced all 3 fuses (15A). EAM 1524665 http://nams.mll.co.nz/Schedule/Edit/4595 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1307 | 2025-01-05-0010 | French Pass - REC160 | CB45-French Pass | 2025-01-05 15:32 | 2025-01-05 15:32 | 0.0006256 | 0.0006256 | 17 | 17 | Unplanned | Unknown | REC160 - Squally Cove, reclosed on phase OC. Cyclo 49. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1308 | 2025-01-06-0011 | Waihopai Valley - SUB3410AQ | CB5493 Waihopai Valley | 2025-01-06 08:30 | 2025-01-06 09:37 | 0.0024656 | 3.68e-05 | 1 | 67 | Planned | Planned interruption | Planned shutdown for customer work. Replacing exiting service fuses and adding another for new supply. EAM 1520510 SAF 4626 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1309 | 2025-01-06-0012 | Okaramio - FUSE3610 | CB104 Okaramio | 2025-01-06 09:12 | 2025-01-06 13:49 | 0.091742 | 0.0003312 | 9 | 2493 | Unplanned | Third party interference | Urgent shutdown to replace broken pole KB9446. EAM 1524661 SAF F4596 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1310 | 2025-01-06-0013 | Tuamarina - SUB356137 | CB188-Tuamarina | 2025-01-06 15:57 | 2025-01-06 18:56 | 0.019762 | 0.0001104 | 3 | 537 | Unplanned | Third party interference | Lines down reported found 4 conductors down between SUB356137 and pole NK1983. Isolated sub, repaired conductors and relivened. http://nams.mll.co.nz/Schedule/Edit/4599 EAM1524984 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1311 | 2025-01-07-0014 | Sounds - REC1170 | CB1170 - Sounds | 2025-01-07 00:43 | 2025-01-07 00:44 | 0 | 0 | 1123 | 0 | Unplanned | Unknown | 11kV REC1170 (Sounds Feeder) reclosed on EF. Cyclo 32. Fault not picked up by any downline devices | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1312 | 2025-01-07-0015 | Waihopai Valley - SUB3414AY | CB5493 Waihopai Valley | 2025-01-07 08:39 | 2025-01-07 08:58 | 0.0013984 | 7.36e-05 | 2 | 38 | Unplanned | Wildlife | Urgent TX shutdown to remove possum from LV bushings. F4600 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1313 | 2025-01-07-0016 | Pelorus - REC5113 | CB5126-Pelorus | 2025-01-07 09:00 | 2025-01-07 13:10 | 0.184 | 0.000736 | 20 | 5000 | Planned | Planned interruption | Planned shutdown to remove burning willow trees from 11kV line. EAM 1496754 SAF 4631 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1314 | 2025-01-07-0017 | French Pass - 0008805353ML8DD | CB45-French Pass | 2025-01-07 21:41 | 2025-01-08 12:59 | 0 | 0 | 1 | 918 | Unplanned | Other cause | Replace Burnt out fuse in SFB Wo 1525837 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1315 | 2025-01-08-0018 | East Coast, REC31 - Ward, REC1432 - Flaxbourne - CB5412 | REC29 - East Coast, REC31 - Ward, REC1432 - Flaxbourne | 2025-01-08 08:50 | 2025-01-08 09:11 | 0.21955 | 0.011592 | 315 | 5966 | Unplanned | Unknown | Tripping of CB 5412 causing loss of supply to Ward Sub No calls received. Trial close - in and holding. http://nams.mll.co.nz/Schedule/Edit/4603 1525847 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1316 | 2025-01-08-0021 | Ngakuta - SUB321105 | REC1562-Ngakuta | 2025-01-08 12:13 | 2025-01-08 13:27 | 0 | 0 | 2 | 148 | Planned | Planned interruption | SD of SUB321105 for OHUG of servie at 1397 Queen Charlotte Drive SAF 4634 EAM1509231 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1317 | 2025-01-08-0022 | Taylor Pass - 0001196083MLFCA | CB1089-Taylor Pass | 2025-01-08 15:21 | 2025-01-08 16:37 | 0 | 0 | 1 | 77 | Unplanned | Other cause | Replaced burnt out fuse in SFB WO 1527345 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1318 | 2025-01-09-0023 | Taylor Pass - FUSE2943 | CB1089-Taylor Pass | 2025-01-09 08:34 | 2025-01-09 13:17 | 0.062707 | 0.0002208 | 6 | 1704 | Planned | Planned interruption | Replacement of red tagged pole AA1513 at 66 Maxwell Pass Rd SAF 4640 - EAM 1522116 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1319 | 2025-01-09-0024 | Omaka - SUB362209 | CB1088 - Omaka | 2025-01-09 08:37 | 2025-01-09 12:00 | 0 | 0 | 3 | 612 | Planned | Planned interruption | Green Lane Planned Work SAF4655 - WO1492293 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1320 | 2025-01-09-0025 | Omaka - SUB362266 | CB1088 - Omaka | 2025-01-09 08:54 | 2025-01-09 13:56 | 0.022227 | 7.36e-05 | 2 | 604 | Planned | Planned interruption | Planned shutdown to replace TX footing & upgrade earths. EAM 1490034 SAF 4252 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1321 | 2025-01-09-0026 | Sounds - SUB326017 | REC1170-Sounds | 2025-01-09 09:10 | 2025-01-09 13:57 | 0.031685 | 0.0001104 | 3 | 861 | Planned | Planned interruption | Clova Bay Planned Work SAF4607 - WO1519049 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1322 | 2025-01-09-0027 | Murphys Rd - 0001132089MLD33 | CB68-Murphys Rd | 2025-01-09 17:00 | 2025-01-09 18:10 | 0 | 0 | 1 | 70 | Unplanned | Unknown | Replaced a burnt-out Lv fuse in a meterbox. Restored 1810 WO 1528556 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1323 | 2025-01-09-0028 | Parker St - 0001138150ML964 | CB1516-Parker St | 2025-01-09 20:57 | 2025-01-09 22:00 | 0 | 0 | 1 | 63 | Unplanned | Defective equipment | Faulty oven causing the fuse to blow. Un-plugged the oven and replaced the blown fuse. WO 1528557 -- | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1324 | 2025-01-10-0029 | Grovetown - SUB370292 | CB1465-Grovetown | 2025-01-10 08:36 | 2025-01-10 11:07 | 0.011114 | 7.36e-05 | 2 | 302 | Planned | Planned interruption | Planned maintenance at pole VA1737 SAF4441 WO1501793 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1325 | 2025-01-10-0030 | Grovetown - SUB370275 | CB1465-Grovetown | 2025-01-10 11:31 | 2025-01-10 14:02 | 0.011187 | 7.36e-05 | 2 | 304 | Planned | Planned interruption | Planned shutdown to pull up low spans of 11kVEAM 1504830 SAF 4425 http://nams.mll.co.nz/Schedule/Edit/4437 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1326 | 2025-01-10-0031 | Seafair - 0003360296ML7D9 | CB5098-Seafair | 2025-01-10 14:15 | 2025-01-10 15:14 | 0 | 0 | 1 | 60 | Unplanned | Unknown | replaced fuse in SFB Suspect overload EAM 1528727 - Part power, red phase blown at XA2552, 3PH 32A, SUB348014, | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1327 | 2025-01-10-0032 | Waikawa - 0006618426MLD55 | CB109- Waikawa | 2025-01-10 17:53 | 2025-01-10 19:30 | 0 | 0 | 1 | 98 | Unplanned | Defective equipment | Replaced an old grease tube on the jumper from the fuse to the main line. Restored 1930. EAM 1528741 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1328 | 2025-01-11-0033 | Seymour St - 0001165457ML8FF | CB51-Seymour St | 2025-01-11 14:02 | 2025-01-11 14:45 | 0 | 0 | 1 | 44 | Unplanned | Defective equipment | Blown 30A HRC fuse, suspect customer fault as a MCB tripped when owner installed a new lightbulb. Replaced blown fuse, retored 1445. WO 1528743 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1329 | 2025-01-12-0035 | Taylor Pass - 0001195420ML5F4 | CB1089-Taylor Pass | 2025-01-12 14:48 | 2025-01-12 16:55 | 0 | 0 | 1 | 128 | Unplanned | Defective equipment | Burnt out Lv fuse, removed and used a spare fuse. Restored 1655. EAM 1528745 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1330 | 2025-01-13-0038 | Rai Valley - CB2032 | CB43 - Rai Valley, CB45 - French Pass, CB5126 - Pelorus | 2025-01-12 19:05 | 2025-01-12 19:06 | 0 | 0 | 917 | 0 | Unplanned | Unknown | Successful reclose of CB 2032 GXP Earth fault Blue Phase | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1331 | 2025-01-12-0037 | Sounds - FUSE2408 | REC1170-Sounds | 2025-01-12 20:08 | 2025-01-12 21:54 | 0.007728 | 7.36e-05 | 2 | 210 | Unplanned | Defective equipment | Portage peninsula fault reported by customer tipped 11kV TX Fuse arm SUB 325219. Isolation at Fuse 2408 to make repairs. 1528746 http://nams.mll.co.nz/Schedule/Edit/4614 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1332 | 2025-01-13-0039 | French Pass - REC1466 | CB45-French Pass | 2025-01-13 09:03 | 2025-01-13 13:18 | 0.33915 | 0.0013248 | 36 | 9216 | Planned | Planned interruption | Tree cutting between poles AP1926 and MA1276 - Elaine Bay SAF 4646 - WO 1523215 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1333 | 2025-01-13-0040 | Rai Valley - 0007714101ML19A | CB43-Rai Valley | 2025-01-13 12:42 | 2025-01-13 13:45 | 0 | 0 | 1 | 64 | Planned | Planned interruption | replace service fuse on pole JA2669 SAF 4605 - WO 1518261 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1334 | 2025-01-13-0041 | Wairau Valley - LVUG133796 | CB5399 Wairau Valley | 2025-01-13 14:20 | 2025-01-13 14:59 | 0 | 0 | 6 | 228 | Unplanned | Third party interference | Water Leak around SFB 286 Delta Lake Isolation and access permit to investigate. 1528923 http://nams.mll.co.nz/Schedule/Edit/4615 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1335 | 2025-01-14-0042 | Omaka - ABS1776-B | CB1088 - Omaka | 2025-01-14 08:00 | 2025-01-14 10:42 | 0.11327 | 0.0006992 | 19 | 3078 | Planned | Planned interruption | Planned shutdown to install LV disconnect units in SUB362206. EAM 1492293 SAF 4657 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1336 | 2025-01-14-0043 | French Pass - FUSE2299 | CB45-French Pass | 2025-01-14 08:30 | 2025-01-14 14:36 | 0.36266 | 0.0009936 | 27 | 9855 | Planned | Planned interruption | Various HV maintenance works in the Te Towaka area http://nams.mll.linesmarl.co.nz/Schedule/Edit/4510 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1337 | 2025-01-14-0044 | Rai Valley - SUB335307 | CB43-Rai Valley | 2025-01-14 08:46 | 2025-01-14 15:00 | 0.068632 | 0.000184 | 5 | 1865 | Planned | Planned interruption | Planned shutdown for LV crossarm replacements and arborist work. EAM 1509959 SAF 4547 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1338 | 2025-01-14-0045 | Colemans Rd - LVOH5420-S100 | CB1512-Colemans Rd | 2025-01-14 17:01 | 2025-01-14 19:31 | 0 | 0 | 1 | 150 | Unplanned | Third party interference | N/S pulled off house, 300mm of mains pulled out, broken mains entry. Service tested, mains entry replaced. delivery truck has pulled wire down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1339 | 2025-01-15-0046 | French Pass - FUSE4040 | CB45-French Pass | 2025-01-15 08:30 | 2025-01-15 11:34 | 0.0067344 | 3.68e-05 | 1 | 183 | Planned | Planned interruption | Various HV maintenance works in the Te Towaka area http://nams.mll.linesmarl.co.nz/Schedule/Edit/4551 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1340 | 2025-01-15-0047 | French Pass - REC1310 | CB45-French Pass | 2025-01-15 08:30 | 2025-01-15 11:40 | 0.076507 | 0.0004048 | 11 | 2079 | Planned | Planned interruption | Various HV maintenance works in the Te Towaka area http://nams.mll.linesmarl.co.nz/Schedule/Edit/4535 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1341 | 2025-01-15-0048 | Omaka - LVOH7508 | CB1088 - Omaka | 2025-01-15 08:46 | 2025-01-15 15:47 | 0 | 0 | 2 | 842 | Planned | Planned interruption | Planned shutdown to replace pole. EAM 1510378 SAF4542 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1342 | 2025-01-15-0049 | Ward - SUB352438 | REC31-Ward | 2025-01-15 16:44 | 2025-01-15 17:58 | 0.0138 | 0.000184 | 5 | 375 | Unplanned | Third party interference | LV wire brought down by digger working at Ward Solar farm. Isolated at TX fuses for repairs under AP. F4629 EAM1529305 Mango Incident number 02243 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1343 | 2025-01-16-0050 | Waikawa - SUB330407 | CB109- Waikawa | 2025-01-16 08:30 | 2025-01-16 11:47 | 0.0072128 | 3.68e-05 | 1 | 196 | Planned | Planned interruption | Maintenance tasks at SUB330407 EAM 1509262 http://nams.mll.linesmarl.co.nz/Schedule/Edit/4493 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1344 | 2025-01-16-0051 | Weld St - FUSE2198 | CB71-Weld St | 2025-01-16 08:30 | 2025-01-16 17:41 | 0.48664 | 0.0008832 | 24 | 13224 | Planned | Planned interruption | Planned shutdown for transformer upgrade. EAM 1503928 SAF4471 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1345 | 2025-01-16-0053 | Kaituna - SUB340123 | CB5448 Kaituna | 2025-01-16 08:30 | 2025-01-16 13:06 | 0.010157 | 3.68e-05 | 1 | 276 | Planned | Planned interruption | Planned shutdown to replace transformer bearer arms. SAF 4129 EAM1470350 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1346 | 2025-01-16-0052 | French Pass - FUSE2308 | CB45-French Pass | 2025-01-16 08:38 | 2025-01-16 13:23 | 0.083904 | 0.0002944 | 8 | 2280 | Planned | Planned interruption | Various planned maintenance tasks in the Te Towaka area WO 1408890 http://nams.mll.linesmarl.co.nz/Schedule/Edit/4542 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1347 | 2025-01-16-0054 | Old Renwick Rd - FUSE2044 | CB66-Old Renwick Rd | 2025-01-16 11:02 | 2025-01-16 12:03 | 0.002208 | 3.68e-05 | 1 | 60 | Unplanned | Wildlife | Found 2 blown 11kV fuses at fuse site 2044 and a dead duck carcass located 2 spans beyond. Confirmed voltage okay at pump shed. EAM 1529397 FS F4633 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1348 | 2025-01-16-0055 | Craiglochart - FUSE2135 | REC1391-Craiglochart | 2025-01-16 11:52 | 2025-01-16 14:08 | 0.004968 | 3.68e-05 | 1 | 135 | Unplanned | Defective equipment | Urgent shutdown to replace suspected cracked 11kV insulator on SWER line. EAM 1529377 F4632 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1349 | 2025-01-16-0056 | Vernon - FUSE21885 | CB5184-Vernon | 2025-01-16 16:01 | 2025-01-16 16:51 | 0 | 0 | 4 | 200 | Unplanned | Third party interference | Fire Comms reported box on fire.SFB XA0991 damaged by fire and isolated at LV fuse 21885. Inspection found box looks undamaged inside and just requires lid replacement. EAM 1529561 FS F4636 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1350 | 2025-01-17-0057 | Craiglochart - FUSE2135 | REC1391-Craiglochart | 2025-01-17 08:45 | 2025-01-17 11:15 | 0.0054832 | 3.68e-05 | 1 | 149 | Unplanned | Defective equipment | Urgent shutdown to replace insulators on SWER line at Poles ET3052 & ET3054 due to leakage. EAM 1529377 F4635 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1351 | 2025-01-18-0058 | Sounds - SUB326058 | REC1170-Sounds | 2025-01-18 11:29 | 2025-01-18 15:44 | 0.018768 | 7.36e-05 | 2 | 510 | Unplanned | Wildlife | dead bird at base of pole and scorch mark near HV bushing on lead. Recommends falcon protection and tape to prevent reoccurrence. http://nams.mll.co.nz/Schedule/Edit/4641 EAM 1529792 Sub326058 1 phase 30kVa SWER 3A | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1352 | 2025-01-19-0059 | Parker St - 0001147377ML025 | CB1516-Parker St | 2025-01-19 11:53 | 2025-01-19 13:00 | 0 | 0 | 1 | 66 | Unplanned | Defective equipment | Burnt fuse holder in Gyro Box EAM 1529794 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1353 | 2025-01-19-0060 | French Pass - REC5024 | CB45-French Pass | 2025-01-19 15:29 | 2025-01-19 20:08 | 0.76084 | 0.00276 | 75 | 20675 | Unplanned | Defective equipment | AC Fail alarms at Saddle Hill Radio site and D'Urville East & West Reclosers. No tripping on 5024 but no load showing. Opened for safety. Chopper to patrol line. Suspect fault between 5024 & take off line to Saddle hill radio site. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1354 | 2025-01-19-0064 | French Pass - FUSE3943 | CB45-French Pass | 2025-01-19 17:21 | 2025-01-19 20:09 | 0.51932 | 0.0030912 | 84 | 14112 | Unplanned | Defective equipment | Urgent shutdown to repair swinging wire at pole AX2078 above Te Towaka due to broken binder. EAM 1529795 F4642 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1355 | 2025-01-20-0065 | French Pass - REC1309 | CB45-French Pass | 2025-01-20 08:32 | 2025-01-20 15:22 | 0.57474 | 0.0013984 | 38 | 15618 | Planned | Planned interruption | Various maintenance tasks in the Te Towaka area WO 1408890 http://nams.mll.linesmarl.co.nz/Schedule/Edit/4552 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1356 | 2025-01-20-0066 | Tuamarina - 0003310273MLA95 | CB188-Tuamarina | 2025-01-20 13:00 | 2025-01-20 14:01 | 0 | 0 | 1 | 60 | Planned | Planned interruption | planned work http://nams.mll.co.nz/Schedule/Edit/4597 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1357 | 2025-01-21-0067 | Havelock Canvastown - REC5247 | CB103 Havelock Canvastown | 2025-01-21 04:28 | 2025-01-21 04:28 | 0 | 0 | 101 | 0 | Unplanned | Wildlife | Succesful Auto Reclose on Phase OC. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1358 | 2025-01-21-0069 | French Pass - ENS7003-B | CB45-French Pass | 2025-01-21 08:30 | 2025-01-21 17:26 | 0.68878 | 0.0030912 | 84 | 18717 | Planned | Planned interruption | Te Towaka planned maintenance - SD5 WO 1408890 http://nams.mll.linesmarl.co.nz/Schedule/Edit/4606 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1359 | 2025-01-21-0070 | Rai Valley - REC5167 | CB43-Rai Valley | 2025-01-21 09:32 | 2025-01-21 14:48 | 0 | 0 | 104 | 6806 | Unplanned | Third party interference | Line down REC5167 opened for safety. EAM1530236 NAMS F4648 LV line from SUB335325 is down on the road. REC5167 Opened for safety SUB335325 Isolated to reinstate LV Line REC5167 Closed SUB335325 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1360 | 2025-01-22-0071 | Sounds - SUB325009 | REC1170-Sounds | 2025-01-22 07:42 | 2025-01-22 15:45 | 0.11426 | 0.0002576 | 7 | 3105 | Unplanned | Unknown | 2 blown fuses at SUB325009 Fuses replaced but 1 fuse blew on restoration. SFB XA2959 found to be on fire. Fire put out and isolation carried out at SUB325009 SFB XA2959 repaired and power restored EAM 1530481 NAMS F4657 2025-01-22-0071 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1361 | 2025-01-22-0072 | French Pass - ENS7003-B | CB45-French Pass | 2025-01-22 08:30 | 2025-01-22 16:01 | 1.391 | 0.0030912 | 84 | 37800 | Planned | Planned interruption | Planned maintenance at Te Towaka - SD6 WO 1408890 http://nams.mll.linesmarl.co.nz/Schedule/Edit/4607 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1362 | 2025-01-22-0073 | McLauchlan St - 0001130271ML677 | CB65 - McLauchlan St | 2025-01-22 14:00 | 2025-01-22 14:57 | 0 | 0 | 1 | 58 | Unplanned | Defective equipment | Service fuse replaced EAM 1530652 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1363 | 2025-01-22-0074 | Grassmere - 0005506193ML0F3 | CB1253-Grassmere | 2025-01-22 14:44 | 2025-01-22 17:35 | 0 | 0 | 1 | 171 | Unplanned | Unknown | Blown 30A pole fuse, no cause found. Restored 1735. EAM 1530674 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1364 | 2025-01-22-0076 | Redwood St Sth - 0001189177ML652 | CB1673-Redwood St Sth | 2025-01-22 20:25 | 2025-01-22 20:57 | 0 | 0 | 1 | 31 | Unplanned | Defective equipment | Burnt out Lv RW fuse, replaced with 60A HRC. Restored 2057. WO1530743 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1365 | 2025-01-23-0077 | French Pass - SUB336334 | CB45-French Pass | 2025-01-23 08:31 | 2025-01-23 09:47 | 0.0027968 | 3.68e-05 | 1 | 76 | Planned | Planned interruption | Replacement of TX at SUB336334 - Waikawa Bay, French Pass http://nams.mll.linesmarl.co.nz/Schedule/Edit/4644 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1366 | 2025-01-23-0078 | Parker St - FUSE22271 | CB1516-Parker St | 2025-01-23 09:04 | 2025-01-23 15:48 | 0 | 0 | 4 | 1616 | Planned | Planned interruption | Installation of SFB45 Girling Ave http://nams.mll.linesmarl.co.nz/Schedule/Edit/4611 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1367 | 2025-01-23-0079 | Old Renwick Rd - FUSE3520 | CB66-Old Renwick Rd | 2025-01-23 11:56 | 2025-01-23 22:15 | 0.022816 | 3.68e-05 | 1 | 620 | Unplanned | Third party interference | 11kV cable failed at the base of pole JA3670 beneath the cable cover. Cable up pole replaced and jointed below ground. http://nams.mll.linesmarl.co.nz/Schedule/Edit/4668 EAM 1530881 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1368 | 2025-01-23-0080 | Parker St - 0001137313ML466 | CB1516-Parker St | 2025-01-23 12:51 | 2025-01-23 16:26 | 0 | 0 | 1 | 215 | Unplanned | Defective equipment | Blown fuse - fuse was corroded EAM 15308942 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1369 | 2025-01-24-0081 | Old Renwick Rd - 0003330350MLBC9 | CB66-Old Renwick Rd | 2025-01-24 09:25 | 2025-01-24 10:53 | 0 | 0 | 1 | 88 | Unplanned | Defective equipment | Blown 30A fuse, replaced and blew again, main switch off turned off and replaced.EAM 1531061 - Part power | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1370 | 2025-01-24-0082 | Parker St - 0001137525ML417 | CB1516-Parker St | 2025-01-24 14:33 | 2025-01-24 16:07 | 0 | 0 | 1 | 94 | Unplanned | Unknown | Replaced blown service fuse - suspect overloading EAM 1531239 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1371 | 2025-01-25-0083 | Rai Valley - FUSE2291 | CB43-Rai Valley | 2025-01-25 04:17 | 2025-01-25 10:09 | 0.12954 | 0.000368 | 10 | 3520 | Unplanned | Unknown | EAM 1531304 NAMS F4670 FUSE2291 2 x blown fuses found Line patrol carried out | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1372 | 2025-01-25-0087 | Okaramio - FUSE3610 | CB104 Okaramio | 2025-01-25 11:57 | 2025-01-25 15:48 | 0.076507 | 0.0003312 | 9 | 2079 | Unplanned | Vegetation | Tree on line at Poles DF4133 / BF2502 Lines re-instated, Poles will need to be replaced EAM1531307 NAMS F4671 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1373 | 2025-01-26-0088 | Okaramio - FUSE3610 | CB104 Okaramio | 2025-01-26 09:12 | 2025-01-26 13:35 | 0.087437 | 0.0003312 | 9 | 2376 | Unplanned | Vegetation | EAM1531307 NAMS F4672 Poles DF4133 / BF2502 replaced following trees damaing lines on 25/01 (2025-01-25-0087) 2025-01-26-0088 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1374 | 2025-01-26-0090 | Ngakuta - REC5130 | REC1562-Ngakuta | 2025-01-26 14:44 | 2025-01-26 20:57 | 0.68451 | 0.0092368 | 251 | 18601 | Unplanned | Third party interference | Pole has come down / Car needs to be pulled out Event number P061415128 LV Pole KB5054 down blocking Road pole repalced power restored EAM1531308 NAMSF4674 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1375 | 2025-01-26-0092 | Wairau Valley - REC1697 | CB5399 Wairau Valley | 2025-01-26 20:30 | 2025-01-26 20:30 | 0 | 0 | 21 | 0 | Unplanned | Unknown | 26/01/2025 8:33:00 pm Successful reclose | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1376 | 2025-01-27-0093 | Tuamarina - HVOH130774 | CB188-Tuamarina | 2025-01-27 08:42 | 2025-01-27 15:06 | 0.25436 | 0.0006624 | 18 | 6912 | Planned | Planned interruption | Installation of new SUB3561AA and removal of 2x redundant SUB's SAF4394 - WO1502193 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1377 | 2025-01-27-0094 | Richmond Brook - SUB353065 | CB1250-Richmond Brook | 2025-01-27 08:59 | 2025-01-27 10:08 | 0.015456 | 0.0002208 | 6 | 420 | Planned | Planned interruption | Shutdown of SUB353065 in Foster St for the move of a high load under lines at ET2818 SAF4658 - WO1529129 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1378 | 2025-01-27-0095 | Grassmere - SUB352017 | CB1253-Grassmere | 2025-01-27 10:10 | 2025-01-27 12:13 | 0.013469 | 0.0001104 | 3 | 366 | Planned | Planned interruption | Shutdown of SUB352017 in Blind River Loop Rd for the move of a high load under lines at PT1066 SAF4658 - WO1529129 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1379 | 2025-01-27-0096 | Grassmere - ABS15022-B | CB1253-Grassmere | 2025-01-27 10:31 | 2025-01-27 12:59 | 0.2233 | 0.0015088 | 41 | 6068 | Planned | Planned interruption | Shutdown from ABS15022 in Blind River Loop Rd for the move of a high load under lines at KB4469 (Merrifields Rd) SAF4658 - WO1529129 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1380 | 2025-01-27-0097 | Vernon - FUSE3408 | CB5184-Vernon | 2025-01-27 12:27 | 2025-01-28 14:48 | 0.10654 | 0.0002576 | 7 | 2895 | Unplanned | Lightning | Power out Upline shows as Fuse 3408 Permission sought for access to property ) EAM1531417 NAMS F4677 After Lightning storm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1381 | 2025-01-28-0098 | Causeway - SUB320102 | CB1683 Causeway | 2025-01-28 08:41 | 2025-01-28 14:59 | 0.01391 | 3.68e-05 | 1 | 378 | Planned | Planned interruption | Planned shutdown to replace transformer. SAF 4247 EAM 1212679 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1382 | 2025-01-28-0100 | Waikawa - LVUG2889 | CB109- Waikawa | 2025-01-28 09:33 | 2025-01-28 11:51 | 0 | 0 | 6 | 828 | Planned | Planned interruption | Removal of tee joint connection to http://nams.mll.linesmarl.co.nz/Schedule/Edit/4675 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1383 | 2025-01-28-0102 | Waikawa - 0006615190ML14D | CB109- Waikawa | 2025-01-28 09:33 | 2025-01-28 11:51 | 0 | 0 | 1 | 138 | Planned | Planned interruption | Removal of tee joint connection to http://nams.mll.linesmarl.co.nz/Schedule/Edit/4675 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1384 | 2025-01-28-0103 | Waikawa - 0006615048ML71F | CB109- Waikawa | 2025-01-28 09:33 | 2025-01-28 11:51 | 0 | 0 | 1 | 138 | Planned | Planned interruption | Removal of tee joint connection to http://nams.mll.linesmarl.co.nz/Schedule/Edit/4675 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1385 | 2025-01-28-0104 | Waikawa - 0006615060ML85E | CB109- Waikawa | 2025-01-28 09:33 | 2025-01-28 11:51 | 0 | 0 | 1 | 138 | Planned | Planned interruption | Removal of tee joint connection to http://nams.mll.linesmarl.co.nz/Schedule/Edit/4675 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1386 | 2025-01-28-0105 | Waikawa - 0006615054MLEAC | CB109- Waikawa | 2025-01-28 09:33 | 2025-01-28 11:51 | 0 | 0 | 1 | 138 | Planned | Planned interruption | Removal of tee joint connection to http://nams.mll.linesmarl.co.nz/Schedule/Edit/4675 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1387 | 2025-01-28-0106 | Waikawa - 0006615478MLCE6 | CB109- Waikawa | 2025-01-28 09:33 | 2025-01-28 11:51 | 0 | 0 | 1 | 138 | Planned | Planned interruption | Removal of tee joint connection to http://nams.mll.linesmarl.co.nz/Schedule/Edit/4675 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1388 | 2025-01-28-0107 | Waikawa - 0006615187ML62A | CB109- Waikawa | 2025-01-28 09:33 | 2025-01-28 11:51 | 0 | 0 | 1 | 138 | Planned | Planned interruption | Removal of tee joint connection to http://nams.mll.linesmarl.co.nz/Schedule/Edit/4675 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1389 | 2025-01-28-0108 | Parker St - 0001146565MLDAB | CB1516-Parker St | 2025-01-28 11:59 | 2025-01-28 13:26 | 0 | 0 | 1 | 87 | Unplanned | Defective equipment | Old wiring blew fuse now replaced EAM 1531701 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1390 | 2025-01-28-0109 | Colemans Rd - 0001131309ML99A | CB1512-Colemans Rd | 2025-01-28 12:02 | 2025-01-28 16:30 | 0 | 0 | 1 | 267 | Unplanned | Third party interference | Replaced blown service fuse - EAM 1531704 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1391 | 2025-01-29-0110 | Omaka - ABS1899-B | CB1088 - Omaka | 2025-01-29 08:30 | 2025-01-29 17:39 | 0.73902 | 0.0013616 | 37 | 20082 | Planned | Planned interruption | Connection of new 11kV UG network and removal of redundant 11kV OH in Aerodrome Rd for Vector one nine subdivision. SAF4391 WO 1492293 Outage 1 of 2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1392 | 2025-01-29-0111 | Omaka - HVUG133882 | CB1088 - Omaka | 2025-01-29 08:30 | 2025-01-29 17:34 | 0.34033 | 0.0006256 | 17 | 9248 | Planned | Planned interruption | Connection of new 11kV UG network and removal of redundant 11kV OH in Aerodrome Rd for Vector one nine subdivision. SAF4391 WO 1492293 Outage 2 of 2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1393 | 2025-01-29-0112 | Wairau Valley - SUB341526 | CB5399 Wairau Valley | 2025-01-29 19:18 | 2025-01-29 20:56 | 0.0036064 | 3.68e-05 | 1 | 98 | Unplanned | Unknown | found the HV fuse open at SUB341526. No cause found. Replaced fuse (3A) EAM1532084 NAMS F4686 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1394 | 2025-01-30-0113 | Hawkesbury Road - 0002271226MLEFF | CB5457 Hawkesbury Road | 2025-01-30 07:20 | 2025-01-30 09:10 | 0 | 0 | 1 | 109 | Unplanned | Defective equipment | Burnt out cutout, DP service restored EAM 1532096 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1395 | 2025-01-30-0114 | Redwood St Nth - SUB3700DU | CB1655-Redwood St Nth | 2025-01-30 08:11 | 2025-01-30 14:17 | 0.2155 | 0.0005888 | 16 | 5856 | Planned | Planned interruption | Planned shutdown to disconnect SUB3700DU and liven up new SUB3700RB and associated 11kV RMU. EAM 1419129 SAF 4579. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1396 | 2025-01-30-0115 | Spring Creek - FUSE2393 | CB187-Spring Creek | 2025-01-30 08:44 | 2025-01-30 14:57 | 0.054905 | 0.0001472 | 4 | 1492 | Planned | Planned interruption | Planned shutdown to replace TX and hardware. EAM 1501538 SAF 4559 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1397 | 2025-01-30-0116 | Grovetown - FUSE2177 | CB1465-Grovetown | 2025-01-30 09:09 | 2025-01-30 15:05 | 0.18341 | 0.0005152 | 14 | 4984 | Planned | Planned interruption | removing vegetation around the 11kV http://nams.mll.linesmarl.co.nz/Schedule/Edit/4653 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1398 | 2025-01-30-0117 | Rai Valley - CB5391 | CB43 - Rai Valley, CB45 - French Pass, CB5126 - Pelorus | 2025-01-30 09:16 | 2025-01-30 09:16 | 0 | 0 | 918 | 0 | Unplanned | Unknown | CB5391 reclosed on EF. Cyco 166 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1399 | 2025-01-30-0118 | Havelock Canvastown - SUB320356 | CB103 Havelock Canvastown | 2025-01-30 09:39 | 2025-01-30 11:50 | 0.0096416 | 7.36e-05 | 2 | 262 | Planned | Planned interruption | Isolation of SUB for testing of the earth grid following EPR issues at the ICP Also Safety Disco http://nams.mll.linesmarl.co.nz/Schedule/Edit/4669 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1400 | 2025-01-30-0120 | McLauchlan St - 0001130241ML18F | CB65 - McLauchlan St | 2025-01-30 18:02 | 2025-01-30 19:11 | 0 | 0 | 1 | 69 | Unplanned | Defective equipment | Blown 30A fuse caused by a faulty ovenEAM 1532224 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1401 | 2025-01-31-0121 | Waikawa - REC17 | CB109- Waikawa | 2025-01-31 02:00 | 2025-01-31 02:01 | 0 | 0 | 92 | 0 | Unplanned | Unknown | REC17 (Boons Valley) reclosed on EF1+. Cyclo 108 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1402 | 2025-01-31-0122 | Waikawa - REC17 | CB109- Waikawa | 2025-01-31 02:26 | 2025-01-31 02:27 | 0 | 0 | 92 | 0 | Unplanned | Unknown | REC17 (Boons Valley) reclosed on EF1+. Cyclo 109 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1403 | 2025-01-31-0123 | Godfrey Road - 0002271670MLB79 | CB5367 Godfrey Road | 2025-01-31 05:53 | 2025-01-31 07:15 | 0 | 0 | 1 | 83 | Unplanned | Other cause | Blown service fuse replace - overload. Fuse letter to be sent. EAM 1532231 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1404 | 2025-01-31-0124 | Waihopai Valley - FUSE2127 | CB5493 Waihopai Valley | 2025-01-31 07:16 | 2025-01-31 08:43 | 0.012659 | 0.0001472 | 4 | 344 | Unplanned | Unknown | Found 11kV spur line fuses open and nothing found on patrol beyond. Confirmed power restored with Customer. EAM 1532226 F4689 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1405 | 2025-01-31-0125 | Old Renwick Rd - LVOH617 | CB66-Old Renwick Rd | 2025-01-31 10:00 | 2025-01-31 13:28 | 0 | 0 | 2 | 414 | Planned | Planned interruption | Planned shutdown to replace LV cross arms. EAM 1509476 SAF 4541 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1406 | 2025-01-31-0126 | Hutcheson St - 0001154305MLFFC | CB49-Hutcheson St | 2025-01-31 10:00 | 2025-01-31 11:10 | 0 | 0 | 1 | 70 | Unplanned | Third party interference | Accidently disconnected by 3rd Party (MIMS) in error EAM 1532233 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1407 | 2025-02-01-0001 | Renwick Township - 0000053212ML72A | CB5482 Renwick Township | 2025-02-01 08:38 | 2025-02-01 12:01 | 0 | 0 | 1 | 203 | Planned | Planned interruption | Replacement of SFB 34 Inkerman St XA2152 SAF4513 WO1506910 Outage 1 of 2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1408 | 2025-02-01-0002 | Renwick Township - 0000053213MLB6F | CB5482 Renwick Township | 2025-02-01 08:38 | 2025-02-01 12:01 | 0 | 0 | 1 | 203 | Planned | Planned interruption | Replacement of SFB 34 Inkerman St XA2152 SAF4513 WO1506910 Outage 2 of 2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1409 | 2025-02-02-0003 | Parker St - 0001141157ML2B7 | CB1516-Parker St | 2025-02-02 20:53 | 2025-02-02 22:30 | 0 | 0 | 1 | 97 | Unplanned | Defective equipment | Burnt out Lv fuse, replaced. EAM 1532281 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1410 | 2025-02-02-0004 | Godfrey Road - 0002271670MLB79 | CB5367 Godfrey Road | 2025-02-02 21:43 | 2025-02-02 22:25 | 0 | 0 | 1 | 42 | Unplanned | Other cause | Blown service fuse - overload - EAM 1532279 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1411 | 2025-02-02-0005 | Rai Valley - CB5391 | CB43 - Rai Valley, CB45 - French Pass, CB5126 - Pelorus | 2025-02-02 23:34 | 2025-02-02 23:34 | 0 | 0 | 918 | 0 | Unplanned | Unknown | CB5391 (LVY-RAI) reclosed on EF. Cyclo 167 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1412 | 2025-02-03-0006 | Hutcheson St - XB6620-P2 | CB49-Hutcheson St | 2025-02-03 06:00 | 2025-02-03 06:55 | 0 | 0 | 5 | 275 | Planned | Planned interruption | Reconnection of LV cable to POS4 in DP19 Wynen St in preparation of Wynen St Sub commisioning. SAF4666 WO 1372354 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1413 | 2025-02-03-0007 | Redwood St Nth - 0001108301ML602 | CB1655-Redwood St Nth | 2025-02-03 08:42 | 2025-02-03 14:10 | 0 | 0 | 1 | 327 | Planned | Planned interruption | Removal of SFB71A Stevenson St and convesrion of cable to a service http://nams.mll.linesmarl.co.nz/Schedule/Edit/4622 EAM 1522627 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1414 | 2025-02-03-0008 | Wairau Valley - FUSE4107 | CB5399 Wairau Valley | 2025-02-03 12:41 | 2025-02-03 14:14 | 0.0034592 | 3.68e-05 | 1 | 94 | Planned | Planned interruption | Planned shutdown to replace HV crossarm at pole KB4879 Pine Valley. EAM 1529380 SAF 4688 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1415 | 2025-02-03-0009 | East Coast - SUB352609 | REC29-East Coast | 2025-02-03 15:51 | 2025-02-03 18:57 | 0.0068448 | 3.68e-05 | 1 | 186 | Unplanned | Unknown | HV fuse blown at SUB325609. No obvious cause. Replaced fuse (3A). Confirmed power restored. EAM 1532348 http://nams.mll.co.nz/Schedule/Edit/4698 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1416 | 2025-02-04-0010 | Riverlands - 0003350165ML921 | CB1181-Riverlands | 2025-02-04 07:21 | 2025-02-04 09:04 | 0 | 0 | 1 | 103 | Unplanned | Unknown | Power restored blown fused (no cause old rewirable) EAM 1532365 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1417 | 2025-02-04-0011 | Dry Hills - SUB348570-P3 | CB1682-Dry Hills | 2025-02-04 08:30 | 2025-02-04 10:54 | 0 | 0 | 4 | 576 | Planned | Planned interruption | Planned shutdown to replace SFB XA2526 EAM 1511060 SAF 4677 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1418 | 2025-02-04-0013 | Weld St - LVUG3864 | CB71-Weld St | 2025-02-04 08:30 | 2025-02-04 16:50 | 0 | 0 | 3 | 1497 | Planned | Planned interruption | Installation of SFB105 Maxwell Rd http://nams.mll.linesmarl.co.nz/Application/Edit/4663 WO 1525501 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1419 | 2025-02-04-0012 | McLauchlan St - 0001130378ML122 | CB65 - McLauchlan St | 2025-02-04 08:56 | 2025-02-04 10:41 | 0 | 0 | 1 | 104 | Unplanned | Defective equipment | Internal issue EAM 1532379 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1420 | 2025-02-04-0014 | Waikawa - SUB330622 | CB109- Waikawa | 2025-02-04 09:27 | 2025-02-04 13:40 | 0.018621 | 7.36e-05 | 2 | 506 | Planned | Planned interruption | Opua Bay Planned Work - LV maintenance work from SUB330622 http://nams.mll.co.nz/Schedule/Edit/4623 EAM 1495818 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1421 | 2025-02-05-0015 | Waihopai Valley - ABS843-B | CB5493 Waihopai Valley | 2025-02-05 08:42 | 2025-02-05 14:44 | 0.373 | 0.0010304 | 28 | 10136 | Planned | Planned interruption | Planned shutdown to replace red tagged pole at SUB3410LV EAM 1521197 SAF 4641 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1422 | 2025-02-05-0016 | French Pass - LVUG99663 | CB45-French Pass | 2025-02-05 09:42 | 2025-02-05 14:12 | 0 | 0 | 21 | 5670 | Planned | Planned interruption | Archers Road Planned Work - Replacement of XA2847 http://nams.mll.co.nz/Schedule/Edit/4676 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1423 | 2025-02-05-0017 | Havelock Canvastown - FUSE3624 | CB103 Havelock Canvastown | 2025-02-05 09:54 | 2025-02-05 10:10 | 0.002944 | 0.000184 | 5 | 80 | Planned | Planned interruption | Removal of SUB320236 at Takorika http://nams.mll.linesmarl.co.nz/Schedule/Edit/4631 EAM1519457 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1424 | 2025-02-05-0018 | Dashwood - 0005503349ML207 | CB1252-Dashwood | 2025-02-05 19:21 | 2025-02-05 20:44 | 0 | 0 | 1 | 84 | Unplanned | Unknown | blown 30a service fuse with no obvious cause. Replaced fuse and confirmed power restored EAM1532828 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1425 | 2025-02-07-0020 | Kaituna - FUSE2684 | CB5448 Kaituna | 2025-02-07 09:08 | 2025-02-07 10:19 | 0.036579 | 0.0005152 | 14 | 994 | Unplanned | Third party interference | Unplanned shutdown to change pole POLE PT2631 hit by a tractor 6th Feb http://nams.mll.co.nz/Schedule/Edit/4711 1532829 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1426 | 2025-02-08-0021 | Waikawa - CB109 | CB109- Waikawa | 2025-02-08 01:41 | 2025-02-08 01:41 | 0 | 0 | 2141 | 0 | Unplanned | Unknown | Successful reclose of CB109 - Earth fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1427 | 2025-02-09-0022 | Buller St - 0006607381ML603 | CB108-Buller St | 2025-02-09 06:35 | 2025-02-09 08:04 | 0 | 0 | 1 | 88 | Unplanned | Other Cause | failed trurip service line. Repaired line and relivened. EAM1533080 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1428 | 2025-02-09-0023 | Vernon - 0003350126ML744 | CB5184-Vernon | 2025-02-09 08:49 | 2025-02-09 09:25 | 0 | 0 | 1 | 36 | Unplanned | Other cause | blown 60a service fuse with no obvious cause. Possible overloading as engineer welding onsite when fuse blew. EAM1533081 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1429 | 2025-02-09-0024 | Redwood St Nth - CB1655 | CB1655-Redwood St Nth | 2025-02-09 12:14 | 2025-02-09 12:38 | 1.0907 | 0.045448 | 1235 | 29640 | Unplanned | Wildlife | Redwood St North Feeder Tripping Bird Found on Pole DF5235 - Removed with Pokey Stick. Feeder relivened. 1533082 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1430 | 2025-02-10-0028 | Rapaura Rd - 0004421438MLC45 | CB1077-Rapaura Rd | 2025-02-10 09:06 | 2025-02-10 10:32 | 0 | 0 | 1 | 86 | Unplanned | Unknown | Blown fuse - No cause idenfied EAM 1533139 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1431 | 2025-02-10-0029 | Sounds - FUSE3787 | REC1170-Sounds | 2025-02-10 09:24 | 2025-02-10 16:05 | 0.14757 | 0.000368 | 10 | 4010 | Planned | Planned interruption | Maintenance works at poles MA1423 and MA1431 - Kenepuru Rd SAF4337 WO1429189 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1432 | 2025-02-10-0030 | Parker St - 0001146589ML40F | CB1516-Parker St | 2025-02-10 10:41 | 2025-02-10 18:20 | 0 | 0 | 1 | 460 | Unplanned | Other Cause | Trurip faulty near mains entry. Repaired and relivened. EAM 1533179 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1433 | 2025-02-10-0031 | Sounds - SUB325090 | REC1170-Sounds | 2025-02-10 11:08 | 2025-02-10 17:20 | 0 | 0 | 13 | 4836 | Planned | Planned interruption | Kenepuru SD 5B - Replace LV arms at MA1372, KB8360, MA1379 http://nams.mll.linesmarl.co.nz/Application/Edit/4348 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1434 | 2025-02-10-0032 | Koromiko - SUB331224 | CB55-Koromiko | 2025-02-10 12:27 | 2025-02-10 15:14 | 0.0061456 | 3.68e-05 | 1 | 167 | Unplanned | Unknown | Blown 11kV Fuse NO CAUSE FOUND Milsoft modelling error actually SUB 331222 http://nams.mll.co.nz/Schedule/Edit/4721 EAM 1533248 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1435 | 2025-02-10-0033 | Pelorus - 0007713309MLDE9 | CB5126-Pelorus | 2025-02-10 18:52 | 2025-02-10 21:05 | 0 | 0 | 1 | 134 | Unplanned | Unknown | EAM1533338found low voltage at customer installation Issue invetigated with no issues found Voltage ok around 220v | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1436 | 2025-02-10-0034 | Seymour St - 0001166233ML2E3 | CB51-Seymour St | 2025-02-10 19:19 | 2025-02-10 20:02 | 0 | 0 | 1 | 42 | Unplanned | Defective equipment | blown service fuse due to oven failing. replaced fuse and confirmed power restored EAM1533339 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1437 | 2025-02-11-0035 | Sounds - FUSE4327 | REC1170-Sounds | 2025-02-11 08:15 | 2025-02-11 15:41 | 1.9537 | 0.028262 | 403 | 53090 | Planned | Planned interruption | Planned shutdown to replace H structure AE2116/ET1695, Replace x-arms and remove bypass ABS1805 at MA1317 / KB8123 EAM 1429189 SAF 4340.1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1438 | 2025-02-11-0037 | Richmond Brook - 0005503003ML130 | CB1250-Richmond Brook | 2025-02-11 09:11 | 2025-02-11 17:35 | 0 | 0 | 1 | 505 | Unplanned | Defective equipment | EAM 1533389 3ph 32amp Sub3530AB Lights feed to sub | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1439 | 2025-02-11-0038 | Sounds - SEC153 | REC1170-Sounds | 2025-02-11 10:00 | 2025-02-11 12:37 | 1.1432 | 0.00736 | 200 | 31064 | Planned | Planned interruption | removal of burning vegetation between Poles ZA2567 and ZA2564 Fish bay and Poles ZA2902 and ZA2901 Waitaria bay http://nams.mll.linesmarl.co.nz/Application/Edit/4670 WO 843259 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1440 | 2025-02-11-0039 | Tuamarina - 0003315333ML614 | CB188-Tuamarina | 2025-02-11 11:14 | 2025-02-11 12:45 | 0 | 0 | 1 | 91 | Unplanned | Defective equipment | Meter issue, customer advised to get hold of their retailer EAM 1533462 3ph 60am U/G XA1043 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1441 | 2025-02-11-0041 | Hawkesbury Road - 0000054718ML4DE | CB5457 Hawkesbury Road | 2025-02-11 20:00 | 2025-02-11 21:17 | 0 | 0 | 1 | 76 | Unplanned | Defective equipment | Burnt fuse carrier replaced EAM 1533681 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1442 | 2025-02-12-0042 | Sounds - FUSE3061 | REC1170-Sounds | 2025-02-12 08:30 | 2025-02-12 12:42 | 0.046368 | 0.000184 | 5 | 1260 | Planned | Planned interruption | Planned shutdown to replace LV cross arms at MA1222 in Te Mahia Bay. Part of Kenepuru maintenance project. EAM 1429189 SAF 4341 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1443 | 2025-02-12-0043 | Sounds - SUB3251AG | REC1170-Sounds | 2025-02-12 08:30 | 2025-02-12 13:50 | 0.094208 | 0.0002944 | 8 | 2560 | Planned | Planned interruption | Planned shutdown to replace LV cross arms at MA1264 & MA1273. Replace stub pole DF4753. EAM 1429189 SAF 4351 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1444 | 2025-02-12-0044 | Redwood St Nth - LVUG3420 | CB1655-Redwood St Nth | 2025-02-12 08:30 | 2025-02-12 13:52 | 0 | 0 | 5 | 1602 | Planned | Planned interruption | Replacement of SFB5 Timandra Place witha DP box http://nams.mll.linesmarl.co.nz/Application/Edit/4659 EAM 1505739 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1445 | 2025-02-12-0045 | Seymour St - 0001166561ML56C | CB51-Seymour St | 2025-02-12 09:02 | 2025-02-12 11:01 | 0 | 0 | 1 | 118 | Unplanned | Unknown | 30amp fuse replaced Cause unknown, but fuse letter to be sent EAM 1533713 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1446 | 2025-02-12-0046 | Sounds - SUB3251AV | REC1170-Sounds | 2025-02-12 11:30 | 2025-02-12 14:59 | 0.099985 | 0.0004784 | 13 | 2717 | Planned | Planned interruption | Planned shutdown to replace LV cross arms on pole MA1359 - 2353 Kenepuru Rd EAM 1429189 SAF 4350 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1447 | 2025-02-12-0047 | Sounds - SUB3251AE | REC1170-Sounds | 2025-02-12 13:47 | 2025-02-12 16:21 | 0.011261 | 7.36e-05 | 2 | 306 | Planned | Planned interruption | Kenepuru Road Planned Work - Replace LV arms AE2144 http://nams.mll.co.nz/Schedule/Edit/4109 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1448 | 2025-02-13-0048 | Sounds - REC1350 | REC1170-Sounds | 2025-02-13 08:15 | 2025-02-13 16:05 | 0.59042 | 0.036137 | 508 | 16044 | Planned | Planned interruption | Planned shutdown to Replace H Structure - ET1668/MA1398 Replace poles - BS2000 and BS2001 EAM 1429189 SAF 4338 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1449 | 2025-02-14-0049 | Sounds - 0008810294ML43D | REC1170-Sounds | 2025-02-14 07:08 | 2025-02-14 09:30 | 0 | 0 | 1 | 143 | Unplanned | Defective equipment | Burnt out LV Fuse - loose connection EAM 1533983 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1450 | 2025-02-14-0050 | Grovetown - SUB370239 | CB1465-Grovetown | 2025-02-14 08:30 | 2025-02-14 11:12 | 0.011923 | 7.36e-05 | 2 | 324 | Planned | Planned interruption | Installation of new mains cable for service connection at SUB370239 SAF 4684 WO1529435 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1451 | 2025-02-14-0051 | Seymour St - 0001163304ML6F5 | CB51-Seymour St | 2025-02-14 19:25 | 2025-02-14 20:31 | 0 | 0 | 1 | 67 | Unplanned | Defective equipment | Burnt out Fuse Carrier replaced EAM 1534051 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1452 | 2025-02-15-0053 | Sounds - LVOH153831 | REC1170-Sounds | 2025-02-15 13:17 | 2025-02-16 11:15 | 0 | 0 | 1 | 1318 | Unplanned | Third party interference | Damage Trurip replaced like for like. Too long for N/S, ABC would require inspection EAM 1534353 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1453 | 2025-02-15-0054 | Sounds - 0008810437ML6E4 | REC1170-Sounds | 2025-02-15 16:14 | 2025-02-15 18:42 | 0 | 0 | 1 | 148 | Planned | Planned interruption | Service fuse found removed from a previous planned job where testing could not be completed. Tested service and livened. EAM1534053 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1454 | 2025-02-15-0055 | Howick Rd North - 0001191079ML92C | CB84-Howick Rd North | 2025-02-15 18:11 | 2025-02-15 19:20 | 0 | 0 | 1 | 68 | Unplanned | Defective equipment | Burnt fuse carrier in Gyro replaced EAM: 1534054 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1455 | 2025-02-16-0056 | Grovetown - FUSE2016 | CB1465-Grovetown | 2025-02-16 06:57 | 2025-02-16 08:01 | 0.069368 | 0.0010672 | 29 | 1885 | Unplanned | Unknown | Found 1 blown 11kV fuse2016 and nothing found on patrol. Replaced all 3 with 30A. http://nams.mll.co.nz/Schedule/Edit/4758 EAM 1534055 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1456 | 2025-02-16-0057 | East Coast - SUB352609 | REC29-East Coast | 2025-02-16 11:54 | 2025-02-16 14:40 | 0.0061456 | 3.68e-05 | 1 | 167 | Unplanned | Unknown | TX fuse blown at SUB352609. No obvious cause. http://nams.mll.co.nz/Schedule/Edit/4759 EAM 1535046 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1457 | 2025-02-17-0059 | Parker St - 0001146453ML2D8 | CB1516-Parker St | 2025-02-16 17:06 | 2025-02-16 17:46 | 0 | 0 | 1 | 40 | Unplanned | Unknown | More Blown 30A HRC - letter to be sent. No cause found EAM 1534057 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1458 | 2025-02-16-0058 | Sounds - SUB3251EN | REC1170-Sounds | 2025-02-16 18:02 | 2025-02-17 12:23 | 0.12144 | 0.0001104 | 3 | 3300 | Unplanned | Unknown | 1x blown 11kV fuse found at SUB3251EN. No cause found. Replaced both fuses EAM: 1534058 http://nams.mll.co.nz/Schedule/Edit/4761 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1459 | 2025-02-17-0060 | Renwick Township - LVOH2136 | CB5482 Renwick Township | 2025-02-17 08:30 | 2025-02-17 15:46 | 0 | 0 | 7 | 3045 | Planned | Planned interruption | Removal of SUB342007 in Uxbridge St. Load moved to new GM SUB342091 http://nams.mll.linesmarl.co.nz/Application/Edit/4630 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1460 | 2025-02-17-0061 | Renwick Township - LVOH2897 | CB5482 Renwick Township | 2025-02-17 08:30 | 2025-02-17 15:45 | 0 | 0 | 5 | 2175 | Planned | Planned interruption | Removal of SUB342007 in Uxbridge St. Load moved to new GM SUB342091 http://nams.mll.linesmarl.co.nz/Application/Edit/4630 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1461 | 2025-02-17-0062 | Renwick Township - LVOH2895 | CB5482 Renwick Township | 2025-02-17 08:30 | 2025-02-17 15:45 | 0 | 0 | 1 | 435 | Planned | Planned interruption | Removal of SUB342007 in Uxbridge St. Load moved to new GM SUB342091 http://nams.mll.linesmarl.co.nz/Application/Edit/4630 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1462 | 2025-02-17-0063 | Renwick Township - 0000053171ML719 | CB5482 Renwick Township | 2025-02-17 08:30 | 2025-02-17 15:45 | 0 | 0 | 1 | 435 | Planned | Planned interruption | Removal of SUB342007 in Uxbridge St. Load moved to new GM SUB342091 http://nams.mll.linesmarl.co.nz/Application/Edit/4630 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1463 | 2025-02-17-0064 | Renwick Township - 0000053254ML400 | CB5482 Renwick Township | 2025-02-17 08:30 | 2025-02-17 15:45 | 0 | 0 | 1 | 435 | Planned | Planned interruption | Removal of SUB342007 in Uxbridge St. Load moved to new GM SUB342091 http://nams.mll.linesmarl.co.nz/Application/Edit/4630 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1464 | 2025-02-17-0065 | Renwick Township - 0000053211MLBEA | CB5482 Renwick Township | 2025-02-17 08:30 | 2025-02-17 15:46 | 0 | 0 | 1 | 435 | Planned | Planned interruption | Removal of SUB342007 in Uxbridge St. Load moved to new GM SUB342091 http://nams.mll.linesmarl.co.nz/Application/Edit/4630 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1465 | 2025-02-17-0066 | Renwick Township - 0000053111ML8E9 | CB5482 Renwick Township | 2025-02-17 08:30 | 2025-02-17 15:46 | 0 | 0 | 1 | 435 | Planned | Planned interruption | Removal of SUB342007 in Uxbridge St. Load moved to new GM SUB342091 http://nams.mll.linesmarl.co.nz/Application/Edit/4630 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1466 | 2025-02-17-0067 | Sounds - FUSE4225 | REC1170-Sounds | 2025-02-17 09:45 | 2025-02-17 17:49 | 1.1605 | 0.014278 | 194 | 31536 | Planned | Planned interruption | Planned shutdown - Kenepuru Maintenance SD9 - Replace TX and arms at ET1708. Replace arms at MA1674 EAM 1429189 SAF 4343 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1467 | 2025-02-17-0068 | Flaxbourne - SUB352422 | REC1432-Flaxbourne | 2025-02-17 15:30 | 2025-02-17 20:52 | 0.023699 | 0.0001472 | 2 | 644 | Unplanned | Third party interference | Contractor has damaged LV lines . 2 on the ground and 2 twisted. Reported by consumer http://nams.mll.co.nz/Schedule/Edit/4764 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1468 | 2025-02-17-0069 | French Pass - REC160 | CB45-French Pass | 2025-02-17 17:28 | 2025-02-17 17:28 | 0 | 0 | 17 | 0 | Unplanned | Unknown | REC160 tripped on Phase OC. Auto reclosed succesfully. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1469 | 2025-02-17-0070 | Jacksons Rd - CB1179 | CB1179 - Jacksons Rd | 2025-02-17 19:20 | 2025-02-17 20:02 | 0.1614 | 0.0037536 | 102 | 4386 | Unplanned | Wildlife | CB1179 tripped on phase OC. dead Duck between poles KB9582 & KB9024. No conductor damage apparent but small grass fire had started in paddock which was put out by Farmer. EAM 1534286 http://nams.mll.co.nz/Schedule/Edit/4765 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1470 | 2025-02-20-0098 | French Pass - FUSE4100 | CB45-French Pass | 2025-02-18 05:13 | 2025-02-20 15:28 | 0.40185 | 0.0028704 | 75 | 10920 | Unplanned | Adverse weather | 11kV jumper above fuse 4100 is broken. Staff could not repair due to windy wet unsafe conditions11kV Jumpers above Fuse4100 replaced | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1471 | 2025-02-18-0072 | Thomsons Ford Rd - 0003330300ML3C1 | CB1509-Thomsons Ford Rd | 2025-02-18 07:46 | 2025-02-18 09:47 | 0 | 0 | 1 | 121 | Unplanned | Defective equipment | LV crutch leads burnt out. Repaired (Heat shrink etc) service restored. EAM 1534308 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1472 | 2025-02-18-0073 | Sounds - FUSE2509 | REC1170-Sounds | 2025-02-18 08:41 | 2025-02-18 15:34 | 0.37996 | 0.00092 | 25 | 10325 | Planned | Planned interruption | Kenepuru Mtce Planned Work - Replace pole AP1399, replace arms at poles MA1675 and MA1679 http://nams.mll.co.nz/Schedule/Edit/4702 EAM 1429189 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1473 | 2025-02-18-0075 | Renwick Township - LVUG811 | CB5482 Renwick Township | 2025-02-18 08:47 | 2025-02-18 12:36 | 0 | 0 | 8 | 1832 | Planned | Planned interruption | Planned outage to replace SFB40 High St. EAM 1511208 SAF 4676 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1474 | 2025-02-18-0074 | Sounds - FUSE3092 | REC1170-Sounds | 2025-02-18 09:27 | 2025-02-18 14:23 | 0.45904 | 0.0015456 | 42 | 12474 | Planned | Planned interruption | Remove burning vegetation between Poles ZA3344 and RM2991 Yncyca bay Maintenance works at SUB325955 http://nams.mll.linesmarl.co.nz/Schedule/Edit/4694 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1475 | 2025-03-03-0004 | Havelock Canvastown - SUB320356 | CB103 Havelock Canvastown | 2025-02-18 09:38 | 2025-02-26 13:32 | 0.22017 | 0.0014352 | 29 | 5983 | Unplanned | Defective equipment | Earthing issue Wakamarina Outward bound camp. TX turned off multiple times whilst excavating and drilling for new earthing. http://nams.mll.co.nz/Schedule/Edit/4772 http://nams.mll.co.nz/Schedule/Edit/4762 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1476 | 2025-02-18-0076 | Havelock Canvastown - SUB320356 | CB103 Havelock Canvastown | 2025-02-18 09:55 | 2025-02-18 16:05 | 0 | 0 | 2 | 742 | Unplanned | Defective equipment | Isolate SUB320356 for excavation works for earthing. http://nams.mll.co.nz/Schedule/Edit/4762 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1477 | 2025-02-18-0077 | Grassmere - 0005506193ML0F3 | CB1253-Grassmere | 2025-02-18 17:32 | 2025-02-18 19:13 | 0 | 0 | 1 | 102 | Unplanned | Defective equipment | Replaced HRC fuse, upon reliving only drawing 16 amps W/O 1534500 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1478 | 2025-02-18-0078 | Ngakuta - 0007709601MLC59 | REC1562-Ngakuta | 2025-02-18 22:27 | 2025-02-19 13:26 | 0 | 0 | 1 | 900 | Unplanned | Defective equipment | Faulty trurip - replaced with N/S and service restored EAM 1534502 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1479 | 2025-02-19-0079 | Omaka - CB1088 | CB1088 - Omaka | 2025-02-19 01:28 | 2025-02-19 03:37 | 0.94101 | 0.034665 | 514 | 25571 | Unplanned | Vegeatation | http://nams.mll.linesmarl.co.nz/Schedule/Edit/4767 EAM1534503 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1480 | 2025-02-19-0090 | Sounds - ENS7004-B | REC1170-Sounds | 2025-02-19 08:19 | 2025-02-19 16:00 | 1.1632 | 0.011445 | 194 | 31610 | Planned | Planned interruption | Maintenance work at poles KB8303,AE2140 and AE2122 SAF4345 WO 1496152 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1481 | 2025-02-19-0082 | Spring Creek - SUB355217 | CB187-Spring Creek | 2025-02-19 08:37 | 2025-02-19 14:30 | 0.077942 | 0.0002208 | 6 | 2118 | Planned | Planned interruption | Installation of new SFB318 Wairau Bar Rd SAF4739 - EAM 1532737 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1482 | 2025-02-19-0083 | French Pass - ABS1926-B | CB45-French Pass | 2025-02-19 09:32 | 2025-02-19 13:18 | 0.63756 | 0.0028336 | 77 | 17325 | Planned | Planned interruption | http://nams.mll.linesmarl.co.nz/Application/Edit/4671 EAM 1464101 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1483 | 2025-02-19-0085 | Waikawa - 0006623454ML641 | CB109- Waikawa | 2025-02-19 10:00 | 2025-02-19 11:28 | 0 | 0 | 1 | 88 | Planned | Planned interruption | Lifting of SFB XA0236 SAF4680 EAM 1521413 Outage 1 of 2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1484 | 2025-02-19-0086 | Waikawa - 0006623555ML300 | CB109- Waikawa | 2025-02-19 10:00 | 2025-02-19 11:28 | 0 | 0 | 1 | 88 | Planned | Planned interruption | Lifting of SFB XA0236 SAF4680 EAM 1521413 Outage 2 of 2 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1485 | 2025-02-19-0087 | Murphys Rd - 0001121549ML5D8 | CB68-Murphys Rd | 2025-02-19 10:46 | 2025-02-19 11:43 | 0 | 0 | 1 | 57 | Unplanned | Other Cause | 30 amp blown fuse EAM 1534597 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1486 | 2025-02-19-0088 | Redwood St Nth - 0001108350ML24F | CB1655-Redwood St Nth | 2025-02-19 12:11 | 2025-02-19 13:27 | 0 | 0 | 1 | 77 | Unplanned | Defective equipment | Burnt out Service fuse Replaced service restored EAM 1534664 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1487 | 2025-02-19-0089 | Symons St - 0001156181ML2FB | CB50-Symons St | 2025-02-19 16:10 | 2025-02-19 17:05 | 0 | 0 | 1 | 54 | Unplanned | Defective equipment | Retailer disconnect EAM1535078 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1488 | 2025-02-20-0095 | Seafair - LVUG142157 | CB5098-Seafair | 2025-02-20 08:30 | 2025-02-20 11:50 | 0 | 0 | 1 | 200 | Planned | Planned interruption | Replacement of SFB25 Cloudy Bay Drive http://nams.mll.linesmarl.co.nz/Schedule/Edit/4700 EAM 1528740 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1489 | 2025-02-20-0093 | Murphys Rd - XA1695-P15C | CB68-Murphys Rd | 2025-02-20 08:47 | 2025-02-20 13:18 | 0 | 0 | 1 | 270 | Planned | Planned interruption | Replacement of SFB XA1695 with a TUDS box - 15B Ward St SAF4699 WO 1519996 Outage 1 of 2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1490 | 2025-02-20-0094 | Murphys Rd - XA1695-P15B | CB68-Murphys Rd | 2025-02-20 08:47 | 2025-02-20 13:17 | 0 | 0 | 1 | 270 | Planned | Planned interruption | Replacement of SFB XA1695 with a TUDS box - 15B Ward St SAF4699 WO 1519996 Outage 2 of 2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1491 | 2025-02-20-0096 | Richmond Brook - LVOH4028-S11414 | CB1250-Richmond Brook | 2025-02-20 09:04 | 2025-02-20 13:22 | 0 | 0 | 11 | 2827 | Planned | Planned interruption | Replacement of pole KB3392 http://nams.mll.co.nz/Schedule/Edit/4699 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1492 | 2025-02-20-0097 | East Coast - REC193 | REC29-East Coast | 2025-02-20 09:33 | 2025-02-20 15:13 | 0.12335 | 0.000368 | 10 | 3352 | Planned | Planned interruption | Kekerengu Planned Work - removal of burning trees between Poles AK1744 and KB4371 http://nams.mll.co.nz/Schedule/Edit/4712 EAM 1508423 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1493 | 2025-02-20-0099 | French Pass - REC5024 | CB45-French Pass | 2025-02-20 12:36 | 2025-02-20 15:28 | 0.45573 | 0.0026496 | 72 | 12384 | Unplanned | Adverse weather | Shutdown from REC5024 to repair broken jumper at FUSE4100 See http://nams.mll.linesmarl.co.nz/Schedule/Edit/4771 and 2025-02-20-0098 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1494 | 2025-02-21-0105 | Rai Valley - SUB335341 | CB43-Rai Valley | 2025-02-21 08:37 | 2025-02-21 10:51 | 0.0049312 | 3.68e-05 | 1 | 134 | Unplanned | Wildlife | Bird found below blown fuse, Power restored confirmed at property EAM1535431 F4773 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1495 | 2025-02-21-0101 | Howick Rd North - 0001175234ML528 | CB84-Howick Rd North | 2025-02-21 08:53 | 2025-02-21 14:41 | 0 | 0 | 1 | 348 | Planned | Planned interruption | Replacement of Chorus pole KB7648http://nams.mll.linesmarl.co.nz/Application/Edit/4736 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1496 | 2025-02-21-0102 | Howick Rd North - 0001175225ML3C0 | CB84-Howick Rd North | 2025-02-21 08:54 | 2025-02-21 14:41 | 0 | 0 | 1 | 348 | Planned | Planned interruption | Replacement of Chorus pole KB7648 http://nams.mll.linesmarl.co.nz/Application/Edit/4736 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1497 | 2025-02-21-0104 | Richmond Brook - SUB353065 | CB1250-Richmond Brook | 2025-02-21 10:17 | 2025-02-21 10:47 | 0 | 0 | 6 | 180 | Planned | Planned interruption | Shutdown of SUB353065 for moving of a high load in Foster St http://nams.mll.linesmarl.co.nz/Schedule/Edit/4726 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1498 | 2025-02-23-0106 | Richmond Brook - 0005502461ML3E4 | CB1250-Richmond Brook | 2025-02-23 14:50 | 2025-02-23 17:02 | 0 | 0 | 1 | 131 | Unplanned | Third party interference | Customer cut through OH phase conductor while gardening. Repaired conductor and relivened. W/O1535528 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1499 | 2025-02-23-0107 | Seymour St - 0001155598ML8E6 | CB51-Seymour St | 2025-02-23 19:22 | 2025-02-23 20:02 | 0 | 0 | 1 | 41 | Unplanned | Defective equipment | Internal fault, Tripped RCD EM 1535529 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1500 | 2025-02-24-0108 | Rai Valley - REC5167 | CB43-Rai Valley | 2025-02-24 07:37 | 2025-02-24 07:38 | 0 | 0 | 104 | 0 | Unplanned | Unknown | Sucessful reclose - R-Y 1000Amps | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1501 | 2025-02-24-0109 | Taylor Pass - LVUG162887 | CB1089-Taylor Pass | 2025-02-24 08:32 | 2025-02-24 12:33 | 0 | 0 | 38 | 9120 | Planned | Planned interruption | Replacement of SFB8 Blairich View SAF4700 WO 1530250 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1502 | 2025-02-24-0110 | Sounds - FUSE2344 | REC1170-Sounds | 2025-02-24 08:34 | 2025-02-24 16:17 | 0.49411 | 0.0010672 | 29 | 13427 | Planned | Planned interruption | Maintenance work on arms at pole ET1676 and ET1677 in Onahau Bay SAF4337 WO 1496152 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1503 | 2025-02-24-0112 | Parker St - LVUG2580 | CB1516-Parker St | 2025-02-24 08:46 | 2025-02-24 11:17 | 0 | 0 | 7 | 1057 | Planned | Planned interruption | Replacement of SFB5 Bristol Lane http://nams.mll.linesmarl.co.nz/Schedule/Edit/4707 WO1529395 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1504 | 2025-02-24-0111 | Renwick Township - 0000053254ML400 | CB5482 Renwick Township | 2025-02-24 09:06 | 2025-02-24 10:51 | 0 | 0 | 1 | 106 | Unplanned | Defective equipment | Fuse making poor contact in fuse holder. Adjusted holder.EAM 1535585 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1505 | 2025-02-24-0113 | Sounds - SUB325201 | REC1170-Sounds | 2025-02-24 09:55 | 2025-02-24 16:54 | 0 | 0 | 13 | 5447 | Planned | Planned interruption | Replace x-arms at MA1637, MA1671, MA1673, MA1638 http://nams.mll.linesmarl.co.nz/Schedule/Edit/4709 EAM1496152 NAMS4346 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1506 | 2025-02-24-0114 | Ngakuta - REC5130 | REC1562-Ngakuta | 2025-02-24 11:28 | 2025-02-24 15:10 | 2.0506 | 0.0092368 | 251 | 55722 | Unplanned | Third party interference | Replacement of damaged iron rail pole AP1260 on Queen Charlotte Drive. Suspect damaged by a vehicle. http://nams.mll.linesmarl.co.nz/Schedule/Edit/4782 EAM1535568 F4782 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1507 | 2025-02-25-0115 | Sounds - REC1350 | REC1170-Sounds | 2025-02-25 08:15 | 2025-02-25 16:19 | 1.2708 | 0.032273 | 474 | 34533 | Planned | Planned interruption | Mianenance works (arms and poles) on line between Broughton Bay and Portage - EAM 1429189 SAF4335. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1508 | 2025-02-25-0116 | Nelson St - 0001116089ML27E | CB93-Nelson St | 2025-02-25 08:43 | 2025-02-25 15:13 | 0 | 0 | 1 | 390 | Planned | Planned interruption | Installation of new SFB13 Elzy St http://nams.mll.linesmarl.co.nz/Application/Edit/4738 EAM 1506304 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1509 | 2025-02-25-0117 | Nelson St - 0001116108ML275 | CB93-Nelson St | 2025-02-25 08:43 | 2025-02-25 15:13 | 0 | 0 | 1 | 389 | Planned | Planned interruption | Installation of new SFB13 Elzy St http://nams.mll.linesmarl.co.nz/Application/Edit/4738 EAM 1506304 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1510 | 2025-02-25-0118 | Jacksons Road - 0003330574ML190 | CB1179-Jacksons Road | 2025-02-25 08:50 | 2025-02-25 11:31 | 0 | 0 | 1 | 161 | Unplanned | Defective equipment | Burnt out Pole fuse deterioration EAM 1535680 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1511 | 2025-02-25-0119 | Pelorus - 0007713309MLDE9 | CB5126-Pelorus | 2025-02-25 15:02 | 2025-02-25 18:25 | 0 | 0 | 1 | 202 | Unplanned | Unknown | Blown pole fuse, checked all connections and tested the mains and all okay. Unknown cause. EAM 1535740 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1512 | 2025-02-26-0120 | Okaramio - 0007705349ML26D | CB104 Okaramio | 2025-02-26 07:47 | 2025-02-26 09:30 | 0 | 0 | 1 | 104 | Unplanned | Defective equipment | Blown fuse/Loose connecion EAM 1535765 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1513 | 2025-02-26-0121 | Sounds - REC1350 | REC1170-Sounds | 2025-02-26 08:15 | 2025-02-26 15:53 | 0.54795 | 0.036137 | 508 | 14890 | Planned | Planned interruption | Planned shutdown to Replace H Structure - ET1666/MA1383 Replace H Structure - ET1664/MA1477 as part of Kenepuru Maintenance project. EAM 1429189 SAF 4336 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1514 | 2025-02-26-0122 | Renwick Township - SUB342039 | CB5482 Renwick Township | 2025-02-26 08:30 | 2025-02-26 09:30 | 0.002208 | 3.68e-05 | 1 | 60 | Planned | Planned interruption | Connection of new earths to SUB342039 in Alma St, Renwick http://nams.mll.linesmarl.co.nz/Schedule/Edit/4728 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1515 | 2025-02-26-0123 | Vintage Lane - SUB342079 | CB171-Vintage Lane | 2025-02-26 10:56 | 2025-02-26 11:46 | 0 | 0 | 1 | 50 | Planned | Planned interruption | Connection of new earths at SUB342079 http://nams.mll.linesmarl.co.nz/Schedule/Edit/4730 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1516 | 2025-02-26-0124 | Rai Valley - CB5391 | CB43 - Rai Valley, CB45 - French Pass, CB5126 - Pelorus | 2025-02-26 23:38 | 2025-02-26 23:38 | 0 | 0 | 918 | 0 | Unplanned | Unknown | LVY 33kV CB5391 reclosed on RF. Cyclo 168 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1517 | 2025-02-27-0125 | Waikawa - 0006624120ML373 | CB109- Waikawa | 2025-02-27 08:05 | 2025-02-27 10:36 | 0 | 0 | 1 | 152 | Unplanned | Defective equipment | Internal issue - Oven blew fuse EAM 1535937 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1518 | 2025-02-27-0126 | Sounds - FUSE4327 | REC1170-Sounds | 2025-02-27 08:15 | 2025-02-27 16:13 | 2.8272 | 0.026864 | 365 | 76825 | Planned | Planned interruption | Planned shutdown 8A , Replace H Structure - ET1692/AE121 Replace x arm MA1349 Tara Bay EAM 1429189 SAF 4342 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1519 | 2025-02-27-0127 | Sounds - FUSE3914 | REC1170-Sounds | 2025-02-27 08:56 | 2025-02-27 16:07 | 0.28549 | 0.0006624 | 18 | 7758 | Planned | Planned interruption | Te Mahia Planned Work - Replace arms at MA1385 and MA1217 http://nams.mll.co.nz/Schedule/Edit/4173 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1520 | 2025-02-27-0129 | Parker St - 0001138230ML597 | CB1516-Parker St | 2025-02-27 09:11 | 2025-02-27 10:57 | 0 | 0 | 1 | 106 | Planned | Planned interruption | Dillons Point Road Planned Work - OHUG at 18 Dillons Point Rd http://nams.mll.co.nz/Schedule/Edit/4738 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1521 | 2025-02-27-0128 | Waikawa - 0006602590ML1CD | CB109- Waikawa | 2025-02-27 09:13 | 2025-02-27 10:37 | 0 | 0 | 1 | 84 | Unplanned | Defective equipment | Fuse replaced no reason given, but fuse letter issued EAM 1535946 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1522 | 2025-02-27-0130 | Pelorus - 0007713309MLDE9 | CB5126-Pelorus | 2025-02-27 14:26 | 2025-02-27 18:03 | 0 | 0 | 1 | 216 | Unplanned | Unknown | Blown white phase. No cause found. EAM 1536044 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1523 | 2025-02-27-0131 | Rai Valley - SUB335341 | CB43-Rai Valley | 2025-02-27 18:03 | 2025-02-27 19:28 | 0.003128 | 3.68e-05 | 1 | 85 | Unplanned | Wildlife | Blown HV fuse found at SUB335341, and a dead bird. Replaced all 3 fuses (3A)http://nams.mll.linesmarl.co.nz/Schedule/Edit/4816 EAM 1536067 -- | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1524 | 2025-02-27-0132 | Grassmere - CB1253 | CB1253-Grassmere | 2025-02-27 20:48 | 2025-02-27 20:49 | 0.0050048 | 0.0050048 | 136 | 136 | Unplanned | Unknown | 11kV CB1253 (Grassmere) reclosed on phase OC. Cyclo 3 27/02/2025 8:54:34 pm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1525 | 2025-02-28-0133 | French Pass - REC1466 | CB45-French Pass | 2025-02-28 02:37 | 2025-02-28 02:37 | 0 | 0 | 36 | 0 | Unplanned | Unknown | REC1466 (Elaine Bay) reclosed on phase OC (OC1+). Fault flags showed a Y-E fault @ 196A. Cyclo 143 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1526 | 2025-02-28-0134 | Hospital Rd East - 0001181301ML587 | CB39-Hospital Rd East | 2025-02-28 08:14 | 2025-02-28 09:01 | 0 | 0 | 1 | 46 | Planned | Planned interruption | Replacement of red tagged pole at 27 Gilbert St (PT3611) SAF4695 - WO1525619 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1527 | 2025-02-28-0135 | Waikawa - FUSE2405 | CB109- Waikawa | 2025-02-28 10:40 | 2025-03-01 11:37 | 0.38563 | 0.0002576 | 7 | 10479 | Unplanned | Defective equipment | found FUSE2405 open. EAM 1536079 NAMS F4825 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1528 | 2025-02-28-0136 | Waikawa - SUB330644 | CB109- Waikawa | 2025-02-28 12:12 | 2025-02-28 14:25 | 0 | 0 | 1 | 132 | Planned | Planned interruption | Oyster Bay Planned Work - connection of new earths and OHUG at SUB330644 http://nams.mll.co.nz/Schedule/Edit/4768 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1529 | 2025-02-28-0137 | Waikawa - REC17 | CB109- Waikawa | 2025-02-28 21:51 | 2025-02-28 21:51 | 0.003128 | 0.003128 | 85 | 85 | Unplanned | Unknown | REC17 (Boons Valley) reclosed on EF. Cyclo 110 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1530 | 2025-03-01-0001 | Rai Valley - FUSE2291 | CB43-Rai Valley | 2025-03-01 08:15 | 2025-03-01 14:32 | 0.13874 | 0.000368 | 10 | 3770 | Unplanned | Third party interference | found 2x fuses blown at FUSE2291. Line patrolled. Fishing line removed from line where it crosses Opouri river under access permit by lowering conductor. Replaced fuses (20A). EAM1536120 NAMS F4823 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1531 | 2025-03-01-0002 | Redwood St Sth - 0001183159ML6DC | CB1673-Redwood St Sth | 2025-03-01 09:31 | 2025-03-01 11:20 | 0 | 0 | 1 | 109 | Unplanned | Defective equipment | Burnt out Lv fuse, possible loose connection. Replaced with new fuse EAM1536121 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1532 | 2025-03-03-0003 | Pelorus - SUB335148 | CB5126-Pelorus | 2025-03-03 09:05 | 2025-03-03 09:35 | 0.0011408 | 3.68e-05 | 1 | 31 | Planned | Planned interruption | Connection of new earths at SUB335148 in Kaiuma Bay Rd http://nams.mll.co.nz/Schedule/Edit/4751 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1533 | 2025-03-03-0005 | Pelorus - SUB335022 | CB5126-Pelorus | 2025-03-03 10:50 | 2025-03-03 11:37 | 0.0033856 | 7.36e-05 | 2 | 92 | Planned | Planned interruption | Planned shutdown to upgrade TX earths at SUB335022. SAF 4705 EAM1233512 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1534 | 2025-03-03-0006 | Waikawa - REC17 | CB109- Waikawa | 2025-03-03 22:39 | 2025-03-03 22:56 | 0.057555 | 0.0033856 | 92 | 1564 | Unplanned | Unknown | REC tripped and locked out on EF (cyclo 114). Trial livened sucessfully after 15min. Auto reclose left disabled for 12hrs with no further issues. Given difficulty to patrol line, we will look to fly this line if the issue reoccurs. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1535 | 2025-03-04-0007 | Sounds - REC1350 | REC1170-Sounds | 2025-03-04 08:15 | 2025-03-04 14:37 | 0.44079 | 0.028262 | 403 | 11978 | Planned | Planned interruption | Planned shutdown to Replace H Structure - AE2116/ET1695 (second attempt) EAM 1429189 SAF 4751 Gens supplying beyond REC1350 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1536 | 2025-03-04-0008 | Hawkesbury Road - ABS1808-B | CB5457 Hawkesbury Road | 2025-03-04 08:30 | 2025-03-04 14:21 | 0.29709 | 0.0008464 | 23 | 8073 | Planned | Planned interruption | Replacement of all x-arms on pole KB9378 http://nams.mll.linesmarl.co.nz/Application/Edit/4690 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1537 | 2025-03-04-0010 | Richmond Brook - REC36 | CB1250-Richmond Brook | 2025-03-04 10:47 | 2025-03-04 14:09 | 0.25889 | 0.001288 | 35 | 7035 | Unplanned | Unknown | Tripping of REC 36 Awapiri Line patrolled Trial livening REC 36 stayed closed. Power restored. Confirmed power with customer. EAM 1536464 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1538 | 2025-03-04-0011 | Seymour St - 0001165221MLA2B | CB51-Seymour St | 2025-03-04 14:32 | 2025-03-04 16:03 | 0 | 0 | 1 | 91 | Unplanned | Defective equipment | Internal issue with Oven, that caused the blowing of fuse (wiring in new stove) EAM 1536692 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1539 | 2025-03-05-0012 | Dry Hills - 0001116323MLBF3 | CB1682-Dry Hills | 2025-03-05 07:27 | 2025-03-05 08:42 | 0 | 0 | 1 | 74 | Unplanned | Other Cause | blown fuse as Harvester hit line (submain), which caused line to clash. Inspected conductor and relivened EAM 1536718 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1540 | 2025-03-05-0013 | Ngakuta - SUB321115 | REC1562-Ngakuta | 2025-03-05 09:00 | 2025-03-05 15:52 | 0.015162 | 3.68e-05 | 1 | 412 | Planned | Planned interruption | Replacement of SUB321115 at 387 Anakwia Rd http://nams.mll.linesmarl.co.nz/Schedule/Edit/4760 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1541 | 2025-03-05-0016 | Omaka - 0001124129ML109 | CB1088 - Omaka | 2025-03-05 09:09 | 2025-03-05 14:36 | 0 | 0 | 1 | 327 | Planned | Planned interruption | Aerodrome Road Planned Work - remedial works on Vector One Nine subdivision http://nams.mll.co.nz/Schedule/Edit/4830 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1542 | 2025-03-05-0014 | Sounds - SUB3251AE | REC1170-Sounds | 2025-03-05 09:59 | 2025-03-05 10:07 | 0.0005888 | 7.36e-05 | 2 | 16 | Unplanned | Adverse weather | TX FUSE Spotted blown while crews were driving past http://nams.mll.co.nz/Schedule/Edit/4839 Replaced fuse - relivened 1536735 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1543 | 2025-03-05-0015 | Sounds - SUB3251AG | REC1170-Sounds | 2025-03-05 10:03 | 2025-03-05 10:22 | 0.005888 | 0.0002944 | 8 | 160 | Unplanned | Adverse weather | TX FUSE Spotted blown while crews were driving past Replaced fuse - relivened 5/03/2025 10:15:25 am 1536736 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1544 | 2025-03-05-0017 | Weld St - 0001162417MLE3A | CB71-Weld St | 2025-03-05 17:06 | 2025-03-05 18:17 | 0 | 0 | 1 | 71 | Unplanned | Adverse weather | 2x blown 30A fuses due to clashing toghter in the wind. EAM 1536791 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1545 | 2025-03-06-0019 | Seafair - 0003360296ML7D9 | CB5098-Seafair | 2025-03-06 11:39 | 2025-03-06 13:39 | 0 | 0 | 1 | 120 | Unplanned | Defective equipment | Internal service fault - EAM 1536836 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1546 | 2025-03-07-0020 | Havelock Canvastown - LVUG101011 | CB103 Havelock Canvastown | 2025-03-07 09:07 | 2025-03-07 11:11 | 0 | 0 | 7 | 868 | Planned | Planned interruption | Replacement of SFB XA1427 - 2598 Kaiuma Bay Rd http://nams.mll.linesmarl.co.nz/Schedule/Edit/4658 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1547 | 2025-03-07-0021 | Havelock Canvastown - LVUG101018 | CB103 Havelock Canvastown | 2025-03-07 09:07 | 2025-03-07 11:11 | 0 | 0 | 2 | 248 | Planned | Planned interruption | Replacement of SFB XA1427 - 2598 Kaiuma Bay Rd http://nams.mll.linesmarl.co.nz/Schedule/Edit/4658 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1548 | 2025-03-07-0023 | Waikawa - 0006601352ML241 | CB109- Waikawa | 2025-03-07 15:31 | 2025-03-07 16:56 | 0 | 0 | 1 | 85 | Unplanned | Unknown | Blown re-wireable pole fuse Changed TO HRC EAM 1536904 - ?No power, sb checked. 1PH 60A | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1549 | 2025-03-07-0024 | Waikawa - 0006617346ML4C7 | CB109- Waikawa | 2025-03-07 19:04 | 2025-03-07 20:46 | 0 | 0 | 1 | 103 | Unplanned | Defective equipment | Burnt out Lv fuse, replaced with PF100. 1536906 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1550 | 2025-03-10-0033 | Rai Valley - CB5391 | CB43 - Rai Valley, CB45 - French Pass, CB5126 - Pelorus | 2025-03-08 01:52 | 2025-03-08 01:52 | 0.033672 | 0.033672 | 915 | 915 | Unplanned | Unknown | successful reclose of CB5391 Earth fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1551 | 2025-03-09-0026 | Taylor Pass - FUSE2035 | CB1089-Taylor Pass | 2025-03-09 09:02 | 2025-03-09 11:03 | 0.013358 | 0.0001104 | 3 | 363 | Unplanned | Unknown | http://nams.mll.co.nz/Schedule/Edit/4853 Blown Fuse 2036 Line patrolled no cause found 1536908 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1552 | 2025-03-10-0027 | East Coast - REC1693 | REC29-East Coast | 2025-03-10 07:06 | 2025-03-10 15:46 | 0.076397 | 0.0001472 | 4 | 2076 | Planned | Planned interruption | Lulworth windfarm turned off while 33kV to Ward is isolated for Taimate rebuild. http://nams.mll.co.nz/Schedule/Edit/4795 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1553 | 2025-03-10-0028 | Waihopai Valley - FUSE4047 | CB5493 Waihopai Valley | 2025-03-10 07:52 | 2025-03-10 10:30 | 0.017443 | 0.0001104 | 3 | 474 | Unplanned | Unknown | Gas switch fuses replaced (RMUF5602). Site re-livened. No cause found 1536915 N Blown 11kV Fuse in RMUF5602 http://nams.mll.co.nz/Schedule/Edit/4855 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1554 | 2025-03-10-0030 | Craiglochart - FUSE2142 | REC1391-Craiglochart | 2025-03-10 08:39 | 2025-03-10 15:26 | 0.11982 | 0.0002944 | 8 | 3256 | Planned | Planned interruption | Replacement of x-arms at poles ET1769 & AA1777 - Avon Valley SAF4702 - EAM 1529396 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1555 | 2025-03-10-0029 | Richmond Brook - REC1592 | CB1250-Richmond Brook | 2025-03-10 08:40 | 2025-03-10 12:29 | 0.62361 | 0.0027232 | 74 | 16946 | Planned | Planned interruption | Installation of new SUB353392 st the start of Medway Rd SAF4334 WO 1498683 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1556 | 2025-03-10-0031 | Old Renwick Rd - 0001122037ML4FB | CB66-Old Renwick Rd | 2025-03-10 09:15 | 2025-03-10 14:28 | 0 | 0 | 1 | 313 | Planned | Planned interruption | Moving of service at 33 Rose St into new SFB33 Rose St SAF 4727 EAM 1510036 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1557 | 2025-03-10-0032 | Okaramio - 0007705333ML5A1 | CB104 Okaramio | 2025-03-10 13:59 | 2025-03-10 16:40 | 0 | 0 | 1 | 161 | Unplanned | Unknown | Blown 30A service fuse replaced - No cause found EAM 1536937 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1558 | 2025-03-10-0034 | Craiglochart - 0002273020ML637 | REC1391-Craiglochart | 2025-03-10 18:50 | 2025-03-11 17:30 | 0 | 0 | 1 | 1361 | Unplanned | Defective equipment | Fault found in service cable. Customer left off overnight. . Fault found and repeired. Fault found in service cable to house inside customer boundary. Chargeable job | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1559 | 2025-03-11-0036 | Flaxbourne - ABS15113-B | REC1432-Flaxbourne | 2025-03-11 07:26 | 2025-03-11 15:26 | 0.017664 | 3.68e-05 | 1 | 480 | Planned | Planned interruption | Windfarms turned off while 33kV to Ward is isolated for Taimate rebuild. EAM 1422544 SAF 4589 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1560 | 2025-03-11-0035 | East Coast - REC1693 | REC29-East Coast | 2025-03-11 07:27 | 2025-03-11 15:18 | 0.069331 | 0.0001472 | 4 | 1884 | Planned | Planned interruption | Windfarms turned off while 33kV to Ward is isolated for Taimate rebuild. EAM 1422544 SAF 4589 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1561 | 2025-03-11-0037 | Kaituna - 0007706025MLF60 | CB5448 Kaituna | 2025-03-11 15:36 | 2025-03-11 16:53 | 0 | 0 | 1 | 77 | Unplanned | Unknown | Blown 60A HRC - no cause found EAM 1537065 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1562 | 2025-03-12-0039 | Flaxbourne - ABS15113-B | REC1432-Flaxbourne | 2025-03-12 06:23 | 2025-03-12 15:52 | 0.020939 | 3.68e-05 | 1 | 569 | Planned | Planned interruption | Weld Cone windfarm turned off while 33kV to Ward is isolated for Taimate rebuild. EAM 1422544 SAF 4590 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1563 | 2025-03-12-0038 | East Coast - REC1693 | REC29-East Coast | 2025-03-12 06:25 | 2025-03-12 15:52 | 0.083462 | 0.0001472 | 4 | 2268 | Planned | Planned interruption | Lulworth windfarm turned off while 33kV to Ward is isolated for Taimate rebuild. EAM 1422544 SAF 4590 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1564 | 2025-03-12-0040 | Waihopai Valley - ABS15337-B | CB5493 Waihopai Valley | 2025-03-12 08:30 | 2025-03-12 16:15 | 0.034224 | 7.36e-05 | 2 | 930 | Planned | Planned interruption | Planned shutdown to install pole 3 and replace 11kV ABS at Pole 2. Wairau Valley 33kV project EAM 1469375 SAF 4648 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1565 | 2025-03-12-0041 | Tummil - LVUG3522 | REC1345-Tummil | 2025-03-12 08:30 | 2025-03-12 16:15 | 0.034224 | 7.36e-05 | 2 | 930 | Planned | Planned interruption | Planned shutdown to install pole 3 and replace 11kV ABS at Pole 2. Wairau Valley 33kV project EAM 1469375 SAF 4648 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1566 | 2025-03-12-0042 | Dry Hills - SUB348531 | CB1682-Dry Hills | 2025-03-12 11:18 | 2025-03-12 13:40 | 0 | 0 | 7 | 987 | Unplanned | Third party interference | FENZ reported lines down.LV accross rd broken. Isolated at SUB 348531 for repairs. It was found that a Police survelliance vehicle had hit the lines. EAM 1537131 F4872 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1567 | 2025-03-12-0043 | Sounds - 0008810342ML1F4 | REC1170-Sounds | 2025-03-12 13:03 | 2025-03-12 16:00 | 0 | 0 | 1 | 177 | Unplanned | Unknown | Blown 30amp fuse Cause unknown EAM 1537154 Sub325098 1ph 30amps | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1568 | 2025-03-12-0044 | Havelock Canvastown - SUB320307 | CB103 Havelock Canvastown | 2025-03-12 14:44 | 2025-03-12 16:58 | 0.053838 | 0.0004048 | 11 | 1463 | Unplanned | Unknown | Part Power at SFB XA196 Fuse blown at SUB320307 Fuses replaced in and holding, power confirmed restored EAM1537197 NAMS F4873 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1569 | 2025-03-13-0047 | East Coast - REC1693 | REC29-East Coast | 2025-03-13 06:55 | 2025-03-13 16:07 | 0.081254 | 0.0001472 | 4 | 2208 | Planned | Planned interruption | Lulwoth windfarm shutdown while 33kV rebuild at Taimate is in progress. EAM 1422544 SAF 4591 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1570 | 2025-03-13-0048 | Flaxbourne - ABS15113-B | REC1432-Flaxbourne | 2025-03-13 06:55 | 2025-03-13 16:07 | 0.020314 | 3.68e-05 | 1 | 552 | Planned | Planned interruption | Weld Cone windfarm shutdown while 33kV rebuild at Taimate is in progress. EAM 1422544 SAF 4591 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1571 | 2025-03-13-0046 | Thomsons Ford Rd - 0003330452ML44E | CB1509-Thomsons Ford Rd | 2025-03-13 07:30 | 2025-03-13 09:08 | 0 | 0 | 1 | 98 | Unplanned | Defective equipment | Service fuse blown due to deterioration | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1572 | 2025-03-13-0049 | Tuamarina - 0004421390ML94C | CB188-Tuamarina | 2025-03-13 08:36 | 2025-03-13 10:54 | 0.0050784 | 3.68e-05 | 1 | 138 | Planned | Planned interruption | 13 Hunter Road Planned Work - Lift low LV span DF2018 to RM2857 http://nams.mll.co.nz/Schedule/Edit/4779 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1573 | 2025-03-13-0050 | Rai Valley - SUB335363 | CB43-Rai Valley | 2025-03-13 09:36 | 2025-03-13 10:26 | 0 | 0 | 1 | 50 | Planned | Planned interruption | Connection of new earths at SUB335363 http://nams.mll.linesmarl.co.nz/Schedule/Edit/4808 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1574 | 2025-03-13-0051 | Spring Creek - 0003340209MLE2D | CB187-Spring Creek | 2025-03-13 11:45 | 2025-03-13 13:44 | 0 | 0 | 1 | 119 | Planned | Planned interruption | Replacement of LV service to 40 Gouland Rd http://nams.mll.linesmarl.co.nz/Schedule/Edit/4810 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1575 | 2025-03-13-0052 | Rai Valley - SUB335336 | CB43-Rai Valley | 2025-03-13 11:48 | 2025-03-13 12:48 | 0.002208 | 3.68e-05 | 1 | 60 | Planned | Planned interruption | Planned shutdown to connect upgraded TX earths at SUB335336. EAM 1241821 SAF 4707.2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1576 | 2025-03-13-0053 | Rai Valley - SUB335024 | CB43-Rai Valley | 2025-03-13 13:56 | 2025-03-13 14:28 | 0 | 0 | 1 | 32 | Planned | Planned interruption | Connection of upgraded earths at SUB335024 - Carluke Rd http://nams.mll.linesmarl.co.nz/Schedule/Edit/4813 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1577 | 2025-03-13-0054 | Rai Valley - SUB335041 | CB43-Rai Valley | 2025-03-13 14:45 | 2025-03-13 15:19 | 0 | 0 | 2 | 66 | Planned | Planned interruption | Upgrade of earthing at SUB335041 http://nams.mll.linesmarl.co.nz/Schedule/Edit/4814 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1578 | 2025-03-14-0057 | Tuamarina - 0004421390ML94C | CB188-Tuamarina | 2025-03-13 18:34 | 2025-03-14 09:22 | 0 | 0 | 1 | 887 | Unplanned | Unknown | Blown 30 amp fuse replaced and service restored - Unknown cause To be attended 14/3/25. EAM: 1537297 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1579 | 2025-03-14-0058 | Hardings Rd - FUSE2071 | CB167-Hardings Rd | 2025-03-14 08:51 | 2025-03-14 11:11 | 0.041216 | 0.0002944 | 8 | 1120 | Planned | Planned interruption | Planned shutdown to upgrade TX at SUB349004 Hardings Rd EAM 1533707 SAF 4765 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1580 | 2025-03-14-0059 | Dashwood - 0005504003ML550 | CB1252-Dashwood | 2025-03-14 11:32 | 2025-03-14 13:53 | 0 | 0 | 1 | 142 | Unplanned | Unknown | Blown fuse 30amp cause unknown EAM 1537326 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1581 | 2025-03-14-0060 | Kaituna - SUB340313 | CB5448 Kaituna | 2025-03-14 21:00 | 2025-03-15 00:18 | 0.16645 | 0.0016928 | 46 | 4523 | Unplanned | Defective equipment | Faulty Dominion TX fuses at Sub 343013 on Blicks Rd. Main line shutdown required to replace under AP. http://nams.mll.co.nz/Schedule/Edit/4884 EAM 1537358 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1582 | 2025-03-15-0061 | Richmond Brook - REC37 | CB1250-Richmond Brook | 2025-03-15 03:16 | 2025-03-15 03:16 | 0.0082432 | 0.0082432 | 224 | 224 | Unplanned | Unknown | REC 37 Auto reclosed on phase OC. ENS7001 saw 349A Red & 342A Yellow | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1583 | 2025-03-15-0062 | Hospital Rd West - FUSE2020 | CB47-Hospital Rd West | 2025-03-15 07:46 | 2025-03-15 11:53 | 0.0090896 | 3.68e-05 | 1 | 247 | Planned | Planned interruption | Planned shutdown for bracket installation and cable inspection at SUB3700CE. EAM1514645 SAF4580 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1584 | 2025-03-16-0064 | Craiglochart - SUB341109 | REC1391-Craiglochart | 2025-03-16 08:42 | 2025-03-16 10:12 | 0.006624 | 7.36e-05 | 2 | 180 | Unplanned | Defective equipment | EAM 1537360 Found 1 HV fuse hanging at SUB341109.Not blown. http://nams.mll.co.nz/Schedule/Edit/4888 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1585 | 2025-03-16-0065 | Waikawa - SUB330109 | CB109- Waikawa | 2025-03-16 09:22 | 2025-03-16 10:53 | 0.01656 | 0.000184 | 5 | 450 | Unplanned | Wildlife | Possum on Tx 340109 Open TX fuses and removed possum with LV gloves. 1537361 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1586 | 2025-03-16-0066 | Waikawa - SEC5330 | CB109- Waikawa | 2025-03-16 12:07 | 2025-03-16 12:22 | 0.096563 | 0.0060352 | 164 | 2624 | Unplanned | Defective equipment | SEC5330 Opened with no trip flags or upstream operations. To be followed up with EWS / Engineering Cyclo 28 16/03/2025 12:27:48 pm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1587 | 2025-03-16-0067 | Kaituna - REC5232 | CB5448 Kaituna | 2025-03-16 18:53 | 2025-03-16 18:54 | 0 | 0 | 35 | 0 | Unplanned | Unknown | REC 5232 reclosed on Phase OC. Cyclo 89. Very wind at the time. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1588 | 2025-03-17-0068 | Sounds - REC97 | REC1170-Sounds | 2025-03-17 00:12 | 2025-03-17 00:12 | 0 | 0 | 178 | 0 | Unplanned | Unknown | REC97 succesful Auto Reclose on POC. Yellow 141 Earth 139 Cyclo251 SEC150 Bay of many coves Yellow phase 185, Red phase 126 Earth 141 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1589 | 2025-03-17-0069 | Hawkesbury Road - REC5436 | CB5457 Hawkesbury Road | 2025-03-17 04:17 | 2025-03-17 04:17 | 0 | 0 | 176 | 0 | Unplanned | Vegetation | REC5436 auto reclosed on POC. Cyclo78. Red 1855A Yellow 1836A ENS7005 Red 1836 Yellow 1830A 17/03/2025 3:27:44 pm Line patrol found trees growing into 11kV around pole JA3891. Arborist cut back branches under live line permit. SAF F489 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1590 | 2025-03-17-0073 | Flaxbourne - ABS15113-B | REC1432-Flaxbourne | 2025-03-17 07:06 | 2025-03-17 16:30 | 0.020755 | 3.68e-05 | 1 | 564 | Planned | Planned interruption | Planned shutdown of Windfarms for 33kV rebuild at Taimate. EAM 1422544 SAF 4592 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1591 | 2025-03-17-0074 | East Coast - REC1693 | REC29-East Coast | 2025-03-17 07:06 | 2025-03-17 16:30 | 0.083021 | 0.0001472 | 4 | 2256 | Planned | Planned interruption | Planned shutdown of Windfarms for 33kV rebuild at Taimate. EAM 1422544 SAF 4592 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1592 | 2025-03-17-0070 | Sounds - SUB325517 | REC1170-Sounds | 2025-03-17 07:45 | 2025-03-17 14:34 | 0.12011 | 0.0002944 | 8 | 3264 | Unplanned | Wildlife | Blown TX Fuse - Dead Possum found EAM 1537368 http://nams.mll.co.nz/Schedule/Edit/4893 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1593 | 2025-03-17-0071 | Godfrey Road - SUB343232 | CB5367 Godfrey Road | 2025-03-17 07:48 | 2025-03-17 09:03 | 0.0083904 | 0.0001104 | 3 | 228 | Unplanned | Wildlife | 1 TX fuse open and dead possum at base of pole. No possum guard. EAM 1537365 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1594 | 2025-03-17-0072 | Parker St - 0001146399ML8A4 | CB1516-Parker St | 2025-03-17 14:47 | 2025-03-17 15:52 | 0 | 0 | 1 | 65 | Unplanned | Defective equipment | Internal issue EAM 1537422 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1595 | 2025-03-18-0075 | East Coast - REC1693 | REC29-East Coast | 2025-03-18 07:08 | 2025-03-18 09:44 | 0.022963 | 0.0001472 | 4 | 624 | Planned | Planned interruption | Planned shutdown of Lulworth windfarm for 33kV rebuild at Taimate. EAM1422544 SAF 4593 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1596 | 2025-03-18-0076 | Flaxbourne - ABS15113-B | REC1432-Flaxbourne | 2025-03-18 07:08 | 2025-03-18 09:44 | 0.0057408 | 3.68e-05 | 1 | 156 | Planned | Planned interruption | Planned shutdown of Weld Cone windfarm for 33kV rebuild at Taimate. EAM1422544 SAF 4593 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1597 | 2025-03-18-0077 | French Pass - REC160 | CB45-French Pass | 2025-03-18 09:23 | 2025-03-18 09:41 | 0.011886 | 0.0006256 | 17 | 323 | Unplanned | Defective equipment | REC160 tripped on Phase OC Trial reclose after 15mins REC160 closed in and holding. F4901 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1598 | 2025-03-18-0079 | Sounds - REC97 | REC1170-Sounds | 2025-03-18 09:34 | 2025-03-18 09:34 | 0 | 0 | 178 | 0 | Unplanned | Unknown | Sucessful reclose of 11kV REC97 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1599 | 2025-03-18-0078 | French Pass - REC160 | CB45-French Pass | 2025-03-18 09:52 | 2025-03-18 17:24 | 0.25396 | 0.0006256 | 17 | 6901 | Unplanned | Defective equipment | Line patrolled and no cause found. Line sucessfully relivened EAM 1537485 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1600 | 2025-03-18-0080 | Old Renwick Rd - 0002272061ML977 | CB66-Old Renwick Rd | 2025-03-18 18:27 | 2025-03-18 20:08 | 0.0037536 | 3.68e-05 | 1 | 102 | Unplanned | Unknown | Blown TX fuse - no cause found - EAM1537556 NAMS F4903 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1601 | 2025-03-18-0081 | Parker St - 0001139225ML3D5 | CB1516-Parker St | 2025-03-18 19:48 | 2025-03-18 20:43 | 0 | 0 | 1 | 56 | Unplanned | Defective equipment | Fuse replaced; letter issued at time only drawing 17 amps EAM 1537557 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1602 | 2025-03-19-0082 | French Pass - REC160 | CB45-French Pass | 2025-03-19 08:41 | 2025-03-19 10:58 | 0.085707 | 0.0006256 | 17 | 2329 | Unplanned | Defective equipment | REC160 Tripped Phase OC patrol via Helicopter , found nothing obvious suspect salt build up on network REC160 re livened in and holding EAM1537480 NAMS F4904 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1603 | 2025-03-19-0083 | East Coast - REC1693 | REC29-East Coast | 2025-03-19 08:47 | 2025-03-19 16:52 | 0.071245 | 0.0001472 | 4 | 1936 | Planned | Planned interruption | Shtdown of Lulworth windfarm for Taimate to Ward Beach Road - 33kV Rebuild http://nams.mll.co.nz/Schedule/Edit/4844 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1604 | 2025-03-19-0086 | Flaxbourne - ABS15113-B | REC1432-Flaxbourne | 2025-03-19 08:52 | 2025-03-19 16:52 | 0.017627 | 3.68e-05 | 1 | 479 | Planned | Planned interruption | Shutdown of Weld Cone windfarm for Taimate to Ward Beach Road - 33kV Rebuild http://nams.mll.co.nz/Schedule/Edit/4844 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1605 | 2025-03-19-0084 | Murphys Rd - SUB3700NC | CB68-Murphys Rd | 2025-03-19 09:31 | 2025-03-19 17:28 | 1.3663 | 0.0028704 | 78 | 37128 | Planned | Planned interruption | Planned shutdown to replace 2 pole sub with ground mount sub in Ward St EAM 1422872 SAF 4619 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1606 | 2025-03-19-0085 | Havelock Canvastown - SUB320354 | CB103 Havelock Canvastown | 2025-03-19 10:28 | 2025-03-19 14:10 | 0.040848 | 0.000184 | 5 | 1110 | Unplanned | Unknown | found blown HV fuse at SUB320354 network patrolled no obvious cause found. Fuses replaced power confirmed restored EAM1537683 NAMSF3905 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1607 | 2025-03-19-0087 | Waihopai Valley - REC5512 | CB5493 Waihopai Valley | 2025-03-19 10:42 | 2025-03-19 10:42 | 0.0017664 | 0.0017664 | 48 | 48 | Unplanned | Unknown | Successful reclose | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1608 | 2025-03-19-0088 | French Pass - REC160 | CB45-French Pass | 2025-03-19 11:52 | 2025-03-20 15:30 | 1.0372 | 0.0006256 | 17 | 28186 | Unplanned | Defective equipment | 11kV REC160 tripped on phase OC. Ongoing fault. Line patrolled by drone, but nothing found. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1609 | 2025-03-19-0089 | Flaxbourne - 0005507077ML3E7 | REC1432-Flaxbourne | 2025-03-19 19:50 | 2025-03-19 21:38 | 0 | 0 | 1 | 108 | Unplanned | Defective equipment | Internal fault - fuse letter sent EAM 1537938 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1610 | 2025-03-20-0090 | Flaxbourne - ABS15113-B | REC1432-Flaxbourne | 2025-03-20 07:00 | 2025-03-20 15:48 | 0.01943 | 3.68e-05 | 1 | 528 | Planned | Planned interruption | Shutdown of Weld Cone windfarm for Taimate 33kV line rebuild http://nams.mll.linesmarl.co.nz/Schedule/Edit/4845 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1611 | 2025-03-20-0091 | East Coast - REC1693 | REC29-East Coast | 2025-03-20 07:01 | 2025-03-20 15:48 | 0.077574 | 0.0001472 | 4 | 2108 | Planned | Planned interruption | Planned shutdown of Lulworth windfarm for Taimate - Ward Beach Rd 33kV rebuild http://nams.mll.linesmarl.co.nz/Schedule/Edit/4845 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1612 | 2025-03-20-0092 | Wairau Valley - SUB3414GH | CB5399 Wairau Valley | 2025-03-20 08:04 | 2025-03-20 15:50 | 0.017149 | 3.68e-05 | 1 | 466 | Planned | Planned interruption | Replacement of pole PT3298 for the Wairau Valley Tee installation http://nams.mll.linesmarl.co.nz/Schedule/Edit/4838 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1613 | 2025-03-20-0093 | Okaramio - 0007705349ML26D | CB104 Okaramio | 2025-03-20 08:43 | 2025-03-20 10:01 | 0 | 0 | 1 | 79 | Unplanned | Adverse weather | Blown 30amp HRC. Suspect clashing EAM 1537969 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1614 | 2025-03-20-0094 | Colemans Rd - 0001120149ML879 | CB1512-Colemans Rd | 2025-03-20 09:11 | 2025-03-20 09:53 | 0 | 0 | 1 | 41 | Unplanned | Defective equipment | Blown fuse due to overloading - EAM 1538005 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1615 | 2025-03-21-0101 | Waikawa - REC17 | CB109- Waikawa | 2025-03-20 10:02 | 2025-03-20 10:02 | 0.0033488 | 0.0033488 | 91 | 91 | Unplanned | Unknown | Sucessful reclose of REC17 - Boons Valley | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1616 | 2025-03-20-0095 | Flaxbourne - 0005507077ML3E7 | REC1432-Flaxbourne | 2025-03-20 11:03 | 2025-03-20 14:01 | 0 | 0 | 1 | 178 | Unplanned | Defective equipment | 3 x blown fuses cause faulty water pump relivened to mains entry EAM 1538142 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1617 | 2025-03-21-0102 | Waikawa - REC5191 | CB109- Waikawa | 2025-03-20 22:02 | 2025-03-20 22:02 | 0.04611 | 0.04611 | 1253 | 1253 | Unplanned | Unknown | Sucessful reclose of 11kV REC5191 - Endeavour Park. Reclosed at the same time as REC17 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1618 | 2025-03-21-0098 | Vintage Lane - FUSE2903 | CB171-Vintage Lane | 2025-03-21 04:45 | 2025-03-21 07:30 | 0.024435 | 0.0001472 | 4 | 664 | Unplanned | Third party interference | Tractor V Pole - lines clashed and 11kV fuses blew. Crossarm replaced at KB9887 W/O1538464 NAMS F4909 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1619 | 2025-03-21-0097 | Hardings Rd - 0003350120ML6CB | CB167-Hardings Rd | 2025-03-21 07:21 | 2025-03-21 09:15 | 0 | 0 | 1 | 113 | Unplanned | Unknown | Replaced burnt out fuse holder in SFB EAM 1542572 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1620 | 2025-03-21-0099 | Hutcheson St - 0001102230MLAFB | CB49-Hutcheson St | 2025-03-21 08:41 | 2025-03-21 11:46 | 0 | 0 | 1 | 185 | Unplanned | Other Cause | Red phase found. Blown 32A HRC - cause unknown EAM 1538474 - Part power, lost red phase | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1621 | 2025-03-21-0100 | Flaxbourne - 0005507077ML3E7 | REC1432-Flaxbourne | 2025-03-21 10:00 | 2025-03-21 11:42 | 0 | 0 | 1 | 102 | Unplanned | Defective equipment | Power restored, 3x 30A fuses blown due to faulty main switch EAM 1538478 - Lost 2 phases | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1622 | 2025-03-21-0103 | French Pass - REC160 | CB45-French Pass | 2025-03-21 12:45 | 2025-03-21 15:40 | 0.10403 | 0.0011776 | 17 | 2827 | Unplanned | Defective equipment | Intermittent HV fault causing REC160 to trip on phase OC. 11kV Fuse2297 changed from binder to 6A 11kV Fuse2970 changed to 3A 11kV fuse 2971 difficult to access Whole line has been flown by chopper | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1623 | 2025-03-21-0104 | Redwood St Nth - 0001107517ML246 | CB1655-Redwood St Nth | 2025-03-21 14:55 | 2025-03-21 16:37 | 0 | 0 | 1 | 102 | Unplanned | Defective equipment | Power restored. Burnt out fuse carrier replaced EAM 1540667 - No power | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1624 | 2025-03-21-0105 | Sounds - SUB325995 | REC1170-Sounds | 2025-03-21 18:04 | 2025-03-22 10:32 | 0.036321 | 3.68e-05 | 1 | 987 | Unplanned | Unknown | SUB325995 15kVA 1PH 3A found blown fuse at Tx EAM1541163 NAMS F4912 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1625 | 2025-03-21-0106 | Nelson St - 0001116119ML49D | CB93-Nelson St | 2025-03-21 18:56 | 2025-03-21 19:44 | 0 | 0 | 1 | 49 | Unplanned | Defective equipment | One failed fuse replaced with a HRC and letter was issued EAM 1541164 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1626 | 2025-03-22-0107 | McLauchlan St - 0001129588ML372 | CB65 - McLauchlan St | 2025-03-22 12:12 | 2025-03-22 14:53 | 0 | 0 | 1 | 162 | Unplanned | Human error | Cable repair from previous day failed. Joint re-done and service restored W/O 1540718 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1627 | 2025-03-23-0109 | French Pass - REC160 | CB45-French Pass | 2025-03-23 03:53 | 2025-03-23 13:34 | 0.36347 | 0.0006256 | 17 | 9877 | Unplanned | Defective equipment | Sqaully Cove intermittent fault - line patrolled, nothing found. Ultimately a loose jumper was found EAM1537480 NAMS F4910 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1628 | 2025-03-23-0110 | Richmond Brook - 0005506181MLADB | CB1250-Richmond Brook | 2025-03-23 13:15 | 2025-03-23 15:51 | 0.0057408 | 3.68e-05 | 1 | 156 | Unplanned | Unknown | 2 blown fuses found at sub 353297 , LV patrolled and is ok, no obvious cause found Power confirmed restored W/O 1541168 NAMS F4913 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1629 | 2025-03-23-0111 | Howick Rd North - 0001175061MLA68 | CB84-Howick Rd North | 2025-03-23 13:56 | 2025-03-23 14:40 | 0 | 0 | 1 | 45 | Unplanned | Human error | Reconnection was missed following a safety disconnection. attended and relivened service. W/O 1541169 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1630 | 2025-03-23-0112 | Vintage Lane - 0003335222ML035 | CB171-Vintage Lane | 2025-03-23 16:42 | 2025-03-23 18:09 | 0.0032384 | 3.68e-05 | 1 | 88 | Unplanned | Unknown | Found 1 x blown HV fuse at SUB3680EK nothing obvious found as cause Power confirmed restored EAM1541173 NAMS F4914 2025-03-23-0112 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1631 | 2025-03-24-0113 | Grovetown - FUSE3763 | CB1465-Grovetown | 2025-03-24 06:33 | 2025-03-24 07:53 | 0.035328 | 0.0004416 | 12 | 960 | Unplanned | Wildlife | 2x blown fuses found at FUSE3763 and 1 blown fuse at FUSE2947. SUspect Swans. Line patrolled and no issues found. Replaced fuses, FUSE947 (20A) and FUSE3763 (30A). W/O 1541174 NAMS F4915 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1632 | 2025-03-24-0116 | Flaxbourne - 0009999001MLDC2 | REC1432-Flaxbourne | 2025-03-24 07:02 | 2025-03-24 15:28 | 0.018621 | 3.68e-05 | 1 | 506 | Planned | Planned interruption | Planned shutdown of Weld Cone for Taimate-Ward Beach Rd line rebuild. SAF4596 - WO 1422544 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1633 | 2025-03-24-0115 | East Coast - REC1693 | REC29-East Coast | 2025-03-24 07:19 | 2025-03-24 15:28 | 0.071981 | 0.0001472 | 4 | 1956 | Planned | Planned interruption | Planned shutdown of Lulworth for Taimate-Ward Beach Rd line rebuild. SAF4596 - WO 1422544 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1634 | 2025-03-24-0114 | Sounds - SUB3251ER | REC1170-Sounds | 2025-03-24 08:10 | 2025-03-24 12:38 | 0.0098992 | 3.68e-05 | 1 | 269 | Unplanned | Unknown | 1x TX fuse blown at SUB3251ER. No cause found. Replaced both fuses (6A) and confirmed power restored. EAM 1541177 NAMS F4918 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1635 | 2025-03-24-0117 | Godfrey Road - SUB343057 | CB5367 Godfrey Road | 2025-03-24 08:30 | 2025-03-24 14:09 | 0.012438 | 3.68e-05 | 1 | 338 | Planned | Planned interruption | Planned shutdown to replace pole ET4378 in Godfrey Rd http://nams.mll.linesmarl.co.nz/Schedule/Edit/4826 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1636 | 2025-03-24-0119 | Buller St - LVUG164402 | CB108-Buller St | 2025-03-24 10:37 | 2025-03-24 11:30 | 0 | 0 | 3 | 159 | Planned | Planned interruption | Outage of DP2 Westshore to decommision LV service from Andelec box http://nams.mll.linesmarl.co.nz/Schedule/Edit/4916 EAM1539424 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1637 | 2025-03-24-0118 | Kaituna - 0000050399ML750 | CB5448 Kaituna | 2025-03-24 10:39 | 2025-03-24 11:42 | 0 | 0 | 1 | 64 | Unplanned | Defective equipment | Blue Phase incoming issue at Mains entry EAM 1541193 24/03/2025 10:41:18 am 45 BLICKS ROAD, RENWICK 24/03/2025 10:42:28 am | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1638 | 2025-03-24-0120 | Symons St - RMUF1445 | CB50-Symons St | 2025-03-24 20:07 | 2025-03-24 20:31 | 0.0017664 | 7.36e-05 | 2 | 48 | Planned | Planned interruption | Planned shutdown of SUB3700EY for earth testing http://nams.mll.linesmarl.co.nz/Schedule/Edit/4827 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1639 | 2025-03-25-0122 | East Coast - REC1693 | REC29-East Coast | 2025-03-25 07:00 | 2025-03-25 15:32 | 0.075366 | 0.0001472 | 4 | 2048 | Planned | Planned interruption | SD10 for the Taimate-Ward Beach Rd 33kV rebuild. Shutdown of Lulworth to reduce reactive power. SAF4597 WO 1422544 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1640 | 2025-03-25-0123 | Flaxbourne - 0009999001MLDC2 | REC1432-Flaxbourne | 2025-03-25 07:00 | 2025-03-25 15:58 | 0.019798 | 3.68e-05 | 1 | 538 | Planned | Planned interruption | SD10 for the Taimate-Ward Beach Rd 33kV rebuild. Shutdown of Weld Cone to reduce reactive power. SAF4597 WO 1422544 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1641 | 2025-03-25-0124 | French Pass - LVOH1159 | CB45-French Pass | 2025-03-25 08:53 | 2025-03-25 15:22 | 0 | 0 | 5 | 1945 | Planned | Planned interruption | Replacement of pole AE2203 at French Pass SAF4543 WO 1509022 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1642 | 2025-03-25-0125 | Okaramio - 0007705369MLF38 | CB104 Okaramio | 2025-03-25 08:54 | 2025-03-25 10:54 | 0 | 0 | 1 | 120 | Unplanned | Other Cause | 1541530 - Part Power and HW not working, 1PH lost on SB - Blown pole fuse, supply is actually 3PH 30A | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1643 | 2025-03-25-0127 | Taylor Pass - 0001176061ML888 | CB1089-Taylor Pass | 2025-03-25 09:22 | 2025-03-25 16:00 | 0 | 0 | 1 | 399 | Planned | Planned interruption | 161 Howick road DF3179 - Replacement of red tagged pole http://nams.mll.linesmarl.co.nz/Schedule/Edit/4908 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1644 | 2025-03-25-0128 | Taylor Pass - 0001176065ML982 | CB1089-Taylor Pass | 2025-03-25 09:22 | 2025-03-25 16:00 | 0 | 0 | 1 | 399 | Planned | Planned interruption | 161 Howick road DF3179 - Replacement of red tagged pole http://nams.mll.linesmarl.co.nz/Schedule/Edit/4908 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1645 | 2025-03-25-0130 | French Pass - SUB336304 | CB45-French Pass | 2025-03-25 09:35 | 2025-03-25 09:45 | 0.000368 | 3.68e-05 | 1 | 10 | Unplanned | Defective equipment | replacement of HV fuse for fault finding on Sqaully Cove SWER http://nams.mll.linesmarl.co.nz/Schedule/Edit/4618 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1646 | 2025-03-25-0129 | French Pass - SUB336307 | CB45-French Pass | 2025-03-25 09:39 | 2025-03-25 10:27 | 0.0017664 | 3.68e-05 | 1 | 48 | Unplanned | Defective equipment | replacement of HV fuse for fault finding on Sqaully Cove SWER - also replaced faulty LA http://nams.mll.linesmarl.co.nz/Schedule/Edit/4917 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1647 | 2025-03-25-0131 | French Pass - SUB336306 | CB45-French Pass | 2025-03-25 09:53 | 2025-03-25 10:03 | 0.001104 | 0.0001104 | 3 | 30 | Unplanned | Defective equipment | replacement of HV fuse for fault finding on Sqaully Cove SWER http://nams.mll.linesmarl.co.nz/Schedule/Edit/4917 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1648 | 2025-03-25-0132 | Waikawa - SUB330434 | CB109- Waikawa | 2025-03-25 10:29 | 2025-03-25 15:15 | 0 | 0 | 1 | 286 | Planned | Planned interruption | Installation of new ABC service due to exisiting cable being in a slip - 2395 Port Underwood Rd http://nams.mll.linesmarl.co.nz/Schedule/Edit/4618 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1649 | 2025-03-25-0133 | French Pass - REC160 | CB45-French Pass | 2025-03-25 10:46 | 2025-03-25 12:50 | 0.053765 | 0.0006256 | 17 | 1461 | Unplanned | Defective equipment | Replace Faulty 11kV jumper at pole AK1218 which was clashing with the fuse base causing intermittent faults. http://nams.mll.linesmarl.co.nz/Schedule/Edit/4917 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1650 | 2025-03-25-0134 | French Pass - SUB336305 | CB45-French Pass | 2025-03-25 10:46 | 2025-03-25 10:51 | 0.000552 | 0.0001104 | 3 | 15 | Unplanned | Defective equipment | replacement of HV fuse for fault finding on Sqaully Cove SWER http://nams.mll.linesmarl.co.nz/Schedule/Edit/4917 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1651 | 2025-03-25-0137 | French Pass - SUB336317 | CB45-French Pass | 2025-03-25 13:20 | 2025-03-25 13:28 | 0.0005888 | 7.36e-05 | 2 | 16 | Unplanned | Defective equipment | replacement of HV fuse for fault finding on Sqaully Cove SWER http://nams.mll.linesmarl.co.nz/Schedule/Edit/4917 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1652 | 2025-03-25-0136 | French Pass - SUB336313 | CB45-French Pass | 2025-03-25 13:27 | 2025-03-25 13:31 | 0.0001472 | 3.68e-05 | 1 | 4 | Unplanned | Defective equipment | replacement of HV fuse for fault finding on Sqaully Cove SWER http://nams.mll.linesmarl.co.nz/Schedule/Edit/4917 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1653 | 2025-03-25-0138 | Okaramio - 0007705369MLF38 | CB104 Okaramio | 2025-03-25 15:34 | 2025-03-25 17:30 | 0 | 0 | 1 | 117 | Unplanned | Defective equipment | Faulty elemnent from the hotwatewr cylinder, replaced and restored 1730. EAM 1541940 - Part power again, 2nd time today | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1654 | 2025-03-26-0139 | East Coast - REC1693 | REC29-East Coast | 2025-03-26 07:10 | 2025-03-26 15:42 | 0.075366 | 0.0001472 | 4 | 2048 | Planned | Planned interruption | shutdown of Lulworth windfarm for Taimate - Ward Beach Rd SD11 SAF4598 - WO 1422544 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1655 | 2025-03-26-0140 | Flaxbourne - 0009999001MLDC2 | REC1432-Flaxbourne | 2025-03-26 07:10 | 2025-03-26 15:42 | 0.018842 | 3.68e-05 | 1 | 512 | Planned | Planned interruption | shutdown of Weld Cone windfarm for Taimate - Ward Beach Rd SD11 SAF4598 - WO 1422544 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1656 | 2025-03-26-0141 | Flaxbourne - FUSE2417 | REC1432-Flaxbourne | 2025-03-26 08:13 | 2025-03-26 14:56 | 0.044381 | 0.0001104 | 3 | 1206 | Planned | Planned interruption | Shutdown of 11kV line beyond FUSE2417 for pole replacements on the Taiemate - Ward Beach Rd 33kV rebuild SAF4598 WO 1522544 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1657 | 2025-03-26-0142 | Sounds - FUSE2344 | REC1170-Sounds | 2025-03-26 08:30 | 2025-03-26 13:42 | 0.3319 | 0.0010672 | 29 | 9019 | Planned | Planned interruption | Planned shutdown to install new Sub3251ES. EAM 1508752 SAF 4492 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1658 | 2025-03-26-0143 | Waihopai Valley - SUB3410LD | CB5493 Waihopai Valley | 2025-03-26 08:39 | 2025-03-26 11:32 | 0.025466 | 0.0001472 | 4 | 692 | Planned | Planned interruption | Replace arms and re-sag at pole UG0325 http://nams.mll.linesmarl.co.nz/Schedule/Edit/4833 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1659 | 2025-03-26-0144 | East Coast - FUSE3733 | REC29-East Coast | 2025-03-26 09:36 | 2025-03-26 09:43 | 0.0010304 | 0.0001472 | 4 | 28 | Unplanned | Unknown | Replace 3A fuse with solid link to restore network to normal state. Part of fault investigation. EAM1504281 Sched 4920 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1660 | 2025-03-26-0145 | Omaka - FUSE2630 | CB1088 - Omaka | 2025-03-26 13:14 | 2025-03-26 14:51 | 0.014426 | 0.0001472 | 4 | 392 | Planned | Planned interruption | Replacement of 11kV arms in Bishell Lane http://nams.mll.linesmarl.co.nz/Schedule/Edit/4852 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1661 | 2025-03-27-0146 | East Coast - REC1693 | REC29-East Coast | 2025-03-27 06:56 | 2025-03-27 16:00 | 0.080077 | 0.0001472 | 4 | 2176 | Planned | Planned interruption | Shutdown of Lulworth windfarm for Taimate-Ward Beach Rd 33kV rebuild SD12 SAF4599 WO 1422544 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1662 | 2025-03-27-0147 | Flaxbourne - 0009999001MLDC2 | REC1432-Flaxbourne | 2025-03-27 06:56 | 2025-03-27 16:00 | 0.020019 | 3.68e-05 | 1 | 544 | Planned | Planned interruption | Shutdown of Weld Cone windfarm for Taimate-Ward Beach Rd 33kV rebuild SD12 SAF4599 WO 1422544 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1663 | 2025-03-28-0148 | Sounds - ABS15051-B | REC1170-Sounds | 2025-03-28 09:18 | 2025-03-28 11:41 | 0.026312 | 0.000184 | 5 | 715 | Planned | Planned interruption | Reconfiguration of 11kV at 3046 Kenepuru Rd in prperation for upcoming roading works SAF4786 - WO1536086 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1664 | 2025-03-28-0149 | Seymour St - 0001165241ML5DB | CB51-Seymour St | 2025-03-28 10:17 | 2025-03-28 13:42 | 0 | 0 | 1 | 205 | Unplanned | Defective equipment | No fault customer RCD was in the off position EAM 1542458 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1665 | 2025-03-28-0150 | Ngakuta - 0007715557ML5BC | REC1562-Ngakuta | 2025-03-28 12:48 | 2025-03-28 14:05 | 0 | 0 | 1 | 77 | Unplanned | Defective equipment | Blown Rewirable fuse - due to deterioration EAM 1542490 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1666 | 2025-03-30-0151 | Murphys Rd - 0001120451ML5C5 | CB68-Murphys Rd | 2025-03-30 07:46 | 2025-03-30 12:50 | 0 | 0 | 1 | 304 | Unplanned | Other Cause | Cut service cable repaired - EAM 1542555 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1667 | 2025-03-30-0154 | Richmond Brook - REC36 | CB1250-Richmond Brook | 2025-03-30 10:53 | 2025-03-30 16:18 | 0.41989 | 0.001288 | 35 | 11410 | Unplanned | Unknown | REC36 found open. Patrolled line with helicopter due to fire risk, but nothing found. Trial livened OK. EAM 1542556 http://nams.mll.co.nz/Schedule/Edi | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1668 | 2025-03-30-0155 | Grassmere - FUSE3291 | CB1253-Grassmere | 2025-03-30 20:00 | 2025-03-30 23:28 | 0.052182 | 0.0002944 | 8 | 1418 | Unplanned | Unknown | 2 x blown fuses found at FUSE3291. Line patrolled, nothing found. Replaced fuses (20A) EAM 1542557 http://nams.mll.co.nz/Schedule/Edit/4932 - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1669 | 2025-03-31-0158 | Flaxbourne - 0009999001MLDC2 | REC1432-Flaxbourne | 2025-03-31 07:04 | 2025-03-31 15:52 | 0.01943 | 3.68e-05 | 1 | 528 | Planned | Planned interruption | Disconnection of Weld Cone windfarm for Taimate-Ward Beach Rd 33kV rebuild SD13 SAF4600 WO 1422544 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1670 | 2025-03-31-0157 | East Coast - REC1693 | REC29-East Coast | 2025-03-31 07:06 | 2025-03-31 15:53 | 0.077574 | 0.0001472 | 4 | 2108 | Planned | Planned interruption | Disconnection of Lulworth windfarm for Taimate-Ward Beach Rd 33kV rebuild SD13 SAF4600 WO 1422544 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1671 | 2025-03-31-0156 | Sounds - 0008812609MLBC0 | REC1170-Sounds | 2025-03-31 07:17 | 2025-03-31 13:05 | 0 | 0 | 1 | 349 | Unplanned | Defective equipment | burnt cutout - replaced cutout power confirmed restored EAM 1542558 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1672 | 2025-03-31-0159 | Wairau Valley - SUB3414GH | CB5399 Wairau Valley | 2025-03-31 08:52 | 2025-03-31 16:13 | 0.016266 | 3.68e-05 | 1 | 442 | Planned | Planned interruption | Planned shutdown to install 33kV cable on pole 4. EAM 1469375 SAF 4650 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1673 | 2025-03-31-0160 | French Pass - REC1013 | CB45-French Pass | 2025-03-31 13:16 | 2025-03-31 13:17 | 0 | 0 | 24 | 0 | Unplanned | Unknown | REC1013 - D'Urville Island East reclosed on phase OC. Cyclo 42 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Marlborough Lines | 2025 |  | 1674 | 2025-03-31-0161 | French Pass - FUSE2681 | CB45-French Pass | 2025-03-31 14:29 | 2025-04-01 13:56 | 0.31044 | 0.0002208 | 6 | 8436 | Unplanned | Defective equipment | Swinging LA Found at POLE MA2321. LA bypassed line relivened | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Nelson Electricity | 2025 |  | 9 | 1 | Murphy Street | Emano Street | 2024-05-01 09:10 | 2024-05-01 17:33 | 6.1846 | 0.012296 | 115 | 57845 | Planned | Planned interruption | HV Lines Outage for Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Nelson Electricity | 2025 |  | 10 | 2 | Vanguard Street | Victory Square | 2024-07-27 14:02 | 2024-07-27 15:24 | 0.14904 | 0.0018176 | 17 | 1394 | Planned | Planned interruption | Substation (ABC) outage to change tap & install LV Isolator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Nelson Electricity | 2025 |  | 11 | 3 | Ackersten Street | Vickerman Street | 2024-09-18 11:00 | 2024-09-18 11:42 | 0.026943 | 0.00064151 | 6 | 252 | Planned | Planned interruption | Ackersten Street North Substation outage for Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Nelson Electricity | 2025 |  | 12 | 4 | Konini Street | Snows Hill | 2024-10-04 09:04 | 2024-10-04 14:57 | 2.3023 | 0.006522 | 61 | 21533 | Planned | Planned interruption | Konini Street Substation outage for Lines Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Nelson Electricity | 2025 |  | 13 | 5 | Sealord Site | Sealord 3 | 2024-10-12 08:02 | 2024-10-12 13:35 | 0.10681 | 0.00032075 | 3 | 999 | Planned | Planned interruption | Sealord 3 T1 & T1 Outage for maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Nelson Electricity | 2025 |  | 14 | 6 | Murphy Street | Emano Street | 2024-11-26 08:41 | 2024-11-26 15:12 | 2.9263 | 0.0074842 | 70 | 27370 | Planned | Planned interruption | Outage for tree trimming | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Nelson Electricity | 2025 |  | 15 | 7 | Nile Street | Alma Street | 2024-12-18 11:00 | 2024-12-18 11:49 | 0.005239 | 0.00010692 | 1 | 49 | Planned | Planned interruption | Outage to modify LV board at Nile Street 79 Substation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Nelson Electricity | 2025 |  | 16 | 8 | Harbour Board Substation | Port 1 | 2025-02-26 06:00 | 2025-02-26 06:20 | 0.0042767 | 0.00021384 | 2 | 40 | Planned | Planned interruption | Outage to connect 2 ICPs to Generators for installation works | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Nelson Electricity | 2025 |  | 17 | 9 | Harbour Board Substation | Port 1 | 2025-02-28 14:55 | 2025-02-28 17:00 | 0.0010692 | 0.00021384 | 2 | 10 | Planned | Planned interruption | Outage to reconnect 2 ICPS to main supply after installation works | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Nelson Electricity | 2025 |  | 18 | 10 | Konini Street Substation | Snows Hill | 2025-03-12 09:00 | 2025-03-12 15:38 | 2.5762 | 0.006522 | 61 | 24095 | Planned | Planned interruption | Overhead pole alterations for NCC project in Konini St | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 9 | 8955_1 | MT Burnett | Pakawau | 2024-04-03 09:42 | 2024-04-03 14:58 | 0.036176 | 0.00011448 | 5 | 1580 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 10 | 8956_1 | Cadillac Way | Pascoe St | 2024-04-03 19:37 | 2024-04-03 23:47 | 0.011448 | 4.5793e-05 | 2 | 500 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 11 | 8957_1 | Nayland Road | Nayland | 2024-04-07 12:10 | 2024-04-07 13:15 | 1.2308 | 0.018935 | 827 | 53755 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 12 | 8957_1 | Nayland Road | Nayland | 2024-04-07 13:15 | 2024-04-07 13:21 | 0.098638 | 0 | 0 | 4308 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 13 | 8957_2 | Nayland Road | Nayland | 2024-04-07 13:20 | 2024-04-07 13:21 | 0.0024957 | 0.0024957 | 109 | 109 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 14 | 8961_1 | Motueka Valley Highway | Kohatu | 2024-04-08 15:15 | 2024-04-08 16:15 | 0.01099 | 0.00018317 | 8 | 480 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 15 | 8962_1 | Hillwood Drive | Hira | 2024-04-10 08:53 | 2024-04-10 08:55 | 0.00050372 | 0.00025186 | 11 | 22 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 16 | 8963_1 | York Street Motueka | Queen Victoria | 2024-04-10 09:40 | 2024-04-10 13:58 | 0.30718 | 0.0011906 | 52 | 13416 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 17 | 8963_1 | York Street Motueka | Queen Victoria | 2024-04-10 09:56 | 2024-04-10 13:55 | 0.50345 | 0.0021065 | 92 | 21988 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MURCHISON | 18 | 8964_1 | Tutaki Road North | Paton Road | 2024-04-11 09:49 | 2024-04-11 10:51 | 0.026972 | 0.00043503 | 19 | 1178 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 19 | 8965_1 | Whites road | Longford | 2024-04-11 20:21 | 2024-04-11 21:37 | 0.24362 | 0.0032055 | 140 | 10640 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 20 | 8966_1 | Woodstock , Dovedale | Dovedale A | 2024-04-11 20:21 | 2024-04-11 22:30 | 0.55233 | 0.0042816 | 187 | 24123 | Unplanned | Adverse weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 21 | 8966_1 | Woodstock , Dovedale | Dovedale A | 2024-04-11 22:30 | 2024-04-11 23:13 | 0.078764 | 0.0018317 | 80 | 3440 | Unplanned | Adverse weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 22 | 8966_2 | Woodstock , Dovedale | Dovedale A | 2024-04-11 22:30 | 2024-04-12 00:03 | 0.10647 | 0.0011448 | 50 | 4650 | Unplanned | Adverse weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 23 | 8966_2 | Woodstock , Dovedale | Dovedale A | 2024-04-11 22:30 | 2024-04-12 00:35 | 0.071551 | 0.00057241 | 25 | 3125 | Unplanned | Adverse weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 24 | 8967_1 | Uruwhenua Rd | Uruwhenua | 2024-04-12 17:24 | 2024-04-12 18:37 | 0.0066857 | 9.1586e-05 | 4 | 292 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 25 | 8968_1 | Pupu, Kotinga | Commercial St | 2024-04-13 09:30 | 2024-04-13 10:40 | 0.44236 | 0.0063194 | 276 | 19320 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 26 | 8968_1 | Pupu, Kotinga | Commercial St | 2024-04-13 10:40 | 2024-04-13 11:59 | 0.056073 | 0 | 0 | 2449 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 27 | 8968_1 | Pupu, Kotinga | Commercial St | 2024-04-13 11:59 | 2024-04-13 13:15 | 0.069605 | 0 | 0 | 3040 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 28 | 8968_1 | Pupu, Kotinga | Commercial St | 2024-04-13 11:59 | 2024-04-13 13:33 | 0.0043045 | 0 | 0 | 188 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 29 | 8971_1 | S207 Proper Crisps | Aldinga | 2024-04-16 05:03 | 2024-04-16 05:17 | 0.00032055 | 2.2896e-05 | 1 | 14 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 30 | 8972_1 | Mac Brewery | Main Road | 2024-04-16 06:00 | 2024-04-16 06:30 | 0.0013738 | 4.5793e-05 | 2 | 60 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 31 | 8973_1 | Main Road Stoke, Echodale Place, Sargeson Street | Aldinga | 2024-04-16 09:03 | 2024-04-16 17:11 | 0.011173 | 2.2896e-05 | 1 | 488 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 32 | 8974_1 | Macs Brewery | Main Road | 2024-04-16 17:27 | 2024-04-16 17:54 | 0.0012364 | 4.5793e-05 | 2 | 54 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 33 | 8975_1 | Proper Crisps | Aldinga | 2024-04-16 17:33 | 2024-04-16 17:46 | 0.00029765 | 2.2896e-05 | 1 | 13 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 34 | 8976_1 | Mead Rd, Lee Valley | Ellis St | 2024-04-19 10:34 | 2024-04-19 12:29 | 0.013165 | 0.00011448 | 5 | 575 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 35 | 8977_1 | Collingwood Feeder | Longford | 2024-04-21 01:33 | 2024-04-21 03:15 | 2.3705 | 0.02324 | 1015 | 103530 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MURCHISON | 36 | 8979_1 | Mangles Valley | Collingwood 33kV | 2024-04-21 12:25 | 2024-04-21 16:53 | 0.39886 | 0.0014883 | 65 | 17420 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 37 | 8980_1 | Uruwhenua | Uruwhenua | 2024-04-23 09:00 | 2024-04-23 15:14 | 0.0085633 | 2.2896e-05 | 1 | 374 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 38 | 8980_1 | Uruwhenua | Uruwhenua | 2024-04-23 09:01 | 2024-04-23 15:12 | 0.45871 | 0.0012364 | 54 | 20034 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 39 | 8986_1 | Mc Callum Road | Commercial St | 2024-04-24 09:44 | 2024-04-24 18:13 | 0.058271 | 0.00011448 | 5 | 2545 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 40 | 8987_1 | Clover Road West | Waimea East | 2024-04-29 07:01 | 2024-04-29 07:36 | 0.01763 | 0.00050372 | 22 | 770 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 41 | 8988_1 | Wakapuaka Highway , The Glen | Glenduan | 2024-04-11 09:46 | 2024-04-11 17:11 | 0.040756 | 9.1586e-05 | 4 | 1780 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 42 | 8988_1 | Wakapuaka Highway , The Glen | Glenduan | 2024-04-29 09:47 | 2024-04-29 17:08 | 1.2218 | 0.0027705 | 121 | 53361 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 43 | 8988_1 | Wakapuaka Highway , The Glen | Glenduan | 2024-04-29 09:55 | 2024-04-29 17:14 | 0.010052 | 2.2896e-05 | 1 | 439 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 44 | 8988_1 | Wakapuaka Highway , The Glen | Glenduan | 2024-04-29 10:11 | 2024-04-29 17:02 | 0.23526 | 0.00057241 | 25 | 10275 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 45 | 8991_1 | Mc Callum Road | Commercial St | 2024-04-30 09:05 | 2024-04-30 15:21 | 0.29271 | 0.00077848 | 34 | 12784 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 46 | 8992_1 | Uruwhenua | Uruwhenua | 2024-04-30 09:01 | 2024-04-30 15:27 | 0.47725 | 0.0012364 | 54 | 20844 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 47 | 8993_1 | Songer St & The Ridgeway | Isel | 2024-04-30 16:29 | 2024-04-30 17:28 | 0.60655 | 0.01028 | 449 | 26491 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 48 | 8993_1 | Songer St & The Ridgeway | Isel | 2024-04-30 16:29 | 2024-04-30 17:42 | 0.32593 | 0.0044648 | 195 | 14235 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 49 | 8993_1 | Songer St & The Ridgeway | Isel | 2024-04-30 16:29 | 2024-04-30 17:58 | 0.94145 | 0.010578 | 462 | 41118 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 50 | 8993_1 | Songer St & The Ridgeway | Isel | 2024-04-30 16:29 | 2024-04-30 19:28 | 0.23361 | 0.0013051 | 57 | 10203 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 51 | 8994_1 | Songer St | Isel | 2024-04-30 18:45 | 2024-04-30 19:28 | 0.11716 | 0.0027247 | 119 | 5117 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 52 | 8995_1 | Aniseed Valley | Waimea East | 2024-05-01 09:06 | 2024-05-01 10:40 | 0.14851 | 0.0015799 | 69 | 6486 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 53 | 8996_1 | Parapara | Bainham | 2024-05-01 09:39 | 2024-05-01 16:43 | 2.1552 | 0.005083 | 222 | 94128 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 54 | 8997_1 | Songer St / The Ridgeway | Isel | 2024-05-01 22:07 | 2024-05-01 22:48 | 0.16522 | 0.0040298 | 176 | 7216 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 55 | 9000_1 | Uruwhenua | Uruwhenua | 2024-05-07 09:02 | 2024-05-07 14:37 | 0.4142 | 0.0012364 | 54 | 18090 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 56 | 9000_2 | Uruwhenua | Uruwhenua | 2024-05-07 14:37 | 2024-05-07 14:39 | 4.5793e-05 | 2.2896e-05 | 1 | 2 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 57 | 9002_1 | East Takaka | East Takaka | 2024-05-08 09:33 | 2024-05-08 09:37 | 9.1586e-05 | 2.2896e-05 | 1 | 4 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 58 | 9002_1 | East Takaka | East Takaka | 2024-05-08 09:36 | 2024-05-08 16:11 | 0.70544 | 0.0017859 | 78 | 30810 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 59 | 9002_1 | East Takaka | East Takaka | 2024-05-08 16:11 | 2024-05-08 16:18 | 0.00016027 | 2.2896e-05 | 1 | 7 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 60 | 9003_1 | Rototai road | Commercial St | 2024-05-08 19:16 | 2024-05-08 19:36 | 0.01099 | 0.00054951 | 24 | 480 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 61 | 9004_1 | Cadillac Way | Pascoe St | 2024-05-08 21:31 | 2024-05-09 01:38 | 0.090487 | 0.00036634 | 16 | 3952 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 62 | 9005_1 | Uruwhenua | Uruwhenua | 2024-05-09 09:02 | 2024-05-09 14:35 | 0.0076245 | 2.2896e-05 | 1 | 333 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 63 | 9005_1 | Uruwhenua | Uruwhenua | 2024-05-09 09:03 | 2024-05-09 14:34 | 0.40167 | 0.0012135 | 53 | 17543 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MURCHISON | 64 | 9006_1 | Springs Junction | Maruia | 2024-05-10 10:06 | 2024-05-10 12:29 | 0.029468 | 0.00020607 | 9 | 1287 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 65 | 9007_1 | Hart Road | Paton Road | 2024-05-13 09:44 | 2024-05-13 14:57 | 0.028666 | 9.1586e-05 | 4 | 1252 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 66 | 9007_1 | Hart Road | Paton Road | 2024-05-13 10:20 | 2024-05-13 14:53 | 0.056256 | 0.00020607 | 9 | 2457 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 67 | 9008_1 | Washbourne drive | Waverley St | 2024-05-14 09:01 | 2024-05-14 14:50 | 1.758 | 0.0050372 | 220 | 76780 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 68 | 9009_1 | Dehra Doon | Brooklyn | 2024-05-14 09:35 | 2024-05-14 15:09 | 0.015295 | 4.5793e-05 | 2 | 668 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 69 | 9009_1 | Dehra Doon | Brooklyn | 2024-05-14 09:53 | 2024-05-14 15:03 | 0.19164 | 0.0006182 | 27 | 8370 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 70 | 9015_1 | Rototai Road, Tangmere Road, Nees Road, Arapeta Place, Toiora Close, Takaka | Commercial St | 2024-05-16 09:04 | 2024-05-16 15:58 | 0.34125 | 0.00082427 | 36 | 14904 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 71 | 9015_1 | Rototai Road, Tangmere Road, Nees Road, Arapeta Place, Toiora Close, Takaka | Commercial St | 2024-05-16 09:10 | 2024-05-16 15:54 | 0.222 | 0.00054951 | 24 | 9696 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 72 | 9015_1 | Rototai Road, Tangmere Road, Nees Road, Arapeta Place, Toiora Close, Takaka | Commercial St | 2024-05-16 09:21 | 2024-05-16 15:51 | 0.32147 | 0.00082427 | 36 | 14040 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 73 | 9016_1 | Westdale Road, Stringers Road | Appleby | 2024-05-17 07:55 | 2024-05-17 08:50 | 0.041557 | 0.00075558 | 33 | 1815 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 74 | 9016_1 | Westdale Road, Stringers Road | Appleby | 2024-05-17 07:55 | 2024-05-17 08:52 | 0.090052 | 0.0015799 | 69 | 3933 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 75 | 9017_1 | 270 Collingwood Bainham Main Road | Pakawau | 2024-05-17 10:32 | 2024-05-17 10:48 | 0.00036634 | 2.2896e-05 | 1 | 16 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 76 | 9018_1 | Dehra Doon Road, Riwaka - POSTPONED TO ALTERNATE DATE. | Brooklyn | 2024-05-17 10:04 | 2024-05-17 15:25 | 0.014699 | 4.5793e-05 | 2 | 642 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 77 | 9020_1 | Abel Tasman Drive | Pohara | 2024-05-18 18:00 | 2024-05-18 18:30 | 0.0013738 | 4.5793e-05 | 2 | 60 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 78 | 9022_1 | Chisnall Street, Andrew Street, Black Street, Nayland Road Stoke | Nayland | 2024-05-21 09:40 | 2024-05-21 16:28 | 0.6259 | 0.0015341 | 67 | 27336 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 79 | 9023_1 | Totaranui Road, Takaka | Pohara | 2024-05-21 09:31 | 2024-05-21 15:40 | 0.042244 | 0.00011448 | 5 | 1845 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 80 | 9024_1 | Lyndhurst Drive, Thorp Street, Lodder Lane, High Street North Motueka | Kaiteriteri | 2024-05-22 09:31 | 2024-05-22 15:49 | 0.18175 | 0.00048082 | 21 | 7938 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 81 | 9025_1 | Commercial Street, Junction Street, Takaka | Commercial St | 2024-05-22 19:01 | 2024-05-22 22:15 | 0.191 | 0.00098454 | 43 | 8342 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 82 | 9026_1 | Chisnall Street, Andrew Street, Black Street, Nayland Road Stoke | Nayland | 2024-05-23 09:30 | 2024-05-23 15:01 | 0.50777 | 0.0015341 | 67 | 22177 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 83 | 9027_1 | Quayle Street, High Street, High Street South, Wharf Road, Motueka | Wildman Road | 2024-05-26 09:31 | 2024-05-26 14:08 | 0.24735 | 0.00089296 | 39 | 10803 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 84 | 9028_1 | Golden Downs, Kohatu, Tapawera & Stanley Brook areas | Kohatu | 2024-05-27 01:03 | 2024-05-27 02:45 | 0.058386 | 0.00057241 | 25 | 2550 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 85 | 9028_1 | Golden Downs, Kohatu, Tapawera & Stanley Brook areas | Kohatu | 2024-05-27 01:03 | 2024-05-27 02:46 | 0.91739 | 0.0089067 | 389 | 40067 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 86 | 9029_1 | Matenga Road | Pohara | 2024-05-27 09:18 | 2024-05-27 09:42 | 0.0049456 | 0.00020607 | 9 | 216 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 87 | 9030_1 | Marsden Valley Road, Aniseed Valley Road | Isel | 2024-05-28 09:31 | 2024-05-28 15:53 | 0.0087464 | 2.2896e-05 | 1 | 382 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 88 | 9030_1 | Marsden Valley Road, Aniseed Valley Road | Isel | 2024-05-28 09:47 | 2024-05-28 15:50 | 0.066491 | 0.00018317 | 8 | 2904 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 89 | 9031_1 | Cable Bay Road, Maori pa Road, | Hira | 2024-05-29 04:20 | 2024-05-29 06:22 | 0.40783 | 0.0033429 | 146 | 17812 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 90 | 9032_1 | Talisman Heights, Fairburn Place, Talisman Heights, Portland Place, Kaiteriteri | Kaiteriteri | 2024-05-29 10:06 | 2024-05-29 13:56 | 0.20538 | 0.00089296 | 39 | 8970 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 91 | 9033_1 | Rototai Road, Tangmere Road, Nees Road, Arapeta Place, Toiora Close, Takaka | Commercial St | 2024-05-30 09:03 | 2024-05-30 14:48 | 0.18958 | 0.00054951 | 24 | 8280 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 92 | 9033_1 | Rototai Road, Tangmere Road, Nees Road, Arapeta Place, Toiora Close, Takaka | Commercial St | 2024-05-30 09:05 | 2024-05-30 14:51 | 0.2852 | 0.00082427 | 36 | 12456 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 93 | 9033_1 | Rototai Road, Tangmere Road, Nees Road, Arapeta Place, Toiora Close, Takaka | Commercial St | 2024-05-30 09:32 | 2024-05-30 14:45 | 0.258 | 0.00082427 | 36 | 11268 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 94 | 9034_1 | Songer Street, The Ridgeway, Marsden Valley | Isel | 2024-05-31 03:05 | 2024-05-31 04:10 | 1.2695 | 0.019531 | 853 | 55445 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 95 | 9034_1 | Songer Street, The Ridgeway, Marsden Valley | Isel | 2024-05-31 03:05 | 2024-05-31 09:11 | 0.1676 | 0.00045793 | 20 | 7320 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 96 | 9034_1 | Songer Street, The Ridgeway, Marsden Valley | Isel | 2024-05-31 03:05 | 2024-05-31 09:13 | 2.2076 | 0.0059989 | 262 | 96416 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 97 | 9035_1 | Ridgeview Road, Shirtcliff Lane, Kohuhu Lane, Ribbonwood Lane, Karamu Lane, Toetoe Lane | Appleby | 2024-05-31 09:00 | 2024-05-31 09:30 | 0.059073 | 0.0019691 | 86 | 2580 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 98 | 9036_1 | Memorial Drive, Old Wharf Road, Puketutu Grove, Motueka | Wildman Road | 2024-05-31 10:38 | 2024-05-31 10:53 | 0.020263 | 0.0013509 | 59 | 885 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 99 | 9037_1 | Chamberlain St, Whakarewa St, Grey St, High St, Tudor St and other side streets in Motueka. | Whakarewa | 2024-06-02 08:06 | 2024-06-02 09:10 | 0.021981 | 0.00034345 | 15 | 960 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 100 | 9037_1 | Chamberlain St, Whakarewa St, Grey St, High St, Tudor St and other side streets in Motueka. | Whakarewa | 2024-06-02 08:06 | 2024-06-02 11:03 | 0.19048 | 0.0010761 | 47 | 8319 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 101 | 9037_1 | Chamberlain St, Whakarewa St, Grey St, High St, Tudor St and other side streets in Motueka. | Whakarewa | 2024-06-02 08:37 | 2024-06-02 09:18 | 0.3004 | 0.0073268 | 320 | 13120 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 102 | 9037_1 | Chamberlain St, Whakarewa St, Grey St, High St, Tudor St and other side streets in Motueka. | Whakarewa | 2024-06-02 08:37 | 2024-06-02 09:26 | 0.87622 | 0.017882 | 781 | 38269 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 103 | 9038_1 | Best Island | Appleby | 2024-06-03 15:30 | 2024-06-03 16:25 | 0.013852 | 0.00025186 | 11 | 605 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 104 | 9039_1 | Kohatu-Kawatiri Highway | Korere | 2024-06-04 09:32 | 2024-06-04 13:23 | 0.20098 | 0.00087006 | 38 | 8778 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 105 | 9040_1 | Wakapuaka Road | Glenduan | 2024-06-04 09:03 | 2024-06-04 14:40 | 0.0077161 | 2.2896e-05 | 1 | 337 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 106 | 9041_1 | River Terrace Road, Mount Heslington Road, Lee Valley Road, Garden Valley Road | Ellis St | 2024-06-05 09:30 | 2024-06-05 15:58 | 1.6702 | 0.0043045 | 188 | 72944 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 107 | 9042_1 | Cotterell Road, Ken Beck Drive, Best Road, Appleby Highway | Appleby | 2024-06-06 09:31 | 2024-06-06 15:30 | 0.27947 | 0.00077848 | 34 | 12206 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 108 | 9043_1 | Rototai Rd | Commercial St | 2024-06-08 08:15 | 2024-06-08 09:21 | 0.012089 | 0.00018317 | 8 | 528 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 109 | 9045_1 | Ranzau Road West, Hope | Waimea West | 2024-06-08 08:34 | 2024-06-08 11:09 | 0.0035489 | 2.2896e-05 | 1 | 155 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 110 | 9046_1 | Marahau Valley road. Fault repairs after fire | Kaiterteri | 2024-06-08 12:27 | 2024-06-08 13:49 | 0.099508 | 0.0012135 | 53 | 4346 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 111 | 9047_1 | ruby bay, marriages road, Awa Awa road areas. | Mapua | 2024-06-09 15:41 | 2024-06-09 16:25 | 0.14709 | 0.0033429 | 146 | 6424 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 112 | 9047_1 | ruby bay, marriages road, Awa Awa road areas. | Mapua | 2024-06-09 15:41 | 2024-06-09 16:27 | 0.093738 | 0.0020378 | 89 | 4094 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 113 | 9047_1 | ruby bay, marriages road, Awa Awa road areas. | Mapua | 2024-06-09 15:41 | 2024-06-09 16:34 | 0.066743 | 0.0012593 | 55 | 2915 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 114 | 9047_1 | ruby bay, marriages road, Awa Awa road areas. | Mapua | 2024-06-09 15:41 | 2024-06-09 17:08 | 0.41234 | 0.0047396 | 207 | 18009 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 115 | 9047_1 | ruby bay, marriages road, Awa Awa road areas. | Mapua | 2024-06-09 15:41 | 2024-06-09 17:13 | 0.088472 | 0.00096165 | 42 | 3864 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 116 | 9048_1 | River Terrace Road, Mount Heslington Road, Lee Valley Road, Garden Valley Road | Ellis St | 2024-06-11 09:30 | 2024-06-11 14:43 | 1.3688 | 0.0043732 | 191 | 59783 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 117 | 9049_1 | Cotterell Road, Ken Beck Drive, Best Road, Appleby Highway | Appleby | 2024-06-11 09:34 | 2024-06-11 15:57 | 0.29816 | 0.00077848 | 34 | 13022 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 118 | 9050_1 | Dove Dale | Appleby | 2024-04-02 10:14 | 2024-04-02 13:32 | 0.0045335 | 2.2896e-05 | 1 | 198 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 119 | 9051_1 | Pakawau | Pakawau | 2024-06-11 17:33 | 2024-06-11 18:16 | 0.3377 | 0.0078535 | 343 | 14749 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 120 | 9051_1 | Pakawau | Pakawau | 2024-06-11 17:33 | 2024-06-11 20:28 | 0.15627 | 0.00089296 | 39 | 6825 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 121 | 9051_1 | Pakawau | Pakawau | 2024-06-11 17:33 | 2024-06-11 20:31 | 0.79066 | 0.0044419 | 194 | 34532 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 122 | 9052_1 | Aporo Road, Stagecoach Road, Pomona Road, Marriages Road, Suncrest Drive, Awa Awa Road, Pine Hill Road, Westmere Drive | Mapua | 2024-06-13 09:02 | 2024-06-13 15:34 | 2.2169 | 0.0056554 | 247 | 96824 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 123 | 9053_1 | High Street, Huffam Street, Motueka | Queen Victoria | 2024-06-13 22:03 | 2024-06-14 00:52 | 0.20508 | 0.0012135 | 53 | 8957 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 124 | 9054_1 | Bell Road | Redwoods Valley | 2024-06-17 09:47 | 2024-06-17 09:50 | 0.00075558 | 0.00025186 | 11 | 33 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 125 | 9055_1 | Pigeon Valley Road, Watkins Road, Golf Road, Sharp Road | Spring Grove | 2024-06-17 09:31 | 2024-06-17 10:59 | 0.22768 | 0.0025873 | 113 | 9944 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 126 | 9056_1 | High Street, Lowe Street, Motueka | Whakarewa St | 2024-06-17 19:01 | 2024-06-17 20:16 | 0.073841 | 0.00098454 | 43 | 3225 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 127 | 9057_1 | Marsden Road, The Ridgeway, Sadlier Street, Suter Street, Koromiko Avenue, Hilliard Street, Mules Street | Stoke | 2024-06-18 09:32 | 2024-06-18 15:47 | 0.65255 | 0.0017401 | 76 | 28500 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 128 | 9057_1 | Marsden Road, The Ridgeway, Sadlier Street, Suter Street, Koromiko Avenue, Hilliard Street, Mules Street | Stoke | 2024-06-18 09:36 | 2024-06-18 15:48 | 0.78361 | 0.0021065 | 92 | 34224 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 129 | 9058_1 | Teal Valley & Ross Rd Hira | Hira | 2024-06-18 21:55 | 2024-06-18 22:42 | 0.044121 | 0.00093875 | 41 | 1927 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 130 | 9059_1 | 85 - 162 Richmond Rd Pohara & 772 Bird Rd Clifton | Pohara | 2024-06-18 20:53 | 2024-06-19 00:39 | 0.041397 | 0.00018317 | 8 | 1808 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 131 | 9060_1 | Inglis Street, Motueka | Queen Victoria | 2024-06-19 09:30 | 2024-06-19 15:30 | 1.0221 | 0.0028392 | 124 | 44640 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 132 | 9061_1 | Cable Bay Road - POSTPONED TO ALTERNATE DATE due to wet ground conditions | Hira | 2024-06-19 11:34 | 2024-06-19 16:25 | 0.053303 | 0.00018317 | 8 | 2328 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 133 | 9062_1 | Redwood Valley Road, Red Stag Lane, Redwood Park Road | Redwoods Valley | 2024-06-20 09:37 | 2024-06-20 16:25 | 0.71931 | 0.001763 | 77 | 31416 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 134 | 9063_1 | Cotterill Road, Ken Beck Drive, Best Road, Appleby Highway | Appleby | 2024-06-20 20:01 | 2024-06-21 01:15 | 0.24444 | 0.00077848 | 34 | 10676 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 135 | 9064_1 | High Street, Lowe Street, Motueka | Whakarewa St | 2024-06-24 19:02 | 2024-06-24 19:52 | 0.049227 | 0.00098454 | 43 | 2150 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 136 | 9065_1 | Eban Road, Stringer Road Redwood | Mahana | 2024-06-25 10:31 | 2024-06-25 14:29 | 0.13078 | 0.00054951 | 24 | 5712 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MURCHISON | 137 | 9066_1 | Woolley Road, West Bank Road, Murchison | Maruia | 2024-06-26 13:07 | 2024-06-26 13:39 | 0.016119 | 0.00050372 | 22 | 704 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 138 | 9067_1 | Collingwood, Ferntown, Pakawau, Bainham | Collingwood 33kV | 2024-06-27 23:33 | 2024-06-28 01:11 | 1.2835 | 0.013097 | 572 | 56056 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 139 | 9067_1 | Collingwood, Ferntown, Pakawau, Bainham | Collingwood 33kV | 2024-06-27 23:33 | 2024-06-28 01:27 | 1.1746 | 0.010303 | 450 | 51300 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 140 | 9068_1 | Wakakapuaka Road, Allisdair Street, Ellendale Street | Marybank | 2024-06-27 09:00 | 2024-06-27 13:51 | 0.13326 | 0.00045793 | 20 | 5820 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 141 | 9069_1 | Washbourne Drive, Farnham Drive, Rochfort Drive, Aston Place, Ledger Close, D'Urville Rise, Blair Terrace, Croisilles Place, Richmond | Waverley St | 2024-06-27 13:01 | 2024-06-27 14:51 | 0.55409 | 0.0050372 | 220 | 24200 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MURCHISON | 142 | 9070_1 | Tutaki Road North | Longford | 2024-07-02 08:14 | 2024-07-02 09:02 | 0.020882 | 0.00043503 | 19 | 912 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 143 | 9071_1 | River Terrace Road, Mount Heslington Road, Lee Valley Road, Garden Valley Road | Ellis St | 2024-07-02 09:30 | 2024-07-02 16:37 | 1.8576 | 0.0043503 | 190 | 81130 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 144 | 9072_1 | Songer Street, Alyson Place, Stoke | Isel | 2024-07-02 09:03 | 2024-07-02 09:41 | 0.048724 | 0.0012822 | 56 | 2128 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 145 | 9073_1 | Cable Bay Road | Hira | 2024-07-03 09:38 | 2024-07-03 14:52 | 0.057516 | 0.00018317 | 8 | 2512 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 146 | 9074_1 | Bateup Road, Paton Road, Greenway Crescent, Hallmark Drive | Paton Road | 2024-07-03 10:05 | 2024-07-03 15:02 | 0.21761 | 0.00073268 | 32 | 9504 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 147 | 9075_1 | Wairoa Gorge | Ellis St | 2024-07-05 08:25 | 2024-07-05 08:39 | 0.0096165 | 0.00068689 | 30 | 420 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 148 | 9076_1 | Comercial Street, Motupipi Street, Dodson Road, Edinburg Street, Feary Crescent, Park Avenue | Commercial St | 2024-07-07 16:25 | 2024-07-07 16:30 | 0.05518 | 0.011036 | 482 | 2410 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 149 | 9078_1 | Golden Bay | Golden Bay 66kV | 2024-07-07 09:00 | 2024-07-07 16:41 | 1.615 | 0.0035031 | 153 | 70533 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 150 | 9078_1 | Golden Bay | Golden Bay 66kV | 2024-07-07 09:02 | 2024-07-07 16:27 | 10.3417 | 0.02324 | 1015 | 451675 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 151 | 9078_1 | Golden Bay | Golden Bay 66kV | 2024-07-07 09:02 | 2024-07-07 16:35 | 1.3173 | 0.0029078 | 127 | 57531 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 152 | 9078_1 | Golden Bay | Golden Bay 66kV | 2024-07-07 09:02 | 2024-07-07 16:40 | 0.2307 | 0.00050372 | 22 | 10076 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 153 | 9078_1 | Golden Bay | Golden Bay 66kV | 2024-07-07 09:32 | 2024-07-07 16:22 | 0.54448 | 0.001328 | 58 | 23780 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 154 | 9078_1 | Golden Bay | Golden Bay 66kV | 2024-07-07 09:33 | 2024-07-07 16:22 | 9.861 | 0.02411 | 1053 | 430677 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 155 | 9078_1 | Golden Bay | Golden Bay 66kV | 2024-07-07 10:04 | 2024-07-07 16:18 | 5.6261 | 0.015043 | 657 | 245718 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 156 | 9078_2 | Golden Bay | Golden Bay 66kV | 2024-07-07 16:25 | 2024-07-07 16:30 | 0.029422 | 0.0058844 | 257 | 1285 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 157 | 9079_1 | Queen Victoria Street, Motueka | Queen Victoria | 2024-07-09 09:01 | 2024-07-09 15:13 | 2.2145 | 0.0059531 | 260 | 96720 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 158 | 9080_1 | Queen Victoria Street, Motueka | Queen Victoria | 2024-07-09 09:42 | 2024-07-09 15:12 | 0.045335 | 0.00013738 | 6 | 1980 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 159 | 9081_1 | Nayland Road, Chisnall Street, Fergusson Street | Nayland | 2024-07-10 12:35 | 2024-07-10 13:10 | 0.66274 | 0.018935 | 827 | 28945 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 160 | 9082_1 | Marsden Valley Road, Huntaway Close, Sanctuary Drive, Appletree Way, Quail Rise, Ashley Terrace, Tussock Place, Woolshed Drive, Elderberry Lane - POSTPONED TO ALTERNATE DATE. | Isel | 2024-07-15 09:32 | 2024-07-15 15:23 | 1.3502 | 0.0038466 | 168 | 58968 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 161 | 9082_1 | Marsden Valley Road, Huntaway Close, Sanctuary Drive, Appletree Way, Quail Rise, Ashley Terrace, Tussock Place, Woolshed Drive, Elderberry Lane - POSTPONED TO ALTERNATE DATE. | Isel | 2024-07-15 09:33 | 2024-07-15 15:23 | 0.76932 | 0.0021981 | 96 | 33600 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 162 | 9082_1 | Marsden Valley Road, Huntaway Close, Sanctuary Drive, Appletree Way, Quail Rise, Ashley Terrace, Tussock Place, Woolshed Drive, Elderberry Lane - POSTPONED TO ALTERNATE DATE. | Isel | 2024-07-15 09:37 | 2024-07-15 15:20 | 0.36126 | 0.0010532 | 46 | 15778 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 163 | 9083_1 | Redwood Valley Road, Red Stag Lane, Redwood Park Road | Redwoods Valley | 2024-07-16 09:30 | 2024-07-16 15:30 | 0.63469 | 0.001763 | 77 | 27720 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 164 | 9084_1 | Thorp Street, Motueka | Queen Victoria | 2024-07-18 09:33 | 2024-07-18 14:56 | 2.4257 | 0.00751 | 328 | 105944 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 165 | 9084_1 | Thorp Street, Motueka | Queen Victoria | 2024-07-18 09:35 | 2024-07-18 14:54 | 2.8851 | 0.0090441 | 395 | 126005 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 166 | 9085_1 | Pohara to and including Totaranui | Pohara | 2024-07-19 00:46 | 2024-07-19 01:37 | 0.91666 | 0.017974 | 785 | 40035 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 167 | 9085_1 | Pohara to and including Totaranui | Pohara | 2024-07-19 00:46 | 2024-07-19 03:09 | 0.5828 | 0.0040756 | 178 | 25454 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 168 | 9085_1 | Pohara to and including Totaranui | Pohara | 2024-07-19 00:46 | 2024-07-19 13:53 | 1.4235 | 0.0018088 | 79 | 62173 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 169 | 9085_2 | Pohara to and including Totaranui | Pohara | 2024-07-19 12:57 | 2024-07-19 13:53 | 0.22823 | 0.0040756 | 178 | 9968 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 170 | 9086_1 | Commercial Street, Motupipi Street, Dodson Road, Edinburg Street, Feary Crescent, Park Avenue | Commercial St | 2024-07-21 09:00 | 2024-07-21 16:12 | 1.4738 | 0.0034116 | 149 | 64368 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 171 | 9086_1 | Commercial Street, Motupipi Street, Dodson Road, Edinburg Street, Feary Crescent, Park Avenue | Commercial St | 2024-07-21 09:01 | 2024-07-21 15:01 | 9.2401 | 0.025667 | 1121 | 403560 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 172 | 9086_1 | Commercial Street, Motupipi Street, Dodson Road, Edinburg Street, Feary Crescent, Park Avenue | Commercial St | 2024-07-21 09:03 | 2024-07-21 16:00 | 1.2126 | 0.0029078 | 127 | 52959 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 173 | 9086_1 | Commercial Street, Motupipi Street, Dodson Road, Edinburg Street, Feary Crescent, Park Avenue | Commercial St | 2024-07-21 09:03 | 2024-07-21 16:13 | 0.2166 | 0.00050372 | 22 | 9460 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 174 | 9086_1 | Commercial Street, Motupipi Street, Dodson Road, Edinburg Street, Feary Crescent, Park Avenue | Commercial St | 2024-07-21 09:16 | 2024-07-21 14:57 | 4.4191 | 0.012959 | 566 | 193006 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 175 | 9087_1 | York street, Motueka | Queen Victoria | 2024-07-21 17:05 | 2024-07-21 17:47 | 0.050006 | 0.0011906 | 52 | 2184 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 176 | 9088_1 | Moutere Highway, Carlyon Road, Sunrise Road, Mahana School Road | Upper Moutere | 2024-07-23 09:05 | 2024-07-23 15:41 | 0.39895 | 0.0010074 | 44 | 17424 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 177 | 9090_1 | Pascoe Street, Orion Street, Parkers Road | Merton Place | 2024-07-24 19:08 | 2024-07-24 20:15 | 0.030681 | 0.00045793 | 20 | 1340 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 178 | 9091_1 | Moutere Highway, Carlyon Road, Sunrise Road, Mahana School Road | Upper Moutere | 2024-07-25 09:32 | 2024-07-25 15:17 | 0.34757 | 0.0010074 | 44 | 15180 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 179 | 9092_1 | Collingwood, Bainham, Puponga | Collingwood 33kV | 2024-07-26 21:06 | 2024-07-26 22:43 | 2.2587 | 0.023286 | 1017 | 98649 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 180 | 9093_1 | Hursthouse Street, Main Road Lower Moutere, Kina Peninsula, Easton Loop, Moana Loop, Brooks View Heights | Tasman | 2024-07-27 05:32 | 2024-07-27 07:53 | 1.5787 | 0.011196 | 489 | 68949 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 181 | 9093_1 | Hursthouse Street, Main Road Lower Moutere, Kina Peninsula, Easton Loop, Moana Loop, Brooks View Heights | Tasman | 2024-07-27 05:32 | 2024-07-27 07:56 | 1.0814 | 0.00751 | 328 | 47232 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 182 | 9094_1 | Parkers Road | Tahunanui | 2024-07-29 18:31 | 2024-07-29 19:12 | 0.046938 | 0.0011448 | 50 | 2050 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 183 | 9095_1 | Pascoe Street, Orion Street, Parkers Road | Merton Place | 2024-07-29 19:03 | 2024-07-29 21:15 | 0.060446 | 0.00045793 | 20 | 2640 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 184 | 9096_1 | River Terrace Road, Mount Heslington Road, Lee Valley Road, Garden Valley Road | Ellis St | 2024-07-30 09:30 | 2024-07-30 16:21 | 1.788 | 0.0043503 | 190 | 78090 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 185 | 9097_1 | Westhaven, Puponga, Pakawau. All properties North of 537 Collingwood-Puponga Main Road. Damaged equipment. Approx 1.5 hr restore time. | Pakawau | 2024-07-30 19:37 | 2024-07-30 20:17 | 0.14379 | 0.0035947 | 157 | 6280 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 186 | 9097_1 | Westhaven, Puponga, Pakawau. All properties North of 537 Collingwood-Puponga Main Road. Damaged equipment. Approx 1.5 hr restore time. | Pakawau | 2024-07-30 19:40 | 2024-07-30 20:16 | 0.12117 | 0.0033658 | 147 | 5292 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 187 | 9098_1 | Dakota Street, McLaren Drive, Tangmere Place, Rapide Place | Airport | 2024-07-30 22:02 | 2024-07-31 01:02 | 0.098912 | 0.00054951 | 24 | 4320 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 188 | 9099_1 | Tophouse Road, Lowther Road, Rainbow Road, Wairau Valley Highway | Rotoiti | 2024-07-31 08:39 | 2024-07-31 15:20 | 0.15608 | 0.00038924 | 17 | 6817 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 189 | 9100_1 | Takaka-Collingwood Highway, Washbourn Road, Onekaka Iron Works Road | Waitapu | 2024-07-31 16:35 | 2024-07-31 17:04 | 0.069056 | 0.0023812 | 104 | 3016 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 190 | 9101_1 | Fearon St, Tarrant Place & Walnut Drive Motueka | Pah St | 2024-08-03 12:37 | 2024-08-03 16:53 | 0.31066 | 0.0012135 | 53 | 13568 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 191 | 9102_1 | Ambrosia Street, Berryfield Drive, Summerfields Boulevard, Central Park Lane, Borck Avenue, Kahikatea Way, Mulberry Lane, Herringbone Street, Lotus Street | Richmond West | 2024-08-05 09:36 | 2024-08-05 15:24 | 1.2271 | 0.003526 | 154 | 53592 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 192 | 9103_1 | Aniseed Valley Road, Haycock Road | Waimea East | 2024-08-07 16:27 | 2024-08-07 17:35 | 0.20396 | 0.0029994 | 131 | 8908 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 193 | 9104_1 | Wakefield-Kohatu Highway, Kerr Hill Road, Valley Road, North Road, Gibbs Road | Kohatu | 2024-08-12 12:10 | 2024-08-12 15:33 | 0.1162 | 0.00057241 | 25 | 5075 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 194 | 9105_1 | Eton Street, Kempton Lane, Barnes Lane, Esher Lane, Upton Lane, Oakley Lane, Heston Lane, Woodley Road, Lampton Street, Berryfields | Richmond West | 2024-08-13 09:32 | 2024-08-13 15:04 | 0.28126 | 0.00084717 | 37 | 12284 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 195 | 9105_1 | Eton Street, Kempton Lane, Barnes Lane, Esher Lane, Upton Lane, Oakley Lane, Heston Lane, Woodley Road, Lampton Street, Berryfields | Richmond West | 2024-08-13 09:43 | 2024-08-13 14:50 | 1.3074 | 0.0042587 | 186 | 57102 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 196 | 9106_1 | Kina Beach Road, Cliff Road, Dee Road, Oceanview Lane, Kina Peninsula Road | Tasman | 2024-08-13 09:03 | 2024-08-13 15:29 | 0.93683 | 0.002427 | 106 | 40916 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 197 | 9107_1 | Whakarewa Street, Centre Motueka-High Street. | Whakarewa | 2024-08-14 09:51 | 2024-08-14 10:34 | 0.061042 | 0.0014196 | 62 | 2666 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 198 | 9107_1 | Whakarewa Street, Centre Motueka-High Street. | Whakarewa | 2024-08-14 09:51 | 2024-08-14 10:41 | 0.099599 | 0.001992 | 87 | 4350 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 199 | 9107_1 | Whakarewa Street, Centre Motueka-High Street. | Whakarewa | 2024-08-14 09:51 | 2024-08-14 10:56 | 0.34677 | 0.0053349 | 233 | 15145 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 200 | 9107_1 | Whakarewa Street, Centre Motueka-High Street. | Whakarewa | 2024-08-14 09:51 | 2024-08-14 11:13 | 0.56701 | 0.0069147 | 302 | 24764 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 201 | 9107_1 | Whakarewa Street, Centre Motueka-High Street. | Whakarewa | 2024-08-14 09:51 | 2024-08-14 11:16 | 0.70841 | 0.0083343 | 364 | 30940 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 202 | 9107_1 | Whakarewa Street, Centre Motueka-High Street. | Whakarewa | 2024-08-14 09:51 | 2024-08-14 11:18 | 0.22908 | 0.0026331 | 115 | 10005 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 203 | 9108_1 | Chisnall Street, Andrew Street, Black Street, Stoke | Nayland | 2024-08-14 09:34 | 2024-08-14 15:08 | 0.47414 | 0.0014196 | 62 | 20708 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 204 | 9109_1 | Kina Beach Road, Cliff Road, Dee Road, Oceanview Lane, Kina Peninsula Road | Tasman | 2024-08-15 09:32 | 2024-08-15 13:27 | 0.57035 | 0.002427 | 106 | 24910 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 205 | 9110_1 | Fearon Street, Motueka | Pah St | 2024-08-15 09:37 | 2024-08-15 17:19 | 0.010578 | 2.2896e-05 | 1 | 462 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 206 | 9111_1 | Waiwhero Rd area Ngatimoti | Dovedale B | 2024-08-18 23:28 | 2024-08-19 00:35 | 0.11045 | 0.0016485 | 72 | 4824 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 207 | 9111_1 | Waiwhero Rd area Ngatimoti | Dovedale B | 2024-08-18 23:28 | 2024-08-19 00:54 | 0.10436 | 0.0012135 | 53 | 4558 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 208 | 9111_1 | Waiwhero Rd area Ngatimoti | Dovedale B | 2024-08-18 23:28 | 2024-08-19 00:59 | 0.15002 | 0.0016485 | 72 | 6552 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 209 | 9112_1 | Pakawau Bush Road | Pakawau | 2024-08-20 09:49 | 2024-08-20 16:33 | 0.064751 | 0.00016027 | 7 | 2828 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 210 | 9113_1 | Rowling Road, Torlesse Drive, Kotara Place, Goodall Place, Kaiteriteri | Kaiteriteri | 2024-08-21 09:37 | 2024-08-21 15:51 | 0.97621 | 0.0026102 | 114 | 42636 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 211 | 9114_1 | Blackbird Valley Road, Bensemann Road, Upper Moutere | Upper Moutere | 2024-08-22 09:33 | 2024-08-22 14:35 | 0.14521 | 0.00048082 | 21 | 6342 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 212 | 9115_1 | Main Road Riwaka, Umukuri Road, Lodder Lane, River Road, Anderson Road - POSTPONED TO ALTERNATE DATE. | Kaiteriteri | 2024-08-23 09:36 | 2024-08-23 15:39 | 1.388 | 0.0038237 | 167 | 60621 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 213 | 9116_1 | Pohara, Wainui Bay, Ligar Bay, Tata Beach, Clifton, Motupipi | Pohara | 2024-08-26 15:30 | 2024-08-26 16:34 | 1.1151 | 0.017424 | 761 | 48704 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 214 | 9116_1 | Pohara, Wainui Bay, Ligar Bay, Tata Beach, Clifton, Motupipi | Pohara | 2024-08-26 15:30 | 2024-08-26 16:37 | 0.28533 | 0.0042587 | 186 | 12462 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 215 | 9116_1 | Pohara, Wainui Bay, Ligar Bay, Tata Beach, Clifton, Motupipi | Pohara | 2024-08-26 15:30 | 2024-08-26 18:49 | 0.43286 | 0.0021752 | 95 | 18905 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 216 | 9116_1 | Pohara, Wainui Bay, Ligar Bay, Tata Beach, Clifton, Motupipi | Pohara | 2024-08-26 17:17 | 2024-08-26 18:49 | 0.11586 | 0.0012593 | 55 | 5060 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 217 | 9117_1 | Poole Street, Atkins Street, Wilkie Street, Jocelyn Avenue, Fry Street, Michael Myers Street, Motueka | Pah St | 2024-08-27 09:01 | 2024-08-27 15:18 | 2.2702 | 0.0060218 | 263 | 99151 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 218 | 9118_1 | Poole Street, Atkins Street, Wilkie Street, Jocelyn Avenue, Fry Street, Michael Myers Street, Motueka | Pah St | 2024-08-29 09:01 | 2024-08-29 15:19 | 2.2762 | 0.0060218 | 263 | 99414 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 219 | 9119_1 | Dry Road, Cowin Road, Hudson Street | Pakawau | 2024-08-30 11:20 | 2024-08-30 12:00 | 0.044877 | 0.0011219 | 49 | 1960 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 220 | 9120_1 | Wakefield-Kohatu Highway, Pretty Bridge Valley, Foxhill Road, Quail Valley Road | Spring Grove | 2024-08-30 16:14 | 2024-08-30 16:50 | 0.22585 | 0.0062736 | 274 | 9864 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 221 | 9121_1 | Collingwood, Whanganui, Rockville, Bainham | Collingwood 33kV | 2024-08-31 16:22 | 2024-08-31 17:48 | 2.0026 | 0.023286 | 1017 | 87462 | Unplanned | Adverse weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 222 | 9122_1 | bird road | Pohara | 2024-08-31 18:57 | 2024-08-31 19:49 | 0.017859 | 0.00034345 | 15 | 780 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 223 | 9123_1 | Takaka hill | Cobb Valley | 2024-09-01 13:20 | 2024-09-01 13:36 | 0.0014654 | 9.1586e-05 | 4 | 64 | Unplanned | Lightning |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 224 | 9124_1 | High Street, Tudor Street, Wilkinson Street, Taylor Avenue, Goodman Drive | Whakarewa St | 2024-09-03 09:31 | 2024-09-03 15:50 | 2.3256 | 0.0061362 | 268 | 101572 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 225 | 9125_1 | Hart Road, Aniseed Valley Road, Richmond | Paton Road | 2024-09-04 10:00 | 2024-09-04 13:00 | 0.016485 | 9.1586e-05 | 4 | 720 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 226 | 9126_1 | Enner Glynn Road | Wakatu | 2024-09-04 09:33 | 2024-09-04 13:37 | 0.072627 | 0.00029765 | 13 | 3172 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 227 | 9127_1 | Waimea West Road, Teapot Valley Road, Eves Valley Road | Redwoods Valley | 2024-09-05 09:32 | 2024-09-05 12:33 | 0.12847 | 0.00070979 | 31 | 5611 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 228 | 9128_1 | Dovedale Valley Road | Dovedale A | 2024-09-06 18:13 | 2024-09-06 18:17 | 0.040206 | 0.010052 | 439 | 1756 | Unplanned | Human error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 229 | 9128_1 | Dovedale Valley Road | Dovedale A | 2024-09-06 18:13 | 2024-09-06 19:05 | 0.22264 | 0.0042816 | 187 | 9724 | Unplanned | Human error |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 230 | 9129_1 | Gardner Valley Road and all side roads. | Upper Moutere | 2024-09-06 19:59 | 2024-09-06 20:40 | 0.091059 | 0.002221 | 97 | 3977 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 231 | 9130_1 | Ward - Holmes Road | Waitapu | 2024-09-07 17:00 | 2024-09-07 17:32 | 0.0051288 | 0.00016027 | 7 | 224 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 232 | 9131_1 | Queen Vic St, High St, Old Wharf Road, Thorpe St and side roads. | Queen Victoria | 2024-09-08 18:35 | 2024-09-08 20:00 | 1.4071 | 0.016554 | 723 | 61455 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 233 | 9131_1 | Queen Vic St, High St, Old Wharf Road, Thorpe St and side roads. | Queen Victoria | 2024-09-08 18:35 | 2024-09-08 20:03 | 0.60446 | 0.0068689 | 300 | 26400 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 234 | 9131_1 | Queen Vic St, High St, Old Wharf Road, Thorpe St and side roads. | Queen Victoria | 2024-09-08 18:35 | 2024-09-08 20:26 | 0.81328 | 0.0073268 | 320 | 35520 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 235 | 9131_1 | Queen Vic St, High St, Old Wharf Road, Thorpe St and side roads. | Queen Victoria | 2024-09-08 18:35 | 2024-09-08 21:47 | 0.083526 | 0.00043503 | 19 | 3648 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 236 | 9131_1 | Queen Vic St, High St, Old Wharf Road, Thorpe St and side roads. | Queen Victoria | 2024-09-08 19:49 | 2024-09-08 19:52 | 0.078855 | 0.026285 | 1148 | 3444 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 237 | 9132_1 | Old Wharf Road, Motueka | Wildman Road | 2024-09-09 13:33 | 2024-09-09 15:05 | 0.0021065 | 2.2896e-05 | 1 | 92 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 238 | 9133_1 | Appleby Highway | Appleby | 2024-09-09 17:34 | 2024-09-09 17:59 | 0.038924 | 0.001557 | 68 | 1700 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 239 | 9133_1 | Appleby Highway | Appleby | 2024-09-09 17:34 | 2024-09-09 18:37 | 0.22214 | 0.003526 | 154 | 9702 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 240 | 9133_1 | Appleby Highway | Appleby | 2024-09-09 17:34 | 2024-09-09 18:48 | 0.46764 | 0.0063194 | 276 | 20424 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 241 | 9133_1 | Appleby Highway | Appleby | 2024-09-09 17:34 | 2024-09-09 19:38 | 0.11924 | 0.00096165 | 42 | 5208 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 242 | 9134_1 | Woodlands Avenue, Motueka | Whakarewa St | 2024-09-10 09:45 | 2024-09-10 14:05 | 0.023812 | 9.1586e-05 | 4 | 1040 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 243 | 9135_1 | Pomona Road, Ruby Bay | Mapua | 2024-09-11 09:43 | 2024-09-11 16:14 | 0.089525 | 0.00022896 | 10 | 3910 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 244 | 9136_1 | Bird Road, Carlye Street | Pohara | 2024-09-12 13:35 | 2024-09-12 13:38 | 0.0010303 | 0.00034345 | 15 | 45 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 245 | 9137_1 | Bishopdale Avenue, Clifford Avenue, Vista Drive, Westley Place, Marie Place, Potteries Way | Bishopdale | 2024-09-05 09:01 | 2024-09-05 14:12 | 1.2889 | 0.0041442 | 181 | 56291 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 246 | 9138_1 | Motueka River West Bank Road, Peach Island Road, Shaggery Road, Whakarewa Street | Dovedale A | 2024-09-12 09:00 | 2024-09-12 14:57 | 0.80105 | 0.0022438 | 98 | 34986 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 247 | 9139_1 | All of Pigeon Valley | Spring Grove | 2024-09-16 16:05 | 2024-09-16 16:56 | 0.13195 | 0.0025873 | 113 | 5763 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 248 | 9140_1 | Talbot Street, Queen Street, Churchill ave area | Talbot Street | 2024-09-16 07:42 | 2024-09-16 08:34 | 0.77628 | 0.014928 | 652 | 33904 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 249 | 9140_1 | Talbot Street, Queen Street, Churchill ave area | Talbot Street | 2024-09-16 07:42 | 2024-09-16 10:10 | 0.17282 | 0.0011677 | 51 | 7548 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 250 | 9141_1 | Toru Street | Mapua | 2024-09-18 06:31 | 2024-09-18 07:56 | 0.033085 | 0.00038924 | 17 | 1445 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 251 | 9142_1 | Collingwood-Puponga Main Road | Pakawau | 2024-09-17 09:33 | 2024-09-17 15:57 | 2.2948 | 0.005976 | 261 | 100224 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 252 | 9143_1 | Atawhai Drive, Dodson Valley Road, Tui Glen Road, Hodgson Place, Strathaven Place, Clovelly Street, Matuku Place | Atawhai | 2024-09-19 13:03 | 2024-09-19 14:15 | 0.81603 | 0.011334 | 495 | 35640 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 253 | 9144_1 | Takaka-Collingwood Highway, Rangihaeata Road, Patons Rock Road, Bay View Terrace, Fraser Road, Onahau Road - POSTPONED TO ALTERNATE DATE. | Waitapu | 2024-09-19 09:44 | 2024-09-19 16:27 | 0.54441 | 0.0013509 | 59 | 23777 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 254 | 9145_1 | Cable Bay Road | Glenduan | 2024-09-20 14:34 | 2024-09-20 14:56 | 0.023675 | 0.0010761 | 47 | 1034 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 255 | 9146_1 | Takaka-Collingwood Highway, Rangihaeata Road, Patons Rock Road, Bay View Terrace, Fraser Road, Onahau Road | Waitapu | 2024-09-24 09:31 | 2024-09-24 16:14 | 2.4083 | 0.005976 | 261 | 105183 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 256 | 9147_1 | Talbot St, Linden Court | Talbot Street | 2024-09-25 05:02 | 2024-09-25 05:40 | 0.044373 | 0.0011677 | 51 | 1938 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 257 | 9148_1 | Maitai Valley Road | Maitai | 2024-09-26 09:34 | 2024-09-26 14:02 | 0.04909 | 0.00018317 | 8 | 2144 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 258 | 9149_1 | Edward Street, Treeton Place, Pitfure Road, Arrow Street, Bastin Terrace, Matariki Place, Wakefield | Higgins Road | 2024-10-01 09:41 | 2024-10-01 16:48 | 1.7598 | 0.0041214 | 180 | 76860 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 259 | 9150_1 | Old Coach Road, Bronte Road West, Mahana Ridge, Mahana School Road, Apple Valley Road, Mahoe Close, Mahana | Mahana | 2024-10-02 09:32 | 2024-10-02 12:51 | 0.41463 | 0.0020836 | 91 | 18109 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 260 | 9151_1 | Market Road, Enner Glynn Road, Grampian Road, Bills Drive | Bishopdale | 2024-10-02 09:33 | 2024-10-02 13:47 | 0.098867 | 0.00038924 | 17 | 4318 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 261 | 9152_1 | Whakarewa Street, Manoy Street, Wakatu Place, Motueka | Whakarewa St | 2024-10-04 10:02 | 2024-10-04 11:14 | 0.080778 | 0.0011219 | 49 | 3528 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 262 | 9153_1 | Tadmor-Bushend Road, Wangapeka River Road, Hewitt Road, Sherry River Road, Jones RoadSlippery Road, Fairhall Road | Korere | 2024-10-04 10:33 | 2024-10-04 12:03 | 0.1731 | 0.0019233 | 84 | 7560 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 263 | 9154_1 | Kohatu - Golden Downs, Stanley Brook, Tapawera | Kohatu | 2024-10-05 08:53 | 2024-10-05 13:27 | 2.5973 | 0.0094791 | 414 | 113436 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 264 | 9155_1 | Beach Road, Golf Road, Centennial Road, Jubilee Way, Tahunanui | Moana | 2024-10-08 11:18 | 2024-10-08 14:11 | 0.39611 | 0.0022896 | 100 | 17300 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 265 | 9156_1 | Kina Peninsula Road | Tasman | 2024-10-08 09:35 | 2024-10-08 15:02 | 0.059897 | 0.00018317 | 8 | 2616 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 266 | 9157_1 | Edward Street, Church Valley Road, Gibbs Valley Road, Fellbridge Rise, Wakefield | Higgins Road | 2024-10-08 09:33 | 2024-10-08 15:03 | 0.2569 | 0.00077848 | 34 | 11220 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 267 | 9158_1 | Beach Road, Muritai Street, Centennial Road, Waikare Street, Mata Close, Hounsell Circle, Tahunanui | Moana | 2024-10-10 09:02 | 2024-10-10 17:10 | 1.7878 | 0.0036634 | 160 | 78080 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 268 | 9158_1 | Beach Road, Muritai Street, Centennial Road, Waikare Street, Mata Close, Hounsell Circle, Tahunanui | Moana | 2024-10-10 09:06 | 2024-10-10 16:57 | 0.62548 | 0.001328 | 58 | 27318 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 269 | 9159_1 | Whakarewa Street, Manoy Street, Wakatu Place, Motueka | Whakarewa St | 2024-10-11 14:02 | 2024-10-11 14:57 | 0.061706 | 0.0011219 | 49 | 2695 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 270 | 9160_1 | Edward Street, Church Valley Road, Gibbs Valley Road, Fellbridge Rise, Wakefield | Higgins Road | 2024-10-15 09:37 | 2024-10-15 13:49 | 0.19618 | 0.00077848 | 34 | 8568 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 271 | 9161_1 | Ruby Bay, Stafford Drive, Pomona Road, Awa Awa Road, Marriages Road and side streets. | Mapua | 2024-10-15 14:39 | 2024-10-15 15:02 | 0.079519 | 0.0034574 | 151 | 3473 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 272 | 9161_1 | Ruby Bay, Stafford Drive, Pomona Road, Awa Awa Road, Marriages Road and side streets. | Mapua | 2024-10-15 14:39 | 2024-10-15 15:17 | 0.12094 | 0.0031826 | 139 | 5282 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 273 | 9161_1 | Ruby Bay, Stafford Drive, Pomona Road, Awa Awa Road, Marriages Road and side streets. | Mapua | 2024-10-15 14:39 | 2024-10-15 15:55 | 0.43329 | 0.0057012 | 249 | 18924 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 274 | 9162_1 | NPI - Suffolk Rd 33kV Feeder | Suffolk Road 33kV | 2024-10-16 08:46 | 2024-10-16 10:10 | 0.0019233 | 2.2896e-05 | 1 | 84 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 275 | 9163_1 | Tangmere Road | Commercial St | 2024-10-18 15:42 | 2024-10-18 15:56 | 0.0025644 | 0.00018317 | 8 | 112 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 276 | 9165_1 | The Coastal Highway, Redwood Road | Appleby | 2024-10-21 09:36 | 2024-10-21 15:12 | 0.16156 | 0.00048082 | 21 | 7056 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 277 | 9166_1 | Standish Place | Polstead | 2024-10-22 14:15 | 2024-10-22 14:59 | 0.026193 | 0.00059531 | 26 | 1144 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 278 | 9167_1 | Hursthouse Street, Wildman Road, Quayle Road, Batchelor Ford Road, Main Road Lower Moutere | Kaiteriteri | 2024-10-22 09:31 | 2024-10-22 17:22 | 0.37745 | 0.00080137 | 35 | 16485 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 279 | 9167_1 | Hursthouse Street, Wildman Road, Quayle Road, Batchelor Ford Road, Main Road Lower Moutere | Kaiteriteri | 2024-10-22 09:32 | 2024-10-22 17:19 | 0.51325 | 0.001099 | 48 | 22416 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 280 | 9168_1 | Greenacres Rd Redwood Valley | Redwoods Valley | 2024-10-22 04:31 | 2024-10-22 04:59 | 0.016027 | 0.00057241 | 25 | 700 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 281 | 9169_1 | Green Tree Road, School Road, Riwaka | Kaiteriteri | 2024-10-23 09:57 | 2024-10-23 16:39 | 0.19329 | 0.00048082 | 21 | 8442 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 282 | 9170_1 | Queen Victoria Street, King Edward Street, College Street, Hau Road, Thomason Avenue, Motueka | Queen Victoria | 2024-10-24 09:35 | 2024-10-24 15:38 | 2.1443 | 0.0059073 | 258 | 93654 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 283 | 9171_1 | Rayners Road, Hira | Hira | 2024-10-25 09:33 | 2024-10-25 13:35 | 0.094196 | 0.00038924 | 17 | 4114 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 284 | 9172_1 | Takaka Valley Highway | East Takaka | 2024-10-29 12:02 | 2024-10-29 12:26 | 0.026926 | 0.0011219 | 49 | 1176 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 285 | 9172_1 | Takaka Valley Highway | East Takaka | 2024-10-29 12:02 | 2024-10-29 13:03 | 0.030727 | 0.00050372 | 22 | 1342 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 286 | 9172_1 | Takaka Valley Highway | East Takaka | 2024-10-29 12:02 | 2024-10-29 13:07 | 0.1905 | 0.0029307 | 128 | 8320 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 287 | 9172_1 | Takaka Valley Highway | East Takaka | 2024-10-29 12:02 | 2024-10-29 13:15 | 0.10029 | 0.0013738 | 60 | 4380 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 288 | 9172_1 | Takaka Valley Highway | East Takaka | 2024-10-29 12:02 | 2024-10-29 18:58 | 0.83819 | 0.0020149 | 88 | 36608 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 289 | 9173_1 | Takaka-Collingwood Highway, Milnthorpe Quay, Nelson Street, Kendal Street, Takaka | Waitapu | 2024-10-30 09:33 | 2024-10-30 15:22 | 0.29566 | 0.00084717 | 37 | 12913 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 290 | 9174_1 | Factory Road, Riwaka | Kaiteriteri | 2024-10-31 09:31 | 2024-10-31 15:16 | 0.078993 | 0.00022896 | 10 | 3450 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 291 | 9175_1 | Montebello Avenue, Village Lane, Old Farm Road and side streets. | Polstead | 2024-11-05 13:36 | 2024-11-05 20:29 | 0.76595 | 0.0018546 | 81 | 33453 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 292 | 9175_1 | Montebello Avenue, Village Lane, Old Farm Road and side streets. | Polstead | 2024-11-05 13:37 | 2024-11-05 13:58 | 0.52602 | 0.025049 | 1094 | 22974 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 293 | 9176_1 | Collingwood-Puponga Main Road, Pakawau Bush Road, Totara Avenue, Cowin Road, Hudson Street, Dry Road | Pakawau | 2024-11-06 09:31 | 2024-11-06 15:50 | 0.59876 | 0.0015799 | 69 | 26151 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 294 | 9176_1 | Collingwood-Puponga Main Road, Pakawau Bush Road, Totara Avenue, Cowin Road, Hudson Street, Dry Road | Pakawau | 2024-11-06 09:33 | 2024-11-06 15:49 | 1.2655 | 0.0033658 | 147 | 55272 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 295 | 9177_1 | Merton Place, Orion Street | Merton Place | 2024-11-06 09:15 | 2024-11-06 09:38 | 0.036337 | 0.0015799 | 69 | 1587 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 296 | 9177_1 | Merton Place, Orion Street | Merton Place | 2024-11-06 09:38 | 2024-11-06 10:12 | 0.0023354 | 0 | 0 | 102 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 297 | 9178_1 | Collingwood-Puponga Main Road, Pakawau Bush Road, Cowin Road, Hudson Street, Dry Road | Pakawau | 2024-11-07 09:30 | 2024-11-07 15:30 | 1.3518 | 0.003755 | 164 | 59040 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 298 | 9178_1 | Collingwood-Puponga Main Road, Pakawau Bush Road, Cowin Road, Hudson Street, Dry Road | Pakawau | 2024-11-07 09:32 | 2024-11-07 16:35 | 0.50363 | 0.0011906 | 52 | 21996 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 299 | 9179_1 | Collingwood, Puponga, Bainham and surrounding areas. | Collingwood 33kV | 2024-11-07 19:08 | 2024-11-07 20:17 | 1.6209 | 0.023492 | 1026 | 70794 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 300 | 9180_1 | Takaka-Collingwood Highway, Washbourn Road | Waitapu | 2024-11-08 09:35 | 2024-11-08 13:42 | 0.1018 | 0.00041214 | 18 | 4446 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 301 | 9181_1 | Golf Road, Beach Road, Centennial Road, Green Street, Roto Street, Holly Way, Jubilee Way, Penton Way, Tahunanui - POSTPONED TO ALTERNATE DATE. | Moana | 2024-11-08 09:32 | 2024-11-08 15:45 | 1.5287 | 0.0040985 | 179 | 66767 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 302 | 9181_1 | Golf Road, Beach Road, Centennial Road, Green Street, Roto Street, Holly Way, Jubilee Way, Penton Way, Tahunanui - POSTPONED TO ALTERNATE DATE. | Moana | 2024-11-08 09:37 | 2024-11-08 15:38 | 0.66951 | 0.0018546 | 81 | 29241 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 303 | 9182_1 | Beach Road, Muritai Street, Centennial Road, Waikare Street, Mata Close, Hounsell Circle, Tahunanui | Moana | 2024-11-12 09:03 | 2024-11-12 17:26 | 1.8427 | 0.0036634 | 160 | 80480 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 304 | 9182_1 | Beach Road, Muritai Street, Centennial Road, Waikare Street, Mata Close, Hounsell Circle, Tahunanui | Moana | 2024-11-12 09:05 | 2024-11-12 17:24 | 0.66267 | 0.001328 | 58 | 28942 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 305 | 9183_1 | Pigeon Valley | Spring Grove | 2024-11-12 19:06 | 2024-11-12 20:00 | 0.13971 | 0.0025873 | 113 | 6102 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 306 | 9184_1 | Beach Road, Muritai Street, Centennial Road, Waikare Street, Mata Close, Hounsell Circle, Tahunanui | Moana | 2024-11-14 09:03 | 2024-11-14 13:31 | 0.3559 | 0.001328 | 58 | 15544 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 307 | 9184_1 | Beach Road, Muritai Street, Centennial Road, Waikare Street, Mata Close, Hounsell Circle, Tahunanui | Moana | 2024-11-14 09:04 | 2024-11-14 13:32 | 0.9818 | 0.0036634 | 160 | 42880 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 308 | 9185_1 | Whiting Drive, Mayer Crescent, Wakefield | Spring Grove | 2024-11-14 10:00 | 2024-11-14 11:58 | 0.39716 | 0.0033658 | 147 | 17346 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 309 | 9185_1 | Whiting Drive, Mayer Crescent, Wakefield | Spring Grove | 2024-11-14 10:00 | 2024-11-14 12:04 | 0.12208 | 0.00098454 | 43 | 5332 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 310 | 9186_1 | Main Road Stoke, Polstead Road, Montebelllo Avenue | Polstead | 2024-11-15 15:12 | 2024-11-15 15:50 | 0.72737 | 0.019141 | 836 | 31768 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 311 | 9186_1 | Main Road Stoke, Polstead Road, Montebelllo Avenue | Polstead | 2024-11-15 15:12 | 2024-11-15 15:53 | 0.18869 | 0.0046022 | 201 | 8241 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 312 | 9186_1 | Main Road Stoke, Polstead Road, Montebelllo Avenue | Polstead | 2024-11-15 15:12 | 2024-11-15 17:42 | 0.20263 | 0.0013509 | 59 | 8850 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 313 | 9187_1 | End of college streed | Brooklyn | 2024-11-16 07:44 | 2024-11-16 08:23 | 0.013394 | 0.00034345 | 15 | 585 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 314 | 9188_1 | All of Bainham area and Parapara area | Rockville | 2024-11-18 05:48 | 2024-11-18 08:22 | 1.5867 | 0.010303 | 450 | 69300 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 315 | 9189_1 | Devil's Boots Road, Plain Road, Collingwood | Bainham | 2024-11-20 09:31 | 2024-11-20 12:27 | 0.012089 | 6.8689e-05 | 3 | 528 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 316 | 9190_1 | Pupu Valley Road, Waitapu Wharf Road, Takaka-Collingwood Highway | Commercial St | 2024-11-21 09:33 | 2024-11-21 12:08 | 0.056783 | 0.00036634 | 16 | 2480 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 317 | 9191_1 | Thorpe-Orinoco Road, Lloyd Valley Road, Rosedale Road, Strachan Road | Upper Moutere | 2024-11-21 09:37 | 2024-11-21 15:20 | 0.30629 | 0.00089296 | 39 | 13377 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 318 | 9192_1 | Kaiterireri-Sandy Bay, Marahau Valley, Rowling Heights, Stephens Bay, Bay View, Martin Farm | Kaiterteri | 2024-11-26 09:41 | 2024-11-26 11:14 | 0.52595 | 0.0056554 | 247 | 22971 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 319 | 9192_1 | Kaiterireri-Sandy Bay, Marahau Valley, Rowling Heights, Stephens Bay, Bay View, Martin Farm | Kaiterteri | 2024-11-26 09:41 | 2024-11-26 11:44 | 0.32105 | 0.0026102 | 114 | 14022 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 320 | 9192_1 | Kaiterireri-Sandy Bay, Marahau Valley, Rowling Heights, Stephens Bay, Bay View, Martin Farm | Kaiterteri | 2024-11-26 09:41 | 2024-11-26 12:11 | 0.44648 | 0.0029765 | 130 | 19500 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 321 | 9192_1 | Kaiterireri-Sandy Bay, Marahau Valley, Rowling Heights, Stephens Bay, Bay View, Martin Farm | Kaiterteri | 2024-11-26 09:41 | 2024-11-26 12:46 | 0.042358 | 0.00022896 | 10 | 1850 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 322 | 9192_1 | Kaiterireri-Sandy Bay, Marahau Valley, Rowling Heights, Stephens Bay, Bay View, Martin Farm | Kaiterteri | 2024-11-26 09:41 | 2024-11-26 13:21 | 1.3248 | 0.0060218 | 263 | 57860 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 323 | 9192_1 | Kaiterireri-Sandy Bay, Marahau Valley, Rowling Heights, Stephens Bay, Bay View, Martin Farm | Kaiterteri | 2024-11-26 09:41 | 2024-11-26 21:34 | 0.68566 | 0.00096165 | 42 | 29946 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 324 | 9192_2 | Kaiterireri-Sandy Bay, Marahau Valley, Rowling Heights, Stephens Bay, Bay View, Martin Farm | Kaiterteri | 2024-11-26 11:52 | 2024-11-26 11:59 | 0.059462 | 0.0084946 | 371 | 2597 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 325 | 9193_1 | Maitai Valley Road - POSTPONED TO ALTERNATE DATE. Council contractor delay. | Maitai | 2024-11-28 09:35 | 2024-11-28 15:41 | 0.05028 | 0.00013738 | 6 | 2196 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 326 | 9193_1 | Maitai Valley Road - POSTPONED TO ALTERNATE DATE. Council contractor delay. | Maitai | 2024-11-28 09:35 | 2024-11-28 16:06 | 0.0089525 | 2.2896e-05 | 1 | 391 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 327 | 9194_1 | Westhaven, Pakawau, Wharariki Area | Pakawau | 2024-11-29 09:43 | 2024-11-29 10:14 | 0.21578 | 0.0069605 | 304 | 9424 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 328 | 9195_1 | Werneth Street, Werneth Ridge, Atawhai | Marybank | 2024-11-29 10:24 | 2024-11-29 14:09 | 0.1391 | 0.0006182 | 27 | 6075 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 329 | 9196_1 | Collingwood-Puponga Main Road, Farewell Spit, Seddon Road, Wharariki Road | Pakawau | 2024-12-03 09:30 | 2024-12-03 16:07 | 0.79991 | 0.0020149 | 88 | 34936 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 330 | 9197_1 | Abel Tasman Drive, Bay Vista Drive, Matenga Road, Peninsula Road, Pohara Valley Road, Tata Heights, Totaranui Road | Pohara | 2024-12-04 09:08 | 2024-12-04 15:47 | 1.6992 | 0.0042587 | 186 | 74214 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 331 | 9197_1 | Abel Tasman Drive, Bay Vista Drive, Matenga Road, Peninsula Road, Pohara Valley Road, Tata Heights, Totaranui Road | Pohara | 2024-12-04 09:09 | 2024-12-04 15:44 | 2.1254 | 0.0053807 | 235 | 92825 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 332 | 9198_1 | Collingwood-Puponga Main Road, Farewell Spit, Seddon Road, Wharariki Road | Pakawau | 2024-12-05 09:32 | 2024-12-05 15:28 | 0.7173 | 0.0020149 | 88 | 31328 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 333 | 9199_1 | Onekaka power station 33kv line | Collingwood 33kV | 2024-12-05 17:04 | 2024-12-05 20:07 | 0.0083801 | 4.5793e-05 | 2 | 366 | Unplanned | Adverse Environment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 334 | 9200_1 | Waitapu Road, Waitapu Wharf Road, Takaka | Waitapu | 2024-12-06 09:32 | 2024-12-06 13:40 | 0.051105 | 0.00020607 | 9 | 2232 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 335 | 9201_1 | Central Road South, Edward Road. Moutere Highway, Wills Road, Drummond Road, Flaxmore Road | Dovedale B | 2024-12-06 10:53 | 2024-12-06 11:51 | 0.25763 | 0.0044419 | 194 | 11252 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 336 | 9201_1 | Central Road South, Edward Road. Moutere Highway, Wills Road, Drummond Road, Flaxmore Road | Dovedale B | 2024-12-06 10:53 | 2024-12-06 14:56 | 0.038947 | 0.00016027 | 7 | 1701 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 337 | 9202_1 | Redwood Valley, Moutere Highway, Maisey Road, Mailing Road | Redwoods Valley | 2024-12-06 14:40 | 2024-12-06 15:25 | 0.34104 | 0.0075787 | 331 | 14895 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 338 | 9203_1 | St Arnaud-Kawatiri Highway | Rotoiti | 2024-12-09 10:13 | 2024-12-09 13:41 | 0.0047624 | 2.2896e-05 | 1 | 208 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 339 | 9204_1 | Wharariki Road, Puponga | Pakawau | 2024-12-10 09:50 | 2024-12-10 15:56 | 0.058661 | 0.00016027 | 7 | 2562 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 340 | 9205_1 | Abel Tasman Drive, Bay Vista Drive, Matenga Road, Peninsula Road, Pohara Valley Road, Tata Heights, Totaranui Road | Pohara | 2024-12-11 09:30 | 2024-12-11 16:04 | 1.6779 | 0.0042587 | 186 | 73284 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 341 | 9205_1 | Abel Tasman Drive, Bay Vista Drive, Matenga Road, Peninsula Road, Pohara Valley Road, Tata Heights, Totaranui Road | Pohara | 2024-12-11 09:32 | 2024-12-11 16:04 | 2.1092 | 0.0053807 | 235 | 92120 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 342 | 9206_1 | Middlebank Drive, Olympus Way. | Wensley Road | 2024-12-12 07:52 | 2024-12-12 08:32 | 0.097997 | 0.0024499 | 107 | 4280 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 343 | 9208_1 | Market Road, Enner Glynn Road, Grampian Road, Bills Drive, Bishopdale | Bishopdale | 2024-12-15 09:31 | 2024-12-15 11:23 | 0.043595 | 0.00038924 | 17 | 1904 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 344 | 9209_1 | Tangmere Road | Commercial St | 2024-12-17 05:58 | 2024-12-17 06:12 | 0.0025644 | 0.00018317 | 8 | 112 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 345 | 9210_1 | Kaihoka Road. | Pakawau | 2024-12-17 14:16 | 2024-12-17 14:56 | 0.0073268 | 0.00018317 | 8 | 320 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 346 | 9211_1 | Beach Road, Golf Road, Centennial Road, Jubilee Way, Tahunanui | Tahunanui | 2024-12-18 09:03 | 2024-12-18 11:30 | 0.33658 | 0.0022896 | 100 | 14700 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 347 | 9212_1 | Brabant Drive, Pine Hill Road, Van Beek Place, Ruby Bay | Mapua | 2024-12-18 09:42 | 2024-12-18 15:49 | 0.46216 | 0.0012593 | 55 | 20185 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 348 | 9213_1 | Sutton Street, Gilbert Street, Warren Kelly Street, Richmond | Darcy St | 2024-12-18 09:02 | 2024-12-18 16:23 | 0.67652 | 0.0015341 | 67 | 29547 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 349 | 9214_1 | The Howard and Glenhope area from cap bank | Rotoiti | 2024-12-18 20:24 | 2024-12-19 00:42 | 0.20085 | 0.00077848 | 34 | 8772 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 350 | 9214_1 | The Howard and Glenhope area from cap bank | Rotoiti | 2024-12-18 21:00 | 2024-12-19 00:42 | 0.091494 | 0.00041214 | 18 | 3996 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 351 | 9215_1 | Nguroa Road | Pakawau | 2024-12-19 15:02 | 2024-12-19 16:22 | 0.0036634 | 4.5793e-05 | 2 | 160 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 352 | 9216_1 | Estuary Place, Richmond | Beach Road | 2024-12-30 09:03 | 2024-12-30 15:56 | 0.047281 | 0.00011448 | 5 | 2065 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 353 | 9217_1 | Fittal Street, Beach Road, Richmond | Beach Road | 2024-12-30 05:13 | 2024-12-30 17:41 | 0.017127 | 2.2896e-05 | 1 | 748 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 354 | 9218_1 | Fittal Street, Beach Road, Richmond | Beach Road | 2024-12-30 17:35 | 2024-12-30 17:41 | 0.0012364 | 0.00020607 | 9 | 54 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 355 | 9219_1 | Fittal Street, Richmond | Beach Road | 2024-12-30 05:13 | 2024-12-30 05:58 | 0.009273 | 0.00020607 | 9 | 405 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 356 | 9220_1 | Takaka Hill Highway, Riwaka Valley Road, Dehra Doon | Brooklyn | 2024-12-30 18:18 | 2024-12-30 21:04 | 0.4827 | 0.0029078 | 127 | 21082 | Unplanned | Adverse weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 357 | 9221_1 | Kaiteriteri- Sandy Bay, Marahau, Ngaio Bay | Kaiteriteri | 2024-12-30 19:30 | 2024-12-30 21:40 | 0.78283 | 0.0060218 | 263 | 34190 | Unplanned | Adverse weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 358 | 9222_1 | Tapawera, Kohatu, Stanley Brook, Golden Downs, Motupiko, Tadmor Valley | Kohatu | 2024-12-30 19:43 | 2024-12-30 21:49 | 0.02308 | 0.00018317 | 8 | 1008 | Unplanned | Adverse weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 359 | 9222_1 | Tapawera, Kohatu, Stanley Brook, Golden Downs, Motupiko, Tadmor Valley | Kohatu | 2024-12-30 19:43 | 2024-12-30 22:05 | 1.0144 | 0.0071437 | 312 | 44304 | Unplanned | Adverse weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 360 | 9222_1 | Tapawera, Kohatu, Stanley Brook, Golden Downs, Motupiko, Tadmor Valley | Kohatu | 2024-12-30 19:43 | 2024-12-30 22:06 | 0.25211 | 0.001763 | 77 | 11011 | Unplanned | Adverse weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 361 | 9222_1 | Tapawera, Kohatu, Stanley Brook, Golden Downs, Motupiko, Tadmor Valley | Kohatu | 2024-12-30 19:43 | 2024-12-30 23:32 | 0.083892 | 0.00036634 | 16 | 3664 | Unplanned | Adverse weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 362 | 9222_1 | Tapawera, Kohatu, Stanley Brook, Golden Downs, Motupiko, Tadmor Valley | Kohatu | 2024-12-30 19:43 | 2024-12-30 23:44 | 0.005518 | 2.2896e-05 | 1 | 241 | Unplanned | Adverse weather |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 363 | 9223_1 | Waverly Street, Washbourne Drive, Surrey Road, Rochfort Drive, Hunt Street, Dorset Street | Waverley St | 2024-12-31 10:13 | 2024-12-31 10:41 | 0.59558 | 0.021271 | 929 | 26012 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 364 | 9224_1 | Quarantine Road | Airport | 2025-01-02 06:06 | 2025-01-02 07:12 | 0.077069 | 0.0011677 | 51 | 3366 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 365 | 9225_1 | Nelson Airport | Airport | 2025-01-02 07:14 | 2025-01-02 07:24 | 0.011677 | 0.0011677 | 51 | 510 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 366 | 9226_1 | Tophouse, Howard Valley, Lamb Valley, St Arnaud | Rotoiti | 2025-01-06 12:21 | 2025-01-06 13:11 | 0.072124 | 0.0014425 | 63 | 3150 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 367 | 9226_1 | Tophouse, Howard Valley, Lamb Valley, St Arnaud | Rotoiti | 2025-01-06 12:21 | 2025-01-06 16:47 | 1.9611 | 0.0073726 | 322 | 85652 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 368 | 9226_1 | Tophouse, Howard Valley, Lamb Valley, St Arnaud | Rotoiti | 2025-01-06 12:21 | 2025-01-06 16:49 | 0.55226 | 0.0020607 | 90 | 24120 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 369 | 9227_1 | Vista Drive, Bishopdale | Bishopdale | 2025-01-07 09:04 | 2025-01-07 09:22 | 0.0032971 | 0.00018317 | 8 | 144 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 370 | 9228_1 | Rototai Road, Nees Road, Boundary Road, Tangmere Road, Wadsworth Street, Toiora Close, Arapeta Place Takaka | Commercial St | 2025-01-07 09:33 | 2025-01-07 14:09 | 0.88472 | 0.0032055 | 140 | 38640 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 371 | 9229_1 | Chings road | Dovedale B | 2025-01-07 23:04 | 2025-01-07 23:54 | 0.040069 | 0.00080137 | 35 | 1750 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 372 | 9230_1 | Wills Road, Lower Moutere | Dovedale B | 2025-01-08 09:24 | 2025-01-08 09:37 | 0.0017859 | 0.00013738 | 6 | 78 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 373 | 9231_1 | Boulder Bank Drive, Glenduan | Glenduan | 2025-01-09 09:07 | 2025-01-09 13:08 | 0.005518 | 2.2896e-05 | 1 | 241 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 374 | 9232_1 | Sunset Valley Road, Eggers Road, Deepdale Road, Upper Moutere | Upper Moutere | 2025-01-09 09:32 | 2025-01-09 15:17 | 0.23698 | 0.00068689 | 30 | 10350 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 375 | 9233_1 | Supplejack Valley Road, Sunrise Valley Road, Martin Road | Upper Moutere | 2025-01-09 09:02 | 2025-01-09 16:10 | 0.37239 | 0.00087006 | 38 | 16264 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 376 | 9234_1 | Central Takaka Road, Glenview Road, Hill View Road, Rameka Creek Road | East Takaka | 2025-01-09 10:15 | 2025-01-09 16:08 | 0.40412 | 0.0011448 | 50 | 17650 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 377 | 9235_1 | Parapara Beach Road, Parapara Valley Road, Tukurua Road, Bishop Road, Lookout Road | Bainham | 2025-01-14 09:04 | 2025-01-14 11:56 | 0.87428 | 0.005083 | 222 | 38184 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 378 | 9236_1 | Trafalgar Road, Westdale Road, Stringer Road, Eban Road, Martin Conway Road, Redwood Valley | Mahana | 2025-01-16 09:32 | 2025-01-16 16:41 | 0.67776 | 0.0015799 | 69 | 29601 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 379 | 9236_1 | Trafalgar Road, Westdale Road, Stringer Road, Eban Road, Martin Conway Road, Redwood Valley | Mahana | 2025-01-16 09:38 | 2025-01-16 16:40 | 0.30919 | 0.00073268 | 32 | 13504 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 380 | 9237_1 | Dominion Road, Mapua | Mahana | 2025-01-17 09:55 | 2025-01-17 14:56 | 0.013784 | 4.5793e-05 | 2 | 602 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 381 | 9238_1 | McShanes Road and Appleby Highway. ETA 2PM | Appleby | 2025-01-20 13:10 | 2025-01-20 13:37 | 0.038947 | 0.0014425 | 63 | 1701 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 382 | 9239_1 | Sanderlane Drive, Kakapo Lane, Tui Close, Motueka | Whakarewa St | 2025-01-21 09:32 | 2025-01-21 14:56 | 0.54896 | 0.0016943 | 74 | 23976 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 383 | 9240_1 | Ken Beck Drive, Rabbit Island Road | Appleby | 2025-01-23 09:31 | 2025-01-23 15:54 | 0.043847 | 0.00011448 | 5 | 1915 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 384 | 9241_1 | Ken Beck Drive, Rabbit Island Road | Appleby | 2025-01-24 09:31 | 2025-01-24 14:56 | 0.037207 | 0.00011448 | 5 | 1625 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 385 | 9242_1 | Tangemere road | Commercial St | 2025-01-25 10:50 | 2025-01-25 11:09 | 0.0034803 | 0.00018317 | 8 | 152 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 386 | 9243_1 | Tahuna Area. Including Bullen St, Green St Roto St Golf road Areas | Tahunanui | 2025-01-26 07:34 | 2025-01-26 08:35 | 0.66761 | 0.010944 | 478 | 29158 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 387 | 9243_1 | Tahuna Area. Including Bullen St, Green St Roto St Golf road Areas | Tahunanui | 2025-01-26 07:34 | 2025-01-26 08:53 | 0.30026 | 0.0038008 | 166 | 13114 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 388 | 9243_1 | Tahuna Area. Including Bullen St, Green St Roto St Golf road Areas | Tahunanui | 2025-01-26 07:34 | 2025-01-26 09:09 | 0.69388 | 0.0073039 | 319 | 30305 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 389 | 9243_1 | Tahuna Area. Including Bullen St, Green St Roto St Golf road Areas | Tahunanui | 2025-01-26 07:34 | 2025-01-26 09:11 | 0.039977 | 0.00041214 | 18 | 1746 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 390 | 9243_1 | Tahuna Area. Including Bullen St, Green St Roto St Golf road Areas | Tahunanui | 2025-01-26 07:34 | 2025-01-26 09:43 | 0.26287 | 0.0020378 | 89 | 11481 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 391 | 9243_1 | Tahuna Area. Including Bullen St, Green St Roto St Golf road Areas | Tahunanui | 2025-01-26 07:34 | 2025-01-26 09:45 | 0.59989 | 0.0045793 | 200 | 26200 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 392 | 9243_2 | Tahuna Area. Including Bullen St, Green St Roto St Golf road Areas | Tahunanui | 2025-01-26 09:22 | 2025-01-26 09:32 | 0.077161 | 0.0077161 | 337 | 3370 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 393 | 9243_2 | Tahuna Area. Including Bullen St, Green St Roto St Golf road Areas | Tahunanui | 2025-01-26 09:32 | 2025-01-26 09:40 | 0.061729 | 0.0077161 | 337 | 2696 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MURCHISON | 394 | 9244_1 | Tutaki, Mangles Valley | Longford | 2025-01-29 08:32 | 2025-01-29 09:53 | 0.10386 | 0.0012822 | 56 | 4536 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MURCHISON | 395 | 9244_1 | Tutaki, Mangles Valley | Longford | 2025-01-29 08:32 | 2025-01-29 12:09 | 0.049685 | 0.00022896 | 10 | 2170 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 396 | 9245_1 | Kaiterteri, Kaiteriteri- Sandy Bay, Stephens Bay, Marahau | Kaiteriteri | 2025-01-28 01:55 | 2025-01-28 04:23 | 1.84 | 0.012433 | 543 | 80364 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 397 | 9245_1 | Kaiterteri, Kaiteriteri- Sandy Bay, Stephens Bay, Marahau | Kaiteriteri | 2025-01-28 01:55 | 2025-01-28 06:45 | 0.84991 | 0.0029307 | 128 | 37120 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 398 | 9245_1 | Kaiterteri, Kaiteriteri- Sandy Bay, Stephens Bay, Marahau | Kaiteriteri | 2025-01-28 01:55 | 2025-01-28 06:55 | 1.8065 | 0.0060218 | 263 | 78900 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 399 | 9245_2 | Kaiterteri, Kaiteriteri- Sandy Bay, Stephens Bay, Marahau | Kaiteriteri | 2025-01-28 04:30 | 2025-01-28 06:28 | 0.69436 | 0.0058844 | 257 | 30326 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 400 | 9245_2 | Kaiterteri, Kaiteriteri- Sandy Bay, Stephens Bay, Marahau | Kaiteriteri | 2025-01-28 04:30 | 2025-01-28 06:54 | 0.42862 | 0.0029765 | 130 | 18720 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 401 | 9245_2 | Kaiterteri, Kaiteriteri- Sandy Bay, Stephens Bay, Marahau | Kaiteriteri | 2025-01-28 04:30 | 2025-01-28 07:12 | 0.011128 | 6.8689e-05 | 3 | 486 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 402 | 9245_2 | Kaiterteri, Kaiteriteri- Sandy Bay, Stephens Bay, Marahau | Kaiteriteri | 2025-01-28 04:30 | 2025-01-28 10:25 | 0.317 | 0.00089296 | 39 | 13845 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 403 | 9246_1 | Tarepa Court | Kaiteriteri | 2025-01-28 18:57 | 2025-01-28 19:10 | 0.012501 | 0.00096165 | 42 | 546 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 404 | 9247_1 | Main Road Hope, Clover Road West, Clover Road | Waimea East | 2025-01-31 09:34 | 2025-01-31 14:47 | 0.1505 | 0.00048082 | 21 | 6573 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 405 | 9248_1 | Chings road | Dovedale B | 2025-02-02 08:00 | 2025-02-02 08:28 | 0.022438 | 0.00080137 | 35 | 980 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 406 | 9249_1 | Founders to Dodson Valley areas | Atawhai | 2025-02-10 05:10 | 2025-02-10 06:29 | 0.62042 | 0.0078535 | 343 | 27097 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 407 | 9249_1 | Founders to Dodson Valley areas | Atawhai | 2025-02-10 05:10 | 2025-02-10 06:32 | 0.27975 | 0.0034116 | 149 | 12218 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 408 | 9249_1 | Founders to Dodson Valley areas | Atawhai | 2025-02-10 05:10 | 2025-02-10 07:03 | 0.020698 | 0.00018317 | 8 | 904 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 409 | 9249_1 | Founders to Dodson Valley areas | Atawhai | 2025-02-10 05:10 | 2025-02-10 08:19 | 2.1464 | 0.011357 | 496 | 93744 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 410 | 9250_1 | Golf Haven Way, Cohen Place, Chandler Street, Otterson Street, Bolt Road, Tahunanui | Bolt Road | 2025-02-10 09:39 | 2025-02-10 15:38 | 0.67402 | 0.0018775 | 82 | 29438 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 411 | 9251_1 | Collingwood-Bainham Main Road, Aorere Valley Road, Carter Road, Cook Road, Hickmott Road, James Road, MacKay Pass Road, Pah Road South, Quartz Range Road, Solly Road | Bainham | 2025-02-11 09:44 | 2025-02-11 16:26 | 1.2794 | 0.0031826 | 139 | 55878 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 412 | 9252_1 | Tapawera areas, Valley road.Stanley Brook, Glenrae. | Kohatu | 2025-02-12 18:25 | 2025-02-12 20:11 | 0.019416 | 0.00018317 | 8 | 848 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 413 | 9252_1 | Tapawera areas, Valley road.Stanley Brook, Glenrae. | Kohatu | 2025-02-12 18:24 | 2025-02-12 19:52 | 0.62864 | 0.0071437 | 312 | 27456 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 414 | 9252_1 | Tapawera areas, Valley road.Stanley Brook, Glenrae. | Kohatu | 2025-02-12 18:24 | 2025-02-12 19:53 | 0.15691 | 0.001763 | 77 | 6853 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 415 | 9252_1 | Tapawera areas, Valley road.Stanley Brook, Glenrae. | Kohatu | 2025-02-12 18:24 | 2025-02-12 19:55 | 0.0020836 | 2.2896e-05 | 1 | 91 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 416 | 9252_1 | Tapawera areas, Valley road.Stanley Brook, Glenrae. | Kohatu | 2025-02-12 18:24 | 2025-02-12 20:48 | 0.052753 | 0.00036634 | 16 | 2304 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 417 | 9253_1 | Takaka-Collingwood Highway, Rangihaeata Road, Onahau Road, Fraser Road | Waitapu | 2025-02-13 09:32 | 2025-02-13 15:11 | 1.009 | 0.0029765 | 130 | 44070 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 418 | 9254_1 | Kohatu Cnr. | Kohatu | 2025-02-13 17:59 | 2025-02-13 18:10 | 0.00025186 | 2.2896e-05 | 1 | 11 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 419 | 9254_1 | Kohatu Cnr. | Kohatu | 2025-02-13 18:03 | 2025-02-13 18:10 | 0.0038466 | 0.00054951 | 24 | 168 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 420 | 9255_1 | Lansdowne Road, Appleby | Appleby | 2025-02-17 09:59 | 2025-02-17 16:00 | 0.36369 | 0.0010074 | 44 | 15884 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 421 | 9256_1 | Wharariki Road, Farewell Spit Road, Seddon Street, Ward Place | Pakawau | 2025-02-19 09:34 | 2025-02-19 16:45 | 0.1875 | 0.00043503 | 19 | 8189 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 422 | 9257_1 | Onahau Road | Waitapu | 2025-02-19 19:25 | 2025-02-19 19:52 | 0.0086548 | 0.00032055 | 14 | 378 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 423 | 9258_1 | Montebello Avenue, Greenfield Lane, Hills Tops Way, Village Lane, Waterson Lane | Polstead | 2025-02-20 09:32 | 2025-02-20 14:40 | 0.57122 | 0.0018546 | 81 | 24948 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 424 | 9259_1 | Takaka-Collingwood Highway, Rangihaeata Road, Onahau Road, Fraser Road | Waitapu | 2025-02-20 09:35 | 2025-02-20 15:58 | 1.14 | 0.0029765 | 130 | 49790 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 425 | 9260_1 | Buller Gorge and Shenandoah Highway. | Maruia | 2025-02-21 05:33 | 2025-02-21 06:45 | 0.041214 | 0.00057241 | 25 | 1800 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 426 | 9261_1 | Appleby Highway, Blackbyre Road, Richmond | Appleby | 2025-02-23 09:03 | 2025-02-23 17:16 | 0.47409 | 0.00096165 | 42 | 20706 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 427 | 9262_1 | The Coastal Highway, Research Orchard Road, Ridgeview Road, Redwood Lane, Pukeko Lane, Kohuhu Lane, Ribbonwood Lane, Shirtcliff Lane | Appleby | 2025-02-24 09:32 | 2025-02-24 15:29 | 1.5285 | 0.0042816 | 187 | 66759 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 428 | 9263_1 | Matata Road, Parapara | Bainham | 2025-02-25 09:45 | 2025-02-25 13:49 | 0.011173 | 4.5793e-05 | 2 | 488 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 429 | 9264_1 | Cable Bay Road, Kokorua Road, Maori Pa Road, Whangamoa Road, Hollyman Road | Hira | 2025-02-25 09:30 | 2025-02-25 15:45 | 1.2536 | 0.0033429 | 146 | 54750 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 430 | 9265_1 | Chamberlain Street, College Street, Motueka | Whakarewa St | 2025-02-26 09:30 | 2025-02-26 14:46 | 0.13747 | 0.00043503 | 19 | 6004 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 431 | 9266_1 | Langdale Drive, Iris Drive, Richmond | Wensley Road | 2025-02-26 09:00 | 2025-02-26 18:41 | 0.026606 | 4.5793e-05 | 2 | 1162 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 432 | 9267_1 | Collingwood-Bainham Main Road | Bainham | 2025-02-27 09:46 | 2025-02-27 14:55 | 0.007075 | 2.2896e-05 | 1 | 309 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 433 | 9268_1 | Cable Bay Road, Kokorua Road, Maori Pa Road, Whangamoa Road, Hollyman Road | Hira | 2025-02-27 09:30 | 2025-02-27 15:41 | 1.2402 | 0.0033429 | 146 | 54166 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 434 | 9269_1 | Factory Road, Brfightwater | Waimea East | 2025-03-20 14:12 | 2025-03-20 15:57 | 0.0024041 | 2.2896e-05 | 1 | 105 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 435 | 9270_1 | Waverley Street, Wensley Road, Washbourne Drive, Dorset Street | Waverley St | 2025-02-28 14:43 | 2025-02-28 15:23 | 0.22347 | 0.0055867 | 244 | 9760 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 436 | 9270_1 | Waverley Street, Wensley Road, Washbourne Drive, Dorset Street | Waverley St | 2025-02-28 14:43 | 2025-02-28 15:38 | 0.16497 | 0.0029994 | 131 | 7205 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 437 | 9270_1 | Waverley Street, Wensley Road, Washbourne Drive, Dorset Street | Waverley St | 2025-02-28 14:43 | 2025-02-28 15:44 | 0.71789 | 0.011769 | 514 | 31354 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 438 | 9270_1 | Waverley Street, Wensley Road, Washbourne Drive, Dorset Street | Waverley St | 2025-02-28 14:43 | 2025-02-28 18:23 | 0.20149 | 0.00091586 | 40 | 8800 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 439 | 9270_2 | Waverley Street, Wensley Road, Washbourne Drive, Dorset Street | Waverley St | 2025-02-28 15:40 | 2025-02-28 15:44 | 0.034345 | 0.0085861 | 375 | 1500 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 440 | 9270_3 | Waverley Street, Wensley Road, Washbourne Drive, Dorset Street | Waverley St | 2025-02-28 16:00 | 2025-02-28 16:08 | 0.094699 | 0.011837 | 517 | 4136 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 441 | 9271_1 | Factory Road, Brightwater | Waimea East | 2025-03-03 06:51 | 2025-03-03 07:12 | 0.26109 | 0.012433 | 543 | 11403 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 442 | 9271_1 | Factory Road, Brightwater | Waimea East | 2025-03-03 07:12 | 2025-03-03 13:32 | 0.11311 | 0 | 0 | 4940 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 443 | 9271_2 | Factory Road, Brightwater | Waimea East | 2025-03-03 08:05 | 2025-03-03 13:38 | 0.022873 | 6.8689e-05 | 3 | 999 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 444 | 9271_2 | Factory Road, Brightwater | Waimea East | 2025-03-03 08:15 | 2025-03-03 13:29 | 0.050326 | 0.00016027 | 7 | 2198 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 445 | 9272_1 | Lightband Road | Waimea East | 2025-03-03 14:23 | 2025-03-03 14:25 | 0.00059531 | 0.00029765 | 13 | 26 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 446 | 9272_1 | Lightband Road | Waimea East | 2025-03-03 14:23 | 2025-03-03 15:05 | 0.0067315 | 0.00016027 | 7 | 294 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 447 | 9273_1 | Homestead Avenue, Ashley Terrace, Canary Place, McLaughlin Lane | Isel | 2025-03-03 09:34 | 2025-03-03 15:26 | 0.38686 | 0.001099 | 48 | 16896 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 448 | 9274_1 | Pupu Valley Road, Pupu Springs Road, One Spec Road, Balck Road, Mahutonga Rise, Takaka | Commercial St | 2025-03-04 09:00 | 2025-03-04 15:01 | 0.31409 | 0.00087006 | 38 | 13718 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 449 | 9275_1 | Wharariki Road, Farewell Spit Road, Seddon Street, Ward Place | Pakawau | 2025-03-05 09:31 | 2025-03-05 15:48 | 0.16401 | 0.00043503 | 19 | 7163 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 450 | 9276_1 | Pupu Valley Road, Pupu Springs Road, One Spec Road, Balck Road, Mahutonga Rise, Takaka | Commercial St | 2025-03-06 09:26 | 2025-03-06 15:16 | 0.30452 | 0.00087006 | 38 | 13300 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 451 | 9277_1 | Crescent St & Shearer Richmond | Waverley St | 2025-03-06 23:10 | 2025-03-07 00:22 | 0.065942 | 0.00091586 | 40 | 2880 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 452 | 9278_1 | Redwood Valley - Moutere Highway area from Russes Corner | Redwoods Valley | 2025-03-08 14:09 | 2025-03-08 15:26 | 0.58356 | 0.0075787 | 331 | 25487 | Unplanned | Third party interference |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 453 | 9279_1 | Main Road Stoke, Songer Street, Putaitai Street | Isel | 2025-03-09 23:15 | 2025-03-10 00:27 | 0.093967 | 0.0013051 | 57 | 4104 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 454 | 9280_1 | Pupu Valley Road, Pupu Springs Road, One Spec Road, Balck Road, Mahutonga Rise, Takaka | Commercial St | 2025-03-11 09:08 | 2025-03-11 15:26 | 0.32888 | 0.00087006 | 38 | 14364 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 455 | 9281_1 | One Spec Road, Kotinga | Commercial St | 2025-03-12 09:46 | 2025-03-12 15:44 | 0.049181 | 0.00013738 | 6 | 2148 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 456 | 9282_1 | Langdale Drive, Iris Drive, Richmond | Wensley Road | 2025-03-12 09:04 | 2025-03-12 15:51 | 0.018638 | 4.5793e-05 | 2 | 814 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 457 | 9283_1 | Main Road Stoke, Songer Street, Putaitai Street | Isel | 2025-03-12 22:16 | 2025-03-12 23:32 | 0.099187 | 0.0013051 | 57 | 4332 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 458 | 9284_1 | Pupu Valley Road, Pupu Springs Road, One Spec Road, Balck Road, Mahutonga Rise, Takaka | Commercial St | 2025-03-13 09:15 | 2025-03-13 15:28 | 0.32453 | 0.00087006 | 38 | 14174 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 459 | 9285_1 | Edward Street, Gossey Drive North, Fellbridge Rise, Wakefield | Higgins Road | 2025-03-14 09:35 | 2025-03-14 11:26 | 0.053371 | 0.00048082 | 21 | 2331 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 460 | 9286_1 | Anatoki Track Road, Long Plain Road, McCallum Road, Kotinga | Commercial St | 2025-03-14 09:36 | 2025-03-14 14:06 | 0.055638 | 0.00020607 | 9 | 2430 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 461 | 9287_1 | Packard Road, Takaka | East Takaka | 2025-03-14 14:48 | 2025-03-14 14:58 | 0.00664 | 0.000664 | 29 | 290 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 462 | 9288_1 | Abel Tasman Drive | Pohara | 2025-03-16 07:48 | 2025-03-16 08:04 | 0.0054951 | 0.00034345 | 15 | 240 | Unplanned | Wildlife |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 463 | 9289_1 | Collingwood, Whanganui, Pakawau, Parapara, Rockville | Collingwood 33kV | 2025-03-18 09:02 | 2025-03-18 13:18 | 0.011723 | 4.5793e-05 | 2 | 512 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 464 | 9289_1 | Collingwood, Whanganui, Pakawau, Parapara, Rockville | Collingwood 33kV | 2025-03-18 09:02 | 2025-03-18 13:38 | 3.5831 | 0.012982 | 567 | 156492 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 465 | 9289_1 | Collingwood, Whanganui, Pakawau, Parapara, Rockville | Collingwood 33kV | 2025-03-18 09:02 | 2025-03-18 13:39 | 2.854 | 0.010303 | 450 | 124650 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 466 | 9289_1 | Collingwood, Whanganui, Pakawau, Parapara, Rockville | Collingwood 33kV | 2025-03-18 13:29 | 2025-03-18 13:34 | 0.00022896 | 4.5793e-05 | 2 | 10 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 467 | 9290_1 | Pupu Valley Road, Pupu Springs Road, One Spec Road, Balck Road, Mahutonga Rise, Takaka | Commercial St | 2025-03-18 09:02 | 2025-03-18 15:12 | 0.32192 | 0.00087006 | 38 | 14060 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 468 | 9291_1 | Neudorf Road, Rosedale Road, Rose Road, Blackbird Valley Road | Upper Moutere | 2025-03-19 14:00 | 2025-03-19 14:41 | 0.13424 | 0.0032742 | 143 | 5863 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 469 | 9292_1 | Aston Place, Farnham Drive, Hill Street, Hunter Avenue, Idesia Grove, Ledger Close, Queen Street, Rochfort Drive, Washbourn Drive, Richmond | Waverley St | 2025-03-19 09:30 | 2025-03-19 15:28 | 0.42624 | 0.0011906 | 52 | 18616 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 470 | 9292_1 | Aston Place, Farnham Drive, Hill Street, Hunter Avenue, Idesia Grove, Ledger Close, Queen Street, Rochfort Drive, Washbourn Drive, Richmond | Waverley St | 2025-03-19 09:30 | 2025-03-19 15:30 | 1.731 | 0.0048082 | 210 | 75600 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 471 | 9293_1 | Cemetery Road, Long Plain Road, Kotinga | Commercial St | 2025-03-20 09:40 | 2025-03-20 13:21 | 0.02024 | 9.1586e-05 | 4 | 884 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 472 | 9294_1 | Pigeon Valley Road, Golf Road, Sharp Road, Watkins Lane, Clifford Road, Windlesham Place | Spring Grove | 2025-03-20 09:34 | 2025-03-20 15:57 | 1.2189 | 0.0031826 | 139 | 53237 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 473 | 9295_1 | Dorset Street, Oxford Street, Richmond - POSTPONED TO ALTERNATE DATE. Due to weather. | Waverley St | 2025-03-18 09:33 | 2025-03-18 16:02 | 0.31173 | 0.00080137 | 35 | 13615 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | KIKIWA | 474 | 9296_1 | Lamb Valley Road | Rotoiti | 2025-03-19 09:02 | 2025-03-19 13:50 | 0.085724 | 0.00029765 | 13 | 3744 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 475 | 9297_1 | Bishop Road, Lookout Road, Parapara Beach Road, Prior Road, Takaka- Collingwood Highway, Tukurua Road, - POSTPONED TO ALTERNATE DATE. - due to contractor manpower shortage | Bainham | 2025-03-24 09:33 | 2025-03-24 13:22 | 0.82844 | 0.0036176 | 158 | 36182 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 476 | 9298_1 | Pigeon Valley Road, Golf Road, Sharp Road, Watkins Lane | Spring Grove | 2025-03-25 09:32 | 2025-03-25 15:52 | 0.98317 | 0.0025873 | 113 | 42940 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 477 | 9299_1 | Valhalla Drive, Primrose Place, Kihilla Road, George Kidd Street, Centenary Place, Richmond | Paton Road | 2025-03-25 09:48 | 2025-03-25 15:56 | 0.9774 | 0.002656 | 116 | 42688 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 478 | 9300_1 | Wadsworth Street. Rototai Road, | Commercial St | 2025-03-27 08:52 | 2025-03-27 09:14 | 0.070521 | 0.0032055 | 140 | 3080 | Unplanned | Defective equipment |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 479 | 9301_1 | Whakarewa Street, College Street, Queen Victoria Street, Chamberlain Street, Pah Street, Pamarika Street, Motueka | Queen Victoria | 2025-03-27 09:31 | 2025-03-27 15:33 | 1.235 | 0.0034116 | 149 | 53938 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 480 | 9302_1 | Marsden Valley Road, Stoke - POSTPONED TO ALTERNATE DATE. Staff issue. | Stoke | 2025-03-29 09:08 | 2025-03-29 09:24 | 0.001099 | 6.8689e-05 | 3 | 48 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 481 | 9303_1 | Lower Moutere, Tasman, Kina. | Tasman | 2025-03-30 08:11 | 2025-03-30 09:17 | 1.0699 | 0.016211 | 708 | 46728 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 482 | 9303_1 | Lower Moutere, Tasman, Kina. | Tasman | 2025-03-30 08:11 | 2025-03-30 09:40 | 0.0040756 | 4.5793e-05 | 2 | 178 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 483 | 9303_1 | Lower Moutere, Tasman, Kina. | Tasman | 2025-03-30 08:11 | 2025-03-30 09:43 | 0.12218 | 0.001328 | 58 | 5336 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 484 | 9303_1 | Lower Moutere, Tasman, Kina. | Tasman | 2025-03-30 08:11 | 2025-03-30 09:54 | 0.082541 | 0.00080137 | 35 | 3605 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 485 | 9304_1 | Appleby Highway, Blackbyre Road, Richmond | Appleby | 2025-03-30 09:34 | 2025-03-30 15:00 | 0.3135 | 0.00096165 | 42 | 13692 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 486 | 9326_1 | Sutton Street, Gilbert Street, Warren Kelly Street, Richmond | Darcy St | 2024-12-18 09:02 | 2024-12-18 09:31 | 0.044488 | 0.0015341 | 67 | 1943 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 487 | 9327_1 | Sutton Street, Gilbert Street, Warren Kelly Street, Richmond | Darcy St | 2024-12-18 16:31 | 2024-12-18 16:58 | 0.04142 | 0.0015341 | 67 | 1809 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 488 | 9328_1 | Hursthouse Street, Hurley Road, Mytton Heights, Stony Ridge Way, Starnes Road, Chamberlain Street, Motueka Valley Highway | Dovedale A | 2024-05-20 09:31 | 2024-05-20 15:28 | 0.30244 | 0.00084717 | 37 | 13209 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 489 | 9331_1 | Cable Bay Road | Hira | 2024-06-12 09:51 | 2024-06-12 16:01 | 0.067773 | 0.00018317 | 8 | 2960 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 490 | 9332_1 | McShanes Road | Richmond West | 2024-07-17 08:53 | 2024-08-02 11:52 | 0.53163 | 2.2896e-05 | 1 | 23219 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 491 | 9333_1 | Takaka hill | Brooklyn | 2024-07-24 09:31 | 2024-07-24 15:43 | 0.0085175 | 2.2896e-05 | 1 | 372 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MURCHISON | 492 | 9338_1 | Matiri Hydro | Matiri Hydro | 2024-08-01 11:14 | 2024-08-01 11:56 | 0.00096165 | 2.2896e-05 | 1 | 42 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 493 | 9341_1 | Deepdale Road, Upper Moutere - POSTPONED TO ALTERNATE DATE. Contractor planning issue. | Upper Moutere | 2024-11-18 11:03 | 2024-11-18 16:16 | 0.0215 | 6.8689e-05 | 3 | 939 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | STOKE | 494 | 9342_1 | Appleby Highway, Richmond | Appleby | 2025-03-06 09:32 | 2025-03-07 16:52 | 0.043045 | 2.2896e-05 | 1 | 1880 | Planned | Planned interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MURCHISON | 495 | 9343_1 | Matiri Hydro | Matiri Hydro | 2025-03-18 20:52 | 2025-03-19 08:10 | 0.015524 | 2.2896e-05 | 1 | 678 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUPIPI | 496 | 9345_1 | Richmond Road | Pohara | 2024-08-24 11:28 | 2024-08-24 15:00 | 0.004854 | 2.2896e-05 | 1 | 212 | Unplanned | Vegetation |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 497 | 9350_1 | Whakarewa trip - CB9 | Whakarewa | 2024-09-08 19:49 | 2024-09-08 19:52 | 0.078855 | 0.026285 | 1148 | 3444 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Tasman | 2025 | MOTUEKA | 498 | 9395_1 | Upper Takaka | Whakarewa | 2024-08-26 16:32 | 2024-08-26 16:34 | 0.01589 | 0.007945 | 347 | 694 | Unplanned | Cause unknown |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 9 | MF552 | Lake Waitaki GXP | 464FED | 2024-04-03 08:00 | 2024-04-03 16:39 | 0.92233 | 0.0017771 | 24 | 12456 | Planned | 11.0 Planned Shutdown | To Isolate 33kV Line (Being Constructed) & 11kV Line @ Lake Waitaki GXP to install New Pole 1 & Pole B and install new 33kV Line between Pole 41753 and new Pole B | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 10 | PR119 | Lake Ohau Rd | 490FED | 2024-04-03 08:06 | 2024-04-04 15:34 | 0.33173 | 0.00074047 | 10 | 4480 | Planned | 11.0 Planned Shutdown | Replacing Poles and Crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 11 | MF553 | Waitaki GXP | 464FED | 2024-04-04 08:21 | 2024-04-04 16:49 | 0.90278 | 0.0017771 | 24 | 12192 | Planned | 11.0 Planned Shutdown | To Isolate 11kV & 33kV Lines to reconfigure 33kV Network | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 12 | PR127 | Lake Ohau Rd | 490FED | 2024-04-04 09:03 | 2024-04-04 16:07 | 0.094187 | 0.00022214 | 3 | 1272 | Planned | 11.0 Planned Shutdown | Replacing Pole 17712 & 38863 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 13 | NJ429 | Kurow Duntroon Rd | 470FED | 2024-04-05 08:31 | 2024-04-05 14:22 | 1.0401 | 0.0030359 | 41 | 14046 | Planned | 11.0 Planned Shutdown | Replacing Pole 17177 and 11kVLinks Pole 17182 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 14 | F5051 | 344 Grants Rd | 411FED | 2024-04-07 08:43 | 2024-04-07 10:30 | 0.007923 | 7.4047e-05 | 1 | 107 | Unplanned | 6.0 Wildlife | Rat @ Pole 32772 blew 11kV Links Pole 32770 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 15 | F4649 F16210 | Crm Spring Field @ Fortification Rd | 416FED | 2024-04-08 12:30 | 2024-04-08 13:35 | 0.26953 | 0.0041466 | 56 | 3640 | Unplanned | 8.0 Defective Equipment | Broken Kidney on Pole 30377 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 16 | F16180 | Otematata Substation | 425FED | 2024-04-09 08:03 | 2024-04-09 08:27 | 0.22747 | 0.009478 | 128 | 3072 | Planned | 11.0 Planned Shutdown | Planned Outage for Close Approach Permit 8593 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 17 | NJ432 NJ433 16179 | Livingston Rd / Danseys Pass Rd / Dip Hill Rd | 421FED | 2024-04-09 08:22 | 2024-04-09 16:45 | 1.7542 | 0.0058497 | 79 | 23691 | Planned | 11.0 Planned Shutdown | Replacing Poles, Crossarms and Maintenance & Faulted ABS1143 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 18 | F4436 | 234 Papakaio Rd | 457FED | 2024-04-10 05:47 | 2024-04-10 06:30 | 0.003184 | 7.4047e-05 | 1 | 43 | Unplanned | 6.0 Wildlife | Rat Blew 11kV Links Pole 42086 (Pole 23006) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 19 | F5053 | 331 Gards Rd | 411FED | 2024-04-10 08:22 | 2024-04-10 11:00 | 0.011699 | 7.4047e-05 | 1 | 158 | Unplanned | 9.0 Cause Unknown | No Power 11kV Links Blown @ Pole 32762 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 20 | PR131 | Homestead | 430FED | 2024-04-10 08:46 | 2024-04-10 17:06 | 1.6231 | 0.0033321 | 45 | 21920 | Planned | 11.0 Planned Shutdown | Replacing Pole 15772 and H Structure Pole 15768/15769 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 21 | F16181 | Rocklands Rd | 416FED | 2024-04-16 08:51 | 2024-04-16 08:54 | 0.037097 | 0.012366 | 167 | 501 | Unplanned | 5.0 Third party Interference | NWL Contractor was Tree Felling Rocklands Rd and a Branch hit the 11kV Line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 22 | PR145 | Oamaru Duntroon Rd | 470FED | 2024-04-16 09:05 | 2024-04-16 11:56 | 0.15194 | 0.00088856 | 12 | 2052 | Planned | 11.0 Planned Shutdown | Replacing Transformer T4505 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 23 | NJ435 | Georgetown Pukeuri Rd | 456FED | 2024-04-17 08:47 | 2024-04-17 15:22 | 0.29248 | 0.00074047 | 10 | 3950 | Planned | 11.0 Planned Shutdown | Replacing Poles and Crossarm and Installing Transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 24 | NJ437A | 11kV Line Katiki | 480FED | 2024-04-18 08:02 | 2024-04-18 16:16 | 0.62184 | 0.0012588 | 17 | 8398 | Planned | 11.0 Planned Shutdown | Replacing, Poles Crossarms & Conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 25 | NJ437B | 11kV Line Katiki | 480FED | 2024-04-19 08:04 | 2024-04-19 15:15 | 0.54254 | 0.0012588 | 17 | 7327 | Planned | 11.0 Planned Shutdown | Replacing, Poles Crossarms & Conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 26 | NJ437C | 11kV Line Katiki | 480FED | 2024-04-23 08:07 | 2024-04-23 16:29 | 0.63191 | 0.0012588 | 17 | 8534 | Planned | 11.0 Planned Shutdown | Replacing, Poles Crossarms & Conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 27 | NJ438A | 11kV Line Katiki Straight | 480FED | 2024-04-24 08:00 | 2024-04-24 15:58 | 1.0972 | 0.0022954 | 31 | 14818 | Planned | 11.0 Planned Shutdown | Replacing, Poles Crossarms & 11kV Conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 28 | NJ438B | 11kV Line Katiki Straight | 480FED | 2024-04-26 08:01 | 2024-04-26 14:43 | 0.92277 | 0.0022954 | 31 | 12462 | Planned | 11.0 Planned Shutdown | Replacing, Poles Crossarms & 11kV Conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 29 | F5206 | 68/69 Grants Rd | 483FED | 2024-04-29 07:52 | 2024-04-29 09:45 | 0.016735 | 0.00014809 | 2 | 226 | Unplanned | 6.0 Wildlife | Swan Hit 11kV Line between Pole 25787 17285 Blew 11kV Links Pole 17284 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 30 | NJ438C | 11kV Line Katiki Straight | 480FED | 2024-04-29 08:00 | 2024-04-29 16:23 | 1.1546 | 0.0022954 | 31 | 15593 | Planned | 11.0 Planned Shutdown | Replacing, Poles Crossarms & 11kV Conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 31 | NJ439 | Brinkburn St Oamaru | 409FED | 2024-04-29 09:11 | 2024-04-29 16:55 | 1.4774 | 0.003184 | 43 | 19952 | Planned | 11.0 Planned Shutdown | Replacing Pole 37589 & Pole 11994 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 32 | F5059 | Omarama Twizel 33kV Line | 2192FED | 2024-04-30 01:37 | 2024-04-30 03:55 | 0.80444 | 0.049389 | 667 | 10864 | Unplanned | 9.0 Cause Unknown | CB2192 Tripped | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 33 | NJ438D | 11kV Line Katiki Straight | 480FED | 2024-04-30 08:00 | 2024-04-30 16:07 | 1.1179 | 0.0022954 | 31 | 15097 | Planned | 11.0 Planned Shutdown | Replacing, Poles Crossarms & 11kV Conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 34 | F4668 | 11kV Line Peaks Rd | 449FED | 2024-04-30 13:44 | 2024-04-30 14:22 | 0.04502 | 0.0011847 | 16 | 608 | Unplanned | 8.0 Defective Equipment | No Nuts on Insulaotrs, Replaced Crossarms Pole 38095 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 35 | F5160 | 741 Weston Ngapara Rd | 449FED | 2024-04-30 19:33 | 2024-05-01 07:50 | 0.054572 | 7.4047e-05 | 1 | 737 | Unplanned | 9.0 Cause Unknown | Blown 11kV Links Pole 41699 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 36 | F4712 WA32086 | R686/741 Weston Ngapara Rd | 449FED | 2024-05-01 07:00 | 2024-05-01 07:53 | 0.0039245 | 7.4047e-05 | 1 | 53 | Unplanned | 9.0 Cause Unknown | 11kV Link Blown at Pole 41699 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 37 | NJ443 | McIntyre 11kv Line Ruataniwha Substation | 526FED | 2024-05-02 09:30 | 2024-05-02 13:25 | 0.31322 | 0.0013328 | 18 | 4230 | Planned | 11.0 Planned Shutdown | Connecting New Network 11kV Bypass Line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 38 | F4446 | 22 Kuriheka Rd | 415FED | 2024-05-03 08:19 | 2024-05-03 09:45 | 0.012736 | 0.00014809 | 2 | 172 | Unplanned | 9.0 Cause Unknown | 11kV Links Blown @ Pole 26571 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 39 | NJ440 | 11kV Line Teschemakers Rd | 414FED | 2024-05-03 08:30 | 2024-05-03 15:05 | 0.20474 | 0.00051833 | 7 | 2765 | Planned | 11.0 Planned Shutdown | Replacing 11kV Pole 38225 & 25063 and Replacing 11kV Links Pole 25057 & 25070 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 40 | NJ448 | 11kV Line Taipo Rd | 414FED | 2024-05-03 08:35 | 2024-05-03 16:46 | 0.21814 | 0.00044428 | 6 | 2946 | Planned | 11.0 Planned Shutdown | Replacing Poles & Crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 41 | F4681 | Frenchs Rd | 415FED | 2024-05-10 12:01 | 2024-05-10 12:26 | 0.038874 | 0.001555 | 21 | 525 | Unplanned | 8.0 Defective Equipment | No Nuts on 11kV Insulator at Pole 25709 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 42 | F5060 F16087 | Ngapara Zone Substation | 501FED | 2024-05-11 17:59 | 2024-05-11 19:13 | 0.61088 | 0.039763 | 537 | 8250 | Unplanned | 8.0 Defective Equipment | VT on T1 transformer Faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 43 | PR157A | Pinot Noir Court Omarama | 423FED | 2024-05-15 09:20 | 2024-05-15 16:01 | 0.35631 | 0.00088856 | 12 | 4812 | Planned | 11.0 Planned Shutdown | Replacing Transformer T5510.1 and installing new SFB | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 44 | PR157B/WA32896 | Pinot Noir Court Omarama | 423FED | 2024-05-16 09:43 | 2024-05-16 15:15 | 0.27901 | 0.0017771 | 24 | 3768 | Unplanned | 8.0 Defective Equipment | Replacing Transformer T5510.1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 45 | F5104 | 344 Grants Rd | 411FED | 2024-05-17 07:56 | 2024-05-17 22:03 | 0.0094039 | 7.4047e-05 | 1 | 127 | Unplanned | 6.0 Wildlife | Rodents Blew 11kV Links Pole 32770 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 46 | F5103 | 1119 Georgetown Pukeuri Rd | 456FED | 2024-05-18 04:05 | 2024-05-18 05:07 | 0.0091818 | 0.00014809 | 2 | 124 | Unplanned | 6.0 Wildlife | Possom Blew 11kV Links @ Pole 23878 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 47 | F5105 | 115 Maheno Kakanui Rd | 416FED | 2024-05-18 07:53 | 2024-05-18 09:08 | 0.0055535 | 7.4047e-05 | 1 | 75 | Unplanned | 6.0 Wildlife | Possom Blew 11KV Links @ Pole 71933 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 48 | PR164 | Richmond Rd | 435FED | 2024-05-20 09:48 | 2024-05-20 12:07 | 0.051462 | 0.00037023 | 5 | 695 | Planned | 11.0 Planned Shutdown | Change Cross arms on Pole 41807 and Resag 11kV Line between Pole 22227 and 33042 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 49 | PR162 | Richmond Rd | 435FED | 2024-05-20 09:52 | 2024-05-20 15:56 | 0.080859 | 0.00022214 | 3 | 1092 | Planned | 11.0 Planned Shutdown | Changing Pole 21930 live line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 50 | NJ455 | 33kV/11kV Line Twizel Omarama | 492FED | 2024-05-21 08:06 | 2024-05-21 17:43 | 0.42096 | 0.00074047 | 10 | 5685 | Planned | 11.0 Planned Shutdown | Installing Temp Links Pole 39776, Replacing Poles, Replace ABS3411 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 51 | NJ449 | 11kV Line Papakaio Rd | 457FED | 2024-05-21 09:04 | 2024-05-21 15:25 | 1.0438 | 0.0027397 | 37 | 14097 | Planned | 11.0 Planned Shutdown | Isolating 11kV Line @ Pole 42088 for Omexon to change Transpower Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 52 | PI151 | 11kV Line Mckenzie Rd | 421FED | 2024-05-21 09:43 | 2024-05-21 16:43 | 0.1866 | 0.00044428 | 6 | 2520 | Planned | 11.0 Planned Shutdown | Replacing LV Pole 37163c and 11kV Crossarm on Pole 22465 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 53 | NJ456 | Twizel Omarama Rd | 492FED | 2024-05-22 08:29 | 2024-05-22 15:49 | 0.29174 | 0.00066642 | 9 | 3940 | Planned | 11.0 Planned Shutdown | Replacing 33kV/11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 54 | NJ450 | 11kV Line Georgetown Pukeuri Rd | 456FED | 2024-05-22 08:41 | 2024-05-22 15:19 | 0.32418 | 0.00081451 | 11 | 4378 | Planned | 11.0 Planned Shutdown | Isolating 11kV Line @ Pole 23796 for Omexon to change Transpower Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 55 | PI157 | Twizel Omarama Rd | 492FED | 2024-05-23 08:08 | 2024-05-23 13:52 | 0.22303 | 0.00066642 | 9 | 3012 | Planned | 11.0 Planned Shutdown | Replacing 33kV/11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 56 | F15988 | Serpentine Rd | 415FED | 2024-05-26 04:39 | 2024-05-26 09:25 | 0.68871 | 0.010663 | 144 | 9301 | Unplanned | 2.0 Vegetation | Tree Through 11kV Line Sepentine Rd Burnt Off 11kV Jumper Pole 18598 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 57 | F5169 | Danseys Pass | 421FED | 2024-05-26 14:05 | 2024-05-26 20:53 | 0.29337 | 0.0072566 | 98 | 3962 | Unplanned | 3.0 Adverse Weather | Wire off insulator @ Pole 23357 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 58 | F5067 | Smith Rd | 421FED | 2024-05-26 15:43 | 2024-05-26 19:31 | 0.36187 | 0.0034802 | 47 | 4887 | Unplanned | 2.0 Vegetation | Trees Brought down 11kV Line Smith Rd near Pole 22748 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 59 | NJ459A | 11kV Line Whartons Rd | 415FED | 2024-05-27 08:37 | 2024-05-27 15:35 | 0.52618 | 0.0012588 | 17 | 7106 | Planned | 11.0 Planned Shutdown | Replacing Crossarms, Pole 25543 and 11kV Conductor between Pole 37922 - 25554 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 60 | NJ458A | Twizel Omarama Rd | 492FED | 2024-05-27 10:08 | 2024-05-27 16:11 | 0.026879 | 7.4047e-05 | 1 | 363 | Planned | 11.0 Planned Shutdown | Replacing 33kV/11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 61 | PR178 | Tokarahi Tapui Rd | 421FED | 2024-05-27 11:00 | 2024-05-27 12:51 | 0.016438 | 0.00014809 | 2 | 222 | Planned | 11.0 Planned Shutdown | Hedge Trimming @ Pole 10098 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 62 | NJ458B | Twizel Omarama Rd | 492FED | 2024-05-28 08:00 | 2024-05-28 16:40 | 0.038504 | 7.4047e-05 | 1 | 520 | Planned | 11.0 Planned Shutdown | Replacing 33kV/11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 63 | NJ459B | 11kV Line Whartons Rd | 415FED | 2024-05-28 08:33 | 2024-05-28 17:08 | 0.64828 | 0.0012588 | 17 | 8755 | Planned | 11.0 Planned Shutdown | Replacing Crossarms, Pole 25543 and 11kV Conductor between Pole 37922 - 25554 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 64 | NJ458C | Twizel Omarama Rd | 492FED | 2024-05-29 07:51 | 2024-05-29 15:36 | 0.034432 | 7.4047e-05 | 1 | 465 | Planned | 11.0 Planned Shutdown | Replacing 33kV/11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 65 | F5172 WA27427 | 8 industrial Place | 438FED | 2024-05-29 09:49 | 2024-05-29 10:37 | 0.0035542 | 7.4047e-05 | 1 | 48 | Unplanned | 8.0 Defective Equipment | Replacing LV Pole Fuse Base @ Pole 28008 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 66 | F5173 | Double Hill Rd | 417FED | 2024-05-29 11:08 | 2024-05-29 11:54 | 0.04428 | 0.00096261 | 13 | 598 | Unplanned | 8.0 Defective Equipment | 11kV Wire Floating @ Pole 27319 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 67 | F5175A | 75 Awakino Rd | 411FED | 2024-05-29 11:48 | 2024-05-29 12:04 | 0.066346 | 0.0041466 | 56 | 896 | Unplanned | 2.0 Vegetation | Tree Through 11kV Line between Pole 75662 - Pole 71165 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 68 | F5174 | Double Hill Rd | 417FED | 2024-05-29 14:32 | 2024-05-29 15:26 | 0.051981 | 0.00096261 | 13 | 702 | Unplanned | 8.0 Defective Equipment | 11kV Wire Floating @ Pole 27319 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 69 | NJ465 | Twizel Omarama Rd | 492FED | 2024-05-30 07:57 | 2024-05-30 15:23 | 0.033025 | 7.4047e-05 | 1 | 446 | Planned | 11.0 Planned Shutdown | Replacing 33kV/11kV poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 70 | PR168 | Pukeuri-Oamaru Rd | 432FED | 2024-05-30 08:30 | 2024-05-30 14:58 | 0.02873 | 7.4047e-05 | 1 | 388 | Planned | 11.0 Planned Shutdown | Replacing Transformer @ Pole 25210 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 71 | F5214 | 6 Easons Rd | 479FED | 2024-05-30 12:50 | 2024-05-30 13:33 | 0.060496 | 0.0014069 | 19 | 817 | Unplanned | 8.0 Defective Equipment | Floating 11kV Wire @ Pole 11787 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 72 | F5117 | Haven St Moerkai | 480FED | 2024-05-31 00:34 | 2024-05-31 02:45 | 0.048501 | 0.00037023 | 5 | 655 | Unplanned | 9.0 Cause Unknown | Blown 11kV Link Pole 40094 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 73 | PR179 | Gardiners Rd | 416FED | 2024-05-31 09:40 | 2024-05-31 10:18 | 0.0056275 | 0.00014809 | 2 | 76 | Planned | 11.0 Planned Shutdown | Remove LV service from Pole 36741 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 74 | NJ457 | Georgetown Pukeuri Rd | 456FED | 2024-05-31 10:11 | 2024-05-31 11:31 | 0.011847 | 0.00014809 | 2 | 160 | Planned | 11.0 Planned Shutdown | Resag LV conductor between Pole 23821 - Pole 36745 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 75 | F5069 | 407 Lake Ohau Rd | 490FED | 2024-05-31 17:08 | 2024-05-31 19:14 | 0.01866 | 0.00014809 | 2 | 252 | Unplanned | 9.0 Cause Unknown | Blown 11kV Link Pole 35769 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 76 | F5180 | 67 Dunrobin Rd | 486FED | 2024-05-31 21:00 | 2024-05-31 21:41 | 0.0060718 | 0.00014809 | 2 | 82 | Unplanned | 6.0 Wildlife | Rodents Blew 11kV Links @ Pole 16408 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 77 | F16094A | 11kV Line Ruatihwa | 526FED | 2024-06-01 04:05 | 2024-06-01 07:23 | 0.57194 | 0.0029619 | 40 | 7724 | Unplanned | 8.0 Defective Equipment | Broken Strand on 11kV Jumper at Pole 72036 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 78 | F5119 F16095 | 11kV Line 47 Dip Hill Rd | 421FED | 2024-06-01 11:03 | 2024-06-01 14:45 | 0.9863 | 0.0044428 | 60 | 13320 | Unplanned | 8.0 Defective Equipment | Broken 11kV Pole 22618 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 79 | F5070 F16096 | Serpentine Rd | 415FED | 2024-06-01 16:51 | 2024-06-01 20:18 | 0.21163 | 0.0045909 | 62 | 2858 | Unplanned | 2.0 Vegetation | Tree down on 11kV between Pole 11266 and Pole 11267 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 80 | F5181 F16097 | 11kV Line 117 Grants Rd | 473FED | 2024-06-01 17:28 | 2024-06-01 19:56 | 0.16231 | 0.0030359 | 41 | 2192 | Unplanned | 8.0 Defective Equipment | Broken Binder caused 11kV Wire on ground Grants Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 81 | F4715 | Weston Ngapara Rd | 449FED | 2024-06-01 21:06 | 2024-06-01 21:36 | 0.0022214 | 7.4047e-05 | 1 | 30 | Unplanned | 6.0 Wildlife | Blown 11kV Link Pole 41699 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 82 | F5073 | 741 Weston Ngapara Rd | 449FED | 2024-06-03 19:19 | 2024-06-03 19:52 | 0.0024435 | 7.4047e-05 | 1 | 33 | Unplanned | 6.0 Wildlife | Rodent Blew 11kV Link at Pole 41699 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 83 | NJ466 | 11kV Line Twizel Omarama | 491FED | 2024-06-04 09:54 | 2024-06-04 16:18 | 0.19904 | 0.00051833 | 7 | 2688 | Planned | 11.0 Planned Shutdown | Replacing Poles 21156, 36255. and between Pole 21149 - 36256 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 84 | NJ462 WA36322 | 11kV Line Fortification Rd | 416FED | 2024-06-05 08:00 | 2024-06-05 17:05 | 3.0352 | 0.0057016 | 77 | 40990 | Planned | 11.0 Planned Shutdown | Replacing Crossarms, Poles, Stub Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 85 | NJ467A | 33kV 11kV Lines Omarama Twizel | 491FED | 2024-06-05 08:00 | 2024-06-11 16:28 | 0.26331 | 0.00051833 | 7 | 3556 | Planned | 11.0 Planned Shutdown | Replacing Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 86 | PR188 | 11kV Line Hectors Rd | 483FED | 2024-06-05 08:18 | 2024-06-05 14:11 | 0.41822 | 0.0011847 | 16 | 5648 | Planned | 11.0 Planned Shutdown | Tree Felling between Pole 40317 and Pole 870169 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 87 | NJ467B | 33kV 11kV Lines Omarama Twizel | 491FED | 2024-06-06 08:02 | 2024-06-11 16:46 | 0.2716 | 0.00051833 | 7 | 3668 | Planned | 11.0 Planned Shutdown | Replacing Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 88 | PR181 | 11kV Line Buzan Rd | 415FED | 2024-06-07 08:00 | 2024-06-07 13:15 | 0.069974 | 0.00022214 | 3 | 945 | Planned | 11.0 Planned Shutdown | Replacing Poles, Crossarms, Replacing Conductor between Pole 26550 - Pole 26502 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 89 | NJ467C | 33kV 11kV Lines Omarama Twizel | 491FED | 2024-06-07 08:07 | 2024-06-07 14:50 | 0.20889 | 0.00051833 | 7 | 2821 | Planned | 11.0 Planned Shutdown | Replacing Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 90 | WA16773 | Livingston Duntroon Rd | 470FED | 2024-06-07 12:56 | 2024-06-07 14:13 | 0.079822 | 0.0010367 | 14 | 1078 | Unplanned | 4.0 Adverse Environment | Isolating 11kV Line for Boulder Removal from Cliff Livingstone Duntroon Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 91 | NJ467D | 33kV 11kV Lines Omarama Twizel | 491FED | 2024-06-10 10:28 | 2024-06-10 16:41 | 0.19334 | 0.00051833 | 7 | 2611 | Planned | 11.0 Planned Shutdown | Replacing Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 92 | NJ467E | 33kV 11kV Lines Omarama Twizel | 491FED | 2024-06-11 08:01 | 2024-06-11 16:22 | 0.25968 | 0.00051833 | 7 | 3507 | Planned | 11.0 Planned Shutdown | Replacing Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 93 | NJ470 | 11kV Line Pukeuri Hilderthorpe Rd | 478FED | 2024-06-11 08:36 | 2024-06-11 14:55 | 0.44902 | 0.0011847 | 16 | 6064 | Planned | 11.0 Planned Shutdown | Replacing 11kV Crossarms, LV Poles, LV Arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 94 | NJ471A | Pukeuri Hilderthorpe Rd | 478FED | 2024-06-12 08:00 | 2024-06-12 15:43 | 0.90966 | 0.0019993 | 27 | 12285 | Planned | 11.0 Planned Shutdown | Replacing Crossarms & Poles and Stub Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 95 | NJ467F | 33kV 11kV Lines Omarama Twizel | 491FED | 2024-06-12 08:01 | 2024-06-12 16:43 | 0.27057 | 0.00051833 | 7 | 3654 | Planned | 11.0 Planned Shutdown | Replacing Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 96 | F16099 | Richmond Rd | 435FED | 2024-06-12 13:26 | 2024-06-12 15:18 | 0.02488 | 0.00022214 | 3 | 336 | Unplanned | 8.0 Defective Equipment | Isolation to Replace Crossarm on Pole 34305 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 97 | NJ467G | 33kV 11kV Lines Omarama Twizel | 491FED | 2024-06-13 08:01 | 2024-06-13 22:40 | 0.082414 | 0.00051833 | 7 | 1113 | Planned | 11.0 Planned Shutdown | Replacing Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 98 | NJ471B | Pukeuri Hilderthorpe Rd | 478FED | 2024-06-13 08:10 | 2024-06-13 13:08 | 0.57979 | 0.0019993 | 27 | 7830 | Planned | 11.0 Planned Shutdown | Replacing Crossarms & Poles and Stub Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 99 | F16100 | Omarama Ave | 423FED | 2024-06-13 12:22 | 2024-06-13 14:13 | 1.0411 | 0.028952 | 391 | 14060 | Unplanned | 5.0 Third party Interference | Car vs Pole 14912 Omarama Ave, 11kV Wire hanging in LV | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 100 | PR196 | 11kV Line Livingstone Duntroon Rd | 470FED | 2024-06-17 09:17 | 2024-06-17 16:10 | 0.27523 | 0.00066642 | 9 | 3717 | Planned | 11.0 Planned Shutdown | Replacing Poles , Crossarms , Running 3 Phase Conductor between Pole #22655 - #73158 and installing new Transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 101 | NJ481A | 11kV Line Omarama Twizel Rd | 491FED | 2024-06-18 08:01 | 2024-06-18 16:19 | 0.55313 | 0.0011107 | 15 | 7470 | Planned | 11.0 Planned Shutdown | Replacing Poles and Installing Temp Links at Pole 21233a/b | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 102 | NJ479 | 11kV Line Glenavy Hilderthorpe Rd | 478FED | 2024-06-18 08:09 | 2024-06-18 15:11 | 0.59371 | 0.0014069 | 19 | 8018 | Planned | 11.0 Planned Shutdown | Replacing Crossarms, Poles and Install Transformer at Pole 24222 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 103 | NJ476 | 11kV Line Redcastle Rd | 436FED | 2024-06-18 14:15 | 2024-06-18 15:37 | 0.0060718 | 7.4047e-05 | 1 | 82 | Planned | 11.0 Planned Shutdown | Removing LV line between Pole 33277 - 30868, Install new LV cabe from Pole 30868 to Pole 33277 and install SFB | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 104 | NJ481B | 11kV Line Omarama Twizel Rd | 491FED | 2024-06-19 08:00 | 2024-06-19 13:46 | 0.3843 | 0.0011107 | 15 | 5190 | Planned | 11.0 Planned Shutdown | Replacing Poles and Installing Temp Links at Pole 21233a/b | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 105 | NJ480 | 11kV Line Glenavy Hilderthorpe Rd | 478FED | 2024-06-19 08:00 | 2024-06-19 14:45 | 0.76438 | 0.0019993 | 27 | 10323 | Planned | 11.0 Planned Shutdown | Replacing Crossarms & Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 106 | NJ475 | Georgetown Pukeuri Rd | 456FED | 2024-06-20 09:12 | 2024-06-20 16:30 | 0.064865 | 0.00014809 | 2 | 876 | Planned | 11.0 Planned Shutdown | Replacing ABS1041 Peebles with New TSW1711 Peebles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 107 | PR198 | 11kV Line Mcpherson Rd | 454FED | 2024-06-21 08:30 | 2024-06-21 13:43 | 0.78934 | 0.0029619 | 40 | 10660 | Planned | 11.0 Planned Shutdown | Replacing Pole 22345 and Removing LV span between Pole 22345 and 22344 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 108 | PR199 | 11kV Line Barrie Rd | 456FED | 2024-06-24 09:30 | 2024-06-24 12:53 | 0.075157 | 0.00037023 | 5 | 1015 | Planned | 11.0 Planned Shutdown | Replacing Pole 23554, Replacing Crossarm on Pole 23547 and fit stay insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 109 | NJ468 NJ469 | 11kV Line Ferry Rd | 454FED | 2024-06-24 10:00 | 2024-06-24 15:44 | 0.23576 | 0.001555 | 21 | 3184 | Planned | 11.0 Planned Shutdown | To Replace 11kV Crossarms, 11kV Links & Transformer at Pole 22082 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 110 | F5219 | 11kV Line Light House Rd | 480FED | 2024-06-24 10:16 | 2024-06-24 16:24 | 0.094187 | 0.00059237 | 8 | 1272 | Unplanned | 8.0 Defective Equipment | 11kV Link Blown in 11kV Cubicle Light House Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 111 | F16212 | 11kV Wansbeck St RMU | 409FED | 2024-06-24 18:28 | 2024-06-24 19:29 | 3.9019 | 0.08508 | 1149 | 52695 | Unplanned | 8.0 Defective Equipment | 11kV Wansbeck St RMU Faulted | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 112 | NJ483 | 11kV Line Glenavy Hilderthorpe Rd | 478FED | 2024-06-26 08:14 | 2024-06-26 15:05 | 1.7956 | 0.0043688 | 59 | 24249 | Planned | 11.0 Planned Shutdown | Replacing Crossarms & Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 113 | PR201 | 11kV Line Hakataramea Rd | 413FED | 2024-06-27 09:27 | 2024-06-27 13:49 | 0.058201 | 0.00022214 | 3 | 786 | Planned | 11.0 Planned Shutdown | Relocating Service Fuse Box | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 114 | F15992 | R664 | 421FED | 2024-07-01 01:27 | 2024-07-01 03:20 | 0.25287 | 0.0034061 | 46 | 3415 | Unplanned | 9.0 Cause Unknown | R664 Tripped | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 115 | PR202 | 11kV Line Pringles Gully Rd | 421FED | 2024-07-01 09:23 | 2024-07-01 10:55 | 0.027249 | 0.00029619 | 4 | 368 | Planned | 11.0 Planned Shutdown | New Tx and Tighten and double Nut H Structure Pole 817008 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 116 | NJ484 | LV Line Cosy Dell Rd | 479FED | 2024-07-01 09:48 | 2024-07-01 14:34 | 0.042355 | 0.00014809 | 2 | 572 | Planned | 11.0 Planned Shutdown | Replace Poles, Crossarms and LV Conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 117 | F16215 | 826 Kanaui Valley Rd | 483FED | 2024-07-01 14:44 | 2024-07-01 15:51 | 0.12092 | 0.0051092 | 69 | 1633 | Unplanned | 5.0 Third party Interference | Truck Hit 11kV Line at Pole 71041 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 118 | NJ485 | 11kV Line Ferry Rd | 454FED | 2024-07-02 08:35 | 2024-07-02 16:22 | 1.314 | 0.0028138 | 38 | 17746 | Planned | 11.0 Planned Shutdown | Replacing Crossarms and Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 119 | F16216 | Ruatanhiwa Substation | 526FED | 2024-07-02 13:30 | 2024-07-02 13:40 | 0.012588 | 0.0012588 | 17 | 170 | Unplanned | 8.0 Defective Equipment | Emergency shutdown to shift OPEN Point at Ruantaniwha Sub | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 120 | PR205 | 11kV Line Nicholson Rd | 480FED | 2024-07-03 08:30 | 2024-07-03 14:07 | 0.34935 | 0.0010367 | 14 | 4718 | Planned | 11.0 Planned Shutdown | Replace Crossarms and Tx on Pole 10446 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 121 | PR203 | 11kV Line Weston Ngapara Rd | 449FED | 2024-07-04 08:00 | 2024-07-04 16:41 | 2.5847 | 0.0049611 | 67 | 34907 | Planned | 11.0 Planned Shutdown | Replacing Crossarms and Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 122 | PR206 | 11kV Line Awamoa | 416FED | 2024-07-05 08:00 | 2024-07-05 14:24 | 0.39807 | 0.0010367 | 14 | 5376 | Planned | 11.0 Planned Shutdown | Replacing Crossarms, Poles and Reconductoring | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 123 | F5144 | 15 Cosy Dell Rd | 479FED | 2024-07-05 13:40 | 2024-07-05 15:18 | 0.014513 | 0.00014809 | 2 | 196 | Unplanned | 9.0 Cause Unknown | No Power, Links Blown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 124 | F12624 | Te Akatarawa Rd | 464FED | 2024-07-06 15:55 | 2024-07-07 13:56 | 1.3434 | 0.0041466 | 56 | 18142 | Unplanned | 8.0 Defective Equipment | Insulator came out of xarm and conductor burnt through | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 125 | PR190 | 33/11kV Lines Whitstone Five Forks Rd | 533FED | 2024-07-08 08:33 | 2024-07-08 16:18 | 0.30989 | 0.00066642 | 9 | 4185 | Planned | 11.0 Planned Shutdown | Replace 33/11kV Pole 825924 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 126 | MF529 | 11kV Line Island Stream Rd | 415FED | 2024-07-08 09:29 | 2024-07-08 12:47 | 0.029322 | 0.00014809 | 2 | 396 | Planned | 11.0 Planned Shutdown | Trim Trees Between poles 25960 & 12602 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 127 | PR213 | 11kV Line Light House Rd | 480FED | 2024-07-08 09:54 | 2024-07-08 14:56 | 0.1789 | 0.00059237 | 8 | 2416 | Planned | 11.0 Planned Shutdown | Repairing Transformer T136.3 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 128 | PR207 | 11kV Line Peaks Rd | 449FED | 2024-07-09 08:05 | 2024-07-09 15:10 | 0.53499 | 0.0012588 | 17 | 7225 | Planned | 11.0 Planned Shutdown | Replace Poles, Crossarms and Conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 129 | NJ490 | 11kV Line Wilson Rd | 219FED | 2024-07-10 08:12 | 2024-07-10 16:46 | 0.94706 | 0.0019993 | 27 | 12790 | Planned | 11.0 Planned Shutdown | Replace Poles, Crossarms and Conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 130 | PR194 | 11kV Line Papakaio Rd | 219FED | 2024-07-10 09:23 | 2024-07-10 14:22 | 0.1107 | 0.00037023 | 5 | 1495 | Planned | 11.0 Planned Shutdown | Replace Cable Connections due to cable shear links corroding | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 131 | NJ487 | 11kV Line Pine Hill Rd | 449FED | 2024-07-10 11:52 | 2024-07-10 12:07 | 0.0011107 | 7.4047e-05 | 1 | 15 | Planned | 11.0 Planned Shutdown | Install 28m of new UG cable to new SFB tap onto 11kV Pole 29884 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 132 | NJ491 | 11kV Line Wilson Rd | 219FED | 2024-07-11 08:12 | 2024-07-11 16:46 | 0.55535 | 0.0011107 | 15 | 7500 | Planned | 11.0 Planned Shutdown | Replace Poles, Crossarms and Conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 133 | PR210A | 33/11kV Lines Lake Waitaki to Kurow | 464FED | 2024-07-11 08:42 | 2024-07-11 16:18 | 1.1143 | 0.0024435 | 33 | 15048 | Planned | 11.0 Planned Shutdown | Tightening | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 134 | F12626 | 33kV Lines Omarama to Ohau | 2192FED | 2024-07-11 10:52 | 2024-07-11 11:14 | 0.50226 | 0.049241 | 665 | 6783 | Unplanned | 6.0 Wildlife | CB2192 Tripping - Cause Unknown (suspect bird strike) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 135 | PR210B | 33/11kV Lines Lake Waitaki to Kurow | 464FED | 2024-07-12 08:42 | 2024-07-12 16:18 | 0.4716 | 0.0024435 | 33 | 6369 | Planned | 11.0 Planned Shutdown | Tightening | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 136 | PR214 | 11kV Line Burnside Rd | 449FED | 2024-07-15 08:21 | 2024-07-15 16:24 | 0.80348 | 0.0021474 | 29 | 10851 | Planned | 11.0 Planned Shutdown | Trimming Trees between Pole 40345 and 27966a & b | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 137 | NJ496 | 11kV Lines Alma Maheno Rd | 427FED | 2024-07-15 08:32 | 2024-07-15 17:22 | 2.1977 | 0.0041466 | 56 | 29680 | Planned | 11.0 Planned Shutdown | Replace Poles and Crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 138 | NJ498 | 11kV Line Gibson Rd | 219FED | 2024-07-17 08:35 | 2024-07-17 16:14 | 0.40785 | 0.00088856 | 12 | 5508 | Planned | 11.0 Planned Shutdown | Install new NOJA recloser | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 139 | PR212 | 11kV Line Ben Omar Rd | 424FED | 2024-07-18 08:30 | 2024-07-18 15:15 | 0.41984 | 0.0010367 | 14 | 5670 | Planned | 11.0 Planned Shutdown | Line Shift between poles 29044 and 29037, 6 new poles, replace pole 29307 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 140 | NJ501 | 11kV Line Steward Rd | 478FED | 2024-07-19 09:02 | 2024-07-19 09:32 | 0.0044428 | 0.00014809 | 2 | 60 | Planned | 11.0 Planned Shutdown | Tighten Crossarm on Pole 21903 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 141 | NJ502 | 11kV Line Steward Rd | 478FED | 2024-07-19 10:03 | 2024-07-19 10:36 | 0.0073306 | 0.00022214 | 3 | 99 | Planned | 11.0 Planned Shutdown | Resag LV Line between Pole 21898-871969 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 142 | F4737 | 11kV Line Ferry Rd | 454FED | 2024-07-19 14:19 | 2024-07-19 14:33 | 0.035246 | 0.0025176 | 34 | 476 | Unplanned | 8.0 Defective Equipment | Replace 11kV DDO Pole 22106 (Broken during 11kV Safety Isolation) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 143 | NJ507A | 33kV / 11kV Line Omarama Twizel | 491FED | 2024-07-22 09:40 | 2024-07-22 16:02 | 0.14143 | 0.00037023 | 5 | 1910 | Planned | 11.0 Planned Shutdown | Replacing 33KV / 11KV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 144 | NJ507B | 33kV / 11kV Line Omarama Twizel | 491FED | 2024-07-23 08:31 | 2024-07-23 16:39 | 0.18067 | 0.00037023 | 5 | 2440 | Planned | 11.0 Planned Shutdown | Replacing 33KV / 11KV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 145 | NJ505 | 11kV Line Wellington St | 451FED | 2024-07-23 09:38 | 2024-07-23 12:50 | 0.18482 | 0.00096261 | 13 | 2496 | Planned | 11.0 Planned Shutdown | Install LV Monitor @ Pole 39202, Reconfigure LV & Remove MDI Box | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 146 | F16200 | 11kV Line Livingstone Duntroon Line | 470FED | 2024-07-23 11:10 | 2024-07-23 13:51 | 0.0311 | 0.0020733 | 28 | 420 | Unplanned | 4.0 Adverse Environment | WDC using Explosives to Remove Cliff near Pole 34376 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 147 | NJ507C | 33kV / 11kV Line Omarama Twizel | 491FED | 2024-07-24 08:31 | 2024-07-24 16:20 | 0.17364 | 0.00037023 | 5 | 2345 | Planned | 11.0 Planned Shutdown | Replacing 33KV / 11KV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 148 | NJ512 | 11kV Line Coal Pit Rd | 449FED | 2024-07-24 09:11 | 2024-07-24 11:41 | 0.1666 | 0.0011107 | 15 | 2250 | Planned | 11.0 Planned Shutdown | Replacing Pole 24829 and install New Transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 149 | NJ509 | Omarama Twizel Rd | 491FED | 2024-07-25 08:30 | 2024-07-25 16:18 | 0.17327 | 0.00037023 | 5 | 2340 | Planned | 11.0 Planned Shutdown | Replacing 11KV/33KV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 150 | F16218 F16219 | 529 Tokarahi Duntroon Rd | 421FED | 2024-07-30 00:55 | 2024-07-30 13:28 | 0.7806 | 0.0010367 | 14 | 10542 | Unplanned | 2.0 Vegetation | Tree through 11Kv Line near Pole #40292 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 151 | F4808 | Weston Ngapara Rd | 449FED | 2024-07-30 20:36 | 2024-07-31 00:13 | 1.668 | 0.018512 | 250 | 22527 | Unplanned | 8.0 Defective Equipment | Broken Insulator at Pole 19833. Tripped R686 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 152 | PR220 | 11kV Line Grant Rd | 483FED | 2024-08-01 09:02 | 2024-08-01 12:01 | 0.026509 | 0.00014809 | 2 | 358 | Planned | 11.0 Planned Shutdown | Replacing Pole 25787 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 153 | NJ472 | 11kV Line Georgetown Pukeuri Rd | 456FED | 2024-08-07 10:32 | 2024-08-07 16:10 | 0.025028 | 7.4047e-05 | 1 | 338 | Planned | 11.0 Planned Shutdown | Replace Transformer @ Pole 70960, Replace Crossarms and install LV Cable | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 154 | NJ514 | 11kV Line Black Point Rd | 444FED | 2024-08-08 11:01 | 2024-08-08 12:54 | 0.0083673 | 7.4047e-05 | 1 | 113 | Planned | 11.0 Planned Shutdown | Change Transformer @ Pole 42252 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 155 | F5227 | 18 Airport Rd | 423FED | 2024-08-12 07:57 | 2024-08-12 10:07 | 0.0096261 | 7.4047e-05 | 1 | 130 | Unplanned | 6.0 Wildlife | Possom Blew 11kV Link @ Pole 29590 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 156 | F5100 F16221 | Brockmans Rd | 430FED | 2024-08-12 10:02 | 2024-08-12 15:45 | 0.604 | 0.012514 | 169 | 8157 | Unplanned | 8.0 Defective Equipment | (Rotten at Base) Pole 28198 Fell Down in Wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 157 | NJ515 | 11kV Line Hampden Palmerston | 480FED | 2024-08-13 08:50 | 2024-08-13 14:47 | 0.47582 | 0.0013328 | 18 | 6426 | Planned | 11.0 Planned Shutdown | Replacing Conductor between Pole 31214-31212 and Replace Crossarms on Pole 31212 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 158 | NJ517 | 11kV Line Parsons Rd | 430FED | 2024-08-14 09:07 | 2024-08-14 15:56 | 0.6057 | 0.0014809 | 20 | 8180 | Planned | 11.0 Planned Shutdown | Replacing Pole 42475 and Crossarms on Pole 16107, 42471, 39461, 16119, 42472 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 159 | NJ516 | Hampden Palmerston Rd | 480FED | 2024-08-14 10:02 | 2024-08-14 11:45 | 0.24406 | 0.0023695 | 32 | 3296 | Planned | 11.0 Planned Shutdown | Removing 11KV Links from Pole #41203 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 160 | NJ488 | 11kV Line Ferry Rd | 435FED | 2024-08-15 08:50 | 2024-08-15 13:38 | 0.021325 | 7.4047e-05 | 1 | 288 | Planned | 11.0 Planned Shutdown | Replacing Transformer at Pole 22034 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 161 | NJ518 | 11kV Line Simpson Rd | 478FED | 2024-08-15 09:00 | 2024-08-15 13:53 | 0.4773 | 0.001629 | 22 | 6446 | Planned | 11.0 Planned Shutdown | Replacing Pole 24408 & Various Crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 162 | NJ532 | 11kV Line Elderslie Rd | 449FED | 2024-08-16 10:00 | 2024-08-16 10:56 | 0.0082932 | 0.00014809 | 2 | 112 | Planned | 11.0 Planned Shutdown | Remove 11kV Poles 73742 to 73745 and hardware, Remove T2201 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 163 | NJ524 | 33 & 11kV Lines Papakaio Rd | 457FED | 2024-08-19 08:29 | 2024-08-19 13:46 | 0.35209 | 0.0011107 | 15 | 4755 | Planned | 11.0 Planned Shutdown | Retightening Papakaio Rd 11kV and 33kV | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 164 | F16225/F4759 | 11kV Line Mchenrys Rd | 413FED | 2024-08-19 17:41 | 2024-08-19 17:45 | 0.0050352 | 0.0012588 | 17 | 68 | Unplanned | 2.0 Vegetation | Tree Branch on 11kV Line near Pole 13235 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 165 | PR226 | 11kV Line Mcphersons Rd | 454FED | 2024-08-20 08:52 | 2024-08-20 13:33 | 0.70996 | 0.0028138 | 38 | 9588 | Planned | 11.0 Planned Shutdown | Replacing 11kV Pole 22349 and installing 3 x DDOs 30Amp links crucifix with Las | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 166 | NJ522 | 11kV Line Devils Bridge Rd | 430FED | 2024-08-20 09:02 | 2024-08-20 12:07 | 0.041096 | 0.00022214 | 3 | 555 | Planned | 11.0 Planned Shutdown | Replace LV Pole pole 39990P & LV Cross arm @ Pole 39478 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 167 | F16227/F4815 | 11kV Line Mcpherson Rd | 454FED | 2024-08-21 13:32 | 2024-08-21 15:37 | 0.064791 | 0.00051833 | 7 | 875 | Unplanned | 2.0 Vegetation | Tree Branch on 11kV Line near Pole 73422 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 168 | NJ527 | 11kV Line Jardine Rd | 219FED | 2024-08-23 09:32 | 2024-08-23 12:30 | 0.21088 | 0.0011847 | 16 | 2848 | Planned | 11.0 Planned Shutdown | Retightening Jardine Rd 11kV and 33kV | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 169 | NJ489 | 11kV Line Settlement Rd | 411FED | 2024-08-23 10:05 | 2024-08-23 11:19 | 0.032877 | 0.00044428 | 6 | 444 | Planned | 11.0 Planned Shutdown | Tighten & double nut 11kV pole 11378 carry out other maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 170 | F4858 | 275 Homestead Rd | 430FED | 2024-08-28 22:13 | 2024-08-28 22:50 | 0.0082192 | 0.00022214 | 3 | 111 | Unplanned | 6.0 Wildlife | Blown HV Fuses - Possom | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 171 | NJ530 | 11kV Line Warepa Rd | 219FED | 2024-08-29 08:35 | 2024-08-29 15:52 | 0.16179 | 0.00037023 | 5 | 2185 | Planned | 11.0 Planned Shutdown | Replace Poles and Crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 172 | NJ541 | 11kV Line Georgetown Pukeuri Rd | 444FED | 2024-08-30 10:10 | 2024-08-30 14:59 | 0.021399 | 7.4047e-05 | 1 | 289 | Planned | 11.0 Planned Shutdown | Installing LV Monitoring | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 173 | F5230 | 18 Airport Rd | 423FED | 2024-08-30 13:14 | 2024-08-30 14:13 | 0.2097 | 0.0035542 | 48 | 2832 | Unplanned | 8.0 Defective Equipment | Replacing Faulty Blown LA at Pole 29590 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 174 | PR229 | 11kV Line Roundhill Rd | 428FED | 2024-09-02 09:04 | 2024-09-02 12:15 | 0.48086 | 0.0025176 | 34 | 6494 | Planned | 11.0 Planned Shutdown | Replace Pole 26317, Replace 3 x DDOs on pole 26319. Replace SA on Pole 25153 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 175 | F4859 | State Highway 1 Herbert Hampden Rd | 479FED | 2024-09-02 23:56 | 2024-09-03 13:33 | 1.5359 | 0.030433 | 411 | 20742 | Unplanned | 2.0 Vegetation | Tree Through the 11kV Lines at Pole 28349 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 176 | PR230 | 11kV Line Robbs Crossing Rd | 428FED | 2024-09-03 08:55 | 2024-09-03 15:49 | 0.5518 | 0.0013328 | 18 | 7452 | Planned | 11.0 Planned Shutdown | Replace Poles and Crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 177 | NJ538 | 11kV Line Airedale Rd | 429FED | 2024-09-04 08:30 | 2024-09-04 15:50 | 1.3032 | 0.0029619 | 40 | 17600 | Planned | 11.0 Planned Shutdown | Replace Poles and Crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 178 | NJ539 | 11kV Line Airedale Rd | 429FED | 2024-09-05 08:34 | 2024-09-05 10:20 | 0.0078489 | 7.4047e-05 | 1 | 106 | Planned | 11.0 Planned Shutdown | Replace 15kVA transformer on 11kV Pole 15824 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 179 | PR238 | 11kV Line Waiora Rd | 415FED | 2024-09-05 09:02 | 2024-09-05 11:43 | 0.023843 | 0.00014809 | 2 | 322 | Planned | 11.0 Planned Shutdown | Replace 2 x DDOs Links on pole 12607. Replace SA on pole 12604 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 180 | NJ513 | 11kV Line Falconers Rd | 479FED | 2024-09-05 10:32 | 2024-09-05 12:08 | 0.014217 | 0.00014809 | 2 | 192 | Planned | 11.0 Planned Shutdown | Install LV Monitor onto 11kV Pole 39875 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 181 | NJ540 | 11kV Line Airedale Rd | 429FED | 2024-09-05 12:36 | 2024-09-05 13:46 | 0.0051833 | 7.4047e-05 | 1 | 70 | Planned | 11.0 Planned Shutdown | Replace 15kVA transformer on 11kV Pole 15860 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 182 | PR239A | 11kV Line Kuriheka Rd | 415FED | 2024-09-06 08:41 | 2024-09-06 15:01 | 0.16883 | 0.00044428 | 6 | 2280 | Planned | 11.0 Planned Shutdown | Replace Poles and Crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 183 | PR239B | 11kV Line Kuriheka Rd | 415FED | 2024-09-09 08:48 | 2024-09-09 16:01 | 0.19237 | 0.00044428 | 6 | 2598 | Planned | 11.0 Planned Shutdown | Replace Poles and Crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 184 | F4867 | 47 Teaneaki Settlement Rd | 449FED | 2024-09-09 11:16 | 2024-09-09 11:42 | 0.0038504 | 0.00014809 | 2 | 52 | Unplanned | 8.0 Defective Equipment | No Power. LV service wrapped around itself in wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 185 | F5267 | 151 Earthquakes Rd | 470FED | 2024-09-09 15:54 | 2024-09-09 16:50 | 0.016883 | 0.00022214 | 3 | 228 | Unplanned | 2.0 Vegetation | Branch on Line at Pole 12655 - Blown HV Fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 186 | F16238/16239 | Twizel Omarama Rd | 491FED | 2024-09-10 00:36 | 2024-09-12 13:52 | 0.27708 | 0.0026657 | 36 | 3742 | Unplanned | 8.0 Defective Equipment | 11kV Cable Fault at Pole 11174 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 187 | PR246 | 11kV Line Burnside Rd | 451FED | 2024-09-10 08:39 | 2024-09-10 15:41 | 0.093743 | 0.00022214 | 3 | 1266 | Planned | 11.0 Planned Shutdown | String Third Phase from Pole 27795 to 27807 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 188 | NJ556 | 33kV Line Otematata Substation | 524FED | 2024-09-10 09:11 | 2024-09-10 16:14 | 0.21925 | 0.00051833 | 7 | 2961 | Planned | 11.0 Planned Shutdown | Installing new Pole E and Replacing Conductor between Pole E & Pole C | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 189 | NJ543 | 11kV Line Fortification Rd | 427FED | 2024-09-10 09:15 | 2024-09-10 13:00 | 0.066642 | 0.00029619 | 4 | 900 | Planned | 11.0 Planned Shutdown | Install new LV Span from Poles 20850 to 36278 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 190 | F16240 | 11kV Line Burnside Rd | 451FED | 2024-09-11 08:35 | 2024-09-11 11:41 | 0.013773 | 7.4047e-05 | 1 | 186 | Planned | 11.0 Planned Shutdown | Change Transformer on Pole 27806 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 191 | NJ548 | 11kV Line Twizel Omarama Rd | 492FED | 2024-09-11 09:30 | 2024-09-11 11:37 | 0.094039 | 0.00074047 | 10 | 1270 | Planned | 11.0 Planned Shutdown | Remove Temp Links on Pole 39766 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 192 | PR234 | 11kV Line Manse Rd | 411FED | 2024-09-11 09:32 | 2024-09-11 13:38 | 0.036431 | 0.00014809 | 2 | 492 | Planned | 11.0 Planned Shutdown | Install new SFB | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 193 | F16242 | 11kV Line Prydes Gully Rd | 421FED | 2024-09-11 16:42 | 2024-09-11 16:48 | 0.039985 | 0.0066642 | 90 | 540 | Unplanned | 8.0 Defective Equipment | ABS1176 Springside West Arcing (inspect) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 194 | F16243 | 11kV Line Redcastle Rd | 430FED | 2024-09-11 19:19 | 2024-09-11 21:00 | 0.29167 | 0.0028878 | 39 | 3939 | Unplanned | 5.0 Third party Interference | Car vs Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 195 | NJ560 | 11kV Line Ferry Rd | 435FED | 2024-09-16 10:02 | 2024-09-16 12:18 | 0.01007 | 7.4047e-05 | 1 | 136 | Planned | 11.0 Planned Shutdown | Install LV Monitor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 196 | PR250 | 11kV Line Macdonalds Rd | 454FED | 2024-09-17 10:02 | 2024-09-17 11:58 | 0.18897 | 0.001629 | 22 | 2552 | Planned | 11.0 Planned Shutdown | Transformer Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 197 | PR249 | 11kV Line Jessicas Lane | 430FED | 2024-09-18 10:05 | 2024-09-18 13:35 | 0.062199 | 0.00029619 | 4 | 840 | Planned | 11.0 Planned Shutdown | Replacing Poles and Crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 198 | F15993 | Kakanui Rd | 416FED | 2024-09-20 23:53 | 2024-09-21 02:50 | 0.95676 | 0.0054054 | 73 | 12921 | Unplanned | 5.0 Third party Interference | Car vs Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 199 | F16247 | Milne Rd | 413FED | 2024-09-24 10:48 | 2024-09-24 11:28 | 0.071085 | 0.0017771 | 24 | 960 | Unplanned | 8.0 Defective Equipment | Broken Binder and loose Bolts | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 200 | PR254 | 11kV Line Waianakarua Rd | 479FED | 2024-09-25 08:43 | 2024-09-25 12:21 | 0.032284 | 0.00014809 | 2 | 436 | Planned | 11.0 Planned Shutdown | Repair 11kV cable term on pole 39426 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 201 | F16250 | 11kV Line Livingstone st Duntroon | 470FED | 2024-09-25 08:43 | 2024-09-27 13:40 | 0.4876 | 0.0028138 | 38 | 6585 | Unplanned | 5.0 Third party Interference | Customer cut tree down threw line, started small fire. Damaged poles and equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 202 | F16249 | Settlement Rd | 470FED | 2024-09-25 09:54 | 2024-09-25 10:17 | 0.010218 | 0.00044428 | 6 | 138 | Unplanned | 6.0 Wildlife | Remove Bird Nest | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 203 | NJ574 | 11kV Line Gray Rd | 454FED | 2024-09-27 09:16 | 2024-09-27 11:46 | 0.099963 | 0.00066642 | 9 | 1350 | Planned | 11.0 Planned Shutdown | Remove 11kV Span from Poles 23492 & 21916 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 204 | PR261 | 11kV Line Wainakarua Rd | 479FED | 2024-09-30 08:56 | 2024-09-30 09:39 | 0.090041 | 0.0017771 | 24 | 1216 | Planned | 11.0 Planned Shutdown | Repair 11kV Cable term on Pole 30813 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 205 | NJ541 | 11kV Line Georgetown Pukeuri Rd | 444FED | 2024-09-30 08:59 | 2024-09-30 11:41 | 0.011996 | 7.4047e-05 | 1 | 162 | Planned | 11.0 Planned Shutdown | Installing LV Monitoring on 11kV pole 23675 onto Tx2518 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 206 | NJ547 | Twizel Omarama Rd | 491FED | 2024-10-01 09:00 | 2024-10-01 11:59 | 0.066272 | 0.00037023 | 5 | 895 | Planned | 11.0 Planned Shutdown | Install 33kV clamp top insulators and install double arms on 33kV poles 36251 & 21241 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 207 | NJ525 & PI168 | Papakaio Rd | 491FED | 2024-10-02 09:32 | 2024-10-02 13:02 | 0.57534 | 0.0027397 | 37 | 7770 | Planned | 11.0 Planned Shutdown | TIghtening | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 208 | F16455 | 11kV Line Milne Rd | 413FED | 2024-10-02 11:03 | 2024-10-02 13:13 | 0.038504 | 0.00029619 | 4 | 520 | Unplanned | 8.0 Defective Equipment | Tighten centre bolting at Pole 29349 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 209 | NJ578A | Aitcheson Rd | 219FED | 2024-10-03 08:30 | 2024-10-03 11:39 | 0.72773 | 0.0038504 | 52 | 9828 | Planned | 11.0 Planned Shutdown | Tightening | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 210 | NJ578B | Aitcheson Rd | 219FED | 2024-10-04 08:31 | 2024-10-04 10:54 | 0.55061 | 0.0038504 | 52 | 7436 | Planned | 11.0 Planned Shutdown | Tightening | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 211 | PR262 | 11kV Line Uxbridge Rd | 444FED | 2024-10-09 13:39 | 2024-10-09 17:39 | 0.017771 | 7.4047e-05 | 1 | 240 | Planned | 11.0 Planned Shutdown | Reconfigure 11kV and install Replacement Groundmount | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 212 | PR264 | 11kV Line Kauru Hill Rd | 415FED | 2024-10-10 08:20 | 2024-10-10 15:25 | 1.9197 | 0.0045168 | 61 | 25925 | Planned | 11.0 Planned Shutdown | Replace Poles and Hardware | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 213 | F16457 | Wilson Rd | 219FED | 2024-10-11 06:11 | 2024-10-11 08:12 | 0.41733 | 0.0066642 | 90 | 5636 | Unplanned | 8.0 Defective Equipment | 11kV Wire Down Pole 41569 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 214 | PR269 | 11kV Line Roundhill Rd | 428FED | 2024-10-14 09:34 | 2024-10-14 14:49 | 0.39652 | 0.0012588 | 17 | 5355 | Planned | 11.0 Planned Shutdown | Replacing Transformer @ Pole 26368 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 215 | F4881A | 151 Earthquakes Rd | 470FED | 2024-10-14 12:46 | 2024-10-14 14:23 | 0.021548 | 0.00022214 | 3 | 291 | Unplanned | 6.0 Wildlife | Duck Blew 11kV Links at Pole 12653 and Pole 73776 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 216 | NJ594A | 11kV Line St Helens Rd | 451FED | 2024-10-16 09:01 | 2024-10-16 14:00 | 0.35424 | 0.0011847 | 16 | 4784 | Planned | 11.0 Planned Shutdown | Replace Poles, Crossarms, Conductor and Install Transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 217 | PR267 | 11kV Line Lake Ohau Rd | 490FED | 2024-10-16 09:52 | 2024-10-16 16:18 | 0.34217 | 0.00088856 | 12 | 4621 | Planned | 11.0 Planned Shutdown | Removing Pole 19500B and Replacing ABS1232 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 218 | PR270 | Lake Ohau Rd | 490FED | 2024-10-17 08:31 | 2024-10-17 16:28 | 0.28256 | 0.00059237 | 8 | 3816 | Planned | 11.0 Planned Shutdown | Tighten Between ABS1111 and Pole 35705 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 219 | PR227 | Dunrobin Rd | 486FED | 2024-10-17 08:36 | 2024-10-17 15:11 | 0.32173 | 0.00081451 | 11 | 4345 | Planned | 11.0 Planned Shutdown | Replacing Pole 16477 & Pole 16481 and install Transformers | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 220 | NJ594B | 11kV Line St Helens Rd | 451FED | 2024-10-17 09:03 | 2024-10-17 14:03 | 0.35542 | 0.0011847 | 16 | 4800 | Planned | 11.0 Planned Shutdown | Replace Poles, Crossarms, Conductor and Install Transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 221 | F16456 | Ohau Substation | 2192FED | 2024-10-19 00:13 | 2024-10-19 00:41 | 0.31396 | 0.048204 | 651 | 4240 | Unplanned | 9.0 Cause Unknown | Recloser R818 Tripped | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 222 | PR153 | 11kV Line Island Stream Rd | 415FED | 2024-10-21 08:00 | 2024-10-21 14:32 | 0.028804 | 7.4047e-05 | 1 | 389 | Planned | 11.0 Planned Shutdown | Replacing 11kV Condutor between Pole 25948 - Pole 26489 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 223 | PR271 | Lake Ohau Rd | 490FED | 2024-10-21 09:00 | 2024-10-21 16:29 | 3.5913 | 0.0085154 | 115 | 48500 | Planned | 11.0 Planned Shutdown | Tighten between ABS1022 and ABS1570 and Install 11kV Links at Pole 19496 & 40451 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 224 | PR272 | 11kV Line Ohau Rd | 490FED | 2024-10-22 08:38 | 2024-10-22 13:01 | 0.2134 | 0.00081451 | 11 | 2882 | Planned | 11.0 Planned Shutdown | Tigthtens between ABS1570 and 11kV Links Pole 35915 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 225 | PR274 | 11kV Line Dasher Rd | 415FED | 2024-10-23 08:23 | 2024-10-23 14:13 | 0.025916 | 7.4047e-05 | 1 | 350 | Planned | 11.0 Planned Shutdown | Replace Pole 19896 and Replace Transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 226 | NJ596A | Henburn Rd | 424FED | 2024-10-23 08:31 | 2024-10-23 16:20 | 0.20837 | 0.00044428 | 6 | 2814 | Planned | 11.0 Planned Shutdown | Replace poles, Crossarms and Conductor from pole 14547 to Pole 40230 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 227 | NJ597 | 11kV Line Quailburn Rd | 424FED | 2024-10-24 08:31 | 2024-10-24 14:22 | 0.15594 | 0.00044428 | 6 | 2106 | Planned | 11.0 Planned Shutdown | Relocate ABS1200 and Replace Conductor between Pole 14547 and Pole 10712 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 228 | PR277 | 11kV Line Tilverstowe Rd | 421FED | 2024-10-24 10:14 | 2024-10-24 14:53 | 0.44894 | 0.00311 | 42 | 6063 | Planned | 11.0 Planned Shutdown | Replace Transformer @ Pole 37375 and install 3rd DDO | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 229 | F5284 | 3516 Kurow Duntroon Rd | 470FED | 2024-10-25 06:51 | 2024-10-25 08:00 | 0.020437 | 0.00029619 | 4 | 276 | Unplanned | 6.0 Wildlife | Rodents blew 11kV Links Pole 38844 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 230 | NJ596B | Henburn Rd | 424FED | 2024-10-25 08:32 | 2024-10-25 13:59 | 0.14528 | 0.00044428 | 6 | 1962 | Planned | 11.0 Planned Shutdown | Replace poles, Crossarms and Conductor from pole 14547 to Pole 40230 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 231 | F5285 | Ohau | 490FED | 2024-10-26 14:29 | 2024-10-27 14:26 | 2.196 | 0.001555 | 21 | 29657 | Unplanned | 3.0 Adverse Weather | Broken Conductor @ Pole #874103 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 232 | F4845 | 1490 Birchwood Rd | 424FED | 2024-10-26 15:02 | 2024-10-27 14:12 | 0.63073 | 0.00096261 | 13 | 8518 | Unplanned | 2.0 Vegetation | Tree Through 11Kv Line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 233 | F4847 F30330 | 162 Boundary Creek Rd | 432FED | 2024-10-27 10:25 | 2024-10-27 11:02 | 0.0054795 | 0.00014809 | 2 | 74 | Unplanned | 2.0 Vegetation | Tree Branch through LV Span | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 234 | NJ596C | Henburn Rd | 424FED | 2024-10-29 09:15 | 2024-10-29 16:17 | 0.18749 | 0.00044428 | 6 | 2532 | Planned | 11.0 Planned Shutdown | Replace poles, Crossarms and Conductor from pole 14547 to Pole 40230 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 235 | PR280 | 11kV Line Danseys Pass Rd | 421FED | 2024-10-30 08:14 | 2024-10-30 15:02 | 0.4856 | 0.0014809 | 20 | 6558 | Planned | 11.0 Planned Shutdown | Replacing Poles and Crossarms and Tightening | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 236 | NJ596D | Henburn Rd | 424FED | 2024-10-30 08:31 | 2024-10-30 16:11 | 0.20437 | 0.00044428 | 6 | 2760 | Planned | 11.0 Planned Shutdown | Replace poles, Crossarms and Conductor from pole 14547 to Pole 40230 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 237 | NJ596E | Henburn Rd | 424FED | 2024-10-31 08:30 | 2024-10-31 13:40 | 0.13773 | 0.00044428 | 6 | 1860 | Planned | 11.0 Planned Shutdown | Replace poles, Crossarms and Conductor from pole 14547 to Pole 40230 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 238 | NJ604 | 33kV 11kV Line Omarama Otematata | 424FED | 2024-10-31 09:05 | 2024-10-31 15:50 | 0.47982 | 0.0011847 | 16 | 6480 | Planned | 11.0 Planned Shutdown | 33kV & 11kV Climbing Patrol | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 239 | F4849 | 280 Reservoir Rd | 437FED | 2024-10-31 14:25 | 2024-10-31 15:15 | 0.0037023 | 7.4047e-05 | 1 | 50 | Unplanned | 6.0 Wildlife | Rodent Blew 11kV Link @ Pole 32439 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 240 | NJ620 | 11kV Line Birchwood Rd | 423FED | 2024-11-01 08:39 | 2024-11-01 13:02 | 0.097371 | 0.00037023 | 5 | 1315 | Planned | 11.0 Planned Shutdown | Replace 11kV Poles 37168 & 37171 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 241 | NJ612 | 11kV Line Prohibition Rd | 424FED | 2024-11-04 08:37 | 2024-11-04 15:15 | 0.55994 | 0.0014069 | 19 | 7562 | Planned | 11.0 Planned Shutdown | Climbing Patrol and retighening | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 242 | F5379 | Cochranes Rd | 413FED | 2024-11-05 14:36 | 2024-11-07 14:57 | 0.21037 | 7.4047e-05 | 1 | 2841 | Unplanned | 8.0 Defective Equipment | 11kV Floating Wires and Replace Pole 10912 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 243 | F4903 | 17 Pringles Gully Rd | 421FED | 2024-11-06 07:30 | 2024-11-06 09:47 | 0.010144 | 7.4047e-05 | 1 | 137 | Unplanned | 6.0 Wildlife | Possom Blew 11kV Links @ Pole 22822 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 244 | NJ607A | Maheno Kakanui Rd | 416FED | 2024-11-06 09:03 | 2024-11-06 15:56 | 0.12233 | 0.00029619 | 4 | 1652 | Planned | 11.0 Planned Shutdown | Replace Pole 30612 and install new R712 West Kakanui | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 245 | F5300 | 45 Baghdad | 480FED | 2024-11-06 19:44 | 2024-11-06 21:05 | 0.023991 | 0.00029619 | 4 | 324 | Unplanned | 8.0 Defective Equipment | No Power 11kV Link Corroded | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 246 | NJ610 | Argyle St | 427FED | 2024-11-07 08:41 | 2024-11-07 18:14 | 1.0607 | 0.0018512 | 25 | 14325 | Planned | 11.0 Planned Shutdown | Replacing Pole 28703 and Pole 28702 and ABS1105 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 247 | NJ607B | Maheno Kakanui Rd | 416FED | 2024-11-07 08:57 | 2024-11-07 14:27 | 0.097742 | 0.00029619 | 4 | 1320 | Planned | 11.0 Planned Shutdown | Replace Pole 30612 and install new R712 West Kakanui | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 248 | F16468 | Brookstead Rd | 444FED | 2024-11-07 08:57 | 2024-11-07 14:27 | 0.33388 | 0.0056275 | 76 | 4509 | Unplanned | 5.0 Third party Interference | Truck Against 11kV Line near Pole 15986 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 249 | PR284 | Dunrobin Rd | 486FED | 2024-11-12 08:00 | 2024-11-12 15:32 | 0.60244 | 0.0013328 | 18 | 8136 | Planned | 11.0 Planned Shutdown | Replacing Poles & Crossarms & Tightening | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 250 | NJ618A | 11kV Line Waianakarua Rd | 479FED | 2024-11-12 08:42 | 2024-11-12 15:34 | 0.24339 | 0.00059237 | 8 | 3287 | Planned | 11.0 Planned Shutdown | Replacing ABS1004 with TSW1720 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 251 | F4953 | 507 Whitestone Five Forks Rd | 451FED | 2024-11-13 08:06 | 2024-11-13 09:30 | 0.01866 | 0.00022214 | 3 | 252 | Unplanned | 6.0 Wildlife | Rodents Blew 11kV links Pole 39227 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 252 | PR285 | 11kV Line Dunrobin Rd | 486FED | 2024-11-13 08:10 | 2024-11-13 14:46 | 0.20007 | 0.00051833 | 7 | 2702 | Planned | 11.0 Planned Shutdown | Replacing Poles, Crossarms & Double Nutting | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 253 | NJ618B | 11kV Line Waianakarua Rd | 479FED | 2024-11-13 08:36 | 2024-11-13 13:41 | 0.18016 | 0.00059237 | 8 | 2433 | Planned | 11.0 Planned Shutdown | Replacing ABS1004 with TSW1720 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 254 | PR288 | Hedley Rd | 472FED | 2024-11-15 08:07 | 2024-11-15 17:59 | 0.057386 | 0.0021474 | 29 | 775 | Planned | 11.0 Planned Shutdown | Installing New Pole N1 & N2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 255 | F16474 | Omarama Sub | 2192FED | 2024-11-15 13:32 | 2024-11-15 13:41 | 0.30056 | 0.035394 | 478 | 4059 | Unplanned | 9.0 Cause Unknown | R808 Tripped | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 256 | PI185 | Industrial Park RMU | 438FED | 2024-11-17 14:24 | 2024-11-17 15:00 | 0.071973 | 0.0019993 | 27 | 972 | Planned | 11.0 Planned Shutdown | Changing 11kV Fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 257 | PI184 | Hedley Rd | 472FED | 2024-11-19 08:11 | 2024-11-19 17:59 | 0.062273 | 0.0021474 | 29 | 841 | Planned | 11.0 Planned Shutdown | Removing 11kV Overhead Lines between Poler N1 & N2 and Replacing with 11kV Cable | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 258 | NJ603 | Broken Hut Rd | 423FED | 2024-11-19 09:00 | 2024-11-19 13:15 | 0.2077 | 0.00081451 | 11 | 2805 | Planned | 11.0 Planned Shutdown | Climbing Patrol & Tightens | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 259 | F16476 | Boundary Creek Rd | 432FED | 2024-11-21 09:41 | 2024-11-21 10:31 | 0.0074047 | 0.00014809 | 2 | 100 | Unplanned | 2.0 Vegetation | Erecting LV Wires 2 Pole 33534 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 260 | PI188 | Twizel Omarama Rd | 424FED | 2024-11-22 08:00 | 2024-11-22 14:01 | 0.88145 | 0.0025176 | 34 | 11904 | Unplanned | 8.0 Defective Equipment | Replacing ABS1193 & Pole 29524 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 261 | NJ626 | Livingstone -Duntroon Rd | 421FED | 2024-11-25 08:32 | 2024-11-25 15:35 | 0.93965 | 0.0022214 | 30 | 12690 | Planned | 11.0 Planned Shutdown | Climbing Patrol & Tightening | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 262 | NJ627 | Livingstone Duntroon Rd | 421FED | 2024-11-26 08:33 | 2024-11-26 15:31 | 0.21666 | 0.00051833 | 7 | 2926 | Planned | 11.0 Planned Shutdown | Climbing Patrol & Tightening | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 263 | NJ636 | Otematata Omarama Rd | 425FED | 2024-11-28 08:34 | 2024-11-28 15:40 | 0.53625 | 0.0012588 | 17 | 7242 | Planned | 11.0 Planned Shutdown | Climbing Patrol & Tightening | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 264 | PR295 | Gillies Foundry Halo | 407FED | 2024-11-30 08:08 | 2024-12-01 11:36 | 0.12203 | 7.4047e-05 | 1 | 1648 | Planned | 11.0 Planned Shutdown | Replacing Gillies Foundary Halo | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 265 | F16481 | Omarama Ohau Ruataniwha | 2192FED | 2024-12-01 14:14 | 2024-12-01 16:14 | 0.489 | 0.049537 | 669 | 6604 | Unplanned | 6.0 Wildlife | Bird @ ABS3370 Caused CB2192 Twizel to Trip[ | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 266 | NJ645 | Omarama Twizel Rd | 424FED | 2024-12-03 10:01 | 2024-12-03 13:09 | 0.20881 | 0.0011107 | 15 | 2820 | Planned | 11.0 Planned Shutdown | Retighten & Patrol Between Pole 36198 - Pole 29625 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 267 | F5403 | 1232 Weston Ngapara Rd | 449FED | 2024-12-06 12:59 | 2024-12-06 15:59 | 0.013328 | 7.4047e-05 | 1 | 180 | Unplanned | 9.0 Cause Unknown | Blown DDO at Pole 41331 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 268 | F16484 | Dansey Pass Rd | 421FED | 2024-12-08 19:31 | 2024-12-09 12:18 | 0.32581 | 0.0013328 | 18 | 4400 | Unplanned | 2.0 Vegetation | Tree through 11kV line between Pole 22880 - 22879 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 269 | NJ651 | Livingston Duntroon Rd | 473FED | 2024-12-09 09:30 | 2024-12-09 10:40 | 0.0051833 | 7.4047e-05 | 1 | 70 | Planned | 11.0 Planned Shutdown | Raising and Terminating LV Cable & Install New LV Fuse Base | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 270 | PR302 | Omarama Twizel Rd | 424FED | 2024-12-09 10:30 | 2024-12-09 11:59 | 0.098852 | 0.0011107 | 15 | 1335 | Planned | 11.0 Planned Shutdown | Replacing Pole 29537 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 271 | NJ652A | 11kV Line Birchwood Rd | 423FED | 2024-12-11 08:08 | 2024-12-11 18:07 | 0.044354 | 7.4047e-05 | 1 | 599 | Planned | 11.0 Planned Shutdown | Replacing Poles and Crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 272 | F16486 | 1183 Wainakarua Rd | 479FED | 2024-12-11 15:05 | 2024-12-11 17:24 | 0.020585 | 0.00014809 | 2 | 278 | Unplanned | 8.0 Defective Equipment | Replacing LV Fuse Base @ Pole 70549 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 273 | NJ652B | 11kV Line Birchwood Rd | 423FED | 2024-12-12 08:10 | 2024-12-12 18:29 | 0.036949 | 7.4047e-05 | 1 | 499 | Planned | 11.0 Planned Shutdown | Replacing Poles and Crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 274 | PR295-1 | Gillies Foundry Halo | 407FED | 2024-12-12 09:36 | 2024-12-12 13:32 | 0.019696 | 7.4047e-05 | 1 | 266 | Planned | 11.0 Planned Shutdown | Completing Replacement of Gillies Foundry Halo | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 275 | 2487PI | Omarama Twizel Rd | 492FED | 2024-12-12 10:37 | 2024-12-12 12:16 | 0.087967 | 0.00088856 | 12 | 1188 | Unplanned | 8.0 Defective Equipment | Resage Conductors between Pole 21086 - Pole 41708 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 276 | NJ652C | 11kV Line Birchwood Rd | 423FED | 2024-12-13 08:08 | 2024-12-13 11:32 | 0.015106 | 7.4047e-05 | 1 | 204 | Planned | 11.0 Planned Shutdown | Replacing Poles and Crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 277 | PR298 | Herbert Hampden Rd | 479FED | 2024-12-13 08:57 | 2024-12-13 10:59 | 0.036135 | 0.00029619 | 4 | 488 | Planned | 11.0 Planned Shutdown | Reconfigure LV lines to 3 phase @ Pole 14222 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 278 | NJ653 | Birchwood Rd | 423FED | 2024-12-16 09:34 | 2024-12-16 14:23 | 0.107 | 0.00037023 | 5 | 1445 | Planned | 11.0 Planned Shutdown | Replacing Pole 37169 and installing transformer & maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 279 | PR288-1 | Hedley Rd | 472FED | 2024-12-16 09:57 | 2024-12-16 13:51 | 0.021474 | 0.0020733 | 28 | 290 | Planned | 11.0 Planned Shutdown | Replacing Stays @ New Pole N1 & N2 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 280 | NJ654A | Birchwood Rd | 423FED | 2024-12-17 08:02 | 2024-12-17 15:14 | 0.38386 | 0.00088856 | 12 | 5184 | Planned | 11.0 Planned Shutdown | Replacing Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 281 | PR306 | Milne Rd Haka Valley | 413FED | 2024-12-17 13:00 | 2024-12-17 15:54 | 0.47671 | 0.0027397 | 37 | 6438 | Planned | 11.0 Planned Shutdown | Trim Trees between Pole 39140 - 72757 and Replace Centre Bolt @ Pole 14493 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 282 | NJ654B | Birchwood Rd | 423FED | 2024-12-18 08:02 | 2024-12-18 15:00 | 0.37142 | 0.00088856 | 12 | 5016 | Planned | 11.0 Planned Shutdown | Replacing Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 283 | PR307 | Dansey Pass Rd | 421FED | 2024-12-18 08:37 | 2024-12-18 14:56 | 0.3087 | 0.00081451 | 11 | 4169 | Planned | 11.0 Planned Shutdown | Tree Removal Between Pole 22879 - Pole 22881 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 284 | PR305 | Tenby St Moeraki | 480FED | 2024-12-18 09:04 | 2024-12-18 12:13 | 0.083969 | 0.00044428 | 6 | 1134 | Planned | 11.0 Planned Shutdown | Replacing Transformer on Pole 39256 & Installing NEW SFB from Pole 18471 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 285 | F5411 | Hurstlea Rd | 413FED | 2024-12-18 11:18 | 2024-12-18 11:45 | 0.011996 | 0.00044428 | 6 | 162 | Unplanned | 8.0 Defective Equipment | Replacing Clamp Top Insulator at Pole 18106 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 286 | NJ655 | Birchwood Rd | 423FED | 2024-12-19 08:00 | 2024-12-19 15:28 | 1.0573 | 0.0023695 | 32 | 14279 | Planned | 11.0 Planned Shutdown | Replacing Various poles and Trimming Trees beteen Pole 15181 - Pole 40257 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 287 | F4974 | Arundel St | 445FED | 2024-12-25 02:20 | 2024-12-25 02:26 | 0.412 | 0.015846 | 214 | 5564 | Unplanned | 5.0 Third party Interference | Car vs Pole 32272 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 288 | F4868 | 480 Corbett Rd | 435FED | 2024-12-30 08:57 | 2024-12-30 11:28 | 0.011181 | 7.4047e-05 | 1 | 151 | Unplanned | 6.0 Wildlife | Rat Blew 11kV Links @ Pole 22220 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 289 | F10631 | Taipo Rd | 414FED | 2024-12-30 14:24 | 2024-12-30 14:40 | 0.0023695 | 0.00014809 | 2 | 32 | Unplanned | 8.0 Defective Equipment | Replacing Broken 11kV Dead End @ Pole 25081 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 290 | F4978 | 280 Parsons Rd | 430FED | 2025-01-04 06:43 | 2025-01-04 09:18 | 0.12277 | 0.0014809 | 20 | 1658 | Unplanned | 9.0 Cause Unknown | DDO Fused Tripped & Damaged @ Pole 16126 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 291 | F5016 | Oban St | 408FED | 2025-01-04 09:46 | 2025-01-04 10:15 | 0.13528 | 0.0046649 | 63 | 1827 | Unplanned | 8.0 Defective Equipment | CBS986 Tripped 11KV Cable Fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 292 | F16493 | Maungitiro | 413FED | 2025-01-08 15:38 | 2025-01-09 18:27 | 1.5028 | 0.0033321 | 45 | 20295 | Unplanned | 5.0 Third party Interference | Digger Hit 11kV Cable between Pole 10826 - Pole 18055 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 293 | F10647 | Otematata Station | 425FED | 2025-01-09 06:53 | 2025-01-09 08:27 | 0.0069604 | 7.4047e-05 | 1 | 94 | Unplanned | 6.0 Wildlife | Possom Blew 11kV Links Pole 71827 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 294 | NJ674 | Fuchsia Creek Rd | 483FED | 2025-01-13 08:03 | 2025-01-13 16:06 | 0.91744 | 0.0020733 | 28 | 12390 | Planned | 11.0 Planned Shutdown | Replacing Poles & Crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 295 | NJ675 | Fuchsia Creek Rd | 483FED | 2025-01-14 08:30 | 2025-01-14 16:03 | 1.0368 | 0.0023695 | 32 | 14002 | Planned | 11.0 Planned Shutdown | Replacing Poles & Crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 296 | F5021 | 250 Corbett Rd | 478FED | 2025-01-14 16:02 | 2025-01-14 18:48 | 0.037616 | 0.00074047 | 10 | 508 | Unplanned | 8.0 Defective Equipment | 11kV Jumper Burnt Off Line Side of DDO Pole 37033 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 297 | NJ676A | Fuchsia Creek Rd | 483FED | 2025-01-15 08:30 | 2025-01-15 15:58 | 0.92884 | 0.0020733 | 28 | 12544 | Planned | 11.0 Planned Shutdown | Replacing Poles & Crossarms, Installing 11kV Knife Links @ Pole 37710, Replacing Conductor between Pole 37711 & 17139 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 298 | NJ676B | Fuchsia Creek Rd | 483FED | 2025-01-16 08:30 | 2025-01-16 16:09 | 0.95165 | 0.0020733 | 28 | 12852 | Planned | 11.0 Planned Shutdown | Replacing Poles & Crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 299 | NJ677A | Fuchsia Creek Rd | 483FED | 2025-01-17 08:31 | 2025-01-17 14:42 | 0.40985 | 0.0011107 | 15 | 5535 | Planned | 11.0 Planned Shutdown | Replacing Poles & Crossarms, ABS1146 with 11kV Links, and Conductor between Pole 17139-30996 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 300 | NJ677B | Fuchsia Creek Rd | 483FED | 2025-01-20 08:31 | 2025-01-20 14:49 | 0.41762 | 0.0011107 | 15 | 5640 | Planned | 11.0 Planned Shutdown | Replacing Poles & Crossarms, ABS1146 with 11kV Links, and Conductor between Pole 17139-30996 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 301 | NJ677C | Fuchsia Creek Rd | 483FED | 2025-01-21 08:32 | 2025-01-21 13:34 | 0.33321 | 0.0011107 | 15 | 4500 | Planned | 11.0 Planned Shutdown | Replacing Poles & Crossarms, ABS1146 with 11kV Links, and Conductor between Pole 17139-30996 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 302 | PR312 | Redcastle Rd | 437FED | 2025-01-21 08:39 | 2025-01-21 15:34 | 0.030729 | 7.4047e-05 | 1 | 415 | Planned | 11.0 Planned Shutdown | Replacing 11kV Pot Head @ Pole 71888 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 303 | NJ598 | Roseberry Rd | 430FED | 2025-01-23 09:03 | 2025-01-23 12:35 | 0.094187 | 0.00044428 | 6 | 1272 | Planned | 11.0 Planned Shutdown | Replacing Pole 28169 & 28168 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 304 | PR313 | Corrigals Rd | 413FED | 2025-01-24 09:11 | 2025-01-24 15:44 | 0.1164 | 0.00029619 | 4 | 1572 | Planned | 11.0 Planned Shutdown | Replacing Pole 29346 and install Transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 305 | F5430 | Uxbridge Rd | 444FED | 2025-01-27 13:27 | 2025-01-27 13:42 | 0.0088856 | 0.00059237 | 8 | 120 | Unplanned | 8.0 Defective Equipment | Re Fix Pole Cap @ Pole 23711 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 306 | F5246 | 26 Ridge Rd | 456FED | 2025-01-29 08:00 | 2025-01-29 08:59 | 0.017475 | 0.00029619 | 4 | 236 | Unplanned | 6.0 Wildlife | Rodent Blew 11kV Link Pole 42161 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 307 | PR322 | Whitestone Five Forks | 451FED | 2025-02-04 09:30 | 2025-02-04 12:57 | 0.33721 | 0.001629 | 22 | 4554 | Planned | 11.0 Planned Shutdown | Trimming Trees between Pole 27844 - Pole 39223 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 308 | NJ701 | Burnside Rd | 449FED | 2025-02-04 09:31 | 2025-02-04 11:58 | 0.15861 | 0.0011847 | 16 | 2142 | Planned | 11.0 Planned Shutdown | Shackle off 11KV Conductor @ Pole #27952 , Remove Conductor between Pole #27952 and Pole #71271 and Transformer @ Pole #71271 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 309 | NJ703 | Coal Pit Rd | 449FED | 2025-02-05 09:32 | 2025-02-05 13:05 | 0.23658 | 0.0011107 | 15 | 3195 | Planned | 11.0 Planned Shutdown | Replace Pole 24829 and install 11kV Links | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 310 | PR323 | Kauru Hill Rd | 415FED | 2025-02-05 10:03 | 2025-02-05 14:27 | 1.308 | 0.0049611 | 67 | 17664 | Planned | 11.0 Planned Shutdown | Trimming Trees between Pole 18552 - Pole 18566a/b | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 311 | F5034 | 90 Waiora Rd | 415FED | 2025-02-07 05:41 | 2025-02-07 06:21 | 0.0029619 | 7.4047e-05 | 1 | 40 | Unplanned | 6.0 Wildlife | Possom Blew 11kV Links @ Pole 12607 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 312 | PR325 | Otematata Station | 425FED | 2025-02-07 08:42 | 2025-02-07 13:48 | 0.022658 | 7.4047e-05 | 1 | 306 | Planned | 11.0 Planned Shutdown | Felling Trees | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 313 | F4942 | 261 Peebles Siding Rd | 457FED | 2025-02-09 09:57 | 2025-02-09 12:20 | 0.34698 | 0.0048871 | 66 | 4686 | Unplanned | 8.0 Defective Equipment | 11kV Wire on Ground @ Pole 70837 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 314 | PR318 | Frew Rd | 417FED | 2025-02-10 08:22 | 2025-02-10 16:04 | 0.29478 | 0.0014069 | 19 | 3981 | Planned | 11.0 Planned Shutdown | Replacing Poles & Crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 315 | PR319A | Frew Rd and Herbert Rd | 417FED | 2025-02-11 08:27 | 2025-02-11 14:48 | 0.39496 | 0.0010367 | 14 | 5334 | Planned | 11.0 Planned Shutdown | Replace Poles, Crossarms and Conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 316 | PR319B | Frew Rd and Herbert Rd | 417FED | 2025-02-12 08:22 | 2025-02-12 14:04 | 0.35454 | 0.0010367 | 14 | 4788 | Planned | 11.0 Planned Shutdown | Replace Poles, Crossarms and Conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 317 | PR327 | Special School Rd | 494FED | 2025-02-14 08:43 | 2025-02-14 13:24 | 0.79067 | 0.0028138 | 38 | 10678 | Planned | 11.0 Planned Shutdown | Trimming Trees Between Pole 31949 and 31959 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 318 | NJ714 | Island Cliff Rd | 473FED | 2025-02-20 08:50 | 2025-02-20 12:49 | 0.19467 | 0.00081451 | 11 | 2629 | Planned | 11.0 Planned Shutdown | Tightening 33kV and 11kV Lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 319 | NJ715 | Smillies Rd | 473FED | 2025-02-21 09:03 | 2025-02-21 11:47 | 0.21859 | 0.0013328 | 18 | 2952 | Planned | 11.0 Planned Shutdown | Tightening Various 11kV Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 320 | NJ722 | Shortland Rd | 304FED | 2025-02-24 08:31 | 2025-02-24 13:22 | 0.47405 | 0.001629 | 22 | 6402 | Planned | 11.0 Planned Shutdown | Tightening 33kV and 11kV Lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 321 | PI194A | Haka Valley Rd | 413FED | 2025-02-24 08:49 | 2025-02-24 15:44 | 0.58386 | 0.0014069 | 19 | 7885 | Planned | 11.0 Planned Shutdown | Replace Pole sand Crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 322 | NJ723 | TY Duncan Rd | 304FED | 2025-02-25 08:33 | 2025-02-25 11:05 | 0.033765 | 0.00022214 | 3 | 456 | Planned | 11.0 Planned Shutdown | Tightening 33kV and 11kV Lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 323 | PR333A | Haka Valley Rd | 413FED | 2025-02-25 08:48 | 2025-02-25 15:36 | 0.57401 | 0.0014069 | 19 | 7752 | Planned | 11.0 Planned Shutdown | Replace Poles and Crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 324 | F5461 | Coal Pit Rd | 449FED | 2025-02-25 09:34 | 2025-02-25 11:27 | 0.025102 | 0.00022214 | 3 | 339 | Unplanned | 8.0 Defective Equipment | Change Transformer T2040 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 325 | F5044 | Peebles Area | 219FED | 2025-02-25 12:34 | 2025-02-25 15:23 | 0.23599 | 0.0065902 | 89 | 3187 | Unplanned | 9.0 Cause Unknown | CB219 Peebles Tripped | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 326 | NJ725 | McCullock & Works Rd | 304FED | 2025-02-26 08:16 | 2025-02-26 13:32 | 0.14039 | 0.00044428 | 6 | 1896 | Planned | 11.0 Planned Shutdown | Tightening 33kV and 11kV Lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 327 | PR333B | Haka Valley Rd | 413FED | 2025-02-26 08:48 | 2025-02-26 13:30 | 0.39674 | 0.0014069 | 19 | 5358 | Planned | 11.0 Planned Shutdown | Replace Poles and Crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 328 | NJ732 | Mchenrys Rd | 413FED | 2025-02-27 08:32 | 2025-02-27 12:30 | 0.14098 | 0.00059237 | 8 | 1904 | Planned | 11.0 Planned Shutdown | Climbing and Tightening Patrol | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 329 | PR334 | Dansey Pass Rd | 421FED | 2025-02-28 08:45 | 2025-02-28 13:42 | 0.35187 | 0.0011847 | 16 | 4752 | Planned | 11.0 Planned Shutdown | Replace Pole 22836 and Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 330 | NJ733 | Mchenrys Rd | 413FED | 2025-02-28 09:12 | 2025-02-28 15:15 | 0.34943 | 0.00096261 | 13 | 4719 | Planned | 11.0 Planned Shutdown | Climbing and Tightening Patrol | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 331 | F5466 | 82 Allan Rd | 483FED | 2025-03-03 06:48 | 2025-03-03 10:04 | 0.029026 | 0.00014809 | 2 | 392 | Unplanned | 6.0 Wildlife | Rat Blew DDO Fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 332 | NJ734 | Mchenrys Rd | 413FED | 2025-03-03 08:40 | 2025-03-03 14:44 | 0.18867 | 0.00051833 | 7 | 2548 | Planned | 11.0 Planned Shutdown | Climbing and Tightening Patrol | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 333 | NJ748 | Reservoir Rd | 437FED | 2025-03-04 08:33 | 2025-03-04 10:12 | 0.17593 | 0.0017771 | 24 | 2376 | Planned | 11.0 Planned Shutdown | Install 400A Disconnector and LV monitor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 334 | PR336 | Special School Rd | 494FED | 2025-03-04 09:06 | 2025-03-04 13:32 | 0.72877 | 0.0027397 | 37 | 9842 | Planned | 11.0 Planned Shutdown | Installing 3 x DDOs and 30kVA Tx on Pole 31898 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 335 | NJ749 | Reservoir Rd | 437FED | 2025-03-04 12:30 | 2025-03-04 13:37 | 0.13395 | 0.0019993 | 27 | 1809 | Planned | 11.0 Planned Shutdown | Install 400A Disconnector and LV monitor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 336 | F10745 | 49 Finlanys Rd | 420FED | 2025-03-05 08:24 | 2025-03-05 09:44 | 0.0059237 | 7.4047e-05 | 1 | 80 | Unplanned | 6.0 Wildlife | Possom has caused DDOs to blow | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 337 | PR337 | Omarama-Otematata Rd | 423FED | 2025-03-05 08:25 | 2025-03-05 13:41 | 0.49137 | 0.001555 | 21 | 6636 | Planned | 11.0 Planned Shutdown | Remove 11kV Links on Pole 29693a/b. Replace pole 31079 and install top mount ABS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 338 | F15997 | Yare St | 406FED | 2025-03-05 22:28 | 2025-03-05 23:00 | 2.9154 | 0.10218 | 1380 | 39372 | Unplanned | 6.0 Wildlife | Possum up Pole 16183 caused flashover | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 339 | F10749 | 129 Steward Rd | 432FED | 2025-03-06 08:30 | 2025-03-06 09:29 | 0.0087375 | 0.00014809 | 2 | 118 | Unplanned | 6.0 Wildlife | Blown DDO caused by rat | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 340 | NJ738 | Farm Rd | 413FED | 2025-03-07 08:30 | 2025-03-07 12:50 | 0.019252 | 7.4047e-05 | 1 | 260 | Planned | 11.0 Planned Shutdown | Replace Poles and Crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 341 | F5652 | 84 James Rd | 479FED | 2025-03-08 08:44 | 2025-03-08 09:15 | 0.0065161 | 7.4047e-05 | 1 | 88 | Unplanned | 6.0 Wildlife | Blown HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 342 | NJ739 | Farm Rd | 413FED | 2025-03-10 08:32 | 2025-03-10 14:49 | 0.16749 | 0.00044428 | 6 | 2262 | Planned | 11.0 Planned Shutdown | Replace Poles 14406 and Tx | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 343 | NJ711 | Tokarahi Ngapara Rd | 308FED | 2025-03-10 10:08 | 2025-03-10 14:20 | 0.41051 | 0.001629 | 22 | 5544 | Planned | 11.0 Planned Shutdown | 33 & 11kV Tightening | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 344 | NJ740 | Milne Rd | 413FED | 2025-03-11 08:30 | 2025-03-11 14:52 | 0.31114 | 0.00081451 | 11 | 4202 | Planned | 11.0 Planned Shutdown | Replace Poles and Arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 345 | NJ745 | Lincoln St, Hampden | 480FED | 2025-03-11 10:17 | 2025-03-11 11:06 | 0.1415 | 0.0028878 | 39 | 1911 | Planned | 11.0 Planned Shutdown | Install LV Monitor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 346 | NJ741 | Milne Rd | 413FED | 2025-03-12 08:32 | 2025-03-12 15:27 | 0.64532 | 0.001555 | 21 | 8715 | Planned | 11.0 Planned Shutdown | Replace Poles and Arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 347 | NJ756 | Lambton St | 416FED | 2025-03-13 09:06 | 2025-03-13 11:06 | 0.1866 | 0.001555 | 21 | 2520 | Planned | 11.0 Planned Shutdown | Install LV Monitor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 348 | NJ757 | Beach Rd | 408FED | 2025-03-13 13:37 | 2025-03-13 15:50 | 0.21666 | 0.001629 | 22 | 2926 | Planned | 11.0 Planned Shutdown | Install LV Monitor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 349 | NJ758 | Westview Drive | 427FED | 2025-03-14 09:00 | 2025-03-14 10:37 | 0.19393 | 0.0019993 | 27 | 2619 | Planned | 11.0 Planned Shutdown | Install LV Monitor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 350 | F5702 | 98 Springhill Rd | 428FED | 2025-03-14 15:46 | 2025-03-14 17:45 | 0.044058 | 0.00037023 | 5 | 595 | Unplanned | 5.0 Third party Interference | Digger hit 11kV Line near pole 25892 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 351 | PR342A | Tokarahi Tapui Rd | 421FED | 2025-03-18 08:14 | 2025-03-18 16:24 | 0.2177 | 0.00044428 | 6 | 2940 | Planned | 11.0 Planned Shutdown | Felling Trees between Pole 10076 and 10081 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 352 | F5658 | TY Duncan Rd | 432FED | 2025-03-18 09:37 | 2025-03-18 11:52 | 0.0099963 | 7.4047e-05 | 1 | 135 | Unplanned | 9.0 Cause Unknown | Blown DDOs - Cause Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 353 | NJ783 | Haka Highway | 412FED | 2025-03-18 11:46 | 2025-03-18 12:14 | 0.0020733 | 7.4047e-05 | 1 | 28 | Planned | 11.0 Planned Shutdown | Decomission Chorus Site | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 354 | PR342B | Tokarahi Tapui Rd | 421FED | 2025-03-19 08:00 | 2025-03-19 16:26 | 0.22481 | 0.00044428 | 6 | 3036 | Planned | 11.0 Planned Shutdown | Felling Trees | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 355 | NJ769 | Haka Valley Rd | 413FED | 2025-03-19 08:36 | 2025-03-19 16:00 | 0.52603 | 0.0011847 | 16 | 7104 | Planned | 11.0 Planned Shutdown | Replace Pole sand VLF cable | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 356 | NJ776 | Moorland Settlement Rd | 413FED | 2025-03-20 08:43 | 2025-03-20 12:57 | 0.075231 | 0.00029619 | 4 | 1016 | Planned | 11.0 Planned Shutdown | Replace Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 357 | F12645 | Otiake Rd | 411FED | 2025-03-20 10:15 | 2025-03-20 11:17 | 0.1515 | 0.0024435 | 33 | 2046 | Unplanned | 5.0 Third party Interference | Report of Person trapped in tree near power lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 358 | PR344 | Shortland Rd | 432FED | 2025-03-21 08:28 | 2025-03-21 10:39 | 0.0097001 | 7.4047e-05 | 1 | 131 | Planned | 11.0 Planned Shutdown | Replace Tx with new 15kVA on pole 33203 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 359 | NJ777 | Menzies Rd | 413FED | 2025-03-21 08:35 | 2025-03-21 14:20 | 0.025546 | 7.4047e-05 | 1 | 345 | Planned | 11.0 Planned Shutdown | Replace Poles and tightening | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 360 | F5662 | 330 Springfield Rd | 416FED | 2025-03-24 08:25 | 2025-03-24 09:11 | 0.010218 | 0.00022214 | 3 | 138 | Unplanned | 6.0 Wildlife | Blown HV Fuses - Rats | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 361 | NJ778 | Haka Valley Rd | 413FED | 2025-03-25 09:10 | 2025-03-25 13:45 | 0.10181 | 0.00037023 | 5 | 1375 | Planned | 11.0 Planned Shutdown | Replace Pole 871620 and tightening | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 362 | NJ785 | Weston Rd | 427FED | 2025-03-25 10:01 | 2025-03-25 13:20 | 0.35365 | 0.0017771 | 24 | 4776 | Planned | 11.0 Planned Shutdown | Install LV Monitor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 363 | NJ779 | Haka Valley Rd | 413FED | 2025-03-26 08:50 | 2025-03-26 15:13 | 0.93588 | 0.0024435 | 33 | 12639 | Planned | 11.0 Planned Shutdown | Replace 11kV Pole 13186 and tightening | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 364 | NJ787 | Hilderthorpe Rd | 455FED | 2025-03-26 12:00 | 2025-03-26 13:11 | 0.0052573 | 7.4047e-05 | 1 | 71 | Planned | 11.0 Planned Shutdown | Install LV Monitor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 365 | NJ781 | Haka Valley Rd | 413FED | 2025-03-27 09:51 | 2025-03-27 15:33 | 0.32921 | 0.00096261 | 13 | 4446 | Planned | 11.0 Planned Shutdown | Replace Poles and Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 366 | NJ750 | Main St, Weston | 428FED | 2025-03-28 08:42 | 2025-03-28 10:43 | 0.017919 | 0.00014809 | 2 | 242 | Planned | 11.0 Planned Shutdown | Install LV Monitor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 367 | F12648 | Peebles Rd | 219FED | 2025-03-30 08:39 | 2025-03-30 09:35 | 0.087079 | 0.001555 | 21 | 1176 | Unplanned | 6.0 Wildlife | 11kV Conductor broken by Possum at Pole 2457 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Network Waitaki | 2025 |  | 368 | NJ791 | Haka Valley Rd | 413FED | 2025-03-31 09:08 | 2025-03-31 13:48 | 0.14513 | 0.00051833 | 7 | 1960 | Planned | 11.0 Planned Shutdown | Replace Crossarms and Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 9 | F-5419-A | Mata | Ruakaka CB3 | 2024-04-02 08:44 | 2024-04-02 11:37 | 0.12447 | 0.0016224 | 104 | 7979 | Unplanned | Defective Equipment | FP 380845 Shutdown to replace HV fuses Tx X221 (faulty) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 10 | O-406-C | Puwera | Maungatapere CB7 | 2024-04-02 09:07 | 2024-04-02 14:36 | 0.31821 | 0.00096721 | 62 | 20398 | Planned | Planned Interruption | Replace poles and crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 11 | O-640-C | Kensington | Alexander St CB8 | 2024-04-02 09:12 | 2024-04-02 14:40 | 0.62937 | 0.0019188 | 123 | 40344 | Planned | Planned Interruption | 123 ICP's advertised, OMS logged 89 (replaced Tx WC131 with Tx WC468 with 0 ICP's) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 12 | O-541-C | Swamp North | Hikurangi CB1042 | 2024-04-03 09:05 | 2024-04-03 13:40 | 0.20163 | 0.00073321 | 47 | 12925 | Planned | Planned Interruption | Replace cross arms and HV fuses at Dsubs KB337, KB306 and HV links 6750 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 13 | F-5434-A | Kaiatea | Ngunguru CB1072 | 2024-04-03 19:23 | 2024-04-03 19:24 | 0.012402 | 0.010624 | 681 | 795 | Unplanned | Unknown | Tripped O/C - Unknown cause - F5 - Sw 720 FPI activated | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 14 | F-5437-A | Coast | Dargaville CB6 | 2024-04-04 08:06 | 2024-04-04 08:22 | 0.24626 | 0.016255 | 1042 | 15786 | Unplanned | Unknown | A & C Phase OC trip. F4. Closed & held after 15 min | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 15 | O-736-C | Coast | Dargaville CB6 | 2024-04-04 09:45 | 2024-04-04 17:04 | 0.29679 | 0.00078001 | 50 | 19025 | Planned | Planned Interruption | X arm replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 16 | F-5455-A | Kensington | Alexander St CB8 | 2024-04-05 00:05 | 2024-04-05 00:21 | 0.18652 | 0.011513 | 738 | 11956 | Unplanned | Unknown | Trip EF - Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 17 | O-760-C | Wharekohe | Poroti CB1062 | 2024-04-05 09:34 | 2024-04-05 11:45 | 0.15123 | 0.0011544 | 74 | 9694 | Planned | Planned Interruption | Remove Knife links 8150KL. Remove OLD LS TX W133, DOF's and pole 54601 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 18 | F-5458-A | Taipuha | Mareretu CB1 | 2024-04-05 11:39 | 2024-04-05 12:55 | 0.10789 | 0.0014196 | 91 | 6916 | Unplanned | Defective Equipment | FP 380965 Cracked porcelain on DDO | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 19 | F-5470-A | Matapouri | Ngunguru CB1032 | 2024-04-05 23:48 | 2024-04-06 01:52 | 0.029562 | 0.0004524 | 29 | 1895 | Unplanned | Vegetation | FP 381053 - Gum Tree fell from slope into 11kV jumpers/ bushings/ HV Fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 20 | F-5473-A | Access Rd | Ruawai CB1022 | 2024-04-06 07:21 | 2024-04-06 07:42 | 0.078656 | 0.0052416 | 336 | 5042 | Unplanned | Unknown | CB 1022 RWI Trip Overcurrent B & C. Reclosed & BTN. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 21 | F-5476-A | Taipuha | Mareretu CB1 | 2024-04-06 09:43 | 2024-04-06 11:28 | 0.3906 | 0.0037128 | 238 | 25038 | Unplanned | Wildlife | Leech Road. Magpie found on pole top. Cause overcurrent trip. Removed & BTN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 22 | O-649-C | Puwera | Maungatapere CB7 | 2024-04-08 09:04 | 2024-04-08 13:43 | 0.091401 | 0.0003276 | 21 | 5859 | Planned | Planned Interruption | Pole and Xarm replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 23 | F-5515-A | Jordan Valley | Hikurangi CB1102 | 2024-04-09 03:36 | 2024-04-09 03:37 | 0.011294 | 0.0085801 | 550 | 724 | Unplanned | Unknown | CB 1102 HIK Trip & Close | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 24 | O-616-C | Access Rd | Ruawai CB1022 | 2024-04-09 09:03 | 2024-04-09 15:25 | 0.43503 | 0.0011388 | 73 | 27886 | Planned | Planned Interruption | X arm replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 25 | O-12991-A | Waipu | Ruakaka CB2 | 2024-04-09 09:07 | 2024-04-09 14:38 | 0.91913 | 0.0027768 | 178 | 58918 | Planned | Planned Interruption | Xarm and pole replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 26 | O-622-C | Jordan Valley | Hikurangi CB1102 | 2024-04-09 09:36 | 2024-04-09 15:03 | 0.16324 | 0.0004992 | 32 | 10464 | Planned | Planned Interruption | Xarm & pole replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 27 | O-397-C | Whakapara | Hikurangi CB1112 | 2024-04-10 09:05 | 2024-04-10 14:20 | 0.54009 | 0.001716 | 110 | 34621 | Planned | Planned Interruption | pole and x Arm replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 28 | F-5530-A | Ararua | Mareretu CB2 | 2024-04-10 14:07 | 2024-04-10 14:24 | 0.001326 | 7.8001e-05 | 5 | 85 | Unplanned | Defective Equipment | FP381151 Check & clean contacts on HV fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 29 | F-5533-A | Mangawhai Heads | Mangawhai North CB1 | 2024-04-10 20:32 | 2024-04-10 21:21 | 1.0532 | 0.021575 | 1383 | 67513 | Unplanned | Unknown | 381171 - Tripped O/C A&B phase, F3 so patrolled and livened - Unknown cause | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 30 | O-13036-A | Swamp North | Hikurangi CB1042 | 2024-04-11 08:47 | 2024-04-11 13:31 | 0.23924 | 0.00084241 | 54 | 15336 | Planned | Planned Interruption | Install New Tx KB 167 (CST live edit required) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 31 | O-3541-B | Austin Road | Maunu CB1072 | 2024-04-11 09:01 | 2024-04-11 16:27 | 0.4105 | 0.00092041 | 59 | 26314 | Planned | Planned Interruption | Cut into existing 3core 35mm XLPE operation past Ashbury Height Subdivision between switch 7748 and 7749 Turn into newly instal | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 32 | O-748-C | Tangaihi | Ruawai CB1032 | 2024-04-11 09:13 | 2024-04-11 15:37 | 0.041933 | 0.0001092 | 7 | 2688 | Planned | Planned Interruption | Install new Transformer K474 & Remove transformer K320 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 33 | F-5536-A | Coast | Dargaville CB6 | 2024-04-11 12:03 | 2024-04-11 19:31 | 3.496 | 0.02379 | 1525 | 224100 | Unplanned | Vegetation | FP381218 Tree falled across lines - Sw 2120. Only 1 faultman available for several feeder faults. Isolated for Tree cutters. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 34 | F-5539-A | North Dargaville | Dargaville CB1 | 2024-04-11 12:15 | 2024-04-11 15:37 | 0.39545 | 0.0040092 | 257 | 25349 | Unplanned | Vegetation | 381221 - Branch on line @ pole 24761 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 35 | F-5542-A | Tangowahine | Dargaville CB8 | 2024-04-11 12:32 | 2024-04-11 18:57 | 0.64806 | 0.00195 | 125 | 41542 | Unplanned | Unknown | 381230 -OC Trip BC.Shortage of fault staff for initial restoration.Recl 1504 found faulty, would not close,Marlon attended 12/04 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 36 | F-5548-A | Montgomery Ave | Onerahi CB8 | 2024-04-11 13:06 | 2024-04-11 15:20 | 0.77342 | 0.016193 | 1038 | 49578 | Unplanned | Adverse Weather | FP381231 Sw 938 indicated fault ABC phase. Remotely liven to Sw 938, Patrol and liven remaining. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 37 | F-5545-A | North Dargaville | Dargaville CB1 | 2024-04-11 13:08 | 2024-04-11 15:48 | 0.33472 | 0.0020904 | 134 | 21456 | Unplanned | Defective Equipment | FP381229 Report of LV lines down on fence. De-energised 11kV remotely til staff could attend to isolate | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 38 | F-5572-A | Bickerstaff | Maungaturoto CB2 | 2024-04-11 13:54 | 2024-04-11 23:34 | 0.19216 | 0.01209 | 775 | 12318 | Unplanned | Defective Equipment | Tripped OC A & B Phase (F4) on F-5557-A Fault found later on F-5572-A (381259) - HV jumper off @ pole 16244 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 39 | F-5560-A | North Kaiwaka | Kaiwaka CB1022 | 2024-04-11 15:23 | 2024-04-12 06:28 | 0.59945 | 0.016755 | 1074 | 38426 | Unplanned | Vegetation | 381251 - Tripped twice on E/F - Patrolled and found stick on line, all clear | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 40 | F-5563-A | Turiwiri | Dargaville CB9 | 2024-04-11 15:54 | 2024-04-11 23:36 | 0.52611 | 0.027472 | 1761 | 33725 | Unplanned | Vegetation | 381249 - Trees in lines Between pole 21511 & 21512. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 41 | F-5566-A | Town Dargaville | Dargaville CB3 | 2024-04-11 19:59 | 2024-04-12 01:58 | 0.32378 | 0.0011388 | 73 | 20755 | Unplanned | Defective Equipment | DA11 & DA48 lv back feed & DA 48 shut down to remove gen @ 2250hrs Kere has tied LV to all ICP's off Tx DA11 @ 0158hrs Kere | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 42 | O-643-C | Puwera | Maungatapere CB7 | 2024-04-12 10:04 | 2024-04-12 12:51 | 0.036473 | 0.0002184 | 14 | 2338 | Planned | Planned Interruption | X arm replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 43 | F-5599-A | Pataua | Parua Bay CB1 | 2024-04-12 19:21 | 2024-04-12 22:39 | 0.0052728 | 6.2401e-05 | 4 | 338 | Unplanned | Defective Equipment | FP 381304-Replace HV Fuse carriers Tx OO242 (1 broken). 2nd shut to replace L9085 fuses & barrells (1 corroded) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 44 | F-5605-A | Kaiwaka South | Kaiwaka CB1072 | 2024-04-13 12:01 | 2024-04-13 17:21 | 0.26572 | 0.0022932 | 147 | 17033 | Unplanned | Vegetation | 381315 Tree across the line btween poles 33809 - 33810 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 45 | O-3547-B | Montgomery Ave | Onerahi CB8 | 2024-04-15 09:05 | 2024-04-15 15:12 | 0.81066 | 0.0024024 | 154 | 51965 | Planned | Planned Interruption | Replace pole and OH TX OP248 with Ground mount TX OP256 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 46 | O-775-C | Puwera | Maungatapere CB7 | 2024-04-15 09:49 | 2024-04-15 12:28 | 0.22324 | 0.001404 | 90 | 14310 | Planned | Planned Interruption | Clear trees around lines from pole 46407 to pole 46411 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 47 | F-5620-A | Pataua | Parua Bay CB1 | 2024-04-15 15:47 | 2024-04-15 16:43 | 0.1717 | 0.0030732 | 197 | 11006 | Unplanned | Defective Equipment | 381375. Replace faulty DDOs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 48 | F-5623-A | ToeToe Rd | Kioreroa CB7 | 2024-04-15 16:38 | 2024-04-15 17:28 | 0.068641 | 0.0013572 | 87 | 4400 | Unplanned | Defective Equipment | 381346. Replace DDOs Tx X279 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 49 | O-3004-B | Whatatiri | Maungatapere CB8 | 2024-04-16 08:59 | 2024-04-16 14:31 | 0.68884 | 0.0020748 | 133 | 44156 | Planned | Planned Interruption | Replace Cross arms and refurbish Dsubs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 50 | O-178-C | Coast | Dargaville CB6 | 2024-04-17 09:03 | 2024-04-17 16:05 | 1.9983 | 0.0047424 | 304 | 128098 | Planned | Planned Interruption | Remove switches 2158 & 2159. Install Switches 10162 &10163. Outages on DAR CB6 & CB7 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 51 | O-811-C | Swamp North | Hikurangi CB1042 | 2024-04-17 09:07 | 2024-04-17 14:53 | 0.54516 | 0.0015756 | 101 | 34946 | Planned | Planned Interruption | x Arm replacements, straighten poles, replace Tx | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 52 | O-12799-A | Whatatiri | Maungatapere CB8 | 2024-04-18 08:35 | 2024-04-18 13:17 | 0.58513 | 0.0020748 | 133 | 37508 | Planned | Planned Interruption | Replace Cross arms, HV transformer fuses at Dsub W420 W343 and connections. Work is between poles 60005,304795 and 59980 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 53 | O-652-C | King Road | Mangawhai North CB2 | 2024-04-18 10:25 | 2024-04-18 13:59 | 0.0434 | 0.0002028 | 13 | 2782 | Planned | Planned Interruption | Network Maintenance - straighten pole 32475 and re-do connections at pole 32477 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 54 | F-5689-A | North River | Ruakaka CB7 | 2024-04-19 08:00 | 2024-04-19 12:56 | 0.70914 | 0.0041964 | 269 | 45457 | Unplanned | Defective Equipment | FP 381499 - Lines down between 44012 & 44016. Eye bolt ripped out of Crossarm. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 55 | O-631-C | Puwera | Maungatapere CB7 | 2024-04-19 09:01 | 2024-04-19 13:23 | 0.077689 | 0.0002964 | 19 | 4980 | Planned | Planned Interruption | Replace pole 46034 and cross arms at numerous sites and connections at Dsub O129 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 56 | O-661-C | One Tree Point | Ruakaka CB6 | 2024-04-19 09:06 | 2024-04-19 13:12 | 0.78671 | 0.003198 | 205 | 50430 | Planned | Planned Interruption | Replace cross arms and connections and replace pole 19949 and change TX RO366 from 30kVA to 50kVA | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 57 | F-5701-A | Titoki | Poroti CB1032 | 2024-04-20 09:43 | 2024-04-20 09:57 | 0.19408 | 0.013369 | 857 | 12441 | Unplanned | Unknown | O/C. Also took out part of DAR CB 8 due to network in abnormal state (SW2061 open, Sw2175 open) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 58 | F-5710-A | Whakapara | Hikurangi CB1112 | 2024-04-20 15:27 | 2024-04-20 19:10 | 0.57337 | 0.011279 | 723 | 36754 | Unplanned | Third Party Interference | FP 381543. De-energised HV following report of car vs pole. LV pole 42411 replaced. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 59 | F-5719-A | Coast | Dargaville CB6 | 2024-04-21 20:35 | 2024-04-22 00:46 | 0.17249 | 0.00068641 | 44 | 11057 | Unplanned | Defective Equipment | Rotten xarm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 60 | F-5725-A | North Kaiwaka | Kaiwaka CB1022 | 2024-04-21 23:24 | 2024-04-22 09:55 | 0.95537 | 0.0072697 | 466 | 61241 | Unplanned | Wildlife | Curtis Point Rd - broken HV line Pole 29850. 2nd feeder fault - tripped again. Road closed Mountain Rd near pole 29817 by geeze | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 61 | F-5731-A | Poroti | Maungatapere CB2 | 2024-04-22 04:35 | 2024-04-22 06:05 | 0.4686 | 0.0096253 | 617 | 30038 | Unplanned | Unknown | 381553. Patrol lines after feeder fault. Nothing found & Line BTN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 62 | F-5734-A | Turiwiri | Dargaville CB9 | 2024-04-22 06:34 | 2024-04-22 06:50 | 0.076472 | 0.0078625 | 504 | 4902 | Unplanned | Unknown | CB9 DAR Trip & 15 Min Close. Overcurrent A & B | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 63 | F-5737-A | Ararua | Mareretu CB2 | 2024-04-22 10:54 | 2024-04-22 12:25 | 0.39607 | 0.0043524 | 279 | 25389 | Unplanned | Defective Equipment | 381561. Isolate HV to repair spragged wires & install temp links for upcoming shutdown. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 64 | F-5740-A | Ararua | Mareretu CB2 | 2024-04-22 11:35 | 2024-04-22 13:09 | 0.0014664 | 1.56e-05 | 1 | 94 | Unplanned | Defective Equipment | 1 x HV fuse blown. Isolated & replaced fuse holder due to damage. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 65 | O-262-C | Hokianga Rd | Dargaville CB7 | 2024-04-23 09:02 | 2024-04-23 17:08 | 0.0075973 | 1.56e-05 | 1 | 487 | Planned | Planned Interruption | 11kV OHUG, connect 2x 11kV cables & liven. Cut away redundant overhead lines. Large work load resulting in late restoration. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 66 | O-838-C | Ararua | Mareretu CB2 | 2024-04-23 09:11 | 2024-04-23 14:45 | 0.17641 | 0.0005304 | 34 | 11308 | Planned | Planned Interruption | Network Maintenance - replace pole 48576, hardware and change transformer like for like | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 67 | O-3574-B | Kaiwaka South | Kaiwaka CB1072 | 2024-04-23 09:12 | 2024-04-23 12:50 | 0.50314 | 0.0023088 | 148 | 32252 | Planned | Planned Interruption | Network Maintenance - REPLACE Sw3950 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 68 | F-5746-A | Springs Flat | Kamo CB1 | 2024-04-23 09:22 | 2024-04-23 09:37 | 0.099685 | 0.0084241 | 540 | 6390 | Unplanned | Unknown | A, B, C & E fault. Closed and held in after 15 mins. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 69 | O-3616-B | Te Kopuru | Dargaville CB2 | 2024-04-23 09:48 | 2024-04-23 13:36 | 0.01067 | 4.68e-05 | 3 | 684 | Planned | Planned Interruption | LV Voltage Maintenance/Install | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 70 | O-667-C | 2nd Ave | Alexander St CB3 | 2024-04-23 10:32 | 2024-04-23 13:11 | 0.3299 | 0.0020748 | 133 | 21147 | Planned | Planned Interruption | Investigate High Partial discharge at switches 9010-9011-9012 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 71 | O-844-C | Swamp North | Hikurangi CB1042 | 2024-04-24 09:04 | 2024-04-24 12:54 | 0.36239 | 0.0015756 | 101 | 23230 | Planned | Planned Interruption | Replacing cross arms straightening poles & replacing TX. Repalcing Sw 679 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 72 | O-496-C | Tikipunga Hill | Tikipunga CB4 | 2024-04-24 09:05 | 2024-04-24 12:06 | 0.0084709 | 4.68e-05 | 3 | 543 | Planned | Planned Interruption | Install pole to reduce span length and raise LV arm. Remove temp switch @pole 32174 on completion of work. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 73 | F-5758-A | Swamp North | Hikurangi CB1042 | 2024-04-24 21:52 | 2024-04-25 02:16 | 0.46935 | 0.011373 | 729 | 30086 | Unplanned | Defective Equipment | 381739. Line down at pole 38449. No cause found. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 74 | F-5761-A | Swamp North | Hikurangi CB1042 | 2024-04-24 21:58 | 2024-04-24 22:00 | 0.01429 | 0.0073945 | 474 | 916 | Unplanned | Defective Equipment | 381739. During fault on CB 1042 the FPIs for Sw 10010 should have activated as the lines down was past it. See CE Notes F-5761-A | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 75 | F-5770-A | One Tree Point | Ruakaka CB6 | 2024-04-26 14:51 | 2024-04-26 15:40 | 0.31213 | 0.0063961 | 410 | 20008 | Unplanned | Unknown | FP 381812. Patrolled before livening due to heavy fault current | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 76 | O-3622-B | Kaka St | Whangarei South CB1032 | 2024-04-28 09:01 | 2024-04-28 13:47 | 0.11365 | 0.0004056 | 26 | 7285 | Planned | Planned Interruption |  | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 77 | O-823-C | Hakaru | Kaiwaka CB1032 | 2024-04-30 09:05 | 2024-04-30 14:30 | 0.35997 | 0.0011076 | 71 | 23075 | Planned | Planned Interruption | hardware replacements and changing DSUB MC302 like for like | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 78 | O-544-C | ToeToe Rd | Kioreroa CB7 | 2024-04-30 09:12 | 2024-04-30 14:25 | 0.12695 | 0.0004056 | 26 | 8138 | Planned | Planned Interruption | Pole and cross arm replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 79 | F-5785-A | Town Dargaville | Dargaville CB3 | 2024-04-30 16:04 | 2024-04-30 18:16 | 0.42755 | 0.014087 | 903 | 27407 | Unplanned | Third Party Interference | FP - 381956 / Event # - F3965949 - LV Lines down @ road crossing 32701 to 54143. Caused by Truck. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 80 | O-3580-B | Kaiwaka South | Kaiwaka CB1072 | 2024-05-01 09:25 | 2024-05-01 15:30 | 0.039793 | 0.00010902 | 7 | 2555 | Planned | Planned Interruption | Network Maintenance - replace pole 33930 and transformer like for like | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 81 | O-3625-B | Paranui | Tikipunga CB6 | 2024-05-01 09:30 | 2024-05-01 10:53 | 0.020683 | 0.00024919 | 16 | 1328 | Planned | Planned Interruption | Network Extension upgrade tx from 75kVA to a 100kVA | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 82 | F-5803-A | Access Rd | Ruawai CB1022 | 2024-05-01 18:17 | 2024-05-01 21:12 | 0.1281 | 0.0018845 | 121 | 8225 | Unplanned | Defective Equipment | FP 382001 LV lines down across Rd - lv cut away between poles 44561 & 44562 - ICP 530929 previously electrially disconnected - | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 83 | O-3730-B | Fert. Works | Kioreroa CB6 | 2024-05-02 04:32 | 2024-05-02 04:48 | 0.0017443 | 0.00010902 | 7 | 112 | Planned | Planned Interruption | Replacement HV fuses to correct sizing - down gradded to 50A- KN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 84 | O-3631-B | Pataua | Parua Bay CB1 | 2024-05-02 09:01 | 2024-05-02 15:20 | 1.601 | 0.0050461 | 324 | 102798 | Planned | Planned Interruption | Improvements in Supply Quality - REMOVE Sw's 9885 & 9912, REPOSITION & INSTALL NEW Sw's 10134 & 10135 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 85 | O-3577-B | Waipu | Ruakaka CB2 | 2024-05-02 09:25 | 2024-05-02 13:29 | 0.20521 | 0.00084102 | 54 | 13176 | Planned | Planned Interruption | Network Maintenance replacing cross arms on poles 10383 and 10384 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 86 | O-3583-B | Dunns Rd | Ruawai CB1082 | 2024-05-02 09:36 | 2024-05-02 10:47 | 0.087357 | 0.0012304 | 79 | 5609 | Planned | Planned Interruption | Reconfigure jumpers at pole 906579 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 87 | F-5812-A | North Dargaville | Dargaville CB1 | 2024-05-02 11:57 | 2024-05-02 18:19 | 0.28195 | 0.0023985 | 154 | 18103 | Unplanned | Third Party Interference | F3967151 / FP 382028 - Car vs pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 88 | O-3586-B | Whangarei Heads | Parua Bay CB3 | 2024-05-03 09:08 | 2024-05-03 14:18 | 1.0629 | 0.0034264 | 220 | 68248 | Planned | Planned Interruption | Network Maintenance replacing Cross arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 89 | O-3862-B | Tangowahine | Dargaville CB8 | 2024-05-03 09:36 | 2024-05-03 13:33 | 0.23983 | 0.0010435 | 67 | 15399 | Planned | Planned Interruption | Replace damaged Recloser 1504 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 90 | O-3754-B | Onoke | Kamo CB8 | 2024-05-05 09:15 | 2024-05-05 14:54 | 0.35374 | 0.0010435 | 67 | 22713 | Planned | Planned Interruption | Upgrade ground mount D-Sub KV108 to 300kva. Replace concrete base. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 91 | O-3751-B | Titoki | Poroti CB1032 | 2024-05-05 10:12 | 2024-05-05 11:39 | 0.17655 | 0.0020247 | 130 | 11336 | Planned | Planned Interruption | Isolate 11kv for Fulton hogan to replace Road sign near lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 92 | O-3652-B | Charles St | Kamo CB2 | 2024-05-06 09:00 | 2024-05-06 13:13 | 0.14973 | 0.00059183 | 38 | 9614 | Planned | Planned Interruption | Network Maintenance - Replace LV arms at Pole 64319 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 93 | O-3655-B | Dunns Rd | Ruawai CB1082 | 2024-05-06 09:38 | 2024-05-06 14:03 | 0.11969 | 0.00045166 | 29 | 7685 | Planned | Planned Interruption | Drop lines from pole 45724 to pole 45725 for vegetation to drop tree. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 94 | O-3775-B | Taipuha | Mareretu CB1 | 2024-05-06 09:51 | 2024-05-06 12:49 | 0.016634 | 9.3447e-05 | 6 | 1068 | Planned | Planned Interruption | Liven new Tx B264 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 95 | F-5833-A | Maungatapere - Dairy Factory | Maungatapere CB6 | 2024-05-06 18:27 | 2024-05-07 03:40 | 0.59613 | 0.005638 | 362 | 38276 | Unplanned | Third Party Interference | FP382234 / F-5833-A - Car V Pole (No trip,Pole broken at base) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 96 | F-5839-A | Swamp North | Hikurangi CB1042 | 2024-05-06 20:33 | 2024-05-06 22:09 | 0.0029903 | 3.1149e-05 | 2 | 192 | Unplanned | Defective Equipment | FP382233 - F-5839-A. HV Jumper off @ Tx, Terminal bolt broken | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 97 | O-700-C | Swamp North | Hikurangi CB1042 | 2024-05-07 09:02 | 2024-05-07 13:59 | 0.68459 | 0.002305 | 148 | 43956 | Planned | Planned Interruption | Replace Cross arms and connections. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 98 | O-3649-B | Puwera | Maungatapere CB7 | 2024-05-07 09:06 | 2024-05-07 15:06 | 0.072889 | 0.00020247 | 13 | 4680 | Planned | Planned Interruption | Network Maintenance - ARM & HARDWARE REPLACEMENTS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 99 | O-3658-B | Marsden Pt | Ruakaka CB1 | 2024-05-07 09:08 | 2024-05-07 13:12 | 0.65743 | 0.0026944 | 173 | 42212 | Planned | Planned Interruption | Network Extension install new TX on pole 16569 and disconnect the old LV overhead cable between poles 16570-332013 and run & ere | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 100 | O-3778-B | Charles St | Kamo CB2 | 2024-05-07 09:17 | 2024-05-07 14:56 | 0.20063 | 0.00059183 | 38 | 12882 | Planned | Planned Interruption | Upgrade transformer KT104 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 101 | O-3784-B | Langs Beach | Mangawhai North CB3 | 2024-05-07 09:45 | 2024-05-07 13:39 | 0.014578 | 6.2298e-05 | 4 | 936 | Planned | Planned Interruption | Network Extension - Replace pole 10718. Erect & liven 30kVA Tx RR353. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 102 | O-3646-B | Pataua | Parua Bay CB1 | 2024-05-08 09:02 | 2024-05-08 15:12 | 0.47253 | 0.0012771 | 82 | 30340 | Planned | Planned Interruption | Network Maintenance - REPLACE POLE 24608 (TxPO117) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 103 | O-703-C | Jordan Valley | Hikurangi CB1102 | 2024-05-08 09:09 | 2024-05-08 14:42 | 0.25921 | 0.00077873 | 50 | 16643 | Planned | Planned Interruption | Replace HV & LV cross arms. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 104 | O-3694-B | Town Hikurangi | Hikurangi CB1082 | 2024-05-08 09:31 | 2024-05-08 15:17 | 0.3341 | 0.00096562 | 62 | 21452 | Planned | Planned Interruption | Network Maintenance Replace Transformer KS145 & run new HV & LV cables up pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 105 | F-5854-A | ToeToe Rd | Kioreroa CB7 | 2024-05-08 10:51 | 2024-05-08 12:01 | 0.13246 | 0.0033641 | 216 | 8505 | Unplanned | Defective Equipment | LV - ABC Lines down @ Pole 327366 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 106 | O-3664-B | Jordan Valley | Hikurangi CB1102 | 2024-05-09 09:03 | 2024-05-09 12:51 | 0.088775 | 0.00038936 | 25 | 5700 | Planned | Planned Interruption | Replace HV & LV cross arms, HV fuses and connections | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 107 | O-3865-B | Montgomery Ave | Onerahi CB8 | 2024-05-10 09:03 | 2024-05-10 15:57 | 0.61681 | 0.0014952 | 96 | 39604 | Planned | Planned Interruption | Replacing 11kv 400v poles 36555 & 36556 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 108 | O-3676-B | Puwera | Maungatapere CB7 | 2024-05-10 09:08 | 2024-05-10 12:50 | 0.093354 | 0.00042051 | 27 | 5994 | Planned | Planned Interruption | Network Maintenance replacing poles cross arms HV connections | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 109 | O-3667-B | Alamein Ave | Onerahi CB3 | 2024-05-10 09:11 | 2024-05-10 13:42 | 0.16461 | 0.00060741 | 39 | 10569 | Planned | Planned Interruption | Network Maintenance - LV ARM & HARDWARE REPLACEMENTS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 110 | O-3793-B | Paparoa | Mareretu CB6 | 2024-05-10 09:36 | 2024-05-10 13:41 | 0.045789 | 0.00018689 | 12 | 2940 | Planned | Planned Interruption | Reface pole 31131 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 111 | F-5878-A | Maungakaramea | Maungatapere CB3 | 2024-05-10 15:48 | 2024-05-10 16:31 | 0.040852 | 0.00095004 | 61 | 2623 | Unplanned | Defective Equipment | FP 382401 Broken Xarm @ pole 53736 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 112 | F-5884-A | Swamp North | Hikurangi CB1042 | 2024-05-13 08:12 | 2024-05-13 08:27 | 0.045992 | 0.0062921 | 404 | 2953 | Unplanned | Unknown | Sw 10010 indicated B phase. Sw 10010 closed after 15 minutes | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 113 | O-3679-B | Turiwiri | Dargaville CB9 | 2024-05-13 09:04 | 2024-05-13 15:04 | 0.17942 | 0.00049838 | 32 | 11520 | Planned | Planned Interruption | Replace HV poles and crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 114 | O-820-C | Whatatiri | Maungatapere CB8 | 2024-05-14 09:01 | 2024-05-14 14:22 | 0.50888 | 0.0015886 | 102 | 32674 | Planned | Planned Interruption | Replace cross arms at numerous sites and pole 60121 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 115 | O-3796-B | Titoki | Poroti CB1032 | 2024-05-14 10:04 | 2024-05-14 13:19 | 0.0060741 | 3.1149e-05 | 2 | 390 | Planned | Planned Interruption | Urgent Repairs - Transformer replacement & LV maintenance.. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 116 | F-5890-A | Waipu | Ruakaka CB2 | 2024-05-15 03:49 | 2024-05-15 07:01 | 0.90932 | 0.016338 | 1049 | 58385 | Unplanned | Vegetation | FP382507 - Found gum bark across 11kV Tx RR194 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 117 | F-5893-A | ToeToe Rd | Kioreroa CB7 | 2024-05-15 05:40 | 2024-05-15 08:09 | 0.76952 | 0.013908 | 893 | 49409 | Unplanned | Defective Equipment | 382522/ Jumper On Xarm. Stand off insulator installed (Fault found later on F-5902-A) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 118 | O-847-C | Kaiatea | Ngunguru CB1072 | 2024-05-15 09:13 | 2024-05-15 12:38 | 0.75349 | 0.0036756 | 236 | 48380 | Planned | Planned Interruption | Replant pole 59285 (908217) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 119 | O-3973-B | Puwera | Maungatapere CB7 | 2024-05-15 09:26 | 2024-05-15 14:35 | 0.091594 | 0.00029592 | 19 | 5881 | Planned | Planned Interruption | Acces through 11kv Only to work on 33kV | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 120 | F-5899-A | Pataua | Parua Bay CB1 | 2024-05-15 10:10 | 2024-05-15 13:23 | 0.081751 | 0.00095004 | 61 | 5249 | Unplanned | Defective Equipment | Line side HV jumper off at DDOs & also replaced DDOs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 121 | F-5902-A | ToeToe Rd | Kioreroa CB7 | 2024-05-15 10:43 | 2024-05-15 13:23 | 0.12453 | 0.010715 | 688 | 7996 | Unplanned | Defective Equipment | 382522/ Jumper on Xarm @ pole 46122. Related to earlier tripping F-5893-A | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 122 | O-3799-B | North River | Ruakaka CB7 | 2024-05-16 09:09 | 2024-05-16 12:53 | 0.087217 | 0.00038936 | 25 | 5600 | Planned | Planned Interruption | Network Maintenance, change span of 7064 wire to Flourine | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 123 | O-3895-B | Swamp North | Hikurangi CB1042 | 2024-05-16 09:16 | 2024-05-16 14:01 | 0.24415 | 0.0008566 | 55 | 15676 | Planned | Planned Interruption | Network Maintenance cross arm replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 124 | F-5917-A | Wairere | Mareretu CB5 | 2024-05-16 23:04 | 2024-05-16 23:05 | 0.0081455 | 0.0065101 | 418 | 523 | Unplanned | Unknown | Trip OC Phase BC FPI @ Sw 381 OC Phase AB | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 125 | F-5935-A | Town Hikurangi | Hikurangi CB1082 | 2024-05-17 15:22 | 2024-05-17 15:51 | 0.25175 | 0.0085193 | 547 | 16164 | Unplanned | Defective Equipment | FP:382591 - Customer reported lines down. Jason Rhodes found broken guy wire. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 126 | O-646-C | Treatment | Kioreroa CB2 | 2024-05-19 09:01 | 2024-05-19 14:19 | 1.2288 | 0.0039559 | 254 | 78900 | Planned | Planned Interruption | Network Maintenance - POLE, ARM & HARDWARE REPLACEMENT | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 127 | O-3829-B | Bickerstaff | Maungaturoto CB2 | 2024-05-20 09:39 | 2024-05-20 14:04 | 0.10893 | 0.0013238 | 85 | 6994 | Planned | Planned Interruption | Network Maintenance - replace 11kV fuse carriers. & Replace Tx DA237 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 128 | O-3685-B | Marua | Hikurangi CB1022 | 2024-05-21 09:06 | 2024-05-21 13:49 | 0.21597 | 0.00076315 | 49 | 13867 | Planned | Planned Interruption | Network Maintenance replace poles and cross arms as per plan. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 129 | O-793-C | Paranui | Tikipunga CB6 | 2024-05-21 09:15 | 2024-05-21 10:53 | 0.083947 | 0.0008566 | 55 | 5390 | Planned | Planned Interruption | Replace poles 51103 and 51104 to gain height | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 130 | F-6007-A | Turiwiri | Dargaville CB9 | 2024-05-21 17:13 | 2024-05-21 19:45 | 0.044979 | 0.00029592 | 19 | 2888 | Unplanned | Defective Equipment | FP 382710 Shutdown to repair blown HV jumper @ Tx J248 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 131 | F-6010-A | Te Kopuru | Dargaville CB2 | 2024-05-21 19:31 | 2024-05-21 19:47 | 0.11767 | 0.014874 | 955 | 7555 | Unplanned | Unknown | Tripped O/C B&C phase - Unknown cause - SCADA switching only | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 132 | O-3916-B | Waipu | Ruakaka CB2 | 2024-05-22 09:01 | 2024-05-22 13:25 | 0.50077 | 0.0019001 | 122 | 32153 | Planned | Planned Interruption | Network Maintenance replace cross arms and poles and transformer. Pole 10317.RR159.RR267.Pole 10351 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 133 | O-3985-B | Dunns Rd | Ruawai CB1082 | 2024-05-22 12:31 | 2024-05-22 13:55 | 0.0013083 | 1.5575e-05 | 1 | 84 | Planned | Planned Interruption | Network Maintenance - Replace Tx G142 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 134 | F-6031-A | North Kaiwaka | Kaiwaka CB1022 | 2024-05-23 06:38 | 2024-05-23 10:36 | 0.3893 | 0.0033952 | 218 | 24996 | Unplanned | Wildlife | FP -382784 Lines down Goose vs lines Pt Curtis | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 135 | O-3901-B | Titoki | Poroti CB1032 | 2024-05-23 09:02 | 2024-05-23 13:44 | 0.10541 | 0.00037379 | 24 | 6768 | Planned | Planned Interruption | Network Maintenance new guy wires straighten poles and new cross arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 136 | F-6034-A | Hakaru | Kaiwaka CB1032 | 2024-05-23 11:41 | 2024-05-23 13:05 | 0.087684 | 0.0025231 | 162 | 5630 | Unplanned | Unknown | Devich Rd - Repaired spragged 11kv line FP 382784 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 137 | O-4075-B | Fert. Works | Kioreroa CB6 | 2024-05-23 22:06 | 2024-05-24 01:08 | 0.27212 | 0.0014952 | 96 | 17472 | Planned | Planned Interruption | Transport high load from 17 Fraser street to 340 Port Road, Port Whangarei | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 138 | F-6037-A | Fert. Works | Kioreroa CB6 | 2024-05-24 05:56 | 2024-05-24 07:18 | 0.026819 | 0.00032706 | 21 | 1722 | Unplanned | Defective Equipment | FP382812 - Reinstate cable onto HV DDO Fuse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 139 | O-4033-B | Tikipunga Hill | Tikipunga CB4 | 2024-05-24 09:06 | 2024-05-24 11:35 | 0.0069618 | 4.6724e-05 | 3 | 447 | Planned | Planned Interruption | Replace pole 908166 to gain correct ground clearance. This site has access issues and need to be done before it gets too wet. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 140 | F-6046-A | Western Hills Dr | Alexander St CB7 | 2024-05-24 21:12 | 2024-05-25 03:59 | 1.2043 | 0.016213 | 1041 | 77322 | Unplanned | Third Party Interference | FP382855 Replace pole damaged by vehicle Reg ZJ2940 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 141 | O-4078-B | Fert. Works | Kioreroa CB6 | 2024-05-25 22:02 | 2024-05-26 01:56 | 0.34987 | 0.0014952 | 96 | 22464 | Planned | Planned Interruption | Shut down for high load | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 142 | F-6049-A | Tangaihi | Ruawai CB1032 | 2024-05-26 15:25 | 2024-05-26 15:40 | 0.089257 | 0.0099365 | 638 | 5731 | Unplanned | Unknown | SCADA switching only Tripped O/C - Unknown cause | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 143 | O-841-C | Brynderwyn | Maungaturoto CB1 | 2024-05-27 09:13 | 2024-05-27 12:29 | 0.0030526 | 1.5575e-05 | 1 | 196 | Planned | Planned Interruption | Network Maintenance - straighten pole 305359 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 144 | O-4003-B | Swamp North | Hikurangi CB1042 | 2024-05-27 09:29 | 2024-05-27 13:22 | 0.19596 | 0.00084102 | 54 | 12582 | Planned | Planned Interruption | Refurbish Dsub KB137 and replace HV arms on pole 38612. also replace LV arms at poles 37595, 38584 and 38582 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 145 | O-4069-B | King Road | Mangawhai North CB2 | 2024-05-28 12:32 | 2024-05-28 14:07 | 0.63793 | 0.0066659 | 428 | 40960 | Planned | Planned Interruption | Installing new automated Switch 10092 on pole 17639. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 146 | O-3718-B | Turiwiri | Dargaville CB9 | 2024-05-29 09:05 | 2024-05-29 15:47 | 0.25044 | 0.00062298 | 40 | 16080 | Planned | Planned Interruption | Replace HV and LV cross arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 147 | O-3721-B | Matapouri | Ngunguru CB1032 | 2024-05-29 09:28 | 2024-05-29 13:47 | 0.008052 | 3.1149e-05 | 2 | 517 | Planned | Planned Interruption | Replace HV cross arms at pole 58907/58908 and refurbish Dsub KT190 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 148 | F-6064-A | Kaiwaka South | Kaiwaka CB1072 | 2024-05-29 13:33 | 2024-05-29 13:49 | 0.12673 | 0.0080209 | 515 | 8137 | Unplanned | Unknown | F4 trip and close after 15 mins. No FPIs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 149 | F-6067-A | Poroti | Maungatapere CB2 | 2024-05-29 15:24 | 2024-05-29 18:25 | 0.46051 | 0.022038 | 1415 | 29568 | Unplanned | Vegetation | FP 382990 - Branch in 11kV lines. Removed and relivened. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 150 | F-6070-A | Parua Bay | Parua Bay CB2 | 2024-05-29 16:21 | 2024-05-30 12:52 | 1.5026 | 0.0091578 | 588 | 96476 | Unplanned | Vegetation | 383005 Lines down between poles 63976 & 13540 (SW 960 SCF) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 151 | F-6073-A | Montgomery Ave | Onerahi CB8 | 2024-05-29 16:28 | 2024-05-29 17:12 | 0.32501 | 0.0074602 | 479 | 20868 | Unplanned | Vegetation | 383001 Trees across street light pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 152 | F-6082-A | Tangaihi | Ruawai CB1032 | 2024-05-29 17:20 | 2024-05-29 22:13 | 0.49683 | 0.0019935 | 128 | 31900 | Unplanned | Defective Equipment | 383006 - LV Xarm King bolt fail pole 62138, isolated OH section of LV, unable to complete LV repairs due to wind | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 153 | F-6085-A | Access Rd | Ruawai CB1022 | 2024-05-29 18:15 | 2024-05-30 02:33 | 1.1367 | 0.013425 | 862 | 72982 | Unplanned | Defective Equipment | FP - 383015 HV line down 14019 - 14020 Note: MTU CB 2 tripped at 2007hrs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 154 | F-6088-A | Coast | Dargaville CB6 | 2024-05-29 18:33 | 2024-05-30 23:13 | 1.118 | 0.0025075 | 161 | 71782 | Unplanned | Vegetation | 383016 - HV Pole broken, HV Lines down & LV Pole replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 155 | F-6112-A | Maungakaramea | Maungatapere CB3 | 2024-05-29 19:03 | 2024-05-30 03:41 | 0.07862 | 0.00095004 | 61 | 5048 | Unplanned | Defective Equipment | FP 383019 Repaired blown HV Jumper @ Links 875 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 156 | F-6091-A | Taipuha | Mareretu CB1 | 2024-05-29 19:42 | 2024-05-29 23:51 | 0.76818 | 0.0064323 | 413 | 49323 | Unplanned | Wildlife | FP - 383034 - LA dangling around @ X307. Found bird at base of pole. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 157 | F-6094-A | Ararua | Mareretu CB2 | 2024-05-29 20:07 | 2024-05-30 06:36 | 5.3439 | 0.018456 | 1185 | 343118 | Unplanned | Defective Equipment | FP 385035 - 2x lines down between poles 21690 & 21689 - Backfeeding from switch 2077 to switch 2235 at time of tripping. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 158 | F-6103-A | North Dargaville | Dargaville CB1 | 2024-05-29 20:21 | 2024-05-30 16:38 | 1.2925 | 0.020808 | 1336 | 82988 | Unplanned | Defective Equipment | 383039 Repaired lines down - pole 60974 (Broke at binder | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 159 | F-6139-A | Tangowahine | Dargaville CB8 | 2024-05-30 10:51 | 2024-05-30 14:51 | 0.037379 | 0.00015575 | 10 | 2400 | Unplanned | Defective Equipment | 382997 Repaired broken lines Kirikopuni Valley Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 160 | F-6148-A | One Tree Point | Ruakaka CB6 | 2024-05-30 14:04 | 2024-05-30 17:44 | 0.83996 | 0.013581 | 872 | 53932 | Unplanned | Defective Equipment | 383076 Replaced 11kV insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 161 | O-4087-B | Fraser | Kioreroa CB5 | 2024-05-30 20:41 | 2024-05-30 23:04 | 0.36435 | 0.0027255 | 175 | 23394 | Planned | Planned Interruption | High Load Transport | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 162 | F-6157-A | Mata | Ruakaka CB3 | 2024-05-31 09:25 | 2024-05-31 13:59 | 0.12802 | 0.00046724 | 30 | 8220 | Unplanned | Adverse Environment | 382904 Pole change & crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 163 | F-6166-A | Treatment | Kioreroa CB2 | 2024-06-01 11:34 | 2024-06-01 18:01 | 0.12051 | 0.00031139 | 20 | 7740 | Unplanned | Third Party Interference | 383138. Car Vs GM Tx WO256. Replaced & BTN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 164 | F-6169-A | Titoki | Poroti CB1032 | 2024-06-01 14:50 | 2024-06-01 16:45 | 0.0017905 | 1.557e-05 | 1 | 115 | Unplanned | Unknown | 383143. Blown HV Fuse at L 8200. No Cause Found. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 165 | F-6172-A | Kamo Town | Kamo CB7 | 2024-06-02 03:16 | 2024-06-02 13:47 | 0.0098245 | 1.557e-05 | 1 | 631 | Unplanned | Third Party Interference | 383147. Car Vs Tx KK159. Replaced & BTN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 166 | O-3844-B | Turiwiri | Dargaville CB9 | 2024-06-04 09:05 | 2024-06-04 15:33 | 0.29601 | 0.00076291 | 49 | 19012 | Planned | Planned Interruption | Replacing 11kv pole and cross arms. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 167 | F-6178-A | Bickerstaff | Maungaturoto CB2 | 2024-06-04 15:53 | 2024-06-04 17:58 | 0.3174 | 0.013359 | 858 | 20386 | Unplanned | Third Party Interference | (Salesforce down) Digger strike @ Tx D309 & Also loose connecion found sparking on Links 4028 on livening - Repaired | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 168 | F-6181-A | Treatment | Kioreroa CB2 | 2024-06-04 18:30 | 2024-06-04 20:33 | 0.088093 | 0.0007162 | 46 | 5658 | Unplanned | Defective Equipment | 382561. Emergency shut to Replace crossarm & increase conductor height. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 169 | O-3886-B | Turiwiri | Dargaville CB9 | 2024-06-06 09:05 | 2024-06-06 15:32 | 0.29525 | 0.00076291 | 49 | 18963 | Planned | Planned Interruption | Replacing 11kv pole and cross arms. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 170 | O-4045-B | Puwera | Maungatapere CB7 | 2024-06-06 09:06 | 2024-06-06 15:04 | 0.70232 | 0.0019618 | 126 | 45108 | Planned | Planned Interruption | Network Maintenance - POLE, ARM & CONDUCTOR REPLACEMENT | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 171 | O-3880-B | Kaiwaka Town | Kaiwaka CB1062 | 2024-06-06 09:20 | 2024-06-06 15:07 | 0.086443 | 0.00024911 | 16 | 5552 | Planned | Planned Interruption | Network Maintenance - Replace HV and LV hardware at pole 49213 TX C338 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 172 | O-4024-B | Wairere | Mareretu CB5 | 2024-06-06 09:33 | 2024-06-06 12:28 | 0.0027247 | 1.557e-05 | 1 | 175 | Planned | Planned Interruption | Transformer Upgrade - from 15kVA to 30kVA 3PH pole mount | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 173 | O-3889-B | Otangarei | Tikipunga CB7 | 2024-06-06 09:35 | 2024-06-06 11:32 | 0.16577 | 0.0014168 | 91 | 10647 | Planned | Planned Interruption | Network Maintenance Voltage indicators | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 174 | O-4201-B | Access Rd | Ruawai CB1022 | 2024-06-07 09:37 | 2024-06-07 11:07 | 0.018216 | 0.00020241 | 13 | 1170 | Planned | Planned Interruption | Lower HV Crossarm to extend circuit clearance to the 33KV line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 175 | O-3928-B | Langs Beach | Mangawhai North CB3 | 2024-06-07 09:59 | 2024-06-07 14:20 | 0.040637 | 0.0001557 | 10 | 2610 | Planned | Planned Interruption | P05D RMU servicing. Sw 4137, 4138, 4139, 4140, 4141, 4142, 4143 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 176 | F-6193-A | Coast | Dargaville CB6 | 2024-06-07 11:04 | 2024-06-07 15:38 | 0.2133 | 0.00077848 | 50 | 13700 | Unplanned | Defective Equipment | FP38278 Run LV under HV from pole 24977 - 24981 - Urgent | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 177 | F-6202-A | Whatatiri | Maungatapere CB8 | 2024-06-07 11:22 | 2024-06-07 12:14 | 0.21741 | 0.015648 | 1005 | 13964 | Unplanned | Vegetation | FP383309 - Trip OC BC FPI at Sw 843 Phase ABC Same CB trip data on 2nd fault Pole 59970, branch found on HV Lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 178 | F-6199-A | Hotel | Poroti CB1052 | 2024-06-07 11:33 | 2024-06-07 13:44 | 0.011693 | 9.3418e-05 | 6 | 751 | Unplanned | Defective Equipment | 383292 - Blown top of jumper off DDO when attempting to close x1 HV F W428. Wider outage for Repair work (Fuses 8281) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 179 | O-3919-B | North River | Ruakaka CB7 | 2024-06-07 12:02 | 2024-06-07 14:38 | 0.5622 | 0.0035966 | 231 | 36109 | Planned | Planned Interruption | Replace HV arm and install new DDO's and Liven TX RB333 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 180 | F-6205-A | Bickerstaff | Maungaturoto CB2 | 2024-06-07 16:24 | 2024-06-07 16:37 | 0.00040481 | 3.1139e-05 | 2 | 26 | Unplanned | Defective Equipment | FP 383326 HV fuse burnt in half | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 181 | F-6211-A | Montgomery Ave | Onerahi CB8 | 2024-06-09 08:18 | 2024-06-09 08:32 | 0.23263 | 0.016192 | 1040 | 14941 | Unplanned | Unknown | Trip & successful 15 min close. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 182 | O-4057-B | Thelma Road | Mangawhai North CB4 | 2024-06-09 09:12 | 2024-06-09 14:04 | 0.15458 | 0.00052937 | 34 | 9928 | Planned | Planned Interruption | Transformer Upgrade from 100 to 150kVA pole mount type | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 183 | F-6217-A | Ararua | Mareretu CB2 | 2024-06-09 22:10 | 2024-06-10 03:09 | 0.39044 | 0.015118 | 971 | 25077 | Unplanned | Defective Equipment | 383348 Cracked insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 184 | O-4093-B | Matapouri | Ngunguru CB1032 | 2024-06-10 09:20 | 2024-06-10 11:20 | 0.0037367 | 3.1139e-05 | 2 | 240 | Planned | Planned Interruption | Upgrade Tx from 15 kVA to 50kVA | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 185 | F-6226-A | Hakaru | Kaiwaka CB1032 | 2024-06-11 07:45 | 2024-06-11 08:04 | 0.2418 | 0.012845 | 825 | 15530 | Unplanned | Unknown | OC Trip Phase AB (No FPI indicaiton) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 186 | O-4009-B | Puwera | Maungatapere CB7 | 2024-06-11 09:03 | 2024-06-11 14:21 | 0.089121 | 0.00028025 | 18 | 5724 | Planned | Planned Interruption | Network Maintenance - POLE STRAIGHTENS AND POLE REPLACEMENT | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 187 | O-3940-B | King Road | Mangawhai North CB2 | 2024-06-11 09:10 | 2024-06-11 14:19 | 0.062543 | 0.00020241 | 13 | 4017 | Planned | Planned Interruption | Network Maintenance - replace pole 32475 and re-do connections at pole 32477 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 188 | F-6232-A | Tangowahine | Dargaville CB8 | 2024-06-11 14:54 | 2024-06-11 15:13 | 0.0073956 | 0.00038924 | 25 | 475 | Unplanned | Defective Equipment | FP 383408 - Rebind 2x HV insulators | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 189 | O-3943-B | Turiwiri | Dargaville CB9 | 2024-06-12 09:11 | 2024-06-12 14:49 | 0.29998 | 0.00088747 | 57 | 19267 | Planned | Planned Interruption | Network Maintenance. X-arm & pole changes. OH line alteration to rectify drain collapse | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 190 | O-4108-B | Tikipunga Hill | Tikipunga CB4 | 2024-06-12 12:08 | 2024-06-12 14:07 | 0.24272 | 0.0020396 | 131 | 15589 | Planned | Planned Interruption | Network Extension install new 15kVA TX as per 1c plan - tx KT435 not livened to due earthing. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 191 | O-3946-B | Tikipunga Hill | Tikipunga CB4 | 2024-06-13 09:01 | 2024-06-13 15:10 | 0.44268 | 0.0012456 | 80 | 28432 | Planned | Planned Interruption | Network Maintenance Replacing 11kv 400v pole and Cross arms as per Map plain. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 192 | O-4060-B | Titoki | Poroti CB1032 | 2024-06-13 09:38 | 2024-06-13 13:39 | 0.32648 | 0.0013857 | 89 | 20969 | Planned | Planned Interruption | Clear trees around lines from pole18345 to pole 18333 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 193 | F-6253-A | Maunu Road | Whangarei South CB1102 | 2024-06-14 07:08 | 2024-06-14 17:31 | 0.75893 | 0.0058853 | 378 | 48744 | Unplanned | Third Party Interference | 383512 - Car V HV Pole 36242,No Tripping Cut temp break to reduce outages. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 194 | O-4102-B | One Tree Point | Ruakaka CB6 | 2024-06-14 09:05 | 2024-06-14 14:41 | 0.94165 | 0.0028025 | 180 | 60480 | Planned | Planned Interruption | Network Maintenance replace poles and cross arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 195 | O-3802-B | Access Rd | Ruawai CB1022 | 2024-06-14 09:08 | 2024-06-14 13:16 | 0.13514 | 0.00054494 | 35 | 8680 | Planned | Planned Interruption | Replace HV conductor From pole 39716 to pole 39792 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 196 | F-6265-A | Tangaihi | Ruawai CB1032 | 2024-06-15 06:47 | 2024-06-15 07:04 | 0.10925 | 0.0099179 | 637 | 7017 | Unplanned | Unknown | Trip OC, Phase AC involved in fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 197 | F-6271-A | Ararua | Mareretu CB2 | 2024-06-15 08:42 | 2024-06-15 08:57 | 0.036371 | 0.0023822 | 153 | 2336 | Unplanned | Defective Equipment | 15 MIN reclose successful. Fault found later on F-6280-A ((HV jumper off Pole 21717) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 198 | F-6277-A | North River | Ruakaka CB7 | 2024-06-15 09:57 | 2024-06-15 10:01 | 0.00024911 | 6.2279e-05 | 4 | 16 | Unplanned | Unknown | 383556 1 x HV fuse blown but opened all 3 - Shoemaker Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 199 | F-6280-A | Ararua | Mareretu CB2 | 2024-06-15 17:16 | 2024-06-15 19:55 | 0.12797 | 0.0023822 | 153 | 8219 | Unplanned | Defective Equipment | FP 383561 - HV jumper off pole 21727 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 200 | F-6286-A | Whatatiri | Maungatapere CB8 | 2024-06-15 21:18 | 2024-06-16 00:16 | 0.27494 | 0.00615 | 395 | 17659 | Unplanned | Adverse Environment | FP 383565 Building fire - Tx inside building, left de energised | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 201 | F-6289-A | Access Rd | Ruawai CB1022 | 2024-06-16 02:45 | 2024-06-16 08:05 | 0.37081 | 0.007489 | 481 | 23816 | Unplanned | Lightning | FP 383567_ Access Rd Lines down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 202 | O-4135-B | Fraser | Kioreroa CB5 | 2024-06-16 09:38 | 2024-06-16 15:15 | 0.005247 | 1.557e-05 | 1 | 337 | Planned | Planned Interruption | Remove/decommission Tx WO297. Disconnect 11kv cable between WO227 and WO297 and abandon cable | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 203 | O-4129-B | Fert. Works | Kioreroa CB6 | 2024-06-16 10:11 | 2024-06-16 16:30 | 0.0059009 | 1.557e-05 | 1 | 379 | Planned | Planned Interruption | Replace 1Mva Tx WO300 with a 750kva. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 204 | O-4249-B | Hakaru | Kaiwaka CB1032 | 2024-06-17 09:13 | 2024-06-17 15:34 | 1.2576 | 0.0033008 | 212 | 80772 | Planned | Planned Interruption | Customer Work to upgrade MC229 from 100kva OH TX to 200kva pad mount Tx & other network maintenance. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 205 | O-4177-B | Titoki | Poroti CB1032 | 2024-06-18 09:02 | 2024-06-18 13:43 | 0.18828 | 0.0006695 | 43 | 12093 | Planned | Planned Interruption | Network Maintenance - ARM & HARDWARE REPLACEMENT | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 206 | O-4138-B | North River | Ruakaka CB7 | 2024-06-18 09:33 | 2024-06-18 12:24 | 0.029287 | 0.00017127 | 11 | 1881 | Planned | Planned Interruption | Clear trees in 11kv lines from Pole #44051 to Pole #44052 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 207 | O-4147-B | Kaiwaka South | Kaiwaka CB1072 | 2024-06-18 10:04 | 2024-06-18 13:25 | 0.034425 | 0.00017127 | 11 | 2211 | Planned | Planned Interruption | Network Extension - Upgrade Tx C411 from 50 to 100kVA pole mount type | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 208 | F-6301-A | Thelma Road | Mangawhai North CB4 | 2024-06-18 11:30 | 2024-06-18 11:36 | 0.00056051 | 9.3418e-05 | 6 | 36 | Unplanned | Other Cause | 383389 / Isolate for tap change. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 209 | O-3949-B | Hakaru | Kaiwaka CB1032 | 2024-06-19 09:03 | 2024-06-19 14:08 | 0.076182 | 0.00024911 | 16 | 4893 | Planned | Planned Interruption | Network Maintenance - replace poles and hardware | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 210 | O-4141-B | Puwera | Maungatapere CB7 | 2024-06-19 09:03 | 2024-06-19 14:24 | 0.30987 | 0.00096532 | 62 | 19902 | Planned | Planned Interruption | Network Maintenance replace cross arms and transformers straighten poles and redo connections | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 211 | F-6307-A | Tangaihi | Ruawai CB1032 | 2024-06-19 17:49 | 2024-06-19 18:36 | 0.20782 | 0.0044218 | 284 | 13348 | Unplanned | Defective Equipment | Blown HV Jumper @ pole 11264 FP383690 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 212 | O-3961-B | Otangarei | Tikipunga CB7 | 2024-06-20 09:04 | 2024-06-20 19:16 | 0.94333 | 0.0015414 | 99 | 60588 | Planned | Planned Interruption | Network Maintenance - Cut away cable from SW7001 & Connect to New SW10144 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 213 | O-4150-B | Puwera | Maungatapere CB7 | 2024-06-20 09:10 | 2024-06-20 22:18 | 1.0733 | 0.0014324 | 92 | 68938 | Planned | Planned Interruption | HV & LV pole Cross arm replacement and replace pole 46425 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 214 | O-4288-B | ToeToe Rd | Kioreroa CB7 | 2024-06-20 09:11 | 2024-06-20 16:53 | 0.33808 | 0.00073177 | 47 | 21714 | Planned | Planned Interruption | Urgent Repairs. Tree to be cut between GBC poles 117 and 118. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 215 | O-14629-A | Whakapara | Hikurangi CB1112 | 2024-06-23 23:42 | 2024-06-24 02:23 | 0.12784 | 0.00079405 | 51 | 8211 | Unplanned | Defective Equipment | FP 383782 Broken HV jumper pole 906135 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 216 | F-6463-A | Coast | Dargaville CB6 | 2024-06-24 07:23 | 2024-06-24 14:21 | 0.69319 | 0.00246 | 158 | 44522 | Unplanned | Vegetation | FP 383787 Babylon coast Rd - Line down | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 217 | O-4210-B | Swamp North | Hikurangi CB1042 | 2024-06-24 09:14 | 2024-06-24 14:51 | 0.041976 | 0.00012456 | 8 | 2696 | Planned | Planned Interruption | Network Maintenance replace cross arms and reposition pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 218 | O-3736-B | Otangarei | Tikipunga CB7 | 2024-06-24 09:17 | 2024-06-24 13:14 | 0.28782 | 0.0012144 | 78 | 18486 | Planned | Planned Interruption | Cut away cables at SW7002 & connect to New SW10145 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 219 | O-4222-B | Tangaihi | Ruawai CB1032 | 2024-06-24 09:33 | 2024-06-24 13:52 | 0.0040325 | 1.557e-05 | 1 | 259 | Planned | Planned Interruption | Upgrade transformer & pole top connection for service line OHUG | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 220 | O-4162-B | Puwera | Maungatapere CB7 | 2024-06-25 09:04 | 2024-06-25 12:54 | 0.30797 | 0.001339 | 86 | 19780 | Planned | Planned Interruption | HV & LV pole Cross arm replacement and replace pole 46425 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 221 | O-4243-B | Jordan Valley | Hikurangi CB1102 | 2024-06-26 09:10 | 2024-06-26 15:02 | 0.060286 | 0.00017127 | 11 | 3872 | Planned | Planned Interruption | Network Extension upgrading from 50kVa to 100kVA transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 222 | O-4306-B | Access Rd | Ruawai CB1022 | 2024-06-26 09:31 | 2024-06-26 14:24 | 0.53751 | 0.0018372 | 118 | 34523 | Planned | Planned Interruption | Replace pole 44561 with 12.5m Busck pole, Run new span of Flourine conductor to Lv pole 44562 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 223 | O-4246-B | Langs Beach | Mangawhai North CB3 | 2024-06-26 09:41 | 2024-06-26 14:56 | 1.1231 | 0.0035655 | 229 | 72135 | Planned | Planned Interruption | Replace poles 10598 and 10599. Relocate pole 10599 5m from current location | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 224 | F-6535-A | Marsden South | Bream Bay CB1111 | 2024-06-26 17:38 | 2024-06-26 17:54 | 0.024787 | 0.0015725 | 101 | 1592 | Unplanned | Unknown | Trip OC AB Phase | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 225 | F-6538-A | Titoki | Poroti CB1032 | 2024-06-26 22:56 | 2024-06-27 07:20 | 0.64068 | 0.0052314 | 336 | 41149 | Unplanned | Third Party Interference | 383912 278 Opouteke Rd - Car vs pole rego - LWL27 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 226 | F-6544-A | Town Hikurangi | Hikurangi CB1082 | 2024-06-27 06:34 | 2024-06-27 09:30 | 0.087642 | 0.00049823 | 32 | 5629 | Unplanned | Defective Equipment | Broken jumper and crucifix @ KS125. LV backfed from KS144 while repairs were made. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 227 | O-4315-B | Maunu | Maunu CB1032 | 2024-06-27 09:02 | 2024-06-27 15:19 | 1.8969 | 0.005029 | 323 | 121830 | Planned | Planned Interruption | Network Maintenance. Replacing 400v Cross arms, Running 11kv conductor & Straightening Poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 228 | F-6559-A | Access Rd | Ruawai CB1022 | 2024-06-30 07:59 | 2024-06-30 08:16 | 0.047254 | 0.0052314 | 336 | 3035 | Unplanned | Unknown | Sw 2156 indicating fault - Livened remotely - all restored | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 229 | O-877-C | Whakapara | Hikurangi CB1112 | 2024-07-01 09:00 | 2024-07-01 15:04 | 0.15867 | 0.00043574 | 28 | 10196 | Planned | Planned Interruption | Remove pole 42015. Install new pole. Remove pole mount transformer KS130. Connect and liven new ground mount transformer KS567. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 230 | O-4270-B | North Kaiwaka | Kaiwaka CB1022 | 2024-07-01 09:26 | 2024-07-01 14:42 | 0.068846 | 0.00021787 | 14 | 4424 | Planned | Planned Interruption | Upgrade Tx C184 from 50kVA to a 100kVA | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 231 | F-6589-A | North Kaiwaka | Kaiwaka CB1022 | 2024-07-01 10:49 | 2024-07-01 11:23 | 0.036509 | 0.0010738 | 69 | 2346 | Unplanned | Defective Equipment | Missing nut on the top crossarm pole 325279 - No FP isssued. Carried out with planned job, O-4270-B | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 232 | F-6565-A | Otonga | Hikurangi CB1032 | 2024-07-01 13:05 | 2024-07-01 13:21 | 0.39786 | 0.025288 | 1625 | 25566 | Unplanned | Unknown | T & C Paralleled wtih Whakapara fdr (planned job O-877-C) - no FPI's triggered | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 233 | O-4330-B | MTON - MTO POS | Maungaturoto POS CB1262 | 2024-07-02 08:48 | 2024-07-02 13:38 | 0.53174 | 0.0018363 | 118 | 34169 | Planned | Planned Interruption | 33 kV line height mitigation 11kV isolation only for safety while working on 33kV lines. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 234 | S-1802-A | MTON - MTO POS | Maungaturoto POS CB1262 | 2024-07-02 08:49 | 2024-07-02 13:39 | 0.53272 | 0.0018363 | 118 | 34232 | Planned | Planned Interruption | 33 kV line height mitigation 11kV isolation only for safety while working on 33kV lines. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 235 | O-994-C | King Road | Mangawhai North CB2 | 2024-07-02 09:17 | 2024-07-02 14:54 | 0.0052444 | 1.5562e-05 | 1 | 337 | Planned | Planned Interruption | Network Extension - Upgrade transformer MC564 from 30kva to 300kva. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 236 | F-6574-A | Matapouri | Ngunguru CB1032 | 2024-07-02 11:05 | 2024-07-02 11:15 | 0.0010893 | 0.00010893 | 7 | 70 | Unplanned | Other Cause | FP 384039 Changed tap settings on NT118 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 237 | O-928-C | Turiwiri | Dargaville CB9 | 2024-07-03 09:04 | 2024-07-03 15:03 | 0.27375 | 0.00076254 | 49 | 17591 | Planned | Planned Interruption | Replacing 11kv pole and cross arms. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 238 | O-4261-B | Titoki | Poroti CB1032 | 2024-07-03 09:05 | 2024-07-03 13:58 | 0.33742 | 0.0011516 | 74 | 21682 | Planned | Planned Interruption | Replace HV & LV crossarms. Replace HV fuses at Dsub W222 Install Temp LV break at pole 342753 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 239 | O-4105-B | Paparoa | Mareretu CB6 | 2024-07-03 09:13 | 2024-07-03 14:51 | 0.13676 | 0.00040461 | 26 | 8788 | Planned | Planned Interruption | Network Extension - Replace 11m pole 31146 with new 12.5m type. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 240 | O-4420-B | Titoki | Poroti CB1032 | 2024-07-03 09:27 | 2024-07-03 13:27 | 0.037349 | 0.00015562 | 10 | 2400 | Planned | Planned Interruption | Clearing trees around 11kv lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 241 | F-6583-A | Ararua | Mareretu CB2 | 2024-07-03 12:24 | 2024-07-03 13:13 | 0.11559 | 0.002381 | 153 | 7428 | Unplanned | Defective Equipment | 384072 - Urgent shut to replace Xarm - Missing nut Insulator Pin | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 242 | O-4207-B | Titoki | Poroti CB1032 | 2024-07-04 09:03 | 2024-07-04 15:10 | 0.14278 | 0.00038905 | 25 | 9175 | Planned | Planned Interruption | Refurbish Dsubs TW150 and TW162 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 243 | O-4276-B | Swamp North | Hikurangi CB1042 | 2024-07-04 09:09 | 2024-07-04 13:00 | 0.59315 | 0.0025677 | 165 | 38115 | Planned | Planned Interruption | Replace HV and LV cross arms and refurbish Dsub KB147 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 244 | O-1054-C | North Dargaville | Dargaville CB1 | 2024-07-04 10:16 | 2024-07-04 15:30 | 0.13682 | 0.00043574 | 28 | 8792 | Unplanned | Defective Equipment | Urgent Repairs - Replace transformer pole due to spalling, leaking oil & condition of structure. Continue with LV once pole rep | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 245 | O-4165-B | One Tree Point | Ruakaka CB6 | 2024-07-08 09:09 | 2024-07-08 17:00 | 0.0073297 | 1.5562e-05 | 1 | 471 | Planned | Planned Interruption | NAR 5860 - cancelled part way through due to sw 5178 position indicator. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 246 | O-4345-B | Hakaru | Kaiwaka CB1032 | 2024-07-08 09:38 | 2024-07-08 12:47 | 0.27959 | 0.0014784 | 95 | 17966 | Planned | Planned Interruption | Clear trees around 11kv lines from pole 45865 to pole 45864 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 247 | O-634-C | Titoki | Poroti CB1032 | 2024-07-08 10:18 | 2024-07-08 13:23 | 0.37473 | 0.0020231 | 130 | 24080 | Planned | Planned Interruption | Replace HV cross arm at pole 50799 and refurbish Dsub W159 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 248 | F-6607-A | One Tree Point | Ruakaka CB6 | 2024-07-08 13:19 | 2024-07-08 17:00 | 0.0068784 | 3.1124e-05 | 2 | 442 | Unplanned | Defective Equipment | Faulty switch position indicator - Found during carrying out planned work NAR 5860 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 249 | O-4231-B | Waipu | Ruakaka CB2 | 2024-07-09 09:01 | 2024-07-09 13:09 | 1.0571 | 0.004264 | 274 | 67925 | Planned | Planned Interruption | Network Maintenance replacing cross arms and poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 250 | F-6613-A | One Tree Point | Ruakaka CB6 | 2024-07-09 10:27 | 2024-07-09 15:32 | 0.014177 | 4.6686e-05 | 3 | 911 | Unplanned | Defective Equipment | Replaced faulty RMU | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 251 | O-4435-B | Maungakaramea | Maungatapere CB3 | 2024-07-09 13:44 | 2024-07-09 15:10 | 0.073608 | 0.00085591 | 55 | 4730 | Planned | Planned Interruption | Network Maintenance Fit Neutral lugs flat | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 252 | F-6616-A | Fert. Works | Kioreroa CB6 | 2024-07-09 22:13 | 2024-07-10 00:39 | 0.17776 | 0.0012138 | 78 | 11423 | Unplanned | Defective Equipment | FP 384273 repair damaged conductor at pole 26039 causing arcing at pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 253 | O-4390-B | MTON - MTO POS | Maungaturoto POS CB1262 | 2024-07-10 08:40 | 2024-07-10 14:36 | 1.7082 | 0.0054623 | 351 | 109767 | Planned | Planned Interruption | Improve 33 kV line height mitigation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 254 | O-916-C | KAI - MWI 33kV | Kaiwaka CB52 | 2024-07-11 22:03 | 2024-07-12 05:10 | 17.8401 | 0.045472 | 2922 | 1146388 | Planned | Planned Interruption | Network Maintenance - replacing hardware between poles 17740 and 17651/21289 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 255 | O-931-C | Swamp North | Hikurangi CB1042 | 2024-07-12 09:37 | 2024-07-12 10:04 | 0.0021009 | 7.781e-05 | 5 | 135 | Planned | Planned Interruption | Install guy 33kv guy design insulators | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 256 | O-979-C | Tangowahine | Dargaville CB8 | 2024-07-12 11:02 | 2024-07-12 12:05 | 0.0039216 | 6.2248e-05 | 4 | 252 | Planned | Planned Interruption | Replace 11kv guy wire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 257 | O-973-C | Fert. Works | Kioreroa CB6 | 2024-07-14 09:05 | 2024-07-14 15:39 | 0.079709 | 0.00020231 | 13 | 5122 | Planned | Planned Interruption | Replace HT fuses 9048 and 9096. Replace 11kv cable between fuses 9048 and Tx WO242. Upgrade Tx WO242 from a 200kva to a 500kva. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 258 | O-4408-B | Whakapara | Hikurangi CB1112 | 2024-07-15 09:55 | 2024-07-15 11:19 | 0.039216 | 0.00046686 | 30 | 2520 | Planned | Planned Interruption | Fit neutral lugs flat, paint | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 259 | O-4066-B | Puwera | Maungatapere CB7 | 2024-07-16 09:04 | 2024-07-16 15:12 | 0.35506 | 0.00096485 | 62 | 22816 | Planned | Planned Interruption | Network Maintenance replace cross arms and transformers straighten poles and redo connections | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 260 | F-6664-A | Coast | Dargaville CB6 | 2024-07-17 04:27 | 2024-07-17 10:19 | 0.56926 | 0.0046686 | 300 | 36580 | Unplanned | Defective Equipment | FP 384538 Tripped EF - Replaced polymer at pole 15747 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 261 | O-886-C | One Tree Point | Ruakaka CB6 | 2024-07-18 09:05 | 2024-07-18 12:59 | 0.40057 | 0.0017118 | 110 | 25740 | Planned | Planned Interruption | Ruakaka CB6 : Takahiwai Rd : Network Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 262 | O-4264-B | Titoki | Poroti CB1032 | 2024-07-18 09:14 | 2024-07-18 13:56 | 0.14921 | 0.00052911 | 34 | 9588 | Planned | Planned Interruption | Replace cross arms and refurbish Dsub P194 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 263 | O-4441-B | Kaiatea | Ngunguru CB1072 | 2024-07-18 09:28 | 2024-07-18 10:42 | 0.055276 | 0.00074698 | 48 | 3552 | Planned | Planned Interruption | Network Maintenance Fit neutral lugs flush | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 264 | F-6688-A | Tangaihi | Ruawai CB1032 | 2024-07-18 12:13 | 2024-07-18 15:43 | 0.013197 | 0.00017118 | 11 | 848 | Unplanned | Defective Equipment | FP 384521 - Replaced LV tx fuses & ampacts | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 265 | F-6700-A | Kaiatea | Ngunguru CB1072 | 2024-07-19 07:45 | 2024-07-19 08:01 | 0.071461 | 0.010613 | 682 | 4592 | Unplanned | Unknown | Trip & close to Sw 720. 15 min close on Sw 720 due to All FPIs activating. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 266 | O-1003-C | Ararua | Mareretu CB2 | 2024-07-19 09:09 | 2024-07-19 14:33 | 0.12605 | 0.00038905 | 25 | 8100 | Planned | Planned Interruption | Network Maintenance - Replacement of LV X-Arms & reconductoring works below 11kV circuit | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 267 | O-4369-B | Titoki | Poroti CB1032 | 2024-07-19 09:18 | 2024-07-19 13:32 | 0.17392 | 0.00068473 | 44 | 11176 | Planned | Planned Interruption | Replace HV X arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 268 | F-6706-A | Three Mile Bush | Kamo CB3 | 2024-07-19 13:53 | 2024-07-19 16:53 | 1.1018 | 0.0065205 | 419 | 70800 | Unplanned | Defective Equipment | 384641. Outage to top up oil in RMU and find reason for leak. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 269 | F-6712-A | Whatatiri | Maungatapere CB8 | 2024-07-20 12:52 | 2024-07-20 13:23 | 0.12588 | 0.009664 | 621 | 8089 | Unplanned | Unknown | No Fault Found. BTN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 270 | F-6718-A | Te Kopuru | Dargaville CB2 | 2024-07-20 17:21 | 2024-07-20 17:37 | 0.12686 | 0.014691 | 944 | 8152 | Unplanned | Unknown | Trip EF A B & C. FPIs at Sw 2255 activated. BTN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 271 | O-946-C | Treatment | Kioreroa CB2 | 2024-07-21 06:12 | 2024-07-21 13:49 | 0.092547 | 0.00071585 | 46 | 5947 | Planned | Planned Interruption | - Replace DOF's 9018 and assosiated hardware. - Straight joint 11kv cable feeding WO191A in the ground | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 272 | O-4375-B | Titoki | Poroti CB1032 | 2024-07-22 09:02 | 2024-07-22 12:02 | 0.019608 | 0.00010893 | 7 | 1260 | Planned | Planned Interruption | Replace HV cross arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 273 | F-6727-A | Swamp North | Hikurangi CB1042 | 2024-07-22 17:29 | 2024-07-22 17:43 | 0.092329 | 0.0063026 | 405 | 5933 | Unplanned | Unknown | Tripped O/C & closed after 15mins - Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 274 | O-4378-B | North River | Ruakaka CB7 | 2024-07-23 09:04 | 2024-07-23 14:43 | 0.29015 | 0.00085591 | 55 | 18645 | Planned | Planned Interruption | Refurbish Dub RB120, replace Links 531 and replace cross arms at various poles. Replace LV pole 43770 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 275 | O-985-C | Ruatangata | Kamo CB6 | 2024-07-24 09:01 | 2024-07-24 14:05 | 0.39739 | 0.0013072 | 84 | 25536 | Planned | Planned Interruption | Network Extension Upgrade tx from 100kVA to 150kVA pole mounted transformer and install new HV arm and raise LV arm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 276 | O-4414-B | Titoki | Poroti CB1032 | 2024-07-24 09:08 | 2024-07-24 14:17 | 0.53376 | 0.0017274 | 111 | 34299 | Planned | Planned Interruption | Replace HV cross arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 277 | O-964-C | Dunns Rd | Ruawai CB1082 | 2024-07-24 13:10 | 2024-07-24 15:06 | 0.052351 | 0.0004513 | 29 | 3364 | Planned | Planned Interruption | Install 2x new pole mount transformers G281 & G282 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 278 | O-4384-B | Cairnfield Rd | Tikipunga CB5 | 2024-07-25 09:06 | 2024-07-25 13:52 | 0 | 0 | 0 | 0 | Planned | Planned Interruption | Network Maintenance - 2 POLE Tx STRUCTURE REPLACEMENT. OH/UG CONVERSION OF Tx WC115 TO NEW Tx WC245 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 279 | O-967-C | Coast | Dargaville CB6 | 2024-07-25 09:22 | 2024-07-25 11:51 | 0.20108 | 0.0013539 | 87 | 12921 | Planned | Planned Interruption | Network Extension - Replace11kV x-arm & Install HV fuse links 10186 for transformer L300. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 280 | O-4381-B | Thelma Road | Mangawhai North CB4 | 2024-07-25 09:52 | 2024-07-25 13:20 | 0.025895 | 0.0001245 | 8 | 1664 | Planned | Planned Interruption | Transformer Upgrade - upgrade transformer from 50kva to 100kva | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 281 | F-6775-A | Ararua | Mareretu CB2 | 2024-07-25 22:19 | 2024-07-26 01:10 | 0.074511 | 0.00043574 | 28 | 4788 | Unplanned | Third Party Interference | FP 384823 - Replace damaged pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 282 | O-4297-B | Waipu | Ruakaka CB2 | 2024-07-26 09:39 | 2024-07-26 16:01 | 1.4381 | 0.0038905 | 250 | 92414 | Planned | Planned Interruption | HV/LV Arm and hardware replacements. Replace Tx RB101 - Delay in livening ICPs due to late start (High feeder loading) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 283 | F-6781-A | Kaiatea | Ngunguru CB1072 | 2024-07-26 09:55 | 2024-07-26 11:37 | 0.0063493 | 6.2248e-05 | 4 | 408 | Unplanned | Other Cause | 384604 - Raise Low HV Lines @ road crossing (Temp break installed for isolation) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 284 | F-6784-A | Taipuha | Mareretu CB1 | 2024-07-26 11:21 | 2024-07-26 12:29 | 0.0031747 | 4.6686e-05 | 3 | 204 | Unplanned | Defective Equipment | 384834 - Repair buckarm at transformer B194 @ 248 Swamp Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 285 | F-6787-A | Otonga | Hikurangi CB1032 | 2024-07-27 07:33 | 2024-07-27 12:29 | 0.013819 | 4.6686e-05 | 3 | 888 | Unplanned | Wildlife | 2 x HV fuses blown due to swan. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 286 | F-6790-A | Wairere | Mareretu CB5 | 2024-07-28 03:00 | 2024-07-28 03:16 | 0.065983 | 0.0065205 | 419 | 4240 | Unplanned | Unknown | Trip OC AB - FPI at Swith 381 Phase BC | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 287 | F-6793-A | Te Kopuru | Dargaville CB2 | 2024-07-28 17:27 | 2024-07-28 19:59 | 0.042578 | 0.00028012 | 18 | 2736 | Unplanned | Defective Equipment | 384868/ Replace Faulty Xarms & Insulators. 15943 & 15944 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 288 | O-991-C | North River | Ruakaka CB7 | 2024-07-29 09:14 | 2024-07-29 13:42 | 0.16265 | 0.00060692 | 39 | 10452 | Planned | Planned Interruption | Replace HV cross arms and refurbish Dsub RB230 @ pole 39290 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 289 | F-6802-A | Tangaihi | Ruawai CB1032 | 2024-07-29 11:30 | 2024-07-29 11:43 | 0.00060692 | 4.6686e-05 | 3 | 39 | Unplanned | Vegetation | FP 384900 Tree over HV line, not touching @ pole 14600 - Isolate only | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 290 | O-4426-B | Maunu | Maunu CB1032 | 2024-07-29 13:21 | 2024-07-29 14:34 | 0.034081 | 0.00046686 | 30 | 2190 | Planned | Planned Interruption | Network Maintenance Fit neutral lugs flush | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 291 | O-889-C | North River | Ruakaka CB7 | 2024-07-30 09:02 | 2024-07-30 13:31 | 0.3968 | 0.0014784 | 95 | 25498 | Planned | Planned Interruption | Refurbish Dsubs RB164 and RB166 and replace HV and LV cross arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 292 | O-1006-C | Thelma Road | Mangawhai North CB4 | 2024-07-30 09:27 | 2024-07-30 10:45 | 0.1493 | 0.0019141 | 123 | 9594 | Planned | Planned Interruption | Network Maintenance - Installed T/Break@ Pole 312091, Disconnect cable from SW4184 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 293 | O-1021-C | Hokianga Rd | Dargaville CB7 | 2024-07-30 09:40 | 2024-07-30 14:31 | 0.64758 | 0.0022254 | 143 | 41613 | Planned | Planned Interruption | 11kV line alteration to facilitate relocation of DA44 into the berm (install new HV Fuses) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 294 | O-4462-B | Whangarei Heads | Parua Bay CB3 | 2024-07-31 09:03 | 2024-07-31 15:28 | 0.9119 | 0.0031747 | 204 | 58598 | Planned | Planned Interruption | Replacing Transformer PO274 & Pole 24497 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 295 | O-4429-B | Brynderwyn | Maungaturoto CB1 | 2024-07-31 09:06 | 2024-07-31 13:16 | 0.085591 | 0.00034236 | 22 | 5500 | Planned | Planned Interruption | Network Maintenance - replace pole 48179 and hardware | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 296 | O-4489-B | Jordan Valley | Hikurangi CB1102 | 2024-07-31 09:08 | 2024-07-31 12:41 | 0.082868 | 0.00038905 | 25 | 5325 | Planned | Planned Interruption | Network Extension install new transformer KR309 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 297 | O-1009-C | Puwera | Maungatapere CB7 | 2024-07-31 09:28 | 2024-07-31 14:06 | 0.12792 | 0.00046686 | 30 | 8220 | Planned | Planned Interruption | Refurbish Dsub X228 and replace HV & LV cross arms at various sites | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 298 | O-1012-C | Thelma Road | Mangawhai North CB4 | 2024-07-31 09:31 | 2024-07-31 16:47 | 0.29807 | 0.00068473 | 44 | 19154 | Planned | Planned Interruption | Network Maintenance - Disconnect cables from Sw 4181, SW4182 and SW4183 , trifurcate and connect into new switch unit | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 299 | F-6826-A | Jordan Valley | Hikurangi CB1102 | 2024-07-31 15:04 | 2024-07-31 19:04 | 0.082167 | 0.00034236 | 22 | 5280 | Unplanned | Defective Equipment | Damaged conductor between pole 35312 & 35308 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 300 | O-1018-C | North River | Ruakaka CB7 | 2024-08-01 09:01 | 2024-08-01 13:40 | 0.36446 | 0.0013063 | 84 | 23436 | Planned | Planned Interruption | Replace HV & LV cross arms, guy wires and connections at various sites | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 301 | O-1027-C | Thelma Road | Mangawhai North CB4 | 2024-08-01 09:58 | 2024-08-01 14:42 | 0.0044166 | 1.5551e-05 | 1 | 284 | Planned | Planned Interruption | Network Maintenance - Replace crossarms and hardware at pole 29746 to EOL | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 302 | O-4492-B | Mata | Ruakaka CB3 | 2024-08-02 09:08 | 2024-08-02 11:40 | 0.03073 | 0.00020217 | 13 | 1976 | Planned | Planned Interruption | Replacing 11kv 400v poles & Cross arms and TX RO218 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 303 | O-4501-B | Hokianga Rd | Dargaville CB7 | 2024-08-02 09:18 | 2024-08-02 12:38 | 0.42474 | 0.0022239 | 143 | 27312 | Planned | Planned Interruption | Remove pole #53535, cut LV over on to new Tx DA44, liven new Tx DA44 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 304 | F-6841-A | Paparoa | Mareretu CB6 | 2024-08-02 22:44 | 2024-08-03 00:16 | 0.087275 | 0.00094864 | 61 | 5612 | Unplanned | Adverse Environment | FP 385091 - Isolated for safety - pole straighten & install temp guys | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 305 | F-6850-A | Marsden Bay | Bream Bay CB1107 | 2024-08-04 04:08 | 2024-08-04 04:37 | 0.011275 | 0.00038879 | 25 | 725 | Unplanned | Wildlife | FP385098 - Possum | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 306 | O-4495-B | Waipu | Ruakaka CB2 | 2024-08-05 09:02 | 2024-08-05 14:46 | 1.0539 | 0.0030636 | 197 | 67771 | Planned | Planned Interruption | Network Maintenance replace cross arms connections and ampacts | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 307 | O-1042-C | Langs Beach | Mangawhai North CB3 | 2024-08-05 09:12 | 2024-08-05 09:45 | 0.039003 | 0.0011819 | 76 | 2508 | Planned | Planned Interruption | Replace pole 10598 and HV cable riser/crucifix | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 308 | F-6859-A | Puwera | Maungatapere CB7 | 2024-08-05 14:57 | 2024-08-05 15:34 | 0.072501 | 0.0019595 | 126 | 4662 | Unplanned | Defective Equipment | 385129 / Isolate HV to repair spragged wires between poles 46094 & 46095 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 309 | O-892-C | Montgomery Ave | Onerahi CB8 | 2024-08-06 09:01 | 2024-08-06 15:10 | 0.41874 | 0.0011353 | 73 | 26926 | Planned | Planned Interruption | 11kV Pole & Hardware replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 310 | O-4648-B | Maunu Road | Whangarei South CB1102 | 2024-08-07 09:04 | 2024-08-07 15:13 | 1.0846 | 0.0029392 | 189 | 69741 | Planned | Planned Interruption | HV/LV ARM & HARDWARE REPLACEMENT | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 311 | O-4504-B | Thelma Road | Mangawhai North CB4 | 2024-08-08 09:04 | 2024-08-08 11:52 | 0.14108 | 0.00083978 | 54 | 9072 | Planned | Planned Interruption | Network Maintenance - straighten pole, redo HV & LV connections and remove redundant LV pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 312 | O-4507-B | Puwera | Maungatapere CB7 | 2024-08-08 09:10 | 2024-08-08 12:43 | 0.41737 | 0.0019595 | 126 | 26838 | Planned | Planned Interruption | Network Maintenance - Essential 11kv works | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 313 | F-6883-A | Puwera | Maungatapere CB7 | 2024-08-08 16:41 | 2024-08-09 11:34 | 0.01762 | 1.5551e-05 | 1 | 1133 | Unplanned | Defective Equipment | FP385228 - replaced faulty Tx X200 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 314 | O-4561-B | North River | Ruakaka CB7 | 2024-08-09 09:04 | 2024-08-09 13:53 | 0.87191 | 0.003017 | 194 | 56066 | Planned | Planned Interruption | Replace cross arms and fuses, remove redundant hardware | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 315 | O-4486-B | Langs Beach | Mangawhai North CB3 | 2024-08-09 09:07 | 2024-08-09 12:18 | 0.017822 | 9.3309e-05 | 6 | 1146 | Planned | Planned Interruption | Isolate & earth works area for safety and tidy up work. Remove conductors 400m span over bush area with Skyworks Helicopter | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 316 | O-4360-B | Tikipunga Hill | Tikipunga CB4 | 2024-08-09 09:28 | 2024-08-09 15:51 | 0.27994 | 0.00073092 | 47 | 18001 | Planned | Planned Interruption | Replace concrete base and 11kv cable riser. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 317 | O-1030-C | Thelma Road | Mangawhai North CB4 | 2024-08-09 09:51 | 2024-08-09 14:32 | 0.14858 | 0.00052875 | 34 | 9554 | Planned | Planned Interruption | Install new Tx MC 582 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 318 | F-6880-A | Tangaihi | Ruawai CB1032 | 2024-08-09 10:38 | 2024-08-09 12:32 | 0.16842 | 0.0014774 | 95 | 10830 | Unplanned | Defective Equipment | Urgent shut (not notified) to replace Xarm pole 28865 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 319 | F-6892-A | Marsden Bay | Bream Bay CB1107 | 2024-08-10 09:10 | 2024-08-10 11:16 | 1.6808 | 0.025536 | 1642 | 108078 | Unplanned | Unknown | 385272/ Unknown - Trip O/C Phase BC. Patrolled & Livened in sections. Relay data downloaded. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 320 | F-6901-A | Te Kopuru | Dargaville CB2 | 2024-08-11 05:57 | 2024-08-11 06:13 | 0.19766 | 0.014681 | 944 | 12710 | Unplanned | Unknown | Overcurrent Trip A & C. Successful 15 minute close on CB 2 DAR. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 321 | F-6868-A | North Dargaville | Dargaville CB1 | 2024-08-12 09:36 | 2024-08-12 16:23 | 0.018553 | 4.6654e-05 | 3 | 1193 | Unplanned | Defective Equipment | Pole replacement and line lift @ Pole 25813 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 322 | O-1051-C | Hakaru | Kaiwaka CB1032 | 2024-08-12 10:01 | 2024-08-12 14:25 | 0.2915 | 0.0011042 | 71 | 18744 | Planned | Planned Interruption | LV maintenance to replace Xarms, connections and pillars past L425 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 323 | F-6904-A | Te Kopuru | Dargaville CB2 | 2024-08-12 11:06 | 2024-08-12 11:58 | 0.074912 | 0.0014463 | 93 | 4817 | Unplanned | Defective Equipment | 385290. Isolate to repair blown jumper at pole 301791 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 324 | F-6910-A | Kaiatea | Ngunguru CB1072 | 2024-08-12 14:56 | 2024-08-12 15:12 | 0.071164 | 0.010606 | 682 | 4576 | Unplanned | Unknown | Trip & 15 Min Close on Sw 720. FPIs at Sw 720 Activated. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 325 | O-4564-B | Waipu | Ruakaka CB2 | 2024-08-14 09:03 | 2024-08-14 13:37 | 0.70941 | 0.0025815 | 166 | 45617 | Planned | Planned Interruption | Network Maintenance replacing poles cross arms and connections | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 326 | O-4477-B | Tangowahine | Dargaville CB8 | 2024-08-14 10:16 | 2024-08-14 11:31 | 0.017495 | 0.00023327 | 15 | 1125 | Planned | Planned Interruption | Replace Stud pole underneath 11kV line and re instate guy wire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 327 | F-6922-A | Maungakaramea | Maungatapere CB3 | 2024-08-15 09:52 | 2024-08-15 12:07 | 0.13436 | 0.0009953 | 64 | 8640 | Unplanned | Defective Equipment | FP385390 Repair spragged line/dead end & change rotten cross-arm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 328 | F-6925-A | Ararua | Mareretu CB2 | 2024-08-15 10:31 | 2024-08-15 13:38 | 0.00094864 | 3.1103e-05 | 2 | 61 | Unplanned | Defective Equipment | Transformer replacement E283 due to siezed tapchanger | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 329 | F-6943-A | Charles St | Kamo CB2 | 2024-08-15 13:41 | 2024-08-16 20:16 | 0.028537 | 1.5551e-05 | 1 | 1835 | Unplanned | Defective Equipment | FP385405 UG HV Cable fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 330 | F-6955-A | Te Kopuru | Dargaville CB2 | 2024-08-17 22:07 | 2024-08-18 03:14 | 1.0732 | 0.021834 | 1404 | 69010 | Unplanned | Third Party Interference | FP385454 Car Vs Pole 14046 - Event # F4031845 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 331 | F-6958-A | Te Kopuru | Dargaville CB2 | 2024-08-18 04:20 | 2024-08-18 04:35 | 0.13127 | 0.014681 | 944 | 8441 | Unplanned | Vegetation | Tripped & closed after 15mins - Sw 2255 FPI's activated - Unknown cause, later found line down on F-6979-A caused by rotten tree | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 332 | F-6973-A | North Dargaville | Dargaville CB1 | 2024-08-18 08:32 | 2024-08-19 11:36 | 0.11995 | 0.00038879 | 25 | 7713 | Unplanned | Unknown | FP 385455 - Replace Transformer but no cause found | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 333 | F-6970-A | Te Kopuru | Dargaville CB2 | 2024-08-18 11:46 | 2024-08-18 12:57 | 0.80656 | 0.014681 | 944 | 51864 | Unplanned | Vegetation | FP 385463 - Trip OC Phase AC patrolled nothing found. Later found line down on F-6979-A caused by rotten tree fell on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 334 | F-6967-A | Coast | Dargaville CB6 | 2024-08-18 12:00 | 2024-08-18 19:53 | 0.36009 | 0.001353 | 87 | 23155 | Unplanned | Defective Equipment | FP 385462 / F 4032091 - Reported pole on fire. Replaced DDOs & LV xarm. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 335 | F-6979-A | Te Kopuru | Dargaville CB2 | 2024-08-18 16:11 | 2024-08-19 01:28 | 1.9814 | 0.036142 | 3244 | 128293 | Unplanned | Vegetation | FP 385472 - Lines Down between Poles 14287 & Pole 14286 caused by rotten tree fell on line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 336 | F-6985-A | Tangaihi | Ruawai CB1032 | 2024-08-18 17:36 | 2024-08-18 18:33 | 0.070915 | 0.0012441 | 80 | 4560 | Unplanned | Defective Equipment | FP 385468 - Repair jumper load side of Links 3076 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 337 | F-7003-A | Paranui | Tikipunga CB6 | 2024-08-19 15:04 | 2024-08-19 19:52 | 0.64386 | 0.017604 | 1132 | 41402 | Unplanned | Vegetation | FP 385527 - Removed tree from lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 338 | F-7009-A | Waipu | Ruakaka CB2 | 2024-08-20 07:17 | 2024-08-20 07:32 | 0.071226 | 0.015474 | 995 | 4580 | Unplanned | Unknown | Trip EF A & N. FPIUs Sw 545 activated. 15 Min Close on Swq 545 & BTN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 339 | F-7012-A | Waipu | Ruakaka CB2 | 2024-08-20 08:30 | 2024-08-20 10:52 | 0.43879 | 0.015474 | 995 | 28215 | Unplanned | Unknown | Second trip of day. Trip EF A & N. Fault between Sw 545 & 5434. Patrolled & nothing found. Closed & BTN. Switching on F-7015-A | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 340 | O-14920-A | Ararua | Mareretu CB2 | 2024-08-20 09:12 | 2024-08-20 13:58 | 0.11119 | 0.00038879 | 25 | 7150 | Planned | Planned Interruption | Replacement of LV X-Arms & reconductoring works below 11kV circuit | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 341 | O-15004-A | Thelma Road | Mangawhai North CB4 | 2024-08-20 09:23 | 2024-08-20 13:47 | 0.50499 | 0.0019128 | 123 | 32472 | Planned | Planned Interruption | Remove bonded earth from crucifix at pole 312091, remove temp break at pole 3120 VLF test cable between SW4184 and pole 312091 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 342 | F-7018-A | Ararua | Mareretu CB2 | 2024-08-20 13:23 | 2024-08-20 16:29 | 0.020995 | 0.00012441 | 8 | 1350 | Unplanned | Defective Equipment | 385539 / Isolate via Temp Break at pole 48406 & Straighten poles and re sag low 11kV lines. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 343 | O-4612-B | Hokianga Rd | Dargaville CB7 | 2024-08-21 08:15 | 2024-08-21 14:14 | 0.011182 | 3.1103e-05 | 2 | 719 | Planned | Planned Interruption | Safe Transport of a High Load. House being maneuvered around lines. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 344 | O-15007-A | Te Kopuru | Dargaville CB2 | 2024-08-21 09:39 | 2024-08-21 13:35 | 0.20942 | 0.00088644 | 57 | 13466 | Planned | Planned Interruption | Replace Pole 13925 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 345 | F-7027-A | Bickerstaff | Maungaturoto CB2 | 2024-08-21 14:15 | 2024-08-21 14:47 | 0.011446 | 0.00035768 | 23 | 736 | Unplanned | Defective Equipment | Replace binder - FP385600 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 346 | F-7030-A | Otonga | Hikurangi CB1032 | 2024-08-21 18:46 | 2024-08-22 10:57 | 2.1227 | 0.02566 | 1650 | 136495 | Unplanned | Defective Equipment | FP 385612. HV line down @ pole 57409. Delays due to comms issues & difficulty operating Sw 6059. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 347 | O-4552-B | Hatea Drive | Tikipunga CB3 | 2024-08-22 09:04 | 2024-08-22 16:06 | 0.48564 | 0.0011508 | 74 | 31228 | Planned | Planned Interruption | Installing New Transformer WC286. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 348 | O-15073-A | Turiwiri | Dargaville CB9 | 2024-08-22 09:10 | 2024-08-22 15:09 | 0.11724 | 0.00032658 | 21 | 7539 | Planned | Planned Interruption | Network Maintenance Replace Pole & Crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 349 | F-7045-A | Norfolk St | Alexander St CB1 | 2024-08-22 16:25 | 2024-08-22 21:43 | 0.36596 | 0.0011508 | 74 | 23532 | Unplanned | Defective Equipment | FP 385655 Blown HV fuse @ RMU Sw162 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 350 | F-7048-A | Access Rd | Ruawai CB1022 | 2024-08-22 19:37 | 2024-08-22 19:58 | 0.00032658 | 1.5551e-05 | 1 | 21 | Unplanned | Unknown | 385660 / 1 x HV Fuse blown, Opened remaining fuse and reloaded, Closed. BTN No obvious cause. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 351 | F-7054-A | Whangarei Heads | Parua Bay CB3 | 2024-08-23 11:54 | 2024-08-23 12:09 | 0.081474 | 0.012379 | 796 | 5239 | Unplanned | Unknown | N/A Tripped A&B phase O/C - Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 352 | F-7057-A | Waipu | Ruakaka CB2 | 2024-08-24 03:37 | 2024-08-24 07:01 | 0.68078 | 0.024991 | 1607 | 43776 | Unplanned | Defective Equipment | 385693 / Faulty Jumper at Tx RR104 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 353 | O-4624-B | Titoki | Poroti CB1032 | 2024-08-26 10:24 | 2024-08-26 13:31 | 0.011633 | 6.2206e-05 | 4 | 748 | Planned | Planned Interruption | Refurbish Dsub P183 with the 11KV live overhead and straighten pole 50487 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 354 | F-7078-A | Ruatangata | Kamo CB6 | 2024-08-27 06:48 | 2024-08-27 11:40 | 0.94247 | 0.011586 | 745 | 60603 | Unplanned | Third Party Interference | FENZ F4037448 / FP 385745 - Car Vs Pole - Replaced pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 355 | O-4015-B | Austin Road | Maunu CB1072 | 2024-08-27 09:05 | 2024-08-27 18:55 | 0.57805 | 0.00097974 | 63 | 37170 | Planned | Planned Interruption | Replace SW/7746/7747/7748. Complete joints on existing H/V cables to connect to new switch. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 356 | O-4549-B | Hatea Drive | Tikipunga CB3 | 2024-08-27 09:08 | 2024-08-27 15:05 | 0.43541 | 0.0012286 | 79 | 27998 | Planned | Planned Interruption | Removing TX WC 246, Installing New TX WC283 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 357 | O-4633-B | Access Rd | Ruawai CB1022 | 2024-08-28 09:04 | 2024-08-28 14:13 | 0.51418 | 0.001664 | 107 | 33063 | Planned | Planned Interruption | Replace Xarms and hardware & Redo HV connections | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 358 | O-15010-A | Langs Beach | Mangawhai North CB3 | 2024-08-28 09:41 | 2024-08-28 15:14 | 0.39358 | 0.0011819 | 76 | 25308 | Planned | Planned Interruption | Replace pole 10598 and HV cable riser/crucifix | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 359 | F-7081-A | Access Rd | Ruawai CB1022 | 2024-08-28 10:22 | 2024-08-28 10:38 | 0.08205 | 0.012068 | 776 | 5276 | Unplanned | Unknown | FPIs at switches 2077 and 2156 activated. Note: Sw2077 was Closed & Sw2235 Open due to a planned outage. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 360 | F-7084-A | Marsden Bay | Bream Bay CB1107 | 2024-08-28 14:20 | 2024-08-29 03:51 | 4.1929 | 0.065425 | 4207 | 269612 | Unplanned | Third Party Interference | F4038585 / FP 385804 - Car Vs Pole 13404 & Repair Crucifix at Pole 408734 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 361 | O-4627-B | North River | Ruakaka CB7 | 2024-08-29 09:01 | 2024-08-29 14:14 | 0.46258 | 0.0014774 | 95 | 29745 | Planned | Planned Interruption | Replace poles 40994 and 40979, HV fuses and LA's at Dsub RB169 and HV and LV cross arms at various sites. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 362 | O-4600-B | King Road | Mangawhai North CB2 | 2024-08-29 09:04 | 2024-08-29 14:41 | 0.020963 | 6.2206e-05 | 4 | 1348 | Planned | Planned Interruption | Replace Tx like for like | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 363 | O-4597-B | Maunu Road | Whangarei South CB1102 | 2024-08-29 09:07 | 2024-08-29 14:46 | 0.31632 | 0.00093309 | 60 | 20340 | Planned | Planned Interruption | Network Extension upgrade Tx from 200kVA to a 300kVA | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 364 | F-7093-A | Hakaru | Kaiwaka CB1032 | 2024-08-29 15:14 | 2024-08-29 15:29 | 0.19726 | 0.012892 | 829 | 12684 | Unplanned | Lightning | Tripped on earth fault, no reports called though after 15 min. Closed - BTN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 365 | F-7105-A | Dunns Rd | Ruawai CB1082 | 2024-08-29 15:30 | 2024-08-29 17:21 | 0.0034524 | 3.1103e-05 | 2 | 222 | Unplanned | Lightning | 385845 / 3 x HV fuses blown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 366 | F-7111-A | Fert. Works | Kioreroa CB6 | 2024-08-29 18:18 | 2024-08-29 23:32 | 0.24366 | 0.0017262 | 111 | 15668 | Unplanned | Wildlife | FP 385851 - Sectionlised restoration, found lines down due to duck striking line. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 367 | O-14935-A | Taipuha | Mareretu CB1 | 2024-08-30 09:00 | 2024-08-30 12:34 | 0.14976 | 0.00069982 | 45 | 9630 | Planned | Planned Interruption | Network Maintenance replace cross arms and connections | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 368 | O-14926-A | Ararua | Mareretu CB2 | 2024-08-30 09:11 | 2024-08-30 14:25 | 0.12208 | 0.00038879 | 25 | 7850 | Planned | Planned Interruption | LV reconductoring works below 11kV circuit | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 369 | F-7126-A | Ararua | Mareretu CB2 | 2024-08-30 11:23 | 2024-08-30 13:38 | 0.016796 | 0.00012441 | 8 | 1080 | Unplanned | Defective Equipment | FP 385841 Low HV lines Btwn poles 48449 & 48450 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 370 | F-7147-A | Te Kopuru | Dargaville CB2 | 2024-08-31 12:13 | 2024-08-31 17:09 | 0.62725 | 0.014665 | 943 | 40334 | Unplanned | Third Party Interference | FP385885 Car Vs pole 14472 - Event number F4040278 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 371 | F-7150-A | Hakaru | Kaiwaka CB1032 | 2024-08-31 18:06 | 2024-08-31 18:57 | 0.034104 | 0.00066871 | 43 | 2193 | Unplanned | Lightning | FP 385887 1x HV fuse blown - Unknown (possible lightning). Replaced Fuse barrell. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 372 | F-7159-A | Tangaihi | Ruawai CB1032 | 2024-09-01 01:43 | 2024-09-01 23:49 | 1.9399 | 0.031732 | 2041 | 124770 | Unplanned | Lightning | FP385896 - Tx K325 replaced - Lightning K324 blown fuse links barrell still stuck in. faulty lightning arrestor K312 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 373 | F-7168-A | Wairere | Mareretu CB5 | 2024-09-01 02:02 | 2024-09-01 02:19 | 0.071985 | 0.0064989 | 418 | 4630 | Unplanned | Lightning | Trip EF - FPIs Sw 381 N & C. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 374 | F-7183-A | Bickerstaff | Maungaturoto CB2 | 2024-09-01 02:26 | 2024-09-01 02:48 | 0.245 | 0.012065 | 776 | 15758 | Unplanned | Lightning | EF Trip. Multplie reported of DDOs open on this feeder. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 375 | F-7234-A | Wairere | Mareretu CB5 | 2024-09-01 05:05 | 2024-09-01 08:19 | 0.033178 | 0.00017102 | 11 | 2134 | Unplanned | Lightning | FP - 385900 - Reloaded and closed HV Fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 376 | F-7204-A | Bickerstaff | Maungaturoto CB2 | 2024-09-01 05:44 | 2024-09-01 06:26 | 0.0045554 | 0.00010883 | 7 | 293 | Unplanned | Lightning | FP 385902 - Reload and closed HV Fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 377 | F-7261-A | Access Rd | Ruawai CB1022 | 2024-09-01 05:56 | 2024-09-01 10:48 | 0.031826 | 0.00010883 | 7 | 2047 | Unplanned | Lightning | FP 385904 - 3x blown HV Fuses E384. Reloaded and Closed. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 378 | F-7228-A | Bickerstaff | Maungaturoto CB2 | 2024-09-01 08:07 | 2024-09-01 10:49 | 0.0050374 | 3.1095e-05 | 2 | 324 | Unplanned | Lightning | FP385922 - Repair jumper D178 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 379 | F-7276-A | Bickerstaff | Maungaturoto CB2 | 2024-09-01 08:29 | 2024-09-01 11:55 | 0.012842 | 6.219e-05 | 4 | 826 | Unplanned | Lightning | FP 385926 - Reload and close HV Fuses. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 380 | F-7243-A | Dunns Rd | Ruawai CB1082 | 2024-09-01 08:58 | 2024-09-01 09:19 | 0.063854 | 0.0057059 | 367 | 4107 | Unplanned | Unknown | CB 1082 EF trip. FPIs Sw 2049 EF. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 381 | F-7297-A | Access Rd | Ruawai CB1022 | 2024-09-01 10:48 | 2024-09-01 13:29 | 0.015034 | 9.3285e-05 | 6 | 967 | Unplanned | Lightning | FP385944 - 3x HV fuses blown F104 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 382 | F-7279-A | Ararua | Mareretu CB2 | 2024-09-01 12:04 | 2024-09-01 12:43 | 0.0048508 | 0.00012438 | 8 | 312 | Unplanned | Lightning | FP 385901-HV fuse replaced E221, found also L3060 blown x1 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 383 | F-7306-A | Kaiwaka South | Kaiwaka CB1072 | 2024-09-01 18:59 | 2024-09-01 19:14 | 0.12394 | 0.0080225 | 516 | 7972 | Unplanned | Unknown | Tripped O/C - Unknown Sw 320 B&C phase activated | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 384 | F-7312-A | Tangaihi | Ruawai CB1032 | 2024-09-02 09:06 | 2024-09-02 12:01 | 0.0081469 | 4.6643e-05 | 3 | 524 | Unplanned | Lightning | FP 385969 - 3x blown HV fuses tx K316 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 385 | O-4657-B | Tikipunga Hill | Tikipunga CB4 | 2024-09-02 09:11 | 2024-09-02 15:17 | 0.22193 | 0.00060635 | 39 | 14274 | Planned | Planned Interruption | Replace 150kva Tx TT125 with a 300kva. Replace concrete pad as well. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 386 | O-4537-B | North River | Ruakaka CB7 | 2024-09-03 09:03 | 2024-09-03 13:24 | 0.38634 | 0.001477 | 95 | 24849 | Planned | Planned Interruption | Replace HV and LV cross arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 387 | O-15121-A | Brynderwyn | Maungaturoto CB1 | 2024-09-03 09:12 | 2024-09-03 13:36 | 0.016418 | 6.219e-05 | 4 | 1056 | Planned | Planned Interruption | Network Maintenance - At pole 49851 Redo HV connections, Repair HV pole backstay, Re-sag LV conductors | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 388 | F-7336-A | Waipu | Ruakaka CB2 | 2024-09-03 11:50 | 2024-09-03 16:51 | 0.41989 | 0.02881 | 1853 | 27007 | Unplanned | Vegetation | FP 360038 - Lines down between poles 10383 & 10384 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 389 | O-14941-A | Taipuha | Mareretu CB1 | 2024-09-04 09:01 | 2024-09-04 14:39 | 0.38853 | 0.0011505 | 74 | 24990 | Planned | Planned Interruption | Network Maintenance replace cross arms and connections | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 390 | O-15106-A | Marsden Pt | Ruakaka CB1 | 2024-09-04 09:05 | 2024-09-04 14:17 | 0.14552 | 0.00046643 | 30 | 9360 | Planned | Planned Interruption | Replacing 11kv 400v poles & cross arms and LV conductor. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 391 | F-7348-A | North River | Ruakaka CB7 | 2024-09-04 18:19 | 2024-09-04 19:47 | 0.15734 | 0.001788 | 115 | 10120 | Unplanned | Defective Equipment | FP 386078 - Low Lines - replaced pole to correct height | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 392 | O-4540-B | North River | Ruakaka CB7 | 2024-09-05 09:08 | 2024-09-05 14:12 | 0.44817 | 0.001477 | 95 | 28826 | Planned | Planned Interruption | Replace HV & LV cross arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 393 | O-15049-A | Fraser | Kioreroa CB5 | 2024-09-05 21:44 | 2024-09-05 22:57 | 0.08803 | 0.0011972 | 77 | 5662 | Planned | Planned Interruption | High load transport from 211 Port Road, Whangarei to 245 Port Road, Whangarei | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 394 | O-15001-A | North River | Ruakaka CB7 | 2024-09-06 09:09 | 2024-09-06 14:34 | 0 | 0 | 0 | 0 | Planned | Planned Interruption | Remove/decommission pole mount Tx RB232. Replace 11kv arm and fit new fuses at pole 39107. Connect and liven new ground mount 20 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 395 | O-15130-A | Maungakaramea | Maungatapere CB3 | 2024-09-06 09:31 | 2024-09-06 13:26 | 0.025576 | 0.00010883 | 7 | 1645 | Planned | Planned Interruption | Network Extension upgrade transformer and and hardware as per 1c plan | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 396 | O-14998-A | Turiwiri | Dargaville CB9 | 2024-09-06 09:39 | 2024-09-06 15:03 | 0.2015 | 0.0006219 | 40 | 12960 | Planned | Planned Interruption | Cut Trees around 11kv lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 397 | F-7354-A | Titoki | Poroti CB1032 | 2024-09-06 18:12 | 2024-09-06 18:28 | 0.14971 | 0.011972 | 770 | 9629 | Unplanned | Unknown | Trip OC BC, High fault current measured on POR CB 3022 so left for 15min attempt close - Unknown. No FPI indication | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 398 | F-7360-A | Tangaihi | Ruawai CB1032 | 2024-09-07 14:00 | 2024-09-07 17:08 | 0.18248 | 0.004913 | 316 | 11737 | Unplanned | Defective Equipment | 386175 - Rusted Kingbolt, twisted crossarm. Replace Kingbolt and supporting bracket bolts | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 399 | F-7366-A | North Dargaville | Dargaville CB1 | 2024-09-08 08:39 | 2024-09-08 09:53 | 0.032214 | 0.00043533 | 28 | 2072 | Unplanned | Unknown | FP386179 - Blown Fuse L10099 - patrol line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 400 | O-4660-B | Charles St | Kamo CB2 | 2024-09-08 09:02 | 2024-09-08 14:20 | 0.16316 | 0.00051307 | 33 | 10494 | Planned | Planned Interruption | Remove/decommission existing transformer KR130. Replace pole 54212 with B11. Fit new 11kv fuses and crucifix and connect and l | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 401 | O-4570-B | Whau Valley | Tikipunga CB1 | 2024-09-09 09:16 | 2024-09-09 17:41 | 0.5025 | 0.00099504 | 64 | 32320 | Planned | Planned Interruption | Stage 1 Installation of new RMU 10130, 10131, 10132 & 10133. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 402 | O-4579-B | Whau Valley | Tikipunga CB1 | 2024-09-10 09:05 | 2024-09-10 15:13 | 0.56375 | 0.0015548 | 100 | 36260 | Planned | Planned Interruption | Stage 2 Connect Sw 10133 to Tx KK124, connect Sw 10131 to Tx KK125 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 403 | O-15172-A | Tangaihi | Ruawai CB1032 | 2024-09-10 09:13 | 2024-09-10 13:37 | 0.17239 | 0.000653 | 42 | 11088 | Planned | Planned Interruption | Replace Poles & Crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 404 | O-15370-A | North River | Ruakaka CB7 | 2024-09-10 09:32 | 2024-09-10 11:25 | 0.40599 | 0.0035759 | 230 | 26113 | Planned | Planned Interruption | Replace defective cross arm on pole 39150 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 405 | O-4573-B | Whau Valley | Tikipunga CB1 | 2024-09-11 09:14 | 2024-09-11 18:02 | 0.27911 | 0.00052862 | 34 | 17952 | Planned | Planned Interruption | Remove 11KV cable from Sw7358 (redundant RMU) connect to SW 10130. Network Switching BTN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 406 | O-15019-A | Langs Beach | Mangawhai North CB3 | 2024-09-11 09:32 | 2024-09-11 13:32 | 0.037314 | 0.00015548 | 10 | 2400 | Planned | Planned Interruption | P05D RMU servicing | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 407 | O-15148-A | Mangawhai Heads | Mangawhai North CB1 | 2024-09-11 09:38 | 2024-09-11 15:04 | 0.78055 | 0.0023943 | 154 | 50204 | Planned | Planned Interruption | Network Extension - Replace pole 906635. Install Temp SW on pole 14150 (closed position). Replace pole 14153. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 408 | F-7402-A | Tangowahine | Dargaville CB8 | 2024-09-12 18:47 | 2024-09-12 19:03 | 0.046378 | 0.0089709 | 577 | 2983 | Unplanned | Unknown | Sw 2037 indicating fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 409 | O-15361-A | Tikipunga Hill | Tikipunga CB4 | 2024-09-13 09:01 | 2024-09-13 15:11 | 1.3759 | 0.0037314 | 240 | 88497 | Planned | Planned Interruption | Liven new safelink 10187/10188/10189/10190. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 410 | F-7414-A | Three Mile Bush | Kamo CB3 | 2024-09-13 23:02 | 2024-09-14 01:00 | 0.21832 | 0.0018502 | 119 | 14042 | Unplanned | Defective Equipment | FP 386332 - Replace faulty insulator | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 411 | O-4681-B | Western Hills Dr | Alexander St CB7 | 2024-09-15 22:33 | 2024-09-16 02:12 | 0.010215 | 4.6643e-05 | 3 | 657 | Planned | Planned Interruption | Replacing Transformer WC282 & replacing pillar next to Burger King. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 412 | F-7426-A | One Tree Point | Ruakaka CB6 | 2024-09-15 23:02 | 2024-09-16 04:08 | 0.27087 | 0.0028296 | 182 | 17422 | Unplanned | Defective Equipment | 386353 / Isolate to replace DDOs & Tx RO305 due to Oil leaking. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 413 | F-7429-A | Brynderwyn | Maungaturoto CB1 | 2024-09-16 07:51 | 2024-09-16 10:34 | 0.17845 | 0.0029074 | 187 | 11478 | Unplanned | Third Party Interference | FP386359 Tractor clashed lines at quarry between poles 301379 & 300958 (damaged HV conductor) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 414 | O-4672-B | ToeToe Rd | Kioreroa CB7 | 2024-09-16 09:03 | 2024-09-16 13:30 | 0.36066 | 0.0013526 | 87 | 23197 | Planned | Planned Interruption | ARM & HARDWARE REPLACEMENTS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 415 | F-7405-A | Turiwiri | Dargaville CB9 | 2024-09-16 09:55 | 2024-09-16 11:26 | 0.0056593 | 6.219e-05 | 4 | 364 | Unplanned | Other Cause | FP386094 Install line break to cut away future redundant line & Tx's | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 416 | O-15721-A | Ararua | Mareretu CB2 | 2024-09-16 13:23 | 2024-09-16 14:37 | 0.002301 | 3.1095e-05 | 2 | 148 | Unplanned | Defective Equipment | Broken binder found at Pole 48753 FP386372 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 417 | O-15187-A | Paranui | Tikipunga CB6 | 2024-09-17 09:03 | 2024-09-17 12:18 | 0.39312 | 0.0020212 | 130 | 25285 | Planned | Planned Interruption | Network Extension upgrade from 15kVA to 50kVA transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 418 | O-4585-B | Onoke | Kamo CB8 | 2024-09-17 09:04 | 2024-09-17 10:25 | 0.064227 | 0.00079292 | 51 | 4131 | Planned | Planned Interruption | Re configure Lightning arrrestors and lv fusing on transformer KV163 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 419 | O-15733-A | Taipuha | Mareretu CB1 | 2024-09-17 09:44 | 2024-09-17 09:46 | 6.219e-05 | 3.1095e-05 | 2 | 4 | Unplanned | Lightning | FP386406 1 x blown HV link - removed other two to inspect LV fuse boxes, reloaded blown HV link and closed in | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 420 | F-7447-A | Otonga | Hikurangi CB1032 | 2024-09-17 09:59 | 2024-09-17 10:40 | 0.38496 | 0.0092352 | 594 | 24760 | Unplanned | Defective Equipment | 386410 - LV Lines down outside 1146 Whananaki North Rd,Copper Iso HV for safety. LV Fail due to age. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 421 | F-7450-A | 2nd Ave | Alexander St CB3 | 2024-09-17 12:34 | 2024-09-17 15:07 | 0.53989 | 0.0046176 | 297 | 34725 | Unplanned | Third Party Interference | FP386411 - Car v Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 422 | F-7456-A | Access Rd | Ruawai CB1022 | 2024-09-17 14:44 | 2024-09-17 21:07 | 0.55654 | 0.0051773 | 333 | 35796 | Unplanned | Vegetation | FP386435 HV lines down due to tree falling between poles 338259 & 338425 - High winds | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 423 | F-7480-A | Bickerstaff | Maungaturoto CB2 | 2024-09-17 15:52 | 2024-09-17 18:35 | 0.0025342 | 1.5548e-05 | 1 | 163 | Unplanned | Lightning | FP386440 HV fuses blown - Lightning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 424 | F-7510-A | Maungakaramea | Maungatapere CB3 | 2024-09-17 16:45 | 2024-09-17 20:27 | 0.027581 | 0.00012438 | 8 | 1774 | Unplanned | Lightning | FP 386450 Found HV fuses blown x2 @ Links 875 Intterruption time Ref F-7477-A | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 425 | F-7477-A | Maungakaramea | Maungatapere CB3 | 2024-09-17 16:45 | 2024-09-17 20:45 | 0.0074628 | 3.1095e-05 | 2 | 480 | Unplanned | Lightning | FP 386447 Lightning in area, Thought Tx was faulty but found Links 875 blown after earthing down Tx Ref F-7510-A | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 426 | F-7474-A | Bickerstaff | Maungaturoto CB2 | 2024-09-17 17:42 | 2024-09-17 17:48 | 0.00018657 | 3.1095e-05 | 2 | 12 | Unplanned | Lightning | FP386438 2x HV fuses blown - replaced back to normal | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 427 | F-7489-A | Paparoa | Mareretu CB6 | 2024-09-17 18:47 | 2024-09-17 19:04 | 0.15844 | 0.0094218 | 606 | 10191 | Unplanned | Lightning | Tripped O/C A&B phase - Lightning in the area | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 428 | F-7507-A | Mata | Ruakaka CB3 | 2024-09-18 00:30 | 2024-09-18 01:59 | 0.57701 | 0.0064833 | 417 | 37113 | Unplanned | Defective Equipment | FP386468 Blown HV jumper at pole 416735 towards pole 47073 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 429 | O-15103-A | Langs Beach | Mangawhai North CB3 | 2024-09-18 09:07 | 2024-09-18 14:51 | 0.12836 | 0.00037314 | 24 | 8256 | Planned | Planned Interruption | Upgrade conductor between pole 10705 and pole 10720 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 430 | F-7537-A | Whau Valley | Tikipunga CB1 | 2024-09-18 12:31 | 2024-09-18 16:37 | 1.9284 | 0.01987 | 1278 | 124032 | Unplanned | Third Party Interference | F4051510 / FP386506 - Car Vs Pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 431 | F-7555-A | Hakaru | Kaiwaka CB1032 | 2024-09-18 19:32 | 2024-09-18 23:29 | 0.71856 | 0.012904 | 830 | 46217 | Unplanned | Defective Equipment | FP386520 Binder broken and conductor come off onto Xarm at pole 45906 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 432 | F-7558-A | Whangarei Heads | Parua Bay CB3 | 2024-09-18 23:23 | 2024-09-18 23:38 | 0.12794 | 0.012407 | 798 | 8229 | Unplanned | Unknown | O/C A&B phase - Unknown (F4) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 433 | O-4687-B | ToeToe Rd | Kioreroa CB7 | 2024-09-19 09:02 | 2024-09-19 13:36 | 0.36583 | 0.0013371 | 86 | 23530 | Planned | Planned Interruption | ARM & HARDWARE REPLACEMENTS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 434 | F-7570-A | North River | Ruakaka CB7 | 2024-09-19 22:31 | 2024-09-19 22:47 | 0.15645 | 0.017553 | 1129 | 10063 | Unplanned | Unknown | A B Phase OC. No FPIs on remote switches. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 435 | F-7588-A | Tangowahine | Dargaville CB8 | 2024-09-21 05:51 | 2024-09-21 06:05 | 0.093985 | 0.0090331 | 581 | 6045 | Unplanned | Unknown | B & C Phase OC - No FPIs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 436 | F-7597-A | Marsden Bay | Bream Bay CB1107 | 2024-09-21 15:30 | 2024-09-21 16:35 | 0.51047 | 0.02556 | 1644 | 32833 | Unplanned | Unknown | 386610 / A B & C phase overcurrent. No fault found during patrol. All BTN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 437 | F-7603-A | Springs Flat | Kamo CB1 | 2024-09-22 15:12 | 2024-09-22 15:26 | 0.20995 | 0.016076 | 1034 | 13504 | Unplanned | Unknown | Trip & 15 min close. A B & C Overcurrent | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 438 | O-15289-A | Tangowahine | Dargaville CB8 | 2024-09-23 09:12 | 2024-09-23 13:44 | 0.10572 | 0.00038869 | 25 | 6800 | Planned | Planned Interruption | Network Extension - Replace pole 324039 & liven 11kV up to links 10204 (Links to be left open) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 439 | O-4666-B | Montgomery Ave | Onerahi CB8 | 2024-09-24 05:13 | 2024-09-24 06:48 | 0.12407 | 0.001306 | 84 | 7980 | Planned | Planned Interruption | Isolate 11KV so we can remove 11KV from stand offs on pole 300838. In preparation for switch replacement 285, 286, 287, 288. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 440 | O-4621-B | Kokopu | Poroti CB1022 | 2024-09-24 09:02 | 2024-09-24 13:00 | 0.36633 | 0.0015392 | 99 | 23562 | Planned | Planned Interruption | HV & LV cross arm replacement, LV pole replacement and redo connections | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 441 | O-15637-A | Marsden Bay | Bream Bay CB1107 | 2024-09-24 09:03 | 2024-09-24 14:17 | 0.74693 | 0.0023788 | 153 | 48042 | Planned | Planned Interruption | Straighten double pole due to leaning towards the road (Rework) Re terminate LV terms Re position guy and remove LV connectors | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 442 | O-15385-A | King Road | Mangawhai North CB2 | 2024-09-24 09:04 | 2024-09-24 13:29 | 0.57918 | 0.0021922 | 141 | 37252 | Planned | Planned Interruption | Network Extension - Replace pole 32480 and install 3 phase 100KVA transformer labelled MC584 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 443 | O-15442-A | Brynderwyn | Maungaturoto CB1 | 2024-09-25 09:05 | 2024-09-25 15:26 | 0.27249 | 0.00071519 | 46 | 17526 | Planned | Planned Interruption | Network Maintenance - Replace HV & LV crossarms, straighten poles, redo HV connections. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 444 | F-7633-A | Te Kopuru | Dargaville CB2 | 2024-09-26 08:36 | 2024-09-26 08:52 | 0.034858 | 0.0030473 | 196 | 2242 | Unplanned | Unknown | Relivened | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 445 | O-4684-B | Taipuha | Mareretu CB1 | 2024-09-26 09:02 | 2024-09-26 14:40 | 0.2654 | 0.00079292 | 51 | 17070 | Planned | Planned Interruption | Replace HV and LV poles and cross arms, Remove Tx B208 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 446 | O-15256-A | Titoki | Poroti CB1032 | 2024-09-27 09:03 | 2024-09-27 12:38 | 0.033427 | 0.00015548 | 10 | 2150 | Planned | Planned Interruption | Clear trees around 11kv from Pole 50186 to the end of line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 447 | O-14977-A | Taipuha | Mareretu CB1 | 2024-09-27 09:06 | 2024-09-27 10:51 | 0.0016325 | 1.5548e-05 | 1 | 105 | Planned | Planned Interruption | Replace poles and crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 448 | O-15055-A | Whangarei Heads | Parua Bay CB3 | 2024-09-27 09:11 | 2024-09-27 15:04 | 0.38967 | 0.0011039 | 71 | 25063 | Planned | Planned Interruption | Replace pole 24431 with a B11. Remove and decommission existing Tx PO297. Connect new 11kv cable up pole and liven new Tx PO299 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 449 | O-15259-A | Titoki | Poroti CB1032 | 2024-09-27 09:34 | 2024-09-27 13:31 | 0.14739 | 0.0006219 | 40 | 9480 | Planned | Planned Interruption | Clear trees around network lines from pole Pole #50440 towards Pole #50426 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 450 | F-7642-A | MTON - MTO POS | Maungaturoto POS CB1262 | 2024-09-27 13:03 | 2024-09-27 15:47 | 0.010153 | 6.219e-05 | 4 | 653 | Unplanned | Defective Equipment | 386790 - Repaired Xarm brace (nut off Xarm) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 451 | F-7651-A | Tangaihi | Ruawai CB1032 | 2024-09-28 18:34 | 2024-09-28 22:49 | 0.18225 | 0.0024099 | 155 | 11722 | Unplanned | Defective Equipment | FP 386820 - Lines down in bull paddock. HV isolated remotely for safety. LV lines repaired. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 452 | O-4630-B | Norfolk St | Alexander St CB1 | 2024-09-29 08:38 | 2024-09-29 15:50 | 0.15448 | 0.00035759 | 23 | 9936 | Planned | Planned Interruption | Replace Transformer WC231 & concrete foundation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 453 | O-14971-A | Titoki | Poroti CB1032 | 2024-09-30 09:34 | 2024-09-30 10:50 | 0.040175 | 0.00052862 | 34 | 2584 | Planned | Planned Interruption | Clear trees around 11kv line from pole #346764 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 454 | O-15388-A | Ruawai Town | Ruawai CB1072 | 2024-10-01 09:08 | 2024-10-01 14:03 | 0.28416 | 0.00096325 | 62 | 18290 | Planned | Planned Interruption | replace poles, hardware and transformers like for like between pole 23342 to 23316 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 455 | O-4546-B | Waipu | Ruakaka CB2 | 2024-10-02 09:35 | 2024-10-02 11:41 | 0.12528 | 0.00099432 | 64 | 8064 | Planned | Planned Interruption | Straighten D/Sub RR279. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 456 | O-15208-A | Wairere | Mareretu CB5 | 2024-10-02 09:37 | 2024-10-02 12:59 | 0.3358 | 0.0016624 | 107 | 21614 | Planned | Planned Interruption | Straighten pole #28285 and replace 11kv cross arms, Retention 11kv from Pole #28284 to pole #28285 to gain height | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 457 | F-7663-A | Paparoa | Mareretu CB6 | 2024-10-02 20:57 | 2024-10-03 03:51 | 2.7819 | 0.018612 | 1198 | 179057 | Unplanned | Vegetation | 386935 / Trees on lines causing feeder to trip. Long outage time due to no MTO based staff & insufficent gear to carry out TB. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 458 | O-15652-A | MTON - MTO POS | Maungaturoto POS CB1262 | 2024-10-03 09:04 | 2024-10-03 12:46 | 0.27457 | 0.0012429 | 80 | 17673 | Planned | Planned Interruption | 33kV Height mitigation between poles 23157 and pole 23114 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 459 | O-15430-A | Whau Valley | Tikipunga CB1 | 2024-10-03 09:09 | 2024-10-03 14:59 | 0.0054377 | 1.5536e-05 | 1 | 350 | Planned | Planned Interruption | Replace ground mount D-sub WC109 with 500kva. Install new transformer base. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 460 | O-15544-A | Fraser | Kioreroa CB5 | 2024-10-03 21:02 | 2024-10-03 23:25 | 0.17017 | 0.0011963 | 77 | 10953 | Planned | Planned Interruption | High load transport from 245 Port Road to 211 Port Road Whangarei | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 461 | O-15505-A | Pataua | Parua Bay CB1 | 2024-10-04 09:01 | 2024-10-04 13:59 | 0.47163 | 0.0015847 | 102 | 30357 | Planned | Planned Interruption | Remove L9825 Install new Tx OO561, L10214 & L10215 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 462 | O-15304-A | Bickerstaff | Maungaturoto CB2 | 2024-10-04 09:03 | 2024-10-04 13:30 | 0.23645 | 0.00088557 | 57 | 15219 | Planned | Planned Interruption | Remove TX D350 and install new pad mount TX and label D447 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 463 | O-15565-A | Walton St | Whangarei South CB1022 | 2024-10-04 09:10 | 2024-10-04 14:56 | 0.54218 | 0.0016002 | 103 | 34898 | Planned | Planned Interruption | Network Maintenance - LV ARM & HAREWARE REPLACEMENTS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 464 | O-15283-A | Te Kopuru | Dargaville CB2 | 2024-10-04 10:01 | 2024-10-04 12:41 | 0.43898 | 0.0027499 | 177 | 28255 | Planned | Planned Interruption | Replace Sw 2153 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 465 | F-7678-A | North River | Ruakaka CB7 | 2024-10-05 08:49 | 2024-10-05 17:50 | 0.46676 | 0.0042103 | 271 | 30043 | Unplanned | Third Party Interference | 387007/ Recloser 1542 Trip EF Phase C to lockout. Vehicle hit OH Stay wire causing HV Line down & cracked pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 466 | O-4645-B | Hatea Drive | Tikipunga CB3 | 2024-10-06 08:36 | 2024-10-06 18:28 | 0.70821 | 0.0011963 | 77 | 45584 | Planned | Planned Interruption | Replace CFCF Switch 285-286-288-287. note cable fault between Sw 286 & WC248. ICP's livened WC248 via LV Bfeed from WC231 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 467 | F-7681-A | Jordan Valley | Hikurangi CB1102 | 2024-10-06 15:37 | 2024-10-06 22:09 | 0.4717 | 0.0073953 | 476 | 30361 | Unplanned | Defective Equipment | FP 387016 - lines down Rusk Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 468 | O-4663-B | Montgomery Ave | Onerahi CB8 | 2024-10-07 05:47 | 2024-10-07 06:43 | 0.073083 | 0.001305 | 84 | 4704 | Planned | Planned Interruption | Reconnect 11KV cables back onto stand off's at pole 300838. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 469 | O-15478-A | Coast | Dargaville CB6 | 2024-10-07 09:12 | 2024-10-07 11:36 | 0.11186 | 0.00077681 | 50 | 7200 | Planned | Planned Interruption | Replace 11kv arms at pole #24926 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 470 | O-15592-A | Ararua | Mareretu CB2 | 2024-10-07 09:20 | 2024-10-07 12:58 | 0.094833 | 0.00043502 | 28 | 6104 | Planned | Planned Interruption | Replace 11kv cross arms at Pole #48550 and re tension 11kv lines to Pole #48554 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 471 | O-4555-B | Waipu | Ruakaka CB2 | 2024-10-07 09:42 | 2024-10-07 12:48 | 0.0057795 | 3.1073e-05 | 2 | 372 | Planned | Planned Interruption | High PD Investigate and clean 11KV cables. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 472 | O-15622-A | Titoki | Poroti CB1032 | 2024-10-07 09:57 | 2024-10-07 13:26 | 0.42186 | 0.0020197 | 130 | 27153 | Planned | Planned Interruption | install new 50 kVA tx W545 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 473 | O-15364-A | Mangawhai Heads | Mangawhai North CB1 | 2024-10-08 09:05 | 2024-10-08 13:20 | 0.70059 | 0.0027499 | 177 | 45094 | Planned | Planned Interruption | Replace HV & LV crossarms and LV poles and earthing upgrade at MC252 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 474 | O-15328-A | Ruawai Town | Ruawai CB1072 | 2024-10-08 09:12 | 2024-10-08 15:16 | 0.30524 | 0.00083896 | 54 | 19647 | Planned | Planned Interruption | Network Maintenance - replace TX F207 like for like and hardware. Redo connections at pole 23312. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 475 | F-7711-A | Treatment | Kioreroa CB2 | 2024-10-09 02:57 | 2024-10-09 05:08 | 0.41028 | 0.0034957 | 225 | 26408 | Unplanned | Unknown | 387103/ Trip O/C Phase BC. Patrolled & checked FPI's, Livened in sections. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 476 | O-15556-A | Kokopu | Poroti CB1022 | 2024-10-09 09:01 | 2024-10-09 14:27 | 0.26844 | 0.00082342 | 53 | 17278 | Planned | Planned Interruption | Network Maintenance - POLE, ARM & HARDWARE REPLACEMENTS BETWEEN POLES 31434 & 31322 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 477 | O-15769-A | Kaiwaka South | Kaiwaka CB1072 | 2024-10-09 09:45 | 2024-10-09 15:22 | 0.30367 | 0.0009011 | 58 | 19546 | Planned | Planned Interruption | Upgrade Dsub C452 from 15 to 100kVA pole mount type. Replace 11kV strain insulators & other associated works. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 478 | F-7720-A | Access Rd | Ruawai CB1022 | 2024-10-09 15:24 | 2024-10-09 15:50 | 0.0016158 | 6.2145e-05 | 4 | 104 | Unplanned | Unknown | FP387114 1 x HV Drop Out Fuse Blow with bad corrosion. Other Two dropped out for inspection | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 479 | O-15811-A | Union East | Kioreroa CB1 | 2024-10-10 05:39 | 2024-10-10 07:17 | 0.010658 | 0.00010875 | 7 | 686 | Planned | Planned Interruption | Maintenance on ZZ010 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 480 | O-15307-A | Ruawai Town | Ruawai CB1072 | 2024-10-10 09:10 | 2024-10-10 13:34 | 0.38555 | 0.0014604 | 94 | 24816 | Planned | Planned Interruption | Network Maintenance - Replace HV & LV crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 481 | O-16003-A | Kiripaka Rd | Tikipunga CB8 | 2024-10-10 09:12 | 2024-10-10 16:10 | 0.57798 | 0.0013827 | 89 | 37202 | Planned | Planned Interruption | Overlay existing 11kV underground cable due to storm water replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 482 | O-15358-A | Kokopu | Poroti CB1022 | 2024-10-11 09:00 | 2024-10-11 12:28 | 0.17127 | 0.00082342 | 53 | 11024 | Planned | Planned Interruption | CONDUCTOR, ARM & HARDWARE REPLACMENTS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 483 | F-7732-A | Parua Bay | Parua Bay CB2 | 2024-10-12 01:11 | 2024-10-12 01:51 | 0.032937 | 0.00082342 | 53 | 2120 | Unplanned | Third Party Interference | FP387194 Reported car hit a run stay wire - found broken HV preform @ pole 30279 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 484 | F-7735-A | Tutukaka Block | Ngunguru CB1082 | 2024-10-12 13:52 | 2024-10-12 14:09 | 0.057795 | 0.010254 | 660 | 3720 | Unplanned | Unknown | Sw 7170 indicating Ph A&B. Successfully livened remotely. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 485 | F-7738-A | Te Kopuru | Dargaville CB2 | 2024-10-13 07:32 | 2024-10-13 07:48 | 0.20499 | 0.014697 | 946 | 13194 | Unplanned | Unknown | Trip O/C Phase BC - Unknown. (Feeder Classification F4) 15min successful close | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 486 | O-15481-A | Tangowahine | Dargaville CB8 | 2024-10-14 09:36 | 2024-10-14 10:57 | 0.069214 | 0.0008545 | 55 | 4455 | Planned | Planned Interruption | Replace 11kv Arms and connections at pole #37079 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 487 | O-15631-A | North River | Ruakaka CB7 | 2024-10-15 09:01 | 2024-10-15 14:14 | 0.55923 | 0.0017867 | 115 | 35995 | Planned | Planned Interruption | Pole, arm and hardware replacements | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 488 | O-15220-A | Ruawai Town | Ruawai CB1072 | 2024-10-15 09:06 | 2024-10-15 14:15 | 0.26404 | 0.0008545 | 55 | 16995 | Planned | Planned Interruption | Network Maintenance - replace TX F203 like for like and pole hardware. Replace LV crossarms - LV supplied from F204 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 489 | O-15013-A | Mangawhai Heads | Mangawhai North CB1 | 2024-10-15 09:39 | 2024-10-15 14:24 | 1.0538 | 0.0036976 | 238 | 67830 | Planned | Planned Interruption | P05D RMU service | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 490 | F-7747-A | Access Rd | Ruawai CB1022 | 2024-10-15 17:54 | 2024-10-15 19:16 | 0.01274 | 0.00015536 | 10 | 820 | Unplanned | Defective Equipment | FP 387184 - Replaced 11kV Fuses E313 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 491 | O-976-C | Ararua | Mareretu CB2 | 2024-10-16 09:21 | 2024-10-16 14:40 | 0.2559 | 0.00080789 | 52 | 16471 | Planned | Planned Interruption | Network Extension - Re-route 11kV Double circuit conductors on new poles. Remove Temp Links on pole 21600. Remove Temp SW '347' | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 492 | O-15742-A | Kaiatea | Ngunguru CB1072 | 2024-10-17 09:08 | 2024-10-17 15:09 | 0.16826 | 0.00046609 | 30 | 10830 | Planned | Planned Interruption | Network Extension re-locate poles and install new 30kVA tx NP308 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 493 | O-15355-A | Jordan Valley | Hikurangi CB1102 | 2024-10-17 11:04 | 2024-10-17 13:25 | 0.10953 | 0.00077681 | 50 | 7050 | Planned | Planned Interruption | Replace Pole #35782 with B11 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 494 | O-15922-A | Hakaru | Kaiwaka CB1032 | 2024-10-17 11:31 | 2024-10-17 12:22 | 0.33041 | 0.0064786 | 417 | 21267 | Planned | Planned Interruption | Improvements in Supply Quality. Installing New switch 10174 on pole 411926. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 495 | F-7813-A | Fert. Works | Kioreroa CB6 | 2024-10-18 09:07 | 2024-10-18 09:54 | 0.007302 | 0.00015536 | 10 | 470 | Unplanned | Defective Equipment | FP387385 Broken HV binder @ pole 62490 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 496 | F-7816-A | Whakapara | Hikurangi CB1112 | 2024-10-20 06:15 | 2024-10-20 10:49 | 0.57169 | 0.0067272 | 433 | 36797 | Unplanned | Defective Equipment | FP 387427 - 11kV jumper KB511 fault | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 497 | O-15970-A | Maunu Road | Whangarei South CB1102 | 2024-10-20 09:05 | 2024-10-20 15:45 | 0.37909 | 0.00094771 | 61 | 24400 | Planned | Planned Interruption | OHUG Tx CONVERSION. INSTALL NEW GM Tx's WC469, WC470 & REMOVE EXISTING OH Tx WC322. 61 ICPs to be added to Trouble Order | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 498 | F-7819-A | Kaka St | Whangarei South CB1032 | 2024-10-20 13:32 | 2024-10-20 14:08 | 0.19745 | 0.0057795 | 372 | 12709 | Unplanned | Vegetation | FP 387431 - Patrolled - Palm branch removed from 11kV - repeat offender. Follow up required to remove palm tree pls. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 499 | O-16090-A | Brynderwyn | Maungaturoto CB1 | 2024-10-22 09:02 | 2024-10-22 15:26 | 0.041762 | 0.00010875 | 7 | 2688 | Planned | Planned Interruption | Network Maintenance - relocate TX out of drain area | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 500 | O-16009-A | Taipuha | Mareretu CB1 | 2024-10-22 09:10 | 2024-10-22 12:48 | 0.0033869 | 1.5536e-05 | 1 | 218 | Planned | Planned Interruption | Replace poles 34238 and 34239. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 501 | O-15784-A | Onoke | Kamo CB8 | 2024-10-22 09:16 | 2024-10-22 12:53 | 0.067427 | 0.00031073 | 20 | 4340 | Planned | Planned Interruption | Upgrade pole mount Tx KV122 from a 50kva to a 75kva. Upgrade HT jumpers to 35mm copper. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 502 | O-15334-A | Ruawai Town | Ruawai CB1072 | 2024-10-22 09:17 | 2024-10-22 15:06 | 0.32533 | 0.00093218 | 60 | 20940 | Planned | Planned Interruption | Replace pole, replace crossarms, straighten poles and upgrade F201 to 50KVA | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 503 | O-15748-A | Taipuha | Mareretu CB1 | 2024-10-23 09:01 | 2024-10-23 12:55 | 0.14906 | 0.00063699 | 41 | 9594 | Planned | Planned Interruption | Replace HV cross arms and pole 33695 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 504 | O-15712-A | Paranui | Tikipunga CB6 | 2024-10-23 09:03 | 2024-10-23 12:12 | 0.38213 | 0.0020197 | 130 | 24596 | Planned | Planned Interruption | Clear trees around 11kv lines from pole #51360 to the end of line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 505 | O-15349-A | Te Kopuru | Dargaville CB2 | 2024-10-23 09:04 | 2024-10-23 16:58 | 0.42712 | 0.0009011 | 58 | 27492 | Planned | Planned Interruption | Network Maintenance - pole replacement & replacing LV conductor under 11kV lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 506 | O-16099-A | Thelma Road | Mangawhai North CB4 | 2024-10-23 09:09 | 2024-10-23 13:15 | 0.068795 | 0.00027965 | 18 | 4428 | Planned | Planned Interruption | Level transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 507 | F-7831-A | Ararua | Mareretu CB2 | 2024-10-23 14:56 | 2024-10-23 16:52 | 0.018022 | 0.00015536 | 10 | 1160 | Unplanned | Defective Equipment | 387498 / Carry out repairs to broken 11kV binder and spragged LV below. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 508 | O-16174-A | Fert. Works | Kioreroa CB6 | 2024-10-23 15:55 | 2024-10-23 17:01 | 0.0020508 | 3.1073e-05 | 2 | 132 | Planned | Planned Interruption | Network Maintenance Cleaning Tx room & install fire detector | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 509 | F-7834-A | Paparoa | Mareretu CB6 | 2024-10-23 20:07 | 2024-10-23 21:31 | 0.31484 | 0.0091819 | 591 | 20265 | Unplanned | Unknown | 387505 Report of loud bang near Y184 - nothing found. suspect a bird strike near | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 510 | O-15871-A | Titoki | Poroti CB1032 | 2024-10-24 09:02 | 2024-10-24 13:37 | 0.1709 | 0.00062145 | 40 | 11000 | Planned | Planned Interruption | Clear trees around 11kv lines from pole #50468 to pole #334448 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 511 | O-16051-A | King Road | Mangawhai North CB2 | 2024-10-24 21:32 | 2024-10-25 03:08 | 4.2389 | 0.012647 | 814 | 272839 | Planned | Planned Interruption | Replace Transformer MC287 like for like. Replace HV and LV hardware & straighten poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 512 | O-15874-A | Tangowahine | Dargaville CB8 | 2024-10-25 09:35 | 2024-10-25 15:20 | 0.19296 | 0.00055931 | 36 | 12420 | Planned | Planned Interruption | POLE & HARDWARE REPLACEMENTS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 513 | F-7843-A | Dunns Rd | Ruawai CB1082 | 2024-10-26 05:02 | 2024-10-26 09:42 | 0.31517 | 0.0056397 | 363 | 20286 | Unplanned | Third Party Interference | 387585/ Car v Pole Event No. 4075094 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 514 | O-16258-A | Kaiwaka Town | Kaiwaka CB1062 | 2024-10-29 09:33 | 2024-10-29 12:01 | 0.089675 | 0.00060591 | 39 | 5772 | Planned | Planned Interruption | Clear trees around lines from pole #49334 to the end of line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 515 | O-16168-A | Wairere | Mareretu CB5 | 2024-10-29 09:41 | 2024-10-29 13:25 | 0.017401 | 7.7681e-05 | 5 | 1120 | Planned | Planned Interruption | Transformer Upgrade (15 to 50kVA for existing pump as it has been changed from submain to normal connection with ICP | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 516 | O-15907-A | Hakaru | Kaiwaka CB1032 | 2024-10-30 09:03 | 2024-10-30 12:09 | 0.4439 | 0.0025324 | 163 | 28572 | Planned | Planned Interruption | Installing New Switch 10184 on Pole 47137. Removing Fuses 422 on Pole 334460. Replace tx MC218 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 517 | O-16012-A | Tangowahine | Dargaville CB8 | 2024-10-30 09:12 | 2024-10-30 15:06 | 0.20349 | 0.00057484 | 37 | 13098 | Planned | Planned Interruption | Network Maintenance - HV ARM REPLACEMENTS FROM POLES 37867 & 37863 TO EOL | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 518 | F-7867-A | Ararua | Mareretu CB2 | 2024-10-30 10:23 | 2024-10-30 11:44 | 0.0088091 | 0.00010875 | 7 | 567 | Unplanned | Other Cause | 387528 Low lines - mid span pole to be installed | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 519 | O-15859-A | Waipu | Ruakaka CB2 | 2024-10-30 10:33 | 2024-10-30 14:02 | 0.55205 | 0.0026412 | 170 | 35533 | Planned | Planned Interruption | Replacing 11kv pole 10509 & Fuses 546 with new switch 10182. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 520 | O-15910-A | Hakaru | Kaiwaka CB1032 | 2024-10-31 09:02 | 2024-10-31 12:22 | 0.39259 | 0.0022062 | 142 | 25269 | Planned | Planned Interruption | Removing Fuses 367 (pole 47073) Installing New Switch 10185 (pole 47073) in the open position | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 521 | O-16015-A | North Dargaville | Dargaville CB1 | 2024-10-31 09:04 | 2024-10-31 13:14 | 0.042725 | 0.0001709 | 11 | 2750 | Planned | Planned Interruption | Clear trees around 11kv lines from pole #27079 to pole #27081 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 522 | O-16246-A | Mains Ave | Tikipunga CB2 | 2024-10-31 09:06 | 2024-10-31 12:03 | 0.73973 | 0.0041793 | 269 | 47613 | Planned | Planned Interruption | Network Extension install new 11kV cable and transformer WC474 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 523 | O-15976-A | Marsden Pt | Ruakaka CB1 | 2024-10-31 09:18 | 2024-10-31 12:49 | 0.44911 | 0.0021285 | 137 | 28907 | Planned | Planned Interruption | Repair Leaking bushing tx RP377 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 524 | O-16156-A | Kaiwaka Town | Kaiwaka CB1062 | 2024-10-31 09:32 | 2024-10-31 11:30 | 0.011 | 9.3218e-05 | 6 | 708 | Planned | Planned Interruption | Replace like for like 30kVA TX - C351 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 525 | F-7870-A | Tangaihi | Ruawai CB1032 | 2024-10-31 19:16 | 2024-10-31 19:34 | 0.0022372 | 0.00012429 | 8 | 144 | Unplanned | Vegetation | FP 387739 - Branch in line near pole 28473 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 526 | F-7873-A | Turiwiri | Dargaville CB9 | 2024-10-31 19:21 | 2024-10-31 19:35 | 0.038577 | 0.0077681 | 500 | 2483 | Unplanned | Unknown | FPIs on Sw 2152 ABC phase. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 527 | F-7876-A | Marsden Bay | Bream Bay CB1107 | 2024-11-01 01:04 | 2024-11-01 02:47 | 0.039989 | 0.00038824 | 25 | 2575 | Unplanned | Wildlife | F 4078452 / FP 387741 - FENZ call for pole on fire. Found possum on crucifix, 2 blown HV fuses RO394 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 528 | O-16348-A | Paranui | Tikipunga CB6 | 2024-11-01 09:10 | 2024-11-01 11:35 | 0.0022518 | 1.553e-05 | 1 | 145 | Planned | Planned Interruption | 15kVA to 50kVA upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 529 | F-7885-A | Paranui | Tikipunga CB6 | 2024-11-01 19:47 | 2024-11-02 01:55 | 0.01143 | 3.1059e-05 | 2 | 736 | Unplanned | Defective Equipment | Replace faulty tx | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 530 | F-7888-A | Jordan Valley | Hikurangi CB1102 | 2024-11-02 08:54 | 2024-11-02 12:29 | 0.42489 | 0.014784 | 952 | 27360 | Unplanned | Defective Equipment | FP387773 Line down @ pole 35013 towards pole 324337, Also replaced blown lightning arrester @ Tx KS142 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 531 | O-16135-A | 2nd Ave | Alexander St CB3 | 2024-11-03 08:34 | 2024-11-03 21:29 | 1.0618 | 0.0020499 | 132 | 68371 | Planned | Planned Interruption | Replace RMU with safelink. Outage on HV ended at 2129pm but customers were generated from 1710 as shutdown went well overtime. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 532 | F-7891-A | Tangaihi | Ruawai CB1032 | 2024-11-03 22:15 | 2024-11-03 23:41 | 0.17662 | 0.0020344 | 131 | 11373 | Unplanned | Defective Equipment | 387781 / Isolate to repair HV binder on pole 28765. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 533 | O-15400-A | Tangowahine | Dargaville CB8 | 2024-11-04 09:13 | 2024-11-04 15:32 | 0.064743 | 0.00017083 | 11 | 4169 | Planned | Planned Interruption | Install links 10200, Pole changes & associated works | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 534 | O-16189-A | Langs Beach | Mangawhai North CB3 | 2024-11-04 09:19 | 2024-11-04 13:18 | 0.18187 | 0.00076095 | 49 | 11711 | Planned | Planned Interruption | Network Maintenance - level transformers MC499 and MC500 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 535 | O-16018-A | Tangaihi | Ruawai CB1032 | 2024-11-04 09:32 | 2024-11-04 14:28 | 0.28012 | 0.00094731 | 61 | 18038 | Planned | Planned Interruption | Clear trees around 11kv line from pole #19189 to pole #331282 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 536 | F-7897-A | Waipu | Ruakaka CB2 | 2024-11-04 20:27 | 2024-11-04 23:05 | 0.29444 | 0.0018636 | 120 | 18960 | Unplanned | Defective Equipment | FP 387820 HV line down at pole 10525 (pole 10526 side) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 537 | O-16363-A | Swamp North | Hikurangi CB1042 | 2024-11-05 09:02 | 2024-11-05 11:12 | 0.30155 | 0.0023294 | 150 | 19418 | Planned | Planned Interruption | Upgrade tx from 30kVA to 50kVA & Replace LAs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 538 | O-16192-A | Langs Beach | Mangawhai North CB3 | 2024-11-05 09:25 | 2024-11-05 11:14 | 0.098178 | 0.00090072 | 58 | 6322 | Planned | Planned Interruption | Network Maintenance - Level Transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 539 | O-15937-A | Hokianga Rd | Dargaville CB7 | 2024-11-05 09:26 | 2024-11-05 15:23 | 0.2772 | 0.00077648 | 50 | 17850 | Planned | Planned Interruption | Dismantle pothead and x-arm at pole 54006. Replace 11kV riser from base of pole | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 540 | O-15790-A | Tangowahine | Dargaville CB8 | 2024-11-06 09:09 | 2024-11-06 13:36 | 0.029025 | 0.00010871 | 7 | 1869 | Planned | Planned Interruption | Network Maintenance - Pole & x-arm changes | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 541 | O-15403-A | Hokianga Rd | Dargaville CB7 | 2024-11-06 09:15 | 2024-11-06 14:25 | 0.024071 | 7.7648e-05 | 5 | 1550 | Planned | Planned Interruption | Removed DA70, Install DA140. Incorrect customers logged, due to Tx replacement-Patch process issue. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 542 | O-16138-A | North Kaiwaka | Kaiwaka CB1022 | 2024-11-07 09:03 | 2024-11-07 14:34 | 0.41122 | 0.0012424 | 80 | 26480 | Planned | Planned Interruption | Re-route HV line, connect & liven 2x new 50kVA Tx C546 & C547 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 543 | O-16276-A | Kiripaka Rd | Tikipunga CB8 | 2024-11-07 09:05 | 2024-11-07 14:21 | 0.063796 | 0.00020189 | 13 | 4108 | Planned | Planned Interruption | Replacing Poles & Conductor from poles 40319-40320 & 40323. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 544 | F-7945-A | Maungakaramea | Maungatapere CB3 | 2024-11-07 14:05 | 2024-11-07 14:57 | 0.014536 | 0.00027953 | 18 | 936 | Unplanned | Defective Equipment | 387949 Jumper off insulator at pole 21823 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 545 | O-16261-A | Matapouri | Ngunguru CB1032 | 2024-11-08 09:04 | 2024-11-08 11:17 | 0.014458 | 0.00010871 | 7 | 931 | Planned | Planned Interruption | Level D-sub NT118 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 546 | O-16285-A | Springs Flat | Kamo CB1 | 2024-11-08 09:05 | 2024-11-08 15:29 | 0.059634 | 0.0001553 | 10 | 3840 | Planned | Planned Interruption | -Replacing 11kv Poles, terminating NEW UG cable & VLF testing -Installing New Automated Switch 10165 at pole 40326 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 547 | F-7951-A | Whakapara | Hikurangi CB1112 | 2024-11-08 13:58 | 2024-11-08 14:36 | 0.034817 | 0.00091625 | 59 | 2242 | Unplanned | Defective Equipment | 387967 - Spragged lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 548 | O-16288-A | Springs Flat | Kamo CB1 | 2024-11-10 09:02 | 2024-11-10 13:39 | 0.35805 | 0.0013666 | 88 | 23056 | Planned | Planned Interruption | Connecting 11kV cable at pole 40326 & pole 40323, Installing 11kv Breaks at pole 20372 & pole 17566 & liven new config | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 549 | O-15787-A | North Kaiwaka | Kaiwaka CB1022 | 2024-11-10 09:04 | 2024-11-10 12:16 | 0.22363 | 0.0011647 | 75 | 14400 | Planned | Planned Interruption | Crucifix and DOFs installed at pole 304807 and labelled 10191. 3 phase 50kva ground mount TX C545 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 550 | F-7963-A | Jordan Valley | Hikurangi CB1102 | 2024-11-11 09:40 | 2024-11-11 12:59 | 0.24138 | 0.0073921 | 476 | 15543 | Unplanned | Defective Equipment | FP388016 EF - HV jumper touching polly at pole 35013 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 551 | F-7966-A | Treatment | Kioreroa CB2 | 2024-11-11 10:43 | 2024-11-11 11:08 | 0.086888 | 0.0034942 | 225 | 5595 | Unplanned | Third Party Interference | FP388023 Truck contacted HV lines between pole 304036 & 65238 - Faultman checked network and advised safe to liven | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 552 | O-16216-A | Springs Flat | Kamo CB1 | 2024-11-12 09:01 | 2024-11-12 13:31 | 0.40237 | 0.0014908 | 96 | 25910 | Planned | Planned Interruption | Network Maintenance - HV/LV ARM & HARDWARE REPLACEMENTS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 553 | O-4738-B | Kaiwaka Town | Kaiwaka CB1062 | 2024-11-12 09:24 | 2024-11-12 13:35 | 1.6292 | 0.0064914 | 418 | 104911 | Planned | Planned Interruption | Network Extension - Install new pole and 50kva 3 phase TX labelled C548 between poles 49080 and 49081 Upgrade LV overhead lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 554 | F-7972-A | Bickerstaff | Maungaturoto CB2 | 2024-11-12 17:51 | 2024-11-12 22:15 | 0.31452 | 0.012051 | 776 | 20253 | Unplanned | Defective Equipment | FP388076 Feeder tripped E/F - Customer reported blown @ Tx D180 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 555 | O-16675-A | Okara Drive | Whangarei South CB1092 | 2024-11-13 00:17 | 2024-11-13 03:23 | 0.76527 | 0.0042396 | 273 | 49278 | Unplanned | Defective Equipment | FP388077 Sw 253 oil leak - low oil - oil top up & repair works | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 556 | O-15058-A | Access Rd | Ruawai CB1022 | 2024-11-13 09:01 | 2024-11-13 14:08 | 0.56206 | 0.0018325 | 118 | 36193 | Planned | Planned Interruption | Replace HV and LV cross arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 557 | O-4840-B | Marsden South | Bream Bay CB1111 | 2024-11-13 12:25 | 2024-11-13 16:10 | 0.0034942 | 1.553e-05 | 1 | 225 | Planned | Planned Interruption | Network Maintenance Leaking bushing & insulation work | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 558 | O-16390-A | Swamp North | Hikurangi CB1042 | 2024-11-14 09:06 | 2024-11-14 14:50 | 0.28314 | 0.00082307 | 53 | 18232 | Planned | Planned Interruption | Network Maintenance - HV HARDWARE AND WIRE REPLACEMENT | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 559 | O-16480-A | Ararua | Mareretu CB2 | 2024-11-14 09:08 | 2024-11-14 15:48 | 1.2734 | 0.0031836 | 205 | 82000 | Planned | Planned Interruption | Replace Poles 48964, 48027, 48028 Ran 40min over due to work taking longer than anticipated | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 560 | O-16417-A | ToeToe Rd | Kioreroa CB7 | 2024-11-15 09:02 | 2024-11-15 13:32 | 0.15933 | 0.00059013 | 38 | 10260 | Planned | Planned Interruption | Network Extension - install new pole and HV links, ready for further works. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 561 | O-16273-A | Tangowahine | Dargaville CB8 | 2024-11-15 09:32 | 2024-11-15 11:32 | 0.069309 | 0.0005746 | 37 | 4463 | Planned | Planned Interruption | Replace guy wire pole beneath 11kv line from Pole #37324 to Pole #36856 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 562 | F-8023-A | Puwera | Maungatapere CB7 | 2024-11-17 08:02 | 2024-11-17 11:09 | 0.051652 | 0.00059013 | 38 | 3326 | Unplanned | Defective Equipment | 388165 / Broken DDO at Tx X348 requiring replacement. All 3 replaced. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 563 | F-8029-A | Maungakaramea | Maungatapere CB3 | 2024-11-17 12:32 | 2024-11-17 17:14 | 0.34644 | 0.0020654 | 133 | 22308 | Unplanned | Vegetation | Fault Trip B & C Phase. Found tree on lines at pole 53736 causing damage to two conductors. Repaired & BTN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 564 | F-8347-A | Paranui | Tikipunga CB6 | 2024-11-18 07:52 | 2024-12-28 15:09 | 0.92967 | 0.011321 | 1454 | 60468 | Unplanned | Defective Equipment | 389137/ Broken Xarm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 565 | F-8044-A | Maungatapere - Dairy Factory | Maungatapere CB6 | 2024-11-19 09:18 | 2024-11-19 09:34 | 0.072322 | 0.0045812 | 295 | 4657 | Unplanned | Unknown | Tripped O/C A&B phase - Unknown cause | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 566 | F-8053-A | Titoki | Poroti CB1032 | 2024-11-19 14:57 | 2024-11-19 15:01 | 0.01348 | 0.0040222 | 259 | 868 | Unplanned | Third Party Interference | FP388232 Foil balloon caught in overhead lines mid-span | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 567 | F-8056-A | Pataua | Parua Bay CB1 | 2024-11-20 03:12 | 2024-11-20 03:29 | 0.18056 | 0.014738 | 949 | 11627 | Unplanned | Unknown | Trip Overcurrent A & B. Closed in BTN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 568 | O-4720-B | Springs Flat | Kamo CB1 | 2024-11-20 09:07 | 2024-11-20 14:27 | 0.97894 | 0.0030593 | 197 | 63037 | Planned | Planned Interruption | Network Maintenance REPLACE HV POLES, ARMS & HARDWARE. UPGRADE OH LV. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 569 | O-4789-B | Ararua | Mareretu CB2 | 2024-11-20 09:55 | 2024-11-20 16:17 | 0.56686 | 0.0015685 | 101 | 36502 | Planned | Planned Interruption | Network Maintenance - Replace poles, crossarms & structures at various locations | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 570 | F-8059-A | Kaiwaka Town | Kaiwaka CB1062 | 2024-11-20 11:50 | 2024-11-20 12:16 | 0.16954 | 0.0064914 | 418 | 10917 | Unplanned | Unknown | F-8059-A. Int fault. FPIs indicating betwn Sw 332 & 333 - relocated. RCB returned (Trees) B4 relivening. MP to download 1508 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 571 | O-4780-B | Hakaru | Kaiwaka CB1032 | 2024-11-21 09:04 | 2024-11-21 12:10 | 0.0086655 | 4.6589e-05 | 3 | 558 | Planned | Planned Interruption | Network Maintenance - replace pole 11985 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 572 | O-15178-A | Turiwiri | Dargaville CB9 | 2024-11-21 09:27 | 2024-11-21 14:42 | 0.2541 | 0.00080754 | 52 | 16362 | Planned | Planned Interruption | Replace HV and LV cross arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 573 | O-4717-B | ToeToe Rd | Kioreroa CB7 | 2024-11-22 09:04 | 2024-11-22 14:08 | 0.056652 | 0.00018636 | 12 | 3648 | Planned | Planned Interruption | Connect new 11kV cable up new pole and onto HV links 10217 - O209 isolated for access through LV | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 574 | O-4735-B | Puwera | Maungatapere CB7 | 2024-11-22 09:04 | 2024-11-22 14:27 | 0.75432 | 0.002345 | 151 | 48573 | Planned | Planned Interruption | Maungatapere CB7 : 92 MAUNGAKARAMEA RD : Network Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 575 | O-4834-B | North River | Ruakaka CB7 | 2024-11-22 09:07 | 2024-11-22 14:59 | 0.15853 | 0.00045036 | 29 | 10208 | Planned | Planned Interruption | Network Maintenance - replace TX RB144 like for like and replace pole hardware | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 576 | F-8098-A | Bickerstaff | Maungaturoto CB2 | 2024-11-22 13:51 | 2024-11-22 15:46 | 0.035718 | 0.00031059 | 20 | 2300 | Unplanned | Defective Equipment | 388335 - broken binder pole 333289 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 577 | O-16207-A | Kaka St | Whangarei South CB1032 | 2024-11-24 08:31 | 2024-11-24 18:27 | 0.12958 | 0.00021741 | 14 | 8344 | Planned | Planned Interruption | Replace Total Sub WC219 (RMU & Tx Unit) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 578 | O-4768-B | Brynderwyn | Maungaturoto CB1 | 2024-11-24 09:01 | 2024-11-24 11:46 | 0.10762 | 0.00065224 | 42 | 6930 | Planned | Planned Interruption | Network Maintenance - REPLACE CONDUCTOR BETWEEN POLES 909852 TO POLE 909701 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 579 | F-8104-A | Titoki | Poroti CB1032 | 2024-11-24 12:36 | 2024-11-24 14:02 | 0.0026711 | 3.1059e-05 | 2 | 172 | Unplanned | Wildlife | 388363 / 3 x HV fuses blown due to possum. BTN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 580 | O-4750-B | Marsden Bay | Bream Bay CB1107 | 2024-11-25 09:42 | 2024-11-25 13:55 | 0.015716 | 6.2119e-05 | 4 | 1012 | Planned | Planned Interruption | Tx STRUCTURE REFURBISHMENT, REPLANT OFF FACE POLE | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 581 | F-8110-A | Thelma Road | Mangawhai North CB4 | 2024-11-25 10:14 | 2024-11-25 11:50 | 0.50168 | 0.016927 | 1090 | 32305 | Unplanned | Third Party Interference | 338379 - cable struck by fencing worker | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 582 | O-4816-B | Onoke | Kamo CB8 | 2024-11-26 09:04 | 2024-11-26 14:22 | 0.019754 | 6.2119e-05 | 4 | 1272 | Planned | Planned Interruption | Vegetation clearing 11kv lines from Issuer earths at pole #52755 to the end of line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 583 | O-15760-A | Taipuha | Mareretu CB1 | 2024-11-26 09:05 | 2024-11-26 09:29 | 0.021617 | 0.00090072 | 58 | 1392 | Planned | Planned Interruption | Replace HV & LV cross arms. Remove redundant LV circuit. *Job abandoned soon after starting due to no Generation at school* | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 584 | O-4831-B | Dunns Rd | Ruawai CB1082 | 2024-11-26 09:08 | 2024-11-26 12:21 | 0.1109 | 0.0005746 | 37 | 7141 | Planned | Planned Interruption | Network Maintenance - Install dampers and rebind HV | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 585 | O-15850-A | Titoki | Poroti CB1032 | 2024-11-27 09:02 | 2024-11-27 12:39 | 0.02022 | 9.3178e-05 | 6 | 1302 | Planned | Planned Interruption | Replace poles, establish new Tx's P503 on pole 50446 & Disestablish T P190 from pole 50447. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 586 | O-4792-B | Ararua | Mareretu CB2 | 2024-11-27 09:04 | 2024-11-27 12:45 | 0.34664 | 0.0015685 | 101 | 22321 | Planned | Planned Interruption | Network Renewal - Reconductor 11kV lines from H Structure Pole 48027 - 48028 to EOL | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 587 | F-8116-A | Wairere | Mareretu CB5 | 2024-11-28 06:37 | 2024-11-28 13:31 | 0.72758 | 0.0070505 | 454 | 46851 | Unplanned | Defective Equipment | FP388484 - Unable to bfd Sw381 remotely (Sw 6202 still manual). Sectionalised and patrolled. 2nd man from WHG. HV jumper on xarm | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 588 | O-16438-A | Maungakaramea | Maungatapere CB3 | 2024-11-28 09:08 | 2024-11-28 13:30 | 0.10436 | 0.00060566 | 39 | 6720 | Planned | Planned Interruption | Replace sw 872 with sw 10172 on adjacent switch | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 589 | O-16141-A | Brynderwyn | Maungaturoto CB1 | 2024-11-28 09:18 | 2024-11-28 14:06 | 0.27282 | 0.00094731 | 61 | 17568 | Planned | Planned Interruption | replace cross arms, ampacts, upgrade D320 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 590 | O-4771-B | Hakaru | Kaiwaka CB1032 | 2024-11-29 09:04 | 2024-11-29 14:25 | 0.2343 | 0.00072989 | 47 | 15087 | Planned | Planned Interruption | Kaiwaka CB1032 : Shut 1 - Brown Road Hakaru : Network Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 591 | O-4960-B | Mains Ave | Tikipunga CB2 | 2024-11-29 09:09 | 2024-11-29 15:14 | 0.37978 | 0.0010405 | 67 | 24455 | Planned | Planned Interruption | Connect new TX WC474 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 592 | O-4828-B | Mata | Ruakaka CB3 | 2024-11-29 09:12 | 2024-11-29 15:11 | 0.16725 | 0.00046589 | 30 | 10770 | Planned | Planned Interruption | Cut vegetation 11kv lines from pole #60890 to the end of line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 593 | O-4873-B | Rewa Rewa Rd | Whangarei South CB1082 | 2024-11-29 12:30 | 2024-11-29 12:43 | 0.010094 | 0.00077648 | 50 | 650 | Planned | Planned Interruption | Change tap on TX WO226 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 594 | F-8128-A | Kokopu | Poroti CB1022 | 2024-11-30 16:07 | 2024-11-30 21:37 | 0.62827 | 0.0063361 | 408 | 40456 | Unplanned | Defective Equipment | FP388536 - broken HV jumper on crossarm damaged equipment | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 595 | O-4774-B | Puwera | Maungatapere CB7 | 2024-12-02 09:06 | 2024-12-02 14:17 | 0.68073 | 0.0021888 | 141 | 43851 | Planned | Planned Interruption | POLE, CONDUCTOR & HARDWARE REPLACEMENTS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 596 | O-4879-B | Maungakaramea | Maungatapere CB3 | 2024-12-02 09:10 | 2024-12-02 13:49 | 0.017324 | 6.2094e-05 | 4 | 1116 | Planned | Planned Interruption | Tree clearing work | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 597 | O-4714-B | One Tree Point | Ruakaka CB6 | 2024-12-02 09:56 | 2024-12-02 14:22 | 0.0082586 | 3.1047e-05 | 2 | 532 | Planned | Planned Interruption | Upgrade ground mount D-sub Ro416 from 200kva to 500kva | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 598 | O-16096-A | MTON - MTO POS | Maungaturoto POS CB1262 | 2024-12-02 10:05 | 2024-12-02 14:47 | 0.57347 | 0.0020336 | 131 | 36942 | Planned | Planned Interruption | -Replace crossarms 23177 and install permanant break -Installing access rd RMU | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 599 | F-8140-A | ToeToe Rd | Kioreroa CB7 | 2024-12-02 10:48 | 2024-12-02 11:03 | 0.10913 | 0.009516 | 613 | 7030 | Unplanned | Unknown | Nil / Overcurrent B Phase. 15 Min Closed & BTN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 600 | F-8143-A | One Tree Point | Ruakaka CB6 | 2024-12-02 15:28 | 2024-12-02 15:34 | 0.00018628 | 3.1047e-05 | 2 | 12 | Unplanned | Human Error | Re Isolate to Upgrade fusing that was missed during installation on O-4714-B | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 601 | O-15472-A | Titoki | Poroti CB1032 | 2024-12-03 09:03 | 2024-12-03 14:01 | 0.064765 | 0.00021733 | 14 | 4172 | Planned | Planned Interruption | Replace HV arms and Refurbish Dsub TW128 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 602 | O-15445-A | Turiwiri | Dargaville CB9 | 2024-12-03 09:05 | 2024-12-03 14:05 | 0.18628 | 0.00062094 | 40 | 12000 | Planned | Planned Interruption | Replace HV & LV cross arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 603 | O-15427-A | Titoki | Poroti CB1032 | 2024-12-03 09:07 | 2024-12-03 11:34 | 0.057049 | 0.00038809 | 25 | 3675 | Planned | Planned Interruption | Replace HV pole 18190 and HV arms on various poles. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 604 | O-4795-B | Puwera | Maungatapere CB7 | 2024-12-04 09:03 | 2024-12-04 12:58 | 0.51437 | 0.0021888 | 141 | 33135 | Planned | Planned Interruption | Network Maintenance - POLE, CONDUCTOR & HARDWARE REPLACEMENTS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 605 | O-15550-A | Ararua | Mareretu CB2 | 2024-12-04 09:05 | 2024-12-04 13:15 | 0.0077618 | 3.1047e-05 | 2 | 500 | Planned | Planned Interruption | Refurbish Dsubs A152 and A153 Network Maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 606 | O-4723-B | Charles St | Kamo CB2 | 2024-12-04 09:05 | 2024-12-04 15:37 | 0.46856 | 0.0011953 | 77 | 30184 | Planned | Planned Interruption | Replace Oil Switch 7974-7345-7348-7346. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 607 | F-8149-A | Marsden South | Bream Bay CB1111 | 2024-12-04 16:50 | 2024-12-04 19:40 | 0.002639 | 1.5524e-05 | 1 | 170 | Unplanned | Unknown | 388645 / Isolate to replace blown Fuse on Sw 5287. No Cause Found. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 608 | O-15094-A | Turiwiri | Dargaville CB9 | 2024-12-05 09:01 | 2024-12-05 14:20 | 0.46024 | 0.0014437 | 93 | 29648 | Planned | Planned Interruption | Replace HV and LV cross arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 609 | O-4798-B | Whatatiri | Maungatapere CB8 | 2024-12-05 09:03 | 2024-12-05 10:07 | 0.094384 | 0.0014747 | 95 | 6080 | Planned | Planned Interruption | Clear trees around 11kv lines from pole #60268 to pole #60345 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 610 | O-4855-B | Marsden Pt | Ruakaka CB1 | 2024-12-05 09:09 | 2024-12-05 11:26 | 0.11059 | 0.00080723 | 52 | 7124 | Planned | Planned Interruption | Voltage indicator replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 611 | F-8152-A | Cartwright Rd | Onerahi CB6 | 2024-12-05 22:08 | 2024-12-05 23:30 | 0.74339 | 0.0090658 | 584 | 47888 | Unplanned | Defective Equipment | FP 388664 Repair HV jumper @ Sw 9431 & Clear Vegetation from 11kV | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 612 | O-4786-B | Hakaru | Kaiwaka CB1032 | 2024-12-06 09:01 | 2024-12-06 12:59 | 0.014825 | 6.2094e-05 | 4 | 955 | Planned | Planned Interruption | Network Maintenance - replace poles and crossarms between poles 45962 and 327439 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 613 | O-4882-B | Ararua | Mareretu CB2 | 2024-12-06 09:10 | 2024-12-06 14:36 | 0.060728 | 0.00018628 | 12 | 3912 | Planned | Planned Interruption | Upgrade TX Y100 and Y168 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 615 | F-8155-A | North River | Ruakaka CB7 | 2024-12-07 21:09 | 2024-12-08 00:44 | 0.68057 | 0.02136 | 1376 | 43841 | Unplanned | Defective Equipment | F 4104345 / FP 388713 - Lines clashed/twisted together. Cleared and relivened | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 616 | F-8158-A | King Road | Mangawhai North CB2 | 2024-12-07 21:38 | 2024-12-08 07:31 | 1.1569 | 0.013599 | 876 | 74525 | Unplanned | Third Party Interference | Car vs Pole - F 4104358 / FP 388714 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 617 | O-4993-B | Fert. Works | Kioreroa CB6 | 2024-12-08 12:01 | 2024-12-08 13:10 | 0.035347 | 0.00051228 | 33 | 2277 | Planned | Planned Interruption | Replacing Switch 9045 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 618 | O-4801-B | Hakaru | Kaiwaka CB1032 | 2024-12-09 09:06 | 2024-12-09 12:23 | 0.012233 | 6.2094e-05 | 4 | 788 | Planned | Planned Interruption | Replace conductor between poles 45962 and 45970 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 619 | F-8167-A | Bickerstaff | Maungaturoto CB2 | 2024-12-09 10:06 | 2024-12-09 10:24 | 0.20272 | 0.012062 | 777 | 13059 | Unplanned | Unknown | No FPIs available. Closed after 15min | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 620 | F-8173-A | Jordan Valley | Hikurangi CB1102 | 2024-12-10 07:40 | 2024-12-10 12:45 | 0.20758 | 0.0074048 | 477 | 13372 | Unplanned | Wildlife | 388765/ HV Lines Down at poles 35013 & 35016 caused by ducks | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 622 | O-4891-B | Tangaihi | Ruawai CB1032 | 2024-12-10 09:32 | 2024-12-10 13:19 | 0.021143 | 9.3142e-05 | 6 | 1362 | Planned | Planned Interruption | Cut vegetation from 3092 to EOL | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 623 | F-133-B | Te Kopuru | Dargaville CB2 | 2024-12-10 15:13 | 2024-12-10 16:23 | 0.072806 | 0.0010401 | 67 | 4690 | Unplanned | Defective Equipment | 388779 / Isolate HV to repair broken binders at pole 14497. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 624 | O-4804-B | Ararua | Mareretu CB2 | 2024-12-11 09:09 | 2024-12-11 14:04 | 0.46253 | 0.0015679 | 101 | 29795 | Planned | Planned Interruption | Reconductor 11kV lines from H Structure Pole 48027 - 48028 to EOL | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 625 | O-15487-A | North River | Ruakaka CB7 | 2024-12-11 09:28 | 2024-12-11 13:09 | 0.092629 | 0.00041914 | 27 | 5967 | Planned | Planned Interruption | Replace 13 cross arms and 6 span of conductor. Replace transformer @ Dsub RB146 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 626 | O-16450-A | Parua Bay | Parua Bay CB2 | 2024-12-11 10:03 | 2024-12-11 11:43 | 0.0015524 | 1.5524e-05 | 1 | 100 | Planned | Planned Interruption | Transformer Upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 627 | O-4897-B | Hakaru | Kaiwaka CB1032 | 2024-12-12 09:01 | 2024-12-12 12:05 | 0.01141 | 6.2094e-05 | 4 | 735 | Planned | Planned Interruption | conductor replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 628 | O-4951-B | Onoke | Kamo CB8 | 2024-12-12 09:03 | 2024-12-12 12:25 | 0.28199 | 0.0013971 | 90 | 18165 | Planned | Planned Interruption | Cut vegetation around 11kv lines from pole #908963 to pole #54293 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 629 | O-4966-B | Access Rd | Ruawai CB1022 | 2024-12-12 09:33 | 2024-12-12 13:56 | 0.14727 | 0.00055885 | 36 | 9487 | Planned | Planned Interruption | Replace pole #39801 to mitigate road crossing height issue. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 630 | F-8188-A | Paranui | Tikipunga CB6 | 2024-12-12 22:22 | 2024-12-12 23:07 | 0.0034928 | 7.7618e-05 | 5 | 225 | Unplanned | Unknown | 388852 / 2 x HV fuses blown causing flames on HV fuses. No obvious cause found. BTN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 631 | O-5011-B | Kamo Town | Kamo CB7 | 2024-12-13 09:02 | 2024-12-13 13:47 | 0.49109 | 0.0017231 | 111 | 31635 | Planned | Planned Interruption | New TX KK169 to be added at Pole 30986 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 632 | O-4957-B | Onoke | Kamo CB8 | 2024-12-13 09:05 | 2024-12-13 13:39 | 0.063802 | 0.00023285 | 15 | 4110 | Planned | Planned Interruption | HV crossarms and hardware replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 633 | O-4954-B | Hakaru | Kaiwaka CB1032 | 2024-12-13 09:09 | 2024-12-13 11:15 | 0.023472 | 0.00018628 | 12 | 1512 | Planned | Planned Interruption | Network Maintenance- Replace pole 11952 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 635 | F-8212-A | Coast | Dargaville CB6 | 2024-12-13 18:21 | 2024-12-14 03:13 | 0.18394 | 0.00076066 | 49 | 11849 | Unplanned | Defective Equipment | 388893 / Isolate & Repair broken 25mm XLPE cable at Links 3094 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 636 | F-8218-A | Taipuha | Mareretu CB1 | 2024-12-14 07:21 | 2024-12-14 14:42 | 0.26815 | 0.0036636 | 236 | 17274 | Unplanned | Defective Equipment | 388895/ HV Line down (Center Phase) between pole 34465 & 34466. Deterioration on cable | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 637 | F-8224-A | Marua | Hikurangi CB1022 | 2024-12-14 17:46 | 2024-12-14 19:27 | 0.0015679 | 1.5524e-05 | 1 | 101 | Unplanned | Defective Equipment | FP 388901 - Found fuse link corroded. Replaced. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 638 | F-8227-A | Puwera | Maungatapere CB7 | 2024-12-15 12:43 | 2024-12-15 12:45 | 3.1047e-05 | 1.5524e-05 | 1 | 2 | Unplanned | Defective Equipment | 388904/ x2 blown HV fuses (Undersized), Opened remaining HV fuse to check size & Close | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 639 | F-8239-A | Maunu Mountain | Maungatapere CB1 | 2024-12-16 04:41 | 2024-12-16 05:36 | 0.16084 | 0.0041293 | 532 | 10538 | Unplanned | Wildlife | FP 388910 E/F - Possum in lines at Pole 60782 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 640 | O-5059-B | Hakaru | Kaiwaka CB1032 | 2024-12-16 09:02 | 2024-12-16 13:57 | 0.018318 | 6.2094e-05 | 4 | 1180 | Planned | Planned Interruption | Replace 11kV conductor between poles 327439 and 45976 (These poles are being replaced on 06/11 and will have new numbers) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 641 | O-5050-B | North River | Ruakaka CB7 | 2024-12-16 10:05 | 2024-12-16 12:22 | 0.14218 | 0.0010401 | 67 | 9159 | Planned | Planned Interruption | Replace Pole 40898 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 642 | F-8254-A | ToeToe Rd | Kioreroa CB7 | 2024-12-16 16:21 | 2024-12-16 20:05 | 0.57611 | 0.010929 | 704 | 37112 | Unplanned | Defective Equipment | FP 388941 unknown fault betwn Sw 4385 & 929. Left switching abnormal (Sw 929 open), fault found later on F-8263-A | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 643 | O-5026-B | Ararua | Mareretu CB2 | 2024-12-17 09:02 | 2024-12-17 11:36 | 0.73632 | 0.0047813 | 308 | 47432 | Planned | Planned Interruption | Upgrading SW2132 to automated switch | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 644 | O-15517-A | Taipuha | Mareretu CB1 | 2024-12-17 09:05 | 2024-12-17 11:59 | 0.045919 | 0.0002639 | 17 | 2958 | Planned | Planned Interruption | Replace HV crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 645 | O-5056-B | Wairere | Mareretu CB5 | 2024-12-17 09:35 | 2024-12-17 13:44 | 0.79627 | 0.0031979 | 206 | 51294 | Planned | Planned Interruption | Replace pole 23782 with B11m type | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 646 | F-8260-A | Langs Beach | Mangawhai North CB3 | 2024-12-17 13:46 | 2024-12-17 14:02 | 0.20502 | 0.012388 | 798 | 13207 | Unplanned | Unknown | AB Overcurrent trip | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 647 | F-8263-A | ToeToe Rd | Kioreroa CB7 | 2024-12-17 15:26 | 2024-12-17 17:46 | 0.1028 | 0.0020802 | 134 | 6622 | Unplanned | Defective Equipment | FP388976 - Jumper on crossarm @ pole 30947 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 648 | F-8266-A | Titoki | Poroti CB1032 | 2024-12-17 23:44 | 2024-12-17 23:59 | 0.044879 | 0.0047347 | 305 | 2891 | Unplanned | Unknown | Sw 8191 indicating EF. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 649 | O-5062-B | 2nd Ave | Alexander St CB3 | 2024-12-18 09:02 | 2024-12-18 15:28 | 0.66512 | 0.0017231 | 111 | 42846 | Planned | Planned Interruption | Install new transformer WC473 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 650 | O-16498-A | Tangowahine | Dargaville CB8 | 2024-12-18 09:04 | 2024-12-18 15:36 | 0.54682 | 0.0013971 | 90 | 35225 | Planned | Planned Interruption | Remove links 3044. - (Links 10200 installed previoulsy NAR 6153) Replace links 3045 with links 10218 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 651 | F-8275-A | Tangaihi | Ruawai CB1032 | 2024-12-18 15:02 | 2024-12-18 17:45 | 0.70521 | 0.0058058 | 374 | 45428 | Unplanned | Human Error | Remedials for S-2408-A / Isolate & carry out remedials at pole 312410 to fix phase out issue. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 652 | F-8278-A | Whangarei Heads | Parua Bay CB3 | 2024-12-19 07:06 | 2024-12-19 13:25 | 1.3026 | 0.012388 | 798 | 83914 | Unplanned | Third Party Interference | 389000 / A & B Phase OC. Large Drone Vs Lines Craig Road causing line down. Bad access resulting in longer outage. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 653 | O-5065-B | Hotel | Poroti CB1052 | 2024-12-19 09:02 | 2024-12-19 14:12 | 0.21646 | 0.00069856 | 45 | 13944 | Planned | Planned Interruption | TX W166 upgrade to 100kVA | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 654 | O-5077-B | Ararua | Mareretu CB2 | 2024-12-19 09:04 | 2024-12-19 14:53 | 1.1106 | 0.0031823 | 205 | 71545 | Planned | Planned Interruption | Replace OH conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 655 | F-8281-A | Langs Beach | Mangawhai North CB3 | 2024-12-19 09:46 | 2024-12-19 10:02 | 0.19552 | 0.012388 | 798 | 12595 | Unplanned | Unknown | 389010 / Trip B & C Phase OC. FPIs at Sw 5482 Activated. L2 & L3. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 656 | F-142-B | Te Kopuru | Dargaville CB2 | 2024-12-19 12:22 | 2024-12-19 13:01 | 0.14591 | 0.0037412 | 241 | 9399 | Unplanned | Defective Equipment | 388797 / Isolate to repair broken X arm at pole 14358. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 657 | F-8284-A | Titoki | Poroti CB1032 | 2024-12-20 09:47 | 2024-12-20 13:46 | 0.38311 | 0.0047347 | 305 | 24679 | Unplanned | Unknown | FP 389034 - Suspected logging company bringing lines down from loader. Faulty tele switch past fault area. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 658 | F-8287-A | Te Kopuru | Dargaville CB2 | 2024-12-20 12:13 | 2024-12-20 17:54 | 0.035409 | 0.00027943 | 18 | 2281 | Unplanned | Defective Equipment | FP 389038 - Replaced faulty 11kV Fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 659 | F-145-B | Te Kopuru | Dargaville CB2 | 2024-12-21 07:39 | 2024-12-21 08:32 | 0.01481 | 0.00027943 | 18 | 954 | Unplanned | Defective Equipment | FP 389045 - Replaced faulty 11kV Fuses | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 660 | F-8293-A | Treatment | Kioreroa CB2 | 2024-12-23 04:18 | 2024-12-23 08:07 | 0.72146 | 0.0034928 | 225 | 46475 | Unplanned | Defective Equipment | FP389054/389053 Sw9061 faulty indicatio (appeared to be closed but didn't item8 F8290-a). Fault found later on F-8293-a 2nd trip | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 662 | F-8302-A | Treatment | Kioreroa CB2 | 2024-12-25 15:41 | 2024-12-25 20:35 | 0.11866 | 0.00040361 | 26 | 7644 | Unplanned | Defective Equipment | FP 389080 - UG HV fault between L9060 & WO199. Generated overnight | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 663 | F-8308-A | Pataua | Parua Bay CB1 | 2024-12-27 10:28 | 2024-12-27 11:12 | 0.056009 | 0.0012729 | 82 | 3608 | Unplanned | Defective Equipment | FP 389091 - Replace faulty DDOs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 664 | F-8311-A | Mata | Ruakaka CB3 | 2024-12-27 12:22 | 2024-12-27 12:38 | 0.065665 | 0.0069701 | 449 | 4230 | Unplanned | Adverse Weather | FPIs Sw 503 AB ph, OC B ph @ RKA sub. Windy conditions. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 665 | F-8314-A | Bickerstaff | Maungaturoto CB2 | 2024-12-27 12:49 | 2024-12-27 13:11 | 0.25015 | 0.012062 | 777 | 16114 | Unplanned | Adverse Weather | High Winds most likely cause. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 666 | F-8317-A | Matapouri | Ngunguru CB1032 | 2024-12-27 13:21 | 2024-12-27 18:12 | 0.7712 | 0.0076066 | 490 | 49679 | Unplanned | Vegetation | F 4117544 / FP 389096 - Trees in lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 667 | F-8320-A | Taipuha | Mareretu CB1 | 2024-12-27 13:31 | 2024-12-27 19:51 | 0.26297 | 0.0036636 | 236 | 16940 | Unplanned | Vegetation | 389102 - Lines down between 34207 & 32561 Bull Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 668 | F-8323-A | Kaiatea | Ngunguru CB1072 | 2024-12-27 13:49 | 2024-12-27 18:54 | 1.0734 | 0.021174 | 1364 | 69145 | Unplanned | Adverse Weather | FP 389122 - AC FPIs sw 720, light patrol. Field staff advised lines swinging heavily in wind. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 669 | F-8326-A | Thelma Road | Mangawhai North CB4 | 2024-12-27 14:27 | 2024-12-27 19:42 | 0.86654 | 0.013614 | 877 | 55821 | Unplanned | Defective Equipment | 389114 - Lines down - possibly due to clashing | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 670 | F-8329-A | North River | Ruakaka CB7 | 2024-12-27 14:37 | 2024-12-27 20:05 | 5.0242 | 0.037303 | 2403 | 323647 | Unplanned | Defective Equipment | 389104 - replaceed 2 xampacts at pole 337557 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 671 | F-8332-A | Whakapara | Hikurangi CB1112 | 2024-12-27 14:40 | 2024-12-27 17:06 | 0.88152 | 0.0060697 | 391 | 56786 | Unplanned | Adverse Weather | F 4117622 / FP 389117 - FENZ reported low lines. Field staff found Chorus lines. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 672 | F-8341-A | Tamaterau | Onerahi CB7 | 2024-12-27 21:16 | 2024-12-28 00:23 | 0.15676 | 0.00083828 | 54 | 10098 | Unplanned | Defective Equipment | FP 389129 - Repair 11kV cable termination | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 673 | F-8344-A | North Kaiwaka | Kaiwaka CB1022 | 2024-12-27 22:25 | 2024-12-27 23:55 | 0.055652 | 0.0012574 | 81 | 3585 | Unplanned | Defective Equipment | 389125 Jumper off on the line side of Links 419 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 674 | F-8362-A | North Dargaville | Dargaville CB1 | 2024-12-30 15:38 | 2024-12-30 21:29 | 0.20622 | 0.0041603 | 268 | 13284 | Unplanned | Defective Equipment | FP389164/ Replaced Faulty Tx - HV Bushing Fail | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 675 | F-8359-A | Kaiatea | Ngunguru CB1072 | 2024-12-30 15:38 | 2024-12-30 19:53 | 0.96099 | 0.010587 | 682 | 61905 | Unplanned | Defective Equipment | FP389163/ HV Lines Clashing between Spur & Main Line. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 676 | F-8374-A | MTON - MTO POS | Maungaturoto POS CB1262 | 2025-01-02 22:15 | 2025-01-02 22:45 | 2.6803 | 0.10559 | 6805 | 172732 | Unplanned | Lightning | FP 389184. CB 1222 MTO & CB 72 MTON Tripped. Patrolled Relivened - further daylight patrol required, fault found on F-8377-A | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 677 | F-8377-A | MTON - MTO POS | Maungaturoto POS CB1262 | 2025-01-03 14:47 | 2025-01-03 16:23 | 6.0972 | 0.073862 | 4760 | 392931 | Unplanned | Lightning | 389184 / Isolate 33kV to replace blown insulator on pole 17708. Most probable cause from on site staff said lightning stike. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 678 | F-8398-A | Taipuha | Mareretu CB1 | 2025-01-06 14:56 | 2025-01-06 14:57 | 0.0075569 | 0.0070914 | 457 | 487 | Unplanned | Unknown | Trip EF.FPI @ sw364 Phase A & N | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 679 | O-5080-B | Coast | Dargaville CB6 | 2025-01-07 09:02 | 2025-01-07 11:12 | 0.056529 | 0.00043448 | 28 | 3643 | Planned | Planned Interruption | Repair guy wire / replace DOFs L133 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 680 | O-5074-B | Taipuha | Mareretu CB1 | 2025-01-07 09:02 | 2025-01-07 12:18 | 0.1764 | 0.0009 | 58 | 11368 | Planned | Planned Interruption | HV crossarm replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 682 | O-5320-B | King Road | Mangawhai North CB2 | 2025-01-07 13:18 | 2025-01-07 14:08 | 0.010862 | 0.00021724 | 14 | 700 | Planned | Planned Interruption | Inspect HV bushing | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 683 | O-5095-B | Kokopu | Poroti CB1022 | 2025-01-08 09:04 | 2025-01-08 13:54 | 0.198 | 0.00068276 | 44 | 12760 | Planned | Planned Interruption | Replace various crossarms and pole 12793 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 684 | O-5092-B | North River | Ruakaka CB7 | 2025-01-08 09:05 | 2025-01-08 14:10 | 0.5348 | 0.0017534 | 113 | 34465 | Planned | Planned Interruption | Install new transformer RB336, poles and aerial conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 685 | O-5191-B | Turiwiri | Dargaville CB9 | 2025-01-08 10:45 | 2025-01-08 11:37 | 0.0032276 | 6.2069e-05 | 4 | 208 | Planned | Planned Interruption | Drop redundant lines away from pole #21880 remove Tx J210 & J241 from serivce | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 686 | F-8434-A | Jordan Valley | Hikurangi CB1102 | 2025-01-08 16:38 | 2025-01-08 22:27 | 0.45928 | 0.019629 | 1265 | 29598 | Unplanned | Defective Equipment | 389312/Broken Line down from Ampac connection pole 35863. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 687 | O-5104-B | Otangarei | Tikipunga CB7 | 2025-01-09 09:03 | 2025-01-09 12:16 | 0.29649 | 0.0015362 | 99 | 19107 | Planned | Planned Interruption | Replace LV Link Pillar replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 688 | O-5101-B | Titoki | Poroti CB1032 | 2025-01-09 09:16 | 2025-01-09 14:28 | 0.63012 | 0.0020172 | 130 | 40608 | Planned | Planned Interruption | Tree clearing work | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 689 | O-5215-B | Whatatiri | Maungatapere CB8 | 2025-01-09 09:23 | 2025-01-09 14:25 | 0.47262 | 0.0015672 | 101 | 30458 | Planned | Planned Interruption | Replant and straighten various poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 690 | O-5089-B | Jordan Valley | Hikurangi CB1102 | 2025-01-09 09:34 | 2025-01-09 12:41 | 0.058034 | 0.00031034 | 20 | 3740 | Planned | Planned Interruption | TX structure upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 691 | F-8443-A | Taipuha | Mareretu CB1 | 2025-01-09 20:16 | 2025-01-10 14:11 | 0.016681 | 1.5517e-05 | 1 | 1075 | Unplanned | Defective Equipment | FP 389357 - Isolate Tx X387, cable to be repaired. 1 unused water pump | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 692 | O-5164-B | Kiripaka Rd | Tikipunga CB8 | 2025-01-10 09:04 | 2025-01-10 14:13 | 0.12946 | 0.00041897 | 27 | 8343 | Planned | Planned Interruption | Switch 704 decommissioned, switch 10170 being installed | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 693 | O-5110-B | Mata | Ruakaka CB3 | 2025-01-10 09:33 | 2025-01-10 11:27 | 0.0070759 | 6.2069e-05 | 4 | 456 | Planned | Planned Interruption | Bolt down transformer RO269 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 694 | F-8449-A | Kaiwaka South | Kaiwaka CB1072 | 2025-01-11 11:10 | 2025-01-11 11:26 | 0.12366 | 0.0079603 | 513 | 7969 | Unplanned | Unknown | BC ph FPIs @ Sw 320. Sw 320 tele control faulty. Reclosed after 15. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 695 | F-8455-A | Commercial | Mangawhai Central | 2025-01-13 00:57 | 2025-01-13 01:13 | 0.12507 | 0.013609 | 877 | 8060 | Unplanned | Unknown | A, B, C phase beyond Sw 4270 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 696 | O-5116-B | Rewa Rewa Rd | Whangarei South CB1082 | 2025-01-13 09:05 | 2025-01-13 14:43 | 0.30944 | 0.00091552 | 59 | 19942 | Planned | Planned Interruption | Link Pillar replacement - HV isolated to access LV | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 697 | O-5206-B | Kokopu | Poroti CB1022 | 2025-01-13 09:15 | 2025-01-13 13:17 | 0.61597 | 0.0025448 | 164 | 39696 | Planned | Planned Interruption | Replace pole to increase ground clearance, replace crossarms and redo connections | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 698 | O-5218-B | Langs Beach | Mangawhai North CB3 | 2025-01-13 10:07 | 2025-01-13 13:29 | 0.068959 | 0.00034138 | 22 | 4444 | Planned | Planned Interruption | New TX RR354 added to network | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 699 | F-8461-A | Titoki | Poroti CB1032 | 2025-01-13 10:48 | 2025-01-13 13:14 | 0.27313 | 0.0029328 | 189 | 17602 | Unplanned | Defective Equipment | Lines down - FP389430 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 700 | O-5221-B | North Dargaville | Dargaville CB1 | 2025-01-13 10:55 | 2025-01-13 12:42 | 0.076376 | 0.00071379 | 46 | 4922 | Planned | Planned Interruption | Replace 3138KL with NGK 630A type | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 701 | F-8467-A | Tangaihi | Ruawai CB1032 | 2025-01-13 15:02 | 2025-01-13 15:15 | 0.0012103 | 9.3103e-05 | 6 | 78 | Unplanned | Vegetation | FP 389439 - tree branch in OH lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 702 | O-15898-A | Taipuha | Mareretu CB1 | 2025-01-14 09:04 | 2025-01-14 12:26 | 0.024983 | 0.00012414 | 8 | 1610 | Planned | Planned Interruption | Replace pole 34567 and replace cross arms at various poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 703 | O-5119-B | Ararua | Mareretu CB2 | 2025-01-14 09:05 | 2025-01-14 14:47 | 0.57314 | 0.0016759 | 108 | 36936 | Planned | Planned Interruption | Upgrade TX E208 and replace 2 x poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 704 | O-5125-B | Te Kopuru | Dargaville CB2 | 2025-01-14 09:33 | 2025-01-14 13:12 | 0.1937 | 0.00088448 | 57 | 12483 | Planned | Planned Interruption | Tree clearing work | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 705 | F-8473-A | Maungakaramea | Maungatapere CB3 | 2025-01-14 21:53 | 2025-01-15 01:03 | 0.023586 | 0.00012414 | 8 | 1520 | Unplanned | Defective Equipment | 389475 / Isolate HV to replace broken pole 53770 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 706 | O-15127-A | Turiwiri | Dargaville CB9 | 2025-01-15 09:03 | 2025-01-15 14:25 | 0.094934 | 0.00029483 | 19 | 6118 | Planned | Planned Interruption | Replace HV and LV cross arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 707 | O-5203-B | Thelma Road | Mangawhai North CB4 | 2025-01-15 09:06 | 2025-01-15 11:07 | 0.026286 | 0.00021724 | 14 | 1694 | Planned | Planned Interruption | DOF MC288 being replaced | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 709 | F-8479-A | Ruatangata | Kamo CB6 | 2025-01-15 11:15 | 2025-01-15 13:28 | 0.0041276 | 3.1034e-05 | 2 | 266 | Unplanned | Defective Equipment | 389484 Broken DOFs to be replaced | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 710 | F-8488-A | Ararua | Mareretu CB2 | 2025-01-16 08:12 | 2025-01-16 17:51 | 1.1468 | 0.026348 | 1698 | 73904 | Unplanned | Third Party Interference | Agricultural Drone in lines. Crossarm broken, pole cracked. FP 389517 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 711 | O-15928-A | Taipuha | Mareretu CB1 | 2025-01-16 09:03 | 2025-01-16 12:57 | 0.31947 | 0.0013655 | 88 | 20588 | Planned | Planned Interruption | Replace cross arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 712 | O-5155-B | Ararua | Mareretu CB2 | 2025-01-16 09:10 | 2025-01-16 12:40 | 0.66802 | 0.003181 | 205 | 43050 | Planned | Planned Interruption | Replace conductor between poles 911547 and 406935 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 713 | O-16267-A | Paranui | Tikipunga CB6 | 2025-01-16 09:11 | 2025-01-16 11:34 | 0.013314 | 9.3103e-05 | 6 | 858 | Planned | Planned Interruption | Level D-sub KT360 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 714 | O-5224-B | Whatatiri | Maungatapere CB8 | 2025-01-16 09:32 | 2025-01-16 14:24 | 0.43045 | 0.0014741 | 95 | 27740 | Planned | Planned Interruption | Tree clearing work | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 715 | O-5230-B | Matapouri | Ngunguru CB1032 | 2025-01-16 10:10 | 2025-01-16 12:29 | 0.0064707 | 4.6552e-05 | 3 | 417 | Planned | Planned Interruption | Level TX NT201 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 716 | F-8497-A | North Dargaville | Dargaville CB1 | 2025-01-16 20:32 | 2025-01-17 12:21 | 0.79319 | 0.02101 | 1354 | 51117 | Unplanned | Defective Equipment | 389542 Lines down reported at 119 Waikara Road | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 717 | O-5140-B | Turiwiri | Dargaville CB9 | 2025-01-17 09:06 | 2025-01-17 15:08 | 0.1346 | 0.00037241 | 24 | 8674 | Planned | Planned Interruption | Crossarms replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 718 | O-5407-B | Otonga | Hikurangi CB1032 | 2025-01-17 09:31 | 2025-01-17 13:33 | 0.34304 | 0.0015983 | 103 | 22107 | Planned | Planned Interruption | Replace damaged HV cable riser on pole #302523 and re configure cross arm to install crucifix above transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 719 | F-8512-A | Coast | Dargaville CB6 | 2025-01-19 10:43 | 2025-01-19 10:58 | 0.0423 | 0.0027465 | 177 | 2726 | Unplanned | Unknown | Nil / Trip A & B Phase. 15 Min Close & BTN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 720 | F-8515-A | Kiripaka Rd | Tikipunga CB8 | 2025-01-19 13:05 | 2025-01-19 14:06 | 0.0028241 | 4.6552e-05 | 3 | 182 | Unplanned | Unknown | 389575 / 2 x HV fuses blown wth no obvious cause. All BTN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 721 | F-8521-A | Tutukaka Block | Ngunguru CB1082 | 2025-01-19 22:53 | 2025-01-20 03:19 | 1.5277 | 0.010288 | 663 | 98451 | Unplanned | Lightning | FP - 389582 Blown LA at fuses NP181 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 722 | F-8524-A | Coast | Dargaville CB6 | 2025-01-20 01:16 | 2025-01-20 02:04 | 0.037241 | 0.00077586 | 50 | 2400 | Unplanned | Vegetation | 389580 Trees blowing in the HV - started fire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 723 | F-8527-A | Titoki | Poroti CB1032 | 2025-01-21 03:09 | 2025-01-21 10:24 | 0.38337 | 0.011964 | 771 | 24706 | Unplanned | Defective Equipment | FP 389629 - Replace faulty tx | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 724 | F-8533-A | North River | Ruakaka CB7 | 2025-01-21 03:47 | 2025-01-21 11:37 | 0.89795 | 0.0076345 | 492 | 57868 | Unplanned | Vegetation | 389632 Trees in lines at RB120 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 725 | F-8536-A | Tamaterau | Onerahi CB7 | 2025-01-21 04:56 | 2025-01-21 04:58 | 0.016867 | 0.0087207 | 562 | 1087 | Unplanned | Adverse Weather | A & B O/C - Trip and close. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 726 | F-8539-A | Kokopu | Poroti CB1022 | 2025-01-21 05:02 | 2025-01-21 11:17 | 1.2633 | 0.011002 | 709 | 81412 | Unplanned | Defective Equipment | FP 389637 - Repair lines down @ pole 315224 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 727 | F-8542-A | Whatatiri | Maungatapere CB8 | 2025-01-21 06:16 | 2025-01-21 06:31 | 0.13908 | 0.0095431 | 615 | 8963 | Unplanned | Adverse Weather | Fault is beyond SW 843 - closed after 15 min | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 728 | F-8545-A | Whakapara | Hikurangi CB1112 | 2025-01-21 07:22 | 2025-01-21 07:54 | 0.39934 | 0.01696 | 1093 | 25735 | Unplanned | Adverse Weather | Trip and close >15. FPIs Sw 663 ABC | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 729 | F-8548-A | Paranui | Tikipunga CB6 | 2025-01-21 09:05 | 2025-01-21 09:06 | 0.012134 | 0.011374 | 733 | 782 | Unplanned | Unknown | Tripped & Closed | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 730 | O-5233-B | Bickerstaff | Maungaturoto CB2 | 2025-01-21 09:07 | 2025-01-23 13:15 | 0 | 0 | 0 | 0 | Planned | Planned Interruption | Raise RMU | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 731 | O-5143-B | Whatatiri | Maungatapere CB8 | 2025-01-21 10:36 | 2025-01-21 14:36 | 0.73085 | 0.0030414 | 196 | 47099 | Planned | Planned Interruption | Upgrade switch 849 to automated switch | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 732 | F-8554-A | Paparoa | Mareretu CB6 | 2025-01-21 11:02 | 2025-01-21 16:30 | 0.58039 | 0.0091862 | 592 | 37403 | Unplanned | Vegetation | FP 389669 - LV lines down from tree | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 733 | F-8557-A | Puwera | Maungatapere CB7 | 2025-01-21 11:09 | 2025-01-21 17:17 | 0.32901 | 0.0041897 | 270 | 21203 | Unplanned | Defective Equipment | 389674 Lines down near TX X353 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 734 | F-8569-A | Taipuha | Mareretu CB1 | 2025-01-21 14:28 | 2025-01-21 17:23 | 0.081652 | 0.00135 | 87 | 5262 | Unplanned | Defective Equipment | 389685 HV lines down at pole 34207 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 735 | O-5260-B | North River | Ruakaka CB7 | 2025-01-22 07:02 | 2025-01-22 14:06 | 0.7445 | 0.0066259 | 427 | 47979 | Planned | Planned Interruption | Install new OH switch to replace links 542 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 736 | O-5158-B | Tangowahine | Dargaville CB8 | 2025-01-22 09:05 | 2025-01-22 15:27 | 0.065203 | 0.00017069 | 11 | 4202 | Planned | Planned Interruption | Replace poles and 11kV conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 737 | O-16222-A | Titoki | Poroti CB1032 | 2025-01-22 09:06 | 2025-01-22 15:12 | 0.60405 | 0.0017069 | 110 | 38928 | Planned | Planned Interruption | Replace cross arms, Connections and HV links 792 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 738 | O-5251-B | Marsden Pt | Ruakaka CB1 | 2025-01-22 09:22 | 2025-01-22 11:43 | 0.11377 | 0.0008069 | 52 | 7332 | Planned | Planned Interruption | Replace Voltage indicators | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 739 | O-5227-B | Langs Beach | Mangawhai North CB3 | 2025-01-22 09:37 | 2025-01-22 12:19 | 0.062845 | 0.00038793 | 25 | 4050 | Planned | Planned Interruption | Install new TX RR356 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 740 | O-5302-B | Paparoa | Mareretu CB6 | 2025-01-23 09:07 | 2025-01-23 14:37 | 0.87395 | 0.002669 | 172 | 56321 | Planned | Planned Interruption | Replace HV poles and cross arms Refurbish Dsubs A150 and A131 and replace HV and LV cross arms at various sites | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 741 | O-5416-B | North Dargaville | Dargaville CB1 | 2025-01-23 09:19 | 2025-01-23 11:52 | 0.018993 | 0.00012414 | 8 | 1224 | Planned | Planned Interruption | Remove 11KV line From Pole 27184 to Pole 27191 including TX M516 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 743 | O-5209-B | Langs Beach | Mangawhai North CB3 | 2025-01-24 09:04 | 2025-01-24 14:32 | 0.076345 | 0.00023276 | 15 | 4920 | Planned | Planned Interruption | Replace transformer RR221 with a 300kva with existing label RR221 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 745 | F-8599-A | Matapouri | Ngunguru CB1032 | 2025-01-24 09:31 | 2025-01-24 11:26 | 0.3685 | 0.012305 | 793 | 23748 | Unplanned | Third Party Interference | 389807 Tree felled into line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 746 | O-17401-A | Matapouri | Ngunguru CB1032 | 2025-01-24 14:07 | 2025-01-25 10:26 | 0.11131 | 0.00069828 | 45 | 7173 | Unplanned | Defective Equipment | 389815 Generator connected to Tx NT131 @1730hrs Replaced 3x HV fuse bases F7205 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 747 | F-8614-A | Matapouri | Ngunguru CB1032 | 2025-01-26 02:19 | 2025-01-26 02:35 | 0.10583 | 0.01229 | 792 | 6820 | Unplanned | Lightning | Suspected lightning strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 748 | F-8617-A | Langs Beach | Mangawhai North CB3 | 2025-01-26 02:50 | 2025-01-26 10:29 | 5.1949 | 0.012429 | 801 | 334780 | Unplanned | Adverse Weather | 389850 Feeder tripped during weather event,TORNADO Ref: F-8623-a & F-8626-A | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 749 | F-8623-A | KAI - MWI 33kV | Kaiwaka CB52 | 2025-01-26 02:56 | 2025-01-28 16:16 | 25.0559 | 0.063202 | 4073 | 1614712 | Unplanned | Adverse Weather | 389845 / Tornado Damages Mangawhai Ref: F-8623-a | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 750 | O-17410-A | Hakaru | Kaiwaka CB1032 | 2025-01-26 05:56 | 2025-01-26 07:24 | 0.31377 | 0.0035534 | 229 | 20221 | Unplanned | Other Cause | De-energised for safety due to report of sparking on pole. Inspected, no fault found. (33kV FPIs flashing) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 751 | F-8629-A | Tangaihi | Ruawai CB1032 | 2025-01-26 08:23 | 2025-01-26 11:54 | 0.13877 | 0.0014431 | 93 | 8943 | Unplanned | Lightning | 389844 DOFs damaged requiring replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 752 | F-8632-A | One Tree Point | Ruakaka CB6 | 2025-01-26 09:12 | 2025-01-26 09:13 | 0.0066414 | 0.0065328 | 421 | 428 | Unplanned | Unknown | 1 min close | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 753 | F-8641-A | Bickerstaff | Maungaturoto CB2 | 2025-01-26 14:08 | 2025-01-26 17:49 | 0.59645 | 0.0094655 | 610 | 38438 | Unplanned | Defective Equipment | 389852 Blown jumper at pole 23693 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 754 | F-8644-A | Tangowahine | Dargaville CB8 | 2025-01-27 17:41 | 2025-01-27 17:59 | 0.037319 | 0.0089845 | 579 | 2405 | Unplanned | Unknown | Trip Overcurrent A B & C. FPIs at Sw 2037 activated. Closed & BTN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 755 | F-8647-A | Bickerstaff | Maungaturoto CB2 | 2025-01-27 18:54 | 2025-01-27 19:08 | 0.17505 | 0.012072 | 778 | 11281 | Unplanned | Unknown | OC | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 756 | F-8650-A | North Kaiwaka | Kaiwaka CB1022 | 2025-01-27 21:44 | 2025-01-27 21:56 | 0.042284 | 0.0033828 | 218 | 2725 | Unplanned | Unknown | O/C | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 757 | F-8656-A | One Tree Point | Ruakaka CB6 | 2025-01-28 07:11 | 2025-01-28 07:12 | 0.0088138 | 0.0065328 | 421 | 568 | Unplanned | Unknown | Trip B & C Overcurrent. BTN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 758 | O-5437-B | Maunu Mountain | Maungatapere CB1 | 2025-01-28 09:01 | 2025-01-28 10:26 | 0.065452 | 0.00077586 | 50 | 4218 | Planned | Planned Interruption | Remove Links 8842KL and replace with jumpers | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 760 | O-5308-B | Jordan Valley | Hikurangi CB1102 | 2025-01-28 09:39 | 2025-01-28 14:51 | 0.1985 | 0.00063621 | 41 | 12792 | Planned | Planned Interruption | HV Isolation for safety Replacing LV conductor from KR201 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 761 | O-5401-B | Taipuha | Mareretu CB1 | 2025-01-28 09:52 | 2025-01-28 13:17 | 0.025448 | 0.00012414 | 8 | 1640 | Planned | Planned Interruption | LV pole and crossarm replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 762 | F-8665-A | Whakapara | Hikurangi CB1112 | 2025-01-28 10:52 | 2025-01-28 11:07 | 0.19291 | 0.01696 | 1093 | 12432 | Unplanned | Unknown | Fault beyond SW663, closed after 15min, held | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 763 | O-5425-B | Maungatapere - Dairy Factory | Maungatapere CB6 | 2025-01-28 11:31 | 2025-01-28 12:34 | 0.10168 | 0.0015983 | 103 | 6553 | Planned | Planned Interruption | Remove links 8881KL | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 764 | F-8668-A | Te Kopuru | Dargaville CB2 | 2025-01-29 06:24 | 2025-01-29 06:40 | 0.1381 | 0.01471 | 948 | 8900 | Unplanned | Unknown | B ph & N fault - Close >15min | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 765 | O-5392-B | North River | Ruakaka CB7 | 2025-01-29 09:00 | 2025-01-29 12:41 | 0.78738 | 0.003569 | 230 | 50742 | Planned | Planned Interruption | Replace 11kV pole and cross arms, replace one span of 11KV conductor, Refurbish Dsub RB218 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 766 | O-5329-B | Brynderwyn | Maungaturoto CB1 | 2025-01-29 09:22 | 2025-01-29 14:43 | 0.084678 | 0.00026379 | 17 | 5457 | Planned | Planned Interruption | Replace pole hardware & transformer D387 like for like, from pole 23609 to EOL | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 767 | O-15934-A | Ararua | Mareretu CB2 | 2025-01-30 09:01 | 2025-01-30 13:47 | 0.66791 | 0.0023431 | 151 | 43043 | Planned | Planned Interruption | Replace HV & LV cross arms and refurbish various Dsubs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 768 | O-4963-B | Kiripaka Rd | Tikipunga CB8 | 2025-01-30 09:09 | 2025-01-31 15:58 | 1.0985 | 0.0022655 | 146 | 70793 | Planned | Planned Interruption | Install new RMU. Post livening issue. Generation used over night. upgrade TX KT162 following day. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 769 | O-5332-B | Kiripaka Rd | Tikipunga CB8 | 2025-01-31 00:02 | 2025-01-31 01:33 | 0.30924 | 0.0033983 | 219 | 19929 | Planned | Planned Interruption | Improvements in Supply Quality - INSTALL HV POST ISULATORS TO IMPROVE CLEARANCE BETWEEN 11Kv JUMPERS AND CROSSARMS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 770 | O-5434-B | Taipuha | Mareretu CB1 | 2025-01-31 09:05 | 2025-01-31 13:25 | 0.076655 | 0.00029483 | 19 | 4940 | Planned | Planned Interruption | Install TX X525 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 771 | O-5446-B | Ararua | Mareretu CB2 | 2025-01-31 09:16 | 2025-01-31 16:22 | 0.71392 | 0.0016759 | 108 | 46008 | Planned | Planned Interruption | Upgrade LV overhead lines between poles 980606 and 48704. Remove LV overhead lines between poles 909762 and 911799 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 772 | O-5335-B | Puwera | Maungatapere CB7 | 2025-01-31 09:26 | 2025-01-31 10:33 | 0.019598 | 0.00029483 | 19 | 1263 | Planned | Planned Interruption | Remove links 8049KL | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 773 | O-5461-B | Taipuha | Mareretu CB1 | 2025-01-31 10:47 | 2025-01-31 11:50 | 0.087983 | 0.0013966 | 90 | 5670 | Planned | Planned Interruption | Urgent Repairs - replace HV arms, LV connections, Straighten pole and replace stay wires | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 774 | F-8686-A | Waipu | Ruakaka CB2 | 2025-02-01 08:22 | 2025-02-01 09:04 | 0.079594 | 0.001908 | 123 | 5131 | Unplanned | Defective Equipment | FP 390026 - Report of low wire across road - opened Sw 5236 for safety. Broken guy & low LV RR170 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 775 | F-8698-A | Bickerstaff | Maungaturoto CB2 | 2025-02-02 22:01 | 2025-02-02 22:53 | 0.24451 | 0.012069 | 778 | 15762 | Unplanned | Wildlife | FP 390034 - FENZ 4140475 report of bird strike & fire. Found deceased goose. No line damage found. FENZ clear. Relivened. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 776 | F-8701-A | Austin Road | Maunu CB1072 | 2025-02-03 05:10 | 2025-02-03 06:01 | 0.3284 | 0.0063911 | 412 | 21170 | Unplanned | Unknown | FP390035 - Heavy fault - report of bang and flash near Sw 7015. Suspect possum. Checked and relivened | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 777 | O-5263-B | Tangowahine | Dargaville CB8 | 2025-02-03 09:09 | 2025-02-03 14:05 | 0.050508 | 0.00017064 | 11 | 3256 | Planned | Planned Interruption | Replace poles and conductor | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 779 | O-5359-B | Thelma Road | Mangawhai North CB4 | 2025-02-04 09:23 | 2025-02-04 14:26 | 0.5622 | 0.0019856 | 128 | 36242 | Planned | Planned Interruption | Replace pole 29529, straighten poles 29524 and 29522 and level transformer MC463 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 781 | O-5257-B | Wairere | Mareretu CB5 | 2025-02-05 09:46 | 2025-02-05 13:03 | 0.10424 | 0.00052742 | 34 | 6720 | Planned | Planned Interruption | Replace transformer like for like and replace pole hardware | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 782 | O-17563-A | Jordan Valley | Hikurangi CB1102 | 2025-02-08 20:35 | 2025-02-08 23:40 | 0.50788 | 0.0073994 | 477 | 32740 | Unplanned | Wildlife | FP390167 Bird strike causing lines down between pole 35013 and pole 324337 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 783 | F-8725-A | Ararua | Mareretu CB2 | 2025-02-10 01:09 | 2025-02-10 01:10 | 0.013511 | 0.010393 | 670 | 871 | Unplanned | Unknown | T & C | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 784 | O-5362-B | Onoke | Kamo CB8 | 2025-02-10 09:04 | 2025-02-10 14:28 | 0.4514 | 0.0013961 | 90 | 29099 | Planned | Planned Interruption | Replace links 7267KL with SW 10221 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 785 | F-8728-A | Mata | Ruakaka CB3 | 2025-02-10 10:38 | 2025-02-10 11:15 | 0.017219 | 0.00046537 | 30 | 1110 | Unplanned | Defective Equipment | FP 390183 - Fit insulator back on to crossarm, upcoming shutdown in area, full replacement will be done then. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 787 | F-8743-A | Norfolk St | Alexander St CB1 | 2025-02-11 11:57 | 2025-02-11 17:21 | 1.1144 | 0.022369 | 1442 | 71841 | Unplanned | Defective Equipment | FP 390230 - HV Cable fault white phase between Pole 307150 & Switch 271. Cable left disconnected and backfed from Whg CB 1092 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 788 | F-8752-A | Access Rd | Ruawai CB1022 | 2025-02-11 23:50 | 2025-02-12 00:05 | 0.0598 | 0.0052122 | 336 | 3855 | Unplanned | Unknown | 15 min close to Sw 2235 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 789 | O-5452-B | Mata | Ruakaka CB3 | 2025-02-12 09:01 | 2025-02-12 14:11 | 0.33662 | 0.0010859 | 70 | 21700 | Planned | Planned Interruption | HV/LV POLE, ARM & HARDWARE REPLACEMENTS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 790 | F-8764-A | Titoki | Poroti CB1032 | 2025-02-13 07:58 | 2025-02-13 10:03 | 0.29667 | 0.0023734 | 153 | 19125 | Unplanned | Human Error | 390275 / Sw 793 Opened without Authorisation, switch had same Chanel and Address as switch 33/1008 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 791 | F-2537-A | TIK - ONE (Ngunguru) | Tikipunga CB92 | 2025-02-13 09:02 | 2025-02-13 13:41 | 0.31577 | 0.0011324 | 73 | 20356 | Planned | Planned Interruption | Replace various poles from 38178 to EOL | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 794 | F-8803-A | Maungakaramea | Maungatapere CB3 | 2025-02-14 17:40 | 2025-02-14 19:02 | 0.11448 | 0.0013961 | 90 | 7380 | Unplanned | Defective Equipment | 390338 / Isolate area to replace broken crossarm & hardware on pole 12552. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 795 | F-8812-A | One Tree Point | Ruakaka CB6 | 2025-02-15 05:33 | 2025-02-15 07:51 | 0.52685 | 0.0065307 | 421 | 33963 | Unplanned | Unknown | FP390347 Tripped O/C A&B phase, patrolled and found no cause, closed in and holding | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 796 | F-8821-A | One Tree Point | Ruakaka CB6 | 2025-02-15 21:28 | 2025-02-16 00:01 | 0.35191 | 0.019592 | 1263 | 22686 | Unplanned | Unknown | 390352 / Intermittent fault on CB 6 RKA. Patrolled for the second time in 24 hours with no avail. Potential Cracked Insulator. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 797 | F-8818-A | Cartwright Rd | Onerahi CB6 | 2025-02-15 22:08 | 2025-02-16 05:29 | 0.44044 | 0.0063601 | 410 | 28393 | Unplanned | Third Party Interference | 390351 / Car Vs Pole 51973. Cut Break and replace pole. BTN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 798 | F-8824-A | Montgomery Ave | Onerahi CB8 | 2025-02-16 05:13 | 2025-02-16 07:10 | 0.50972 | 0.032359 | 2086 | 32859 | Unplanned | Vegetation | 390353 / Intermittent tripping. Patrolled and found Bark on lines at pole 36557. Removed & BTN. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 799 | O-5506-B | Norfolk St | Alexander St CB1 | 2025-02-16 07:32 | 2025-02-16 17:24 | 0.17448 | 0.00029474 | 19 | 11248 | Planned | Planned Interruption | Replace LV Frame with New one. Some LV backfeed done, only 19 ICPs affected | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 801 | F-8830-A | Mata | Ruakaka CB3 | 2025-02-17 08:17 | 2025-02-17 12:41 | 0.18772 | 0.0016443 | 106 | 12101 | Unplanned | Defective Equipment | FP 390365 - Report of fire on pole, Broken guy wire on 11kV jumper. Pole leaning, isolated for repairs | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 802 | O-5653-B | Puwera | Maungatapere CB7 | 2025-02-17 09:03 | 2025-02-17 11:58 | 0.38548 | 0.0022028 | 142 | 24850 | Planned | Planned Interruption | Install new HV fuses and tx X524 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 804 | F-8836-A | Dunns Rd | Ruawai CB1082 | 2025-02-17 13:31 | 2025-02-17 13:46 | 0.041279 | 0.0027457 | 177 | 2661 | Unplanned | Unknown | 15 min close | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 805 | O-17641-A | Jordan Valley | Hikurangi CB1102 | 2025-02-17 17:14 | 2025-02-18 00:31 | 0.39018 | 0.0074149 | 478 | 25153 | Unplanned | Third Party Interference | FP390403 Car Vs pole 20319 - 33 & 11kV | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 806 | O-5377-B | Montgomery Ave | Onerahi CB8 | 2025-02-18 09:02 | 2025-02-18 14:06 | 0.34503 | 0.0011324 | 73 | 22242 | Planned | Planned Interruption | 11kV WIRE AND HARDWARE REPLACEMENTS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 807 | O-5644-B | Otonga | Hikurangi CB1032 | 2025-02-18 09:19 | 2025-02-18 15:08 | 0.48735 | 0.0015978 | 103 | 31417 | Planned | Planned Interruption | Replace cable and crucifix at pole 302523 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 808 | O-5602-B | Hokianga Rd | Dargaville CB7 | 2025-02-18 09:33 | 2025-02-18 12:29 | 0.054604 | 0.00031025 | 20 | 3520 | Planned | Planned Interruption | Level transformer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 809 | F-8851-A | Mata | Ruakaka CB3 | 2025-02-18 21:42 | 2025-02-19 00:20 | 0.11037 | 0.0020787 | 134 | 7115 | Unplanned | Defective Equipment | FP390440 FENZ report scrub fire. De-energiised remotely. Broken LV line RO426 caused by preform (fuses in tact). 4 dead cows. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 810 | F-8854-A | Swamp North | Hikurangi CB1042 | 2025-02-18 22:25 | 2025-02-19 02:44 | 0.62012 | 0.0062825 | 405 | 39976 | Unplanned | Wildlife | FP390441 - 11kV line down & 1 damaged - paradise duck. Additional 104 customers affected for 3h20m due to Sw 674 not operating. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 811 | O-5629-B | Taipuha | Mareretu CB1 | 2025-02-19 09:02 | 2025-02-19 13:17 | 0.24148 | 0.00094626 | 61 | 15567 | Planned | Planned Interruption | Replace 11kV arms and pole stays at multiple sites | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 813 | O-5131-B | Ruatangata | Kamo CB6 | 2025-02-19 09:06 | 2025-02-19 14:50 | 0.53363 | 0.0015512 | 100 | 34400 | Planned | Planned Interruption | New TX KR310 installation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 814 | O-5365-B | Montgomery Ave | Onerahi CB8 | 2025-02-20 09:02 | 2025-02-20 11:56 | 0.1967 | 0.0011324 | 73 | 12680 | Planned | Planned Interruption | 11kV WIRE AND HARDWARE REPLACEMENTS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 815 | O-5647-B | Kaiwaka Town | Kaiwaka CB1062 | 2025-02-20 09:25 | 2025-02-20 11:33 | 0.081409 | 0.00063601 | 41 | 5248 | Planned | Planned Interruption | Tree clearing work | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 816 | O-5683-B | Hakaru | Kaiwaka CB1032 | 2025-02-20 10:31 | 2025-02-20 13:17 | 0.046351 | 0.00027922 | 18 | 2988 | Planned | Planned Interruption | Replace HV crossarm at pole 47057 and DOFs MC352 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 817 | O-5473-B | Puwera | Maungatapere CB7 | 2025-02-21 09:09 | 2025-02-21 12:57 | 0.39966 | 0.0017529 | 113 | 25764 | Planned | Planned Interruption | Crossarm and hardware replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 818 | O-5488-B | Puwera | Maungatapere CB7 | 2025-02-21 09:09 | 2025-02-21 12:36 | 0.057799 | 0.00027922 | 18 | 3726 | Planned | Planned Interruption | Replace crossarms and hardware | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 819 | O-5851-B | Turiwiri | Dargaville CB9 | 2025-02-21 10:06 | 2025-02-21 10:20 | 0.0008687 | 6.205e-05 | 4 | 56 | Planned | Planned Interruption | Remove reclosing links 3112 & replace with solid links. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 820 | O-5575-B | Norfolk St | Alexander St CB1 | 2025-02-23 07:14 | 2025-02-23 17:24 | 0 | 0 | 0 | 0 | Planned | Planned Interruption | Remove old Transformer WC210 and replace with new Transformer WC210. Liven new Transformer via SW 227 on new siemens switch. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 821 | O-5380-B | Taipuha | Mareretu CB1 | 2025-02-24 09:03 | 2025-02-24 12:28 | 0.1431 | 0.00069806 | 45 | 9225 | Planned | Planned Interruption | Replace poles, cross arms, remove 5 span LV and replace LV conductor at 2 sites. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 822 | F-151-B | Kaiatea | Ngunguru CB1072 | 2025-02-24 16:04 | 2025-02-24 17:12 | 0.45217 | 0.01061 | 684 | 29149 | Unplanned | Adverse Environment | 390579/ Scrub Fire Kakariki road - Feeder dropped for safety, monitored 11kV & 33kV lines. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 823 | F-8890-A | Titoki | Poroti CB1032 | 2025-02-25 04:35 | 2025-02-25 10:39 | 0.62925 | 0.0062825 | 405 | 40564 | Unplanned | Third Party Interference | FP390585 Tripped E/F, 1x HV line down @ pole 50521 (reports of a high load going through this area at time of fault) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 824 | F-8893-A | Te Kopuru | Dargaville CB2 | 2025-02-25 08:21 | 2025-02-25 09:16 | 0.41668 | 0.0075235 | 485 | 26861 | Unplanned | Third Party Interference | 390590/ Truck reported hitting LV pole - LVLines down road crossing. Dropped HV Feeder for safety until confirmed safe to liven | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 825 | O-5530-B | Montgomery Ave | Onerahi CB8 | 2025-02-25 09:02 | 2025-02-25 12:38 | 0.24435 | 0.0011324 | 73 | 15752 | Planned | Planned Interruption | V POLE & HARDWARE REPLACEMENTS. REMOVE HV LINKS 9378 AND HARD TAP SPUR LINE TO OP300 BACK TO MAIN LINE | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 826 | O-5383-B | Mata | Ruakaka CB3 | 2025-02-25 09:06 | 2025-02-25 12:33 | 0.054588 | 0.00026371 | 17 | 3519 | Planned | Planned Interruption | HV POLE REPLACEMENTS pole 12511 to EOL | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 827 | O-5572-B | Kaiwaka Town | Kaiwaka CB1062 | 2025-02-25 09:07 | 2025-02-25 14:13 | 0.16614 | 0.00054293 | 35 | 10710 | Planned | Planned Interruption | replace pole hardware and TX like for like | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 828 | F-8896-A | Maungatapere - Dairy Factory | Maungatapere CB6 | 2025-02-25 14:51 | 2025-02-25 15:36 | 0.13299 | 0.0029784 | 192 | 8573 | Unplanned | Third Party Interference | 390614/ Car v Pole causing ABC conductor LV lines down road crossing (near tx O133. Isolated HV for safety. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 829 | O-5527-B | Matapouri | Ngunguru CB1032 | 2025-02-27 09:01 | 2025-02-27 13:03 | 0.007508 | 3.1025e-05 | 2 | 484 | Planned | Planned Interruption | Replace HV arm at pole 58907/58908 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 830 | O-5533-B | Montgomery Ave | Onerahi CB8 | 2025-02-27 09:02 | 2025-02-27 12:37 | 0.24257 | 0.0011324 | 73 | 15637 | Planned | Planned Interruption | HV CONDUCTOR REPLACEMENT | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 831 | O-5854-B | Pataua | Parua Bay CB1 | 2025-02-27 09:08 | 2025-02-27 14:02 | 0.37853 | 0.0012875 | 83 | 24402 | Planned | Planned Interruption | Pole replacement & Tx upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 832 | F-8899-A | Titoki | Poroti CB1032 | 2025-02-27 17:39 | 2025-02-27 19:57 | 0.019266 | 0.00013961 | 9 | 1242 | Unplanned | Vegetation | 390680/Pine trees fallen & leaning over lines. Dropped lines to clear trees & reinstate power | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 833 | O-5716-B | Coast | Dargaville CB6 | 2025-02-28 09:02 | 2025-02-28 14:54 | 0.27302 | 0.00077562 | 50 | 17600 | Planned | Planned Interruption | Replacing 11kv 400v Poles & Cross arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 834 | F-8905-A | Swamp North | Hikurangi CB1042 | 2025-03-01 20:48 | 2025-03-02 02:29 | 0.41177 | 0.019718 | 1271 | 26542 | Unplanned | Wildlife | 390713 ADMS constantly locking up Two lines down between poles 38815 & 38816 2 x dead ducks | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 835 | O-5806-B | Mains Ave | Tikipunga CB2 | 2025-03-02 09:07 | 2025-03-02 10:15 | 0.19082 | 0.0027925 | 180 | 12300 | Planned | Planned Interruption | Network Maintenance. Removing KL-7159 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 836 | O-5731-B | Cairnfield Rd | Tikipunga CB5 | 2025-03-02 11:45 | 2025-03-02 12:31 | 0.1498 | 0.0032424 | 209 | 9656 | Planned | Planned Interruption | Remove KL 7143 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 837 | O-5803-B | Whau Valley | Tikipunga CB1 | 2025-03-02 14:01 | 2025-03-02 15:12 | 0.26772 | 0.0037698 | 243 | 17257 | Planned | Planned Interruption | Remove links 7130KL from the network | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 838 | O-5824-B | Kaiwaka Town | Kaiwaka CB1062 | 2025-03-03 09:01 | 2025-03-03 11:34 | 0.10444 | 0.0006826 | 44 | 6732 | Planned | Planned Interruption | Network Maintenance - rectify high partial discharge at C350 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 840 | F-8914-A | Paparoa | Mareretu CB6 | 2025-03-04 01:19 | 2025-03-04 04:15 | 0.63288 | 0.010999 | 709 | 40795 | Unplanned | Third Party Interference | 390747 / Car Vs Pole 31157 Paparoa. Isolate, Cut Temp break and replace pole. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 841 | O-5743-B | Austin Road | Maunu CB1072 | 2025-03-05 08:33 | 2025-03-05 16:35 | 0.39147 | 0.00082223 | 53 | 25234 | Planned | Planned Interruption | RMU replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 843 | F-8929-A | Waipu | Ruakaka CB2 | 2025-03-05 15:45 | 2025-03-05 16:51 | 0.28376 | 0.0042973 | 277 | 18291 | Unplanned | Defective Equipment | 390807 Broken HV insulator at pole 10246 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 844 | O-5491-B | Swamp North | Hikurangi CB1042 | 2025-03-06 09:04 | 2025-03-06 14:44 | 0.40087 | 0.001179 | 76 | 25840 | Planned | Planned Interruption | Replace 11kV/400v poles, crossarms and hardware Installing Temp Switches 38436 and 38427 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 845 | F-8947-A | Coast | Dargaville CB6 | 2025-03-07 07:39 | 2025-03-07 08:17 | 0.36153 | 0.016274 | 1049 | 23304 | Unplanned | Wildlife | 390851/ Station Rd Darg.Trip OC Phase ABC. Dead Bird | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 847 | O-5911-B | Ararua | Mareretu CB2 | 2025-03-07 09:09 | 2025-03-07 14:41 | 0.12876 | 0.00038784 | 25 | 8300 | Planned | Planned Interruption | Replace pole, HV & LV crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 848 | F-8944-A | Kiripaka Rd | Tikipunga CB8 | 2025-03-07 11:52 | 2025-03-07 12:37 | 0.00069812 | 1.5514e-05 | 1 | 45 | Unplanned | Defective Equipment | 390862 To isolate last fuse to CP 17 - Dion to arrange removeal of CBP 17 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 849 | F-8962-A | Access Rd | Ruawai CB1022 | 2025-03-08 17:05 | 2025-03-08 17:20 | 0.034611 | 0.0052126 | 336 | 2231 | Unplanned | Unknown | 1 Min Close up to Sw 2235 due to FPIs. 15 Min close on Sw 2235 & BTN | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 850 | F-8965-A | King Road | Mangawhai North CB2 | 2025-03-08 18:55 | 2025-03-08 19:44 | 0.17597 | 0.0036147 | 233 | 11343 | Unplanned | Defective Equipment | 390886 Jumper off the top of the HV fuses MC327 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 851 | F-8971-A | North Kaiwaka | Kaiwaka CB1022 | 2025-03-09 01:37 | 2025-03-09 01:52 | 0.052436 | 0.0033975 | 219 | 3380 | Unplanned | Unknown | A & B phase OC- unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 852 | O-5809-B | Tikipunga Hill | Tikipunga CB4 | 2025-03-09 09:03 | 2025-03-09 09:34 | 0.24296 | 0.0076483 | 493 | 15661 | Planned | Planned Interruption | Remove links 6968 from the network | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 853 | O-5800-B | Charles St | Kamo CB2 | 2025-03-09 11:31 | 2025-03-09 12:44 | 0.17202 | 0.0023426 | 151 | 11088 | Planned | Planned Interruption | Removing KL7429. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 854 | O-5869-B | Ararua | Mareretu CB2 | 2025-03-11 09:07 | 2025-03-11 14:51 | 0.90838 | 0.0026528 | 171 | 58553 | Planned | Planned Interruption | Tree clearing work on double circuit | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 855 | O-5494-B | Swamp North | Hikurangi CB1042 | 2025-03-11 09:11 | 2025-03-11 14:13 | 0.042166 | 0.00013962 | 9 | 2718 | Planned | Planned Interruption | Replacing 11kv 400v poles cross arms & conductor. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 856 | O-5746-B | Town Dargaville | Dargaville CB3 | 2025-03-11 09:23 | 2025-03-11 11:36 | 0.19602 | 0.0014738 | 95 | 12635 | Planned | Planned Interruption | Repair oil leak in tap changer | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 857 | O-5947-B | Ararua | Mareretu CB2 | 2025-03-11 09:26 | 2025-03-11 14:23 | 0.15205 | 0.00051195 | 33 | 9801 | Planned | Planned Interruption | replace pole and pole hardware. Replace TX E407 like for like | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 858 | O-5749-B | Town Dargaville | Dargaville CB3 | 2025-03-11 13:12 | 2025-03-11 15:42 | 0.0023271 | 1.5514e-05 | 1 | 150 | Planned | Planned Interruption | Repair oil leak | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 859 | F-8980-A | Waipu | Ruakaka CB2 | 2025-03-11 20:35 | 2025-03-11 20:36 | 0.016941 | 0.015405 | 993 | 1092 | Unplanned | Wildlife | 390971 / Possum on Tx RR180 Causing Damage to DDOs & LA's | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 860 | F-154-B | Waipu | Ruakaka CB2 | 2025-03-11 20:43 | 2025-03-12 00:40 | 0.042771 | 0.00055849 | 36 | 2757 | Unplanned | Wildlife | 390971 / Shutdown to repair DDO jumpers & LA's at Tx RR180 that caused feeder fault due to Possum Ref: F-8980-A | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 861 | O-5932-B | Ararua | Mareretu CB2 | 2025-03-12 09:11 | 2025-03-12 14:39 | 0.040708 | 0.00012411 | 8 | 2624 | Planned | Planned Interruption | Replace pole, TX, HV & LV crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 862 | O-5632-B | ToeToe Rd | Kioreroa CB7 | 2025-03-12 09:29 | 2025-03-12 12:08 | 0.222 | 0.0013962 | 90 | 14310 | Planned | Planned Interruption | Network Maintenance replace HV arms and replace TX as per network maintenance pack | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 863 | F-8986-A | Access Rd | Ruawai CB1022 | 2025-03-13 06:23 | 2025-03-13 06:24 | 0.005647 | 0.0052126 | 336 | 364 | Unplanned | Unknown | O/C A&B phase, closed in 1min F5, unknown (FPI did not activate at Sw 2235) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 864 | O-5497-B | Swamp North | Hikurangi CB1042 | 2025-03-13 09:01 | 2025-03-13 13:45 | 0.17183 | 0.00060504 | 39 | 11076 | Planned | Planned Interruption | Replacing 11kv 400v Poles & Cross arms. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 865 | F-8992-A | Wharekohe | Poroti CB1062 | 2025-03-14 01:22 | 2025-03-14 01:23 | 0.001179 | 0.001148 | 74 | 76 | Unplanned | Unknown | Tripped O/C AB&C phase, closed in 1min F5, Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 866 | O-5953-B | Tangaihi | Ruawai CB1032 | 2025-03-14 09:05 | 2025-03-14 13:26 | 0.38871 | 0.0014893 | 96 | 25056 | Planned | Planned Interruption | Network Maintenance replacing multiple cross arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 867 | O-5872-B | North River | Ruakaka CB7 | 2025-03-14 09:09 | 2025-03-14 12:09 | 0.027925 | 0.00015514 | 10 | 1800 | Planned | Planned Interruption | TX RB192 & fuses RB335 upgrade | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 868 | F-8995-A | Tamaterau | Onerahi CB7 | 2025-03-14 10:39 | 2025-03-14 12:52 | 0.00619 | 4.6541e-05 | 3 | 399 | Unplanned | Defective Equipment | FP 391024 - Replace crossarm and insulators @ Pole 51816 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 869 | F-9001-A | Whau Valley | Tikipunga CB1 | 2025-03-14 20:02 | 2025-03-15 02:59 | 0.87865 | 0.0055384 | 357 | 56637 | Unplanned | Third Party Interference | Truck & trailer damaged pole. Temp Break installed to replace. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 870 | F-9004-A | Mata | Ruakaka CB3 | 2025-03-15 00:05 | 2025-03-15 00:29 | 0.11609 | 0.0069657 | 449 | 7483 | Unplanned | Unknown | B ph fault - relivened | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 871 | O-5752-B | Awakino Point | Dargaville CB4 | 2025-03-16 09:50 | 2025-03-16 10:59 | 0.012845 | 0.00018616 | 12 | 828 | Planned | Planned Interruption | Level TX DA53. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 872 | O-5503-B | Swamp North | Hikurangi CB1042 | 2025-03-18 09:02 | 2025-03-18 14:14 | 0.049566 | 0.00018616 | 12 | 3195 | Planned | Planned Interruption | Replacing 11v 400v Cross arms & Conductor. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 873 | O-5938-B | Ruawai Town | Ruawai CB1072 | 2025-03-18 09:08 | 2025-03-18 14:45 | 0.12548 | 0.00037233 | 24 | 8088 | Planned | Planned Interruption | Install new TX F230 and hardware | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 874 | F-9022-A | Whatatiri | Maungatapere CB8 | 2025-03-19 07:00 | 2025-03-19 10:40 | 0.16814 | 0.0030252 | 195 | 10838 | Unplanned | Wildlife | FP 391145 - 1x HV line down due to bird strike | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 875 | O-5500-B | Swamp North | Hikurangi CB1042 | 2025-03-19 09:08 | 2025-03-19 14:28 | 0.19361 | 0.00060504 | 39 | 12480 | Planned | Planned Interruption | Replacing 11kv Conductor. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 876 | O-5875-B | Tangowahine | Dargaville CB8 | 2025-03-20 09:06 | 2025-03-20 12:54 | 0.12734 | 0.00055849 | 36 | 8208 | Planned | Planned Interruption | Replace HV and LV crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 877 | O-5944-B | Jordan Valley | Hikurangi CB1102 | 2025-03-20 09:13 | 2025-03-20 15:06 | 0.027304 | 7.7569e-05 | 5 | 1760 | Planned | Planned Interruption | Replace HV conductor and hardware | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 878 | O-5956-B | Hokianga Rd | Dargaville CB7 | 2025-03-20 10:40 | 2025-03-20 13:41 | 0.14602 | 0.00080671 | 52 | 9412 | Planned | Planned Interruption | Transformer maintenance | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 879 | O-15925-A | Parua Bay | Parua Bay CB2 | 2025-03-21 09:07 | 2025-03-21 12:54 | 0.23595 | 0.0010394 | 67 | 15209 | Planned | Planned Interruption | Tx upgrades | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 880 | O-6016-B | Coast | Dargaville CB6 | 2025-03-21 10:02 | 2025-03-21 15:17 | 0.2981 | 0.00094634 | 61 | 19215 | Planned | Planned Interruption | Clear trees around 11kv lines | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 881 | F-9028-A | Titoki | Poroti CB1032 | 2025-03-21 10:57 | 2025-03-21 11:13 | 0.041344 | 0.0047317 | 305 | 2665 | Unplanned | Unknown | Sw 8191 B&C phase indication. Relivened Recl 1520, closed Sw 8191 after 15 mins | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 882 | F-9031-A | Matapouri | Ngunguru CB1032 | 2025-03-21 17:47 | 2025-03-21 18:54 | 0.0062365 | 9.3082e-05 | 6 | 402 | Unplanned | Unknown | FP 391235 - Unknown cause, had to get 2nd man to deliver fuses. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 883 | F-9037-A | Titoki | Poroti CB1032 | 2025-03-22 17:10 | 2025-03-22 17:11 | 0.01238 | 0.011977 | 772 | 798 | Unplanned | Unknown | E/F No FPI's activated | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 884 | O-5893-B | Te Kopuru | Dargaville CB2 | 2025-03-23 09:01 | 2025-03-23 10:58 | 0.12709 | 0.001086 | 70 | 8192 | Planned | Planned Interruption | Remove 3134KL from network | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 885 | O-5587-B | Tangowahine | Dargaville CB8 | 2025-03-24 09:06 | 2025-03-24 15:57 | 0.063761 | 0.00015514 | 10 | 4110 | Planned | Planned Interruption | Replace crossarms. Went over time by 57 mins due to work load. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 886 | O-5590-B | Titoki | Poroti CB1032 | 2025-03-25 09:03 | 2025-03-25 15:03 | 0.055849 | 0.00015514 | 10 | 3600 | Planned | Planned Interruption | Replace crossarms and poles | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 887 | O-6100-B | Hakaru | Kaiwaka CB1032 | 2025-03-25 09:23 | 2025-03-25 15:33 | 0.27599 | 0.00074466 | 48 | 17790 | Planned | Planned Interruption | Network Maintenance - Replace poles & various 11kV works | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 888 | O-5596-B | Titoki | Poroti CB1032 | 2025-03-26 09:05 | 2025-03-26 13:55 | 0.15297 | 0.00052747 | 34 | 9860 | Planned | Planned Interruption | Pole and crossarm replacement | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 889 | F-9046-A | Tikipunga Hill | Tikipunga CB4 | 2025-03-26 21:16 | 2025-03-26 21:36 | 0.14795 | 0.0072294 | 466 | 9537 | Unplanned | Unknown | Trip A Phase. attempted 15 minute close but timed out causing slight delay to re closing. Closed & BTN. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 890 | F-9052-A | Coast | Dargaville CB6 | 2025-03-27 07:58 | 2025-03-27 11:18 | 0.14645 | 0.0013497 | 87 | 9440 | Unplanned | Defective Equipment | FP391328 Replace faulty HV DDO's at Tx L159, damage from burning HV barrel | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 891 | O-6163-B | Maunu | Maunu CB1032 | 2025-03-27 09:02 | 2025-03-27 14:43 | 0.59231 | 0.0017841 | 115 | 38180 | Planned | Planned Interruption | Connect new cable up pole onto new fuses 10016 to live new TX S140 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 892 | O-5593-B | Whakapara | Hikurangi CB1112 | 2025-03-27 09:03 | 2025-03-27 13:09 | 0.12594 | 0.00051195 | 33 | 8118 | Planned | Planned Interruption | Replace HV crossarms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 893 | O-6115-B | Taipuha | Mareretu CB1 | 2025-03-27 09:31 | 2025-03-27 13:26 | 0.047394 | 0.00020168 | 13 | 3055 | Planned | Planned Interruption | At Pole 33636, connect new DOFs & liven new 50kVA Dsub B265 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 894 | O-6043-B | Kaka St | Whangarei South CB1032 | 2025-03-27 23:19 | 2025-03-28 03:41 | 0.024388 | 9.3082e-05 | 6 | 1572 | Planned | Planned Interruption | Repair oil leak | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 895 | F-9055-A | Access Rd | Ruawai CB1022 | 2025-03-28 08:08 | 2025-03-28 08:24 | 0.024062 | 0.0051971 | 335 | 1551 | Unplanned | Unknown | Trip OC Phase AC. FPI's Sw 2156 Phase AC. Unknown | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 896 | O-6199-B | Bickerstaff | Maungaturoto CB2 | 2025-03-28 09:09 | 2025-03-28 12:35 | 0.067112 | 0.00032579 | 21 | 4326 | Planned | Planned Interruption | Install TX D451 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 897 | O-6304-B | Tangaihi | Ruawai CB1032 | 2025-03-28 09:10 | 2025-03-28 13:35 | 0.0082223 | 3.1027e-05 | 2 | 530 | Planned | Planned Interruption | Network Maintenance replace poles and cross arms | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 898 | F-9058-A | Kaiwaka South | Kaiwaka CB1072 | 2025-03-28 10:22 | 2025-03-28 11:27 | 0.10009 | 0.0015359 | 99 | 6452 | Unplanned | Defective Equipment | FP391357 Blown jumper at pole 33872 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 899 | O-6442-B | Fert. Works | Kioreroa CB6 | 2025-03-30 08:08 | 2025-03-30 12:01 | 0.0072294 | 3.1027e-05 | 2 | 466 | Planned | Planned Interruption | Repair oil leaks | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 900 | F-9073-A | Otonga | Hikurangi CB1032 | 2025-03-31 10:28 | 2025-03-31 11:32 | 0.26113 | 0.0040801 | 263 | 16832 | Unplanned | Vegetation | FP391402 Trees in line | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Northpower | 2025 |  | 901 | F-9085-A | Tangaihi | Ruawai CB1032 | 2025-03-31 14:13 | 2025-03-31 15:01 | 0.002234 | 4.6541e-05 | 3 | 144 | Unplanned | Defective Equipment | FP 391423 - Guy wire broken, sitting near HV bushing @ tx K267. 1x HV Fuse blown @ 3311. | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 9 | INCD-60489-K | McDrurys Rd | Prebbleton Unit 113 | 2024-04-02 08:30 | 2024-04-02 10:40 | 0.0039973 | 3.0748e-05 | 7 | 910 | Planned | Planned interruption | (Fuse Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 10 | INCD-60582-K | Aylesbury Rd | Highfield Unit 111 | 2024-04-02 09:34 | 2024-04-02 13:44 | 0.0010981 | 4.3926e-06 | 1 | 250 | Unplanned | Lightning | Lightning Strike - Aylesbury Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 11 | INCD-60486-K | Holmes Rd | Prebbleton Unit 113 | 2024-04-02 12:40 | 2024-04-02 14:58 | 0.00060618 | 4.3926e-06 | 1 | 138 | Planned | Planned interruption | (Fuse Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 12 | INCD-59820-K | Quaifes Rd | Halswell Unit 1 | 2024-04-03 08:45 | 2024-04-03 16:58 | 0.006501 | 1.3178e-05 | 3 | 1480 | Planned | Planned interruption | (Subdiv) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 13 | INCD-59820-K | Quaifes Rd | Halswell Unit 1 | 2024-04-03 08:34 | 2024-04-03 16:58 | 0.026558 | 5.2711e-05 | 12 | 6046 | Planned | Planned interruption | (Subdiv) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 14 | INCD-8144-M | Birmingham Dr | Addington Unit 16 | 2024-04-03 08:45 | 2024-04-03 18:46 | 0.0052799 | 8.7852e-06 | 2 | 1202 | Planned | Planned interruption | (Tx Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 15 | INCD-60612-K | Dyers Pass Rd | Halswell Unit 162 | 2024-04-03 10:13 | 2024-04-03 10:19 | 0.22876 | 0.038233 | 8704 | 52079 | Unplanned | Third party interference | Tree v Line - Contractor - Dyers Pass Rd - LOS Heathcote ZS, Barnett Park ZS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 16 | INCD-60612-K | Dyers Pass Rd | Halswell Unit 162 | 2024-04-03 10:13 | 2024-04-03 10:20 | 0.10672 | 0.015466 | 3521 | 24295 | Unplanned | Third party interference | Tree v Line - Contractor - Dyers Pass Rd - LOS Heathcote ZS, Barnett Park ZS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 17 | INCD-60615-K | Wrights Rd | Greendale Unit 111 | 2024-04-03 10:32 | 2024-04-03 13:51 | 0.00087413 | 4.3926e-06 | 1 | 199 | Unplanned | Other cause | LV Fault - Fuse OH - Wrights Rd - 11kV Isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 18 | INCD-60636-K | Bangor Rd | Kimberley Unit 124 | 2024-04-03 14:29 | 2024-04-03 14:54 | 0.0092508 | 0.00036898 | 84 | 2106 | Unplanned | Third party interference | Car v Pole - Bangor Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 19 | INCD-60636-K | Bangor Rd | Kimberley Unit 124 | 2024-04-03 14:29 | 2024-04-03 14:54 | 0.0048977 | 0.00019327 | 44 | 1115 | Unplanned | Third party interference | Car v Pole - Bangor Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 20 | INCD-60636-K | Bangor Rd | Kimberley Unit 124 | 2024-04-03 14:29 | 2024-04-03 19:00 | 0.014311 | 5.2711e-05 | 12 | 3258 | Unplanned | Third party interference | Car v Pole - Bangor Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 21 | INCD-59856-K | Tancreds Rd | Lincoln Unit 122 | 2024-04-04 09:00 | 2024-04-04 13:51 | 0.038295 | 0.00013178 | 30 | 8718 | Planned | Planned interruption | (Tx New) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 22 | INCD-60654-K | Weedons Ross Rd | Weedons Unit 124 | 2024-04-04 10:19 | 2024-04-04 10:22 | 0.00031627 | 9.2244e-05 | 21 | 72 | Unplanned | Human error | Incorrect Mapping - Weedons Ross Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 23 | INCD-60654-K | Weedons Ross Rd | Weedons Unit 124 | 2024-04-04 10:19 | 2024-04-04 10:24 | 0.0049505 | 0.00091366 | 208 | 1127 | Unplanned | Human error | Incorrect Mapping - Weedons Ross Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 24 | INCD-60654-K | Weedons Ross Rd | Weedons Unit 124 | 2024-04-04 10:19 | 2024-04-04 10:50 | 0.12539 | 0.004006 | 912 | 28546 | Unplanned | Human error | Incorrect Mapping - Weedons Ross Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 25 | INCD-60654-K | Weedons Ross Rd | Weedons Unit 124 | 2024-04-04 10:19 | 2024-04-04 11:03 | 0.0043223 | 9.6637e-05 | 22 | 984 | Unplanned | Human error | Incorrect Mapping - Weedons Ross Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 26 | INCD-60666-K | Christchurch Akaroa Rd | Motukarara Unit 111 | 2024-04-04 16:45 | 2024-04-04 21:40 | 0.011654 | 3.9533e-05 | 9 | 2653 | Unplanned | Defective equipment | Insulator Fault - Christchurch Akaroa Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 27 | INCD-60666-K | Christchurch Akaroa Rd | Motukarara Unit 111 | 2024-04-04 16:45 | 2024-04-04 21:51 | 0.026878 | 8.7852e-05 | 20 | 6119 | Unplanned | Defective equipment | Insulator Fault - Christchurch Akaroa Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 28 | INCD-60666-K | Christchurch Akaroa Rd | Motukarara Unit 111 | 2024-04-04 16:45 | 2024-04-04 21:59 | 0.031719 | 0.00010103 | 23 | 7221 | Unplanned | Defective equipment | Insulator Fault - Christchurch Akaroa Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 29 | INCD-60666-K | Christchurch Akaroa Rd | Motukarara Unit 111 | 2024-04-04 16:45 | 2024-04-04 21:59 | 0.022064 | 7.0281e-05 | 16 | 5023 | Unplanned | Defective equipment | Insulator Fault - Christchurch Akaroa Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 30 | INCD-60666-K | Christchurch Akaroa Rd | Motukarara Unit 111 | 2024-04-04 16:45 | 2024-04-04 22:06 | 0.23394 | 0.00072917 | 166 | 53257 | Unplanned | Defective equipment | Insulator Fault - Christchurch Akaroa Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 31 | INCD-59898-K | Wairewa Pa Rd | Little River Unit 112 | 2024-04-05 09:01 | 2024-04-05 14:07 | 0.17213 | 0.00056225 | 128 | 39187 | Planned | Planned interruption | (Vegetation Management) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 32 | INCD-60690-K | Springs Rd | Lincoln Unit 113 | 2024-04-05 10:02 | 2024-04-05 15:25 | 0.0056752 | 1.757e-05 | 4 | 1292 | Unplanned | Third party interference | Vandalism - Earth Cable Stolen - Springs Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 33 | INCD-59931-K | Maces Rd | Portman Unit 17 | 2024-04-07 08:01 | 2024-04-07 15:30 | 0.017768 | 3.9533e-05 | 9 | 4045 | Planned | Planned interruption | (Kiosk Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 34 | INCD-21091-L | Main South Rd | Dunsandel Unit 121 | 2024-04-08 21:00 | 2024-04-08 22:19 | 0.0035097 | 4.3926e-05 | 10 | 799 | Unplanned | Third party interference | Car v Pole - Main South Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 35 | INCD-8159-M | Leadleys Rd | Prebbleton Unit 113 | 2024-04-10 08:30 | 2024-04-10 13:27 | 0.041747 | 0.00014056 | 32 | 9504 | Planned | Planned interruption | (PRP) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 36 | INCD-8159-M | Leadleys Rd | Prebbleton Unit 113 | 2024-04-10 08:30 | 2024-04-10 14:14 | 0.0015111 | 4.3926e-06 | 1 | 344 | Planned | Planned interruption | (PRP) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 37 | INCD-59955-K | Victoria Park Rd | Milton Unit 13 | 2024-04-10 09:09 | 2024-04-10 15:41 | 0.013784 | 3.5141e-05 | 8 | 3138 | Planned | Planned interruption | (Kiosk Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 38 | INCD-59955-K | Victoria Park Rd | Milton Unit 13 | 2024-04-10 09:09 | 2024-04-10 15:45 | 0.0017395 | 4.3926e-06 | 1 | 396 | Planned | Planned interruption | (Kiosk Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 39 | INCD-60162-K | Christchurch Akaroa Rd | Duvauchelle Unit 123 | 2024-04-10 09:40 | 2024-04-10 13:54 | 0.0011157 | 4.3926e-06 | 1 | 254 | Planned | Planned interruption | (Orange Tag) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 40 | INCD-21166-L | Whitecliffs Rd | Kimberley Unit 124 | 2024-04-10 12:36 | 2024-04-10 13:57 | 0.0003558 | 4.3926e-06 | 1 | 81 | Unplanned | Defective equipment | Tx Fault - Insulation - Whitecliffs Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 41 | INCD-60846-K | Milltown Rd | Hills Rd Unit 113 | 2024-04-11 05:05 | 2024-04-11 06:23 | 0.00034262 | 4.3926e-06 | 1 | 78 | Unplanned | Wildlife | Possum v Line - Milltown Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 42 | INCD-8156-M | Candys Rd | Halswell Unit 1 | 2024-04-11 08:34 | 2024-04-11 10:39 | 0.0082581 | 6.5889e-05 | 15 | 1880 | Planned | Planned interruption | (PRP) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 43 | INCD-8162-M | Leadleys Rd | Prebbleton Unit 113 | 2024-04-11 12:00 | 2024-04-11 13:48 | 0.025231 | 0.00023281 | 53 | 5744 | Planned | Planned interruption | (PRP) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 44 | INCD-60861-K | West Coast Rd | Annat Unit 111 | 2024-04-11 15:41 | 2024-04-11 17:52 | 0.0057543 | 4.3926e-05 | 10 | 1310 | Unplanned | Defective equipment | Conductor off Ins - Binder - West Coast Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 45 | INCD-60861-K | West Coast Rd | Annat Unit 111 | 2024-04-11 15:41 | 2024-04-11 17:57 | 0.0011904 | 8.7852e-06 | 2 | 271 | Unplanned | Defective equipment | Conductor off Ins - Binder - West Coast Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 46 | INCD-60861-K | West Coast Rd | Annat Unit 111 | 2024-04-11 15:41 | 2024-04-11 18:36 | 0.001533 | 8.7852e-06 | 2 | 349 | Unplanned | Defective equipment | Conductor off Ins - Binder - West Coast Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 47 | INCD-60861-K | West Coast Rd | Annat Unit 111 | 2024-04-11 15:41 | 2024-04-11 18:58 | 0.0043267 | 2.1963e-05 | 5 | 985 | Unplanned | Defective equipment | Conductor off Ins - Binder - West Coast Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 48 | INCD-60861-K | West Coast Rd | Annat Unit 111 | 2024-04-11 15:41 | 2024-04-11 22:17 | 0.0069447 | 1.757e-05 | 4 | 1581 | Unplanned | Defective equipment | Conductor off Ins - Binder - West Coast Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 49 | INCD-60867-K | West Coast Rd | Annat Unit 111 | 2024-04-11 18:47 | 2024-04-11 18:50 | 0.0031539 | 0.0013134 | 299 | 718 | Unplanned | Unknown | Conductor off Ins - Binder - West Coast Rd - Tripped During Switching | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 50 | INCD-21259-L | Springston Rolleston Rd | Springston Unit 112 | 2024-04-11 20:53 | 2024-04-12 01:41 | 0.07221 | 0.00025038 | 57 | 16439 | Unplanned | Third party interference | Car v Pole - Springston Rolleston Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 51 | INCD-60876-K | McCormacks Bay Rd | Heathcote Unit 12 | 2024-04-11 23:40 | 2024-04-12 00:20 | 0.019595 | 0.00049197 | 112 | 4461 | Unplanned | Defective equipment | HV Cable Fault - Joint - McCormacks Bay Rd - CD_2203 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 52 | INCD-60876-K | McCormacks Bay Rd | Heathcote Unit 12 | 2024-04-11 23:40 | 2024-04-12 00:42 | 0.016942 | 0.00027234 | 62 | 3857 | Unplanned | Defective equipment | HV Cable Fault - Joint - McCormacks Bay Rd - CD_2203 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 53 | INCD-60192-K | Pawsons Valley Rd | Duvauchelle Unit 121 | 2024-04-12 09:32 | 2024-04-12 12:36 | 0.13774 | 0.00074674 | 170 | 31357 | Planned | Planned interruption | (Vegetation Management) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 54 | INCD-60192-K | Pawsons Valley Rd | Duvauchelle Unit 121 | 2024-04-12 09:31 | 2024-04-12 12:37 | 0.11809 | 0.00063253 | 144 | 26883 | Planned | Planned interruption | (Vegetation Management) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 55 | INCD-60903-K | Newtons Rd | Weedons Unit 113 | 2024-04-13 10:07 | 2024-04-13 11:54 | 0.020184 | 0.00018888 | 43 | 4595 | Unplanned | Third party interference | Contact v Pole - Newtons Rd - Suspect Vehicle | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 56 | INCD-60927-K | Takamatua Bay Rd | Duvauchelle Unit 123 | 2024-04-13 19:30 | 2024-04-16 11:48 | 0.64393 | 0.00016692 | 38 | 146595 | Unplanned | Other cause | LV Fault - Tail off Stanger - Takamatua Bay Rd - 11kV Isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 57 | INCD-60423-K | Curletts Rd | Middleton Unit 4 | 2024-04-15 10:05 | 2024-04-17 15:17 | 0.014021 | 4.3926e-06 | 1 | 3192 | Planned | Planned interruption | (LV Alterations) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 58 | INCD-60963-K | Long Bay Rd | Duvauchelle Unit 123 | 2024-04-15 10:25 | 2024-04-15 13:18 | 0.00075992 | 4.3926e-06 | 1 | 173 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 59 | INCD-21424-L | Southbridge Dunsandel Rd | Brookside Unit 114 | 2024-04-16 17:31 | 2024-04-16 21:27 | 0.0062111 | 2.6356e-05 | 6 | 1414 | Unplanned | Third party interference | Vehicle v Pole - Southbridge Dunsandel Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 60 | INCD-61041-K | McArthurs Rd | Waimakariri Unit 1 | 2024-04-17 10:52 | 2024-04-17 11:00 | 3.5141e-05 | 4.3926e-06 | 1 | 8 | Unplanned | Human error | Incorrect Notification Planned - (Fuse Change) - McArthurs Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 61 | INCD-61050-K | Leadleys Rd | Prebbleton Unit 113 | 2024-04-17 12:35 | 2024-04-17 13:01 | 0.00011421 | 4.3926e-06 | 1 | 26 | Unplanned | Human error | Incorrect Notification Planned - (Fuse Change) - Leadleys Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 62 | INCD-61056-K | Glasseys Rd | Brookside Unit 114 | 2024-04-17 18:28 | 2024-04-17 21:53 | 0.0063034 | 3.0748e-05 | 7 | 1435 | Unplanned | Wildlife | Bird Strike - Magpie - Glasseys Rd - Grass Fire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 63 | INCD-61056-K | Glasseys Rd | Brookside Unit 114 | 2024-04-17 15:44 | 2024-04-17 22:28 | 0.014192 | 3.5141e-05 | 8 | 3231 | Unplanned | Wildlife | Bird Strike - Magpie - Glasseys Rd - Grass Fire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 64 | INCD-61056-K | Glasseys Rd | Brookside Unit 114 | 2024-04-17 15:44 | 2024-04-17 22:39 | 0.0091146 | 2.1963e-05 | 5 | 2075 | Unplanned | Wildlife | Bird Strike - Magpie - Glasseys Rd - Grass Fire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 65 | INCD-61056-K | Glasseys Rd | Brookside Unit 114 | 2024-04-17 15:44 | 2024-04-18 04:17 | 0.0099185 | 1.3178e-05 | 3 | 2258 | Unplanned | Wildlife | Bird Strike - Magpie - Glasseys Rd - Grass Fire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 66 | INCD-21463-L | West Coast Rd | Highfield Unit 114 | 2024-04-18 09:14 | 2024-04-18 10:08 | 0.0002372 | 4.3926e-06 | 1 | 54 | Unplanned | Defective equipment | Conductor Fault - Frayed - West Coast Rd - Suspect Vegetation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 67 | INCD-21502-L | Gebbies Pass Rd | Motukarara Unit 113 | 2024-04-18 17:56 | 2024-04-18 19:59 | 0.0075113 | 6.1496e-05 | 14 | 1710 | Unplanned | Defective equipment | Insulator Fault - Gebbies Pass Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 68 | INCD-61101-K | Dickies Rd | Brookside Unit 124 | 2024-04-18 19:04 | 2024-04-18 20:39 | 0.0012519 | 1.3178e-05 | 3 | 285 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 69 | INCD-8225-M | Cable St | Middleton Unit 4 | 2024-04-18 21:44 | 2024-04-19 00:43 | 0.016512 | 9.2244e-05 | 21 | 3759 | Planned | Planned interruption | (Kiosk New) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 70 | INCD-61107-K | Robinsons Rd | Lincoln Unit 122 | 2024-04-19 01:10 | 2024-04-19 03:24 | 0.003536 | 2.6356e-05 | 6 | 805 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 71 | INCD-61113-K | Hororata Rd | Hororata Unit 112 | 2024-04-19 07:42 | 2024-04-19 09:59 | 0.0012036 | 8.7852e-06 | 2 | 274 | Unplanned | Wildlife | Possum v Tx - Hororata Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 72 | INCD-21382-L | Long Bay Rd | Duvauchelle Unit 123 | 2024-04-19 09:39 | 2024-04-19 13:30 | 0.0010147 | 4.3926e-06 | 1 | 231 | Unplanned | Defective equipment | Tx Fault - Oil Leak - Long Bay Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 73 | INCD-21382-L | Long Bay Rd | Duvauchelle Unit 123 | 2024-04-19 09:39 | 2024-04-19 13:40 | 0.0010586 | 4.3926e-06 | 1 | 241 | Unplanned | Defective equipment | Tx Fault - Oil Leak - Long Bay Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 74 | INCD-8261-M | Ellesmere Junction Rd | Springston Unit 115 | 2024-04-20 05:08 | 2024-04-20 05:34 | 0.00022841 | 8.7852e-06 | 2 | 52 | Planned | Planned interruption | (Priv Network - Blackout Test) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 75 | INCD-21292-L | Detroit Dr | Weedons Unit 121 | 2024-04-20 07:03 | 2024-04-20 07:18 | 6.5889e-05 | 4.3926e-06 | 1 | 15 | Planned | Planned interruption | (Priv Network - Blackout Test) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 76 | INCD-21292-L | Detroit Dr | Weedons Unit 121 | 2024-04-20 07:19 | 2024-04-20 07:35 | 7.0281e-05 | 4.3926e-06 | 1 | 16 | Planned | Planned interruption | (Priv Network - Blackout Test) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 77 | INCD-60405-K | Runners Rd | Rolleston Unit 111 | 2024-04-20 08:15 | 2024-04-20 10:47 | 0.032663 | 0.00021524 | 49 | 7436 | Planned | Planned interruption | (Vegetation Management) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 78 | INCD-61143-K | Robinsons Rd | Prebbleton Unit 123 | 2024-04-20 17:17 | 2024-04-20 17:47 | 0.00013178 | 4.3926e-06 | 1 | 30 | Unplanned | Third party interference | Vandalism - Earth Cable Stolen - Robinsons Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 79 | INCD-61149-K | The Lake Rd | Brookside Unit 124 | 2024-04-20 19:49 | 2024-04-20 20:33 | 0.00038655 | 8.7852e-06 | 2 | 88 | Unplanned | Wildlife | Bird Strike - The Lake Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 80 | INCD-21592-L | The Lake Rd | Brookside Unit 124 | 2024-04-21 04:45 | 2024-04-21 05:40 | 0.001924 | 3.5141e-05 | 8 | 438 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 81 | INCD-60372-K | Menzies St | Barnett Park Unit 10 | 2024-04-22 07:33 | 2024-04-22 17:12 | 0.0025433 | 4.3926e-06 | 1 | 579 | Planned | Planned interruption | (Swgr Replacement) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 82 | INCD-8231-M | Dunns Crossing Rd | Rolleston Unit 111 | 2024-04-22 08:31 | 2024-04-22 11:48 | 0.025929 | 0.00013178 | 30 | 5903 | Planned | Planned interruption | (Reinforcement) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 83 | INCD-8231-M | Dunns Crossing Rd | Rolleston Unit 111 | 2024-04-22 08:31 | 2024-04-22 11:48 | 0.05272 | 0.00026795 | 61 | 12002 | Planned | Planned interruption | (Reinforcement) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 84 | INCD-8192-M | Christchurch Akaroa Rd | Prebbleton Unit 113 | 2024-04-22 09:02 | 2024-04-22 13:55 | 0.064453 | 0.00021963 | 50 | 14673 | Planned | Planned interruption | (Orange Tag) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 85 | INCD-61182-K | Kennedys Bush Rd | Halswell Unit 1 | 2024-04-22 11:57 | 2024-04-22 12:03 | 9.6637e-05 | 1.757e-05 | 4 | 22 | Unplanned | Defective equipment | Fuse OH Fault - Kennedys Bush Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 86 | INCD-8222-M | Ellesmere Rd | Lincoln Unit 122 | 2024-04-22 13:02 | 2024-04-22 14:26 | 0.035066 | 0.0004173 | 95 | 7983 | Planned | Planned interruption | (PRP) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 87 | INCD-21622-L | Kirk Rd | Moffett St Unit 115 | 2024-04-22 15:10 | 2024-04-22 15:14 | 1.757e-05 | 4.3926e-06 | 1 | 4 | Unplanned | Third party interference | Vandalism - Earth Cable Stolen - Kirk Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 88 | INCD-61206-K | Wroots Rd | Halswell Unit 1 | 2024-04-23 06:46 | 2024-04-23 08:10 | 0.0022095 | 2.6356e-05 | 6 | 503 | Unplanned | Wildlife | Bird Strike - Swan - Wroots Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 89 | INCD-61245-K | Johnstons Rd | Hills Rd Unit 114 | 2024-04-23 14:57 | 2024-04-23 15:49 | 0.00022841 | 4.3926e-06 | 1 | 52 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 90 | INCD-8240-M | Leadleys Rd | Prebbleton Unit 113 | 2024-04-24 07:35 | 2024-04-24 10:28 | 0.00075992 | 4.3926e-06 | 1 | 173 | Planned | Planned interruption | (PRP) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 91 | INCD-8240-M | Leadleys Rd | Prebbleton Unit 113 | 2024-04-24 07:35 | 2024-04-24 10:28 | 0.00075992 | 4.3926e-06 | 1 | 173 | Planned | Planned interruption | (PRP) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 92 | INCD-8243-M | Memorial Av | Ilam Unit 7 | 2024-04-24 08:38 | 2024-04-24 13:40 | 0.022552 | 7.4674e-05 | 17 | 5134 | Planned | Planned interruption | (HV Alterations) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 93 | INCD-8255-M | Pole Rd | Darfield Unit 115 | 2024-04-24 09:20 | 2024-04-24 15:04 | 0.0045332 | 1.3178e-05 | 3 | 1032 | Planned | Planned interruption | (LV Alterations) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 94 | INCD-61278-K | Goodericks Rd | Springston Unit 114 | 2024-04-25 05:13 | 2024-04-25 07:08 | 0.0020206 | 1.757e-05 | 4 | 460 | Unplanned | Vegetation | Tree v Line - Goodericks Rd - Orange Wind Warning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 95 | INCD-61293-K | Coleridge Intake Rd | Coleridge GXP Unit 1022 | 2024-04-25 12:10 | 2024-04-25 14:54 | 0.0014408 | 8.7852e-06 | 2 | 328 | Unplanned | Vegetation | Branch v Line - Coleridge Intake Rd - Orange Wind Warning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 96 | INCD-61299-K | Newtons Rd | Weedons Unit 112 | 2024-04-25 13:40 | 2024-04-25 14:44 | 0.00056225 | 8.7852e-06 | 2 | 128 | Unplanned | Vegetation | Branch v Line - Newtons Rd - Orange Wind Warning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 97 | INCD-61305-K | Maddisons Rd | Larcomb Unit 114 | 2024-04-25 13:44 | 2024-04-25 13:48 | 0.00058861 | 0.00016692 | 38 | 134 | Unplanned | Vegetation | Branch v Line - Maddisons Rd - Orange Wind Warning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 98 | INCD-61305-K | Maddisons Rd | Larcomb Unit 114 | 2024-04-25 13:44 | 2024-04-25 14:15 | 0.019626 | 0.00064132 | 146 | 4468 | Unplanned | Vegetation | Branch v Line - Maddisons Rd - Orange Wind Warning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 99 | INCD-61305-K | Maddisons Rd | Larcomb Unit 114 | 2024-04-25 13:44 | 2024-04-25 14:41 | 0.00050076 | 8.7852e-06 | 2 | 114 | Unplanned | Vegetation | Branch v Line - Maddisons Rd - Orange Wind Warning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 100 | INCD-61308-K | Coaltrack Rd | Kimberley Unit 124 | 2024-04-25 15:41 | 2024-04-25 16:43 | 0.057069 | 0.00092244 | 210 | 12992 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 101 | INCD-61308-K | Coaltrack Rd | Kimberley Unit 124 | 2024-04-25 15:41 | 2024-04-25 16:44 | 0.054679 | 0.00086973 | 198 | 12448 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 102 | INCD-61311-K | Point Rd | Hororata Unit 114 | 2024-04-25 18:19 | 2024-04-26 12:05 | 0.009365 | 8.7852e-06 | 2 | 2132 | Unplanned | Vegetation | Tree v Line - Point Rd - Orange Wind Warning | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 103 | INCD-61314-K | Downs Rd | Hororata Unit 112 | 2024-04-25 18:50 | 2024-04-25 19:01 | 0.0017131 | 0.00014935 | 34 | 390 | Unplanned | Defective equipment | Branch v Line - Downs Rd - LFI Fault - Switching Error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 104 | INCD-61326-K | Downs Rd | Hororata Unit 114 | 2024-04-25 18:50 | 2024-04-25 19:00 | 0.012572 | 0.0013617 | 310 | 2862 | Unplanned | Defective equipment | Branch v Line - Downs Rd - LFI Fault - Switching Error | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 105 | INCD-61329-K | Downs Rd | Hororata Unit 114 | 2024-04-25 18:50 | 2024-04-25 19:57 | 0.031991 | 0.00047879 | 109 | 7283 | Unplanned | Vegetation | Branch v Line - Downs Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 106 | INCD-61332-K | Kearneys Rd | Pages-Kearneys Unit 10 | 2024-04-26 03:29 | 2024-04-26 03:31 | 0.01895 | 0.0086139 | 1961 | 4314 | Unplanned | Defective equipment | HV Cable Fault - Run - Kearneys Rd - CD_1053 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 107 | INCD-61338-K | Bealey Rd | Highfield Unit 113 | 2024-04-26 10:11 | 2024-04-26 10:16 | 0.0024115 | 0.0005315 | 121 | 549 | Unplanned | Third party interference | Branch v Line - Contractor - Bealey Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 108 | INCD-61344-K | Old Tai Tapu Rd | Lincoln Unit 122 | 2024-04-26 11:15 | 2024-04-26 13:27 | 0.0017351 | 1.3178e-05 | 3 | 395 | Unplanned | Other cause | LV Fault - Cable Crutch - Old Tai Tapu Rd - 11kV Isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 109 | INCD-61365-K | Greenpark Rd | Springston Unit 114 | 2024-04-27 07:05 | 2024-04-27 10:31 | 0.0027102 | 1.3178e-05 | 3 | 617 | Unplanned | Wildlife | Bird Strike - Swan - Greenpark Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 110 | INCD-8249-M | Waterford Rd | Greendale Unit 112 | 2024-04-29 09:01 | 2024-04-29 14:57 | 0.0093914 | 2.6356e-05 | 6 | 2138 | Planned | Planned interruption | (Vegetation Management) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 111 | INCD-8270-M | Rakaia Terrace Rd | Te Pirita Unit 113 | 2024-04-29 11:41 | 2024-04-29 13:42 | 0.0005315 | 4.3926e-06 | 1 | 121 | Planned | Planned interruption | (Capacitors) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 112 | INCD-61443-K | Dickies Rd | Brookside Unit 124 | 2024-04-30 07:03 | 2024-04-30 07:47 | 0.00057982 | 1.3178e-05 | 3 | 132 | Unplanned | Wildlife | Bird Strike - Dickies Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 113 | INCD-61449-K | Lower Lake Rd | Hills Rd Unit 114 | 2024-04-30 10:01 | 2024-04-30 11:14 | 0.00032066 | 4.3926e-06 | 1 | 73 | Unplanned | Wildlife | Bird Strike - Goose - Lower Lake Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 114 | INCD-61485-K | Sleemans Rd | Hororata Unit 112 | 2024-04-30 21:12 | 2024-04-30 22:27 | 0.00065889 | 8.7852e-06 | 2 | 150 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 115 | INCD-61497-K | Lower Styx Rd | Belfast Unit 19 | 2024-04-30 22:22 | 2024-04-30 22:28 | 0.0018976 | 0.00028991 | 66 | 432 | Unplanned | Third party interference | Car v Pole - Lower Styx Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 116 | INCD-61497-K | Lower Styx Rd | Belfast Unit 19 | 2024-04-30 22:22 | 2024-04-30 23:13 | 0.0060222 | 0.0001186 | 27 | 1371 | Unplanned | Third party interference | Car v Pole - Lower Styx Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 117 | INCD-61497-K | Lower Styx Rd | Belfast Unit 19 | 2024-04-30 22:22 | 2024-04-30 23:26 | 0.064145 | 0.0010059 | 229 | 14603 | Unplanned | Third party interference | Car v Pole - Lower Styx Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 118 | INCD-61497-K | Lower Styx Rd | Belfast Unit 19 | 2024-04-30 22:22 | 2024-04-30 23:27 | 0.0051964 | 7.9067e-05 | 18 | 1183 | Unplanned | Third party interference | Car v Pole - Lower Styx Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 119 | INCD-61497-K | Lower Styx Rd | Belfast Unit 19 | 2024-04-30 22:22 | 2024-05-01 04:40 | 0.093044 | 0.00024599 | 56 | 21182 | Unplanned | Third party interference | Car v Pole - Lower Styx Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 120 | INCD-61509-K | Lower Styx Rd | Belfast Unit 10 | 2024-05-01 10:11 | 2024-05-01 10:19 | 0.00063253 | 7.9067e-05 | 18 | 144 | Unplanned | Third party interference | Car v Pole - Lower Styx Rd - Switching | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 121 | INCD-8300-M | Robinsons Rd | Prebbleton Unit 123 | 2024-05-02 08:31 | 2024-05-02 16:23 | 0.29461 | 0.00062375 | 142 | 67069 | Planned | Planned interruption | (Asset Relocation) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 122 | INCD-8300-M | Robinsons Rd | Prebbleton Unit 123 | 2024-05-02 08:31 | 2024-05-02 16:50 | 0.059164 | 0.0001186 | 27 | 13469 | Planned | Planned interruption | (Asset Relocation) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 123 | INCD-61569-K | Reynolds Av | Papanui Unit 24 | 2024-05-02 09:17 | 2024-05-02 09:43 | 0.080226 | 0.0031319 | 713 | 18264 | Unplanned | Defective equipment | HV Cable Fault - Run - Reynolds Av - CD_2439 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 124 | INCD-61569-K | Reynolds Av | Papanui Unit 24 | 2024-05-02 09:17 | 2024-05-02 09:51 | 0.014276 | 0.00042169 | 96 | 3250 | Unplanned | Defective equipment | HV Cable Fault - Run - Reynolds Av - CD_2439 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 125 | INCD-61569-K | Reynolds Av | Papanui Unit 24 | 2024-05-02 09:17 | 2024-05-02 10:01 | 0.013384 | 0.00030748 | 70 | 3047 | Unplanned | Defective equipment | HV Cable Fault - Run - Reynolds Av - CD_2439 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 126 | INCD-61524-K | Malvern Hills Rd | Annat Unit 113 | 2024-05-02 09:43 | 2024-05-02 13:04 | 0.0017658 | 8.7852e-06 | 2 | 402 | Unplanned | Defective equipment | Tx Fault - Insulation - Malvern Hills Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 127 | INCD-21274-L | Edward St | Lincoln Unit 123 | 2024-05-03 08:41 | 2024-05-03 16:46 | 0.0042608 | 8.7852e-06 | 2 | 970 | Planned | Planned interruption | (Subdiv) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 128 | INCD-22081-L | Weedons Rd | Springston Unit 113 | 2024-05-03 13:30 | 2024-05-03 15:07 | 0.00085216 | 8.7852e-06 | 2 | 194 | Unplanned | Defective equipment | Tx Fault - Oil Leak - Weedons Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 129 | INCD-61608-K | The Lake Rd | Brookside Unit 124 | 2024-05-03 16:17 | 2024-05-03 17:31 | 0.0006545 | 8.7852e-06 | 2 | 149 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 130 | INCD-22135-L | Major Hornbrook Rd | Heathcote Unit 27 | 2024-05-05 02:10 | 2024-05-05 04:01 | 0.0053194 | 4.8319e-05 | 11 | 1211 | Unplanned | Third party interference | Car v Pole - Major Hornbrook Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 131 | INCD-61692-K | Turnbulls Rd | Hororata Unit 112 | 2024-05-06 07:35 | 2024-05-06 08:26 | 0.0013353 | 2.6356e-05 | 6 | 304 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 132 | INCD-8303-M | Lambeth Cr | Papanui Unit 15 | 2024-05-06 08:32 | 2024-05-06 15:03 | 0.099549 | 0.00025477 | 58 | 22663 | Planned | Planned interruption | (LV Panel) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 133 | INCD-61080-K | Bells Rd | Weedons Unit 124 | 2024-05-06 09:39 | 2024-05-06 14:14 | 0.0036239 | 1.3178e-05 | 3 | 825 | Planned | Planned interruption | (Tx Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 134 | INCD-22162-L | Hodgens Rd | Shands Rd Unit 122 | 2024-05-06 13:23 | 2024-05-06 13:51 | 0.00012299 | 4.3926e-06 | 1 | 28 | Unplanned | Third party interference | Vandalism - Earth Cable Stolen - Hodgens Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 135 | INCD-22165-L | Hodgens Rd | Shands Rd Unit 122 | 2024-05-06 13:56 | 2024-05-06 14:12 | 0.00014056 | 8.7852e-06 | 2 | 32 | Unplanned | Third party interference | Vandalism - Earth Cable Stolen - Hodgens Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 136 | INCD-22219-L | Milnes Rd | Hororata Unit 112 | 2024-05-06 20:48 | 2024-05-06 20:57 | 3.9533e-05 | 4.3926e-06 | 1 | 9 | Unplanned | Third party interference | Vandalism - Earth Cable Stolen - Milnes Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 137 | INCD-22216-L | Cordys Rd | Hororata Unit 112 | 2024-05-06 21:13 | 2024-05-06 21:28 | 6.1496e-05 | 4.3926e-06 | 1 | 14 | Unplanned | Third party interference | Vandalism - Earth Cable Stolen - Cordys Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 138 | INCD-22213-L | Cordys Rd | Hororata Unit 112 | 2024-05-06 21:44 | 2024-05-06 21:54 | 8.7852e-05 | 8.7852e-06 | 2 | 20 | Unplanned | Third party interference | Vandalism - Earth Cable Stolen - Cordys Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 139 | INCD-60822-K | Springfield Rd | Annat Unit 112 | 2024-05-07 09:15 | 2024-05-07 14:43 | 0.010085 | 3.0748e-05 | 7 | 2296 | Planned | Planned interruption | (Tx Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 140 | INCD-8234-M | Craigieburn Station Rd | Castle Hill GXP Unit 642 | 2024-05-07 09:18 | 2024-05-07 15:06 | 0.0091717 | 2.6356e-05 | 6 | 2088 | Planned | Planned interruption | (Orange Tag) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 141 | INCD-22243-L | Leeston Dunsandel Rd | Brookside Unit 114 | 2024-05-07 14:04 | 2024-05-07 16:06 | 0.0080033 | 6.5889e-05 | 15 | 1822 | Unplanned | Defective equipment | Insulator Fault - Leeston Dunsandel Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 142 | INCD-61737-K | Prices Valley Rd | Motukarara Unit 111 | 2024-05-07 14:15 | 2024-05-07 15:51 | 0.0012563 | 1.3178e-05 | 3 | 286 | Unplanned | Wildlife | Bird Strike - Magpie - Prices Valley Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 143 | INCD-61731-K | Kowai Rd | Annat Unit 111 | 2024-05-07 14:28 | 2024-05-07 16:19 | 0.016578 | 0.00014935 | 34 | 3774 | Unplanned | Defective equipment | Tx Fault - Tap Changer - Kowai Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 144 | INCD-61749-K | Boundary Creek Rd | Brookside Unit 121 | 2024-05-08 04:52 | 2024-05-08 06:42 | 0.00096198 | 8.7852e-06 | 2 | 219 | Unplanned | Wildlife | Bird Strike - Boundary Creek Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 145 | INCD-60855-K | Springs Rd | Prebbleton Unit 123 | 2024-05-08 08:50 | 2024-05-08 12:07 | 0.00086534 | 4.3926e-06 | 1 | 197 | Planned | Planned interruption | (Fuse Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 146 | INCD-61755-K | Tai Tapu Rd | Lincoln Unit 123 | 2024-05-08 08:52 | 2024-05-08 10:37 | 0.020219 | 0.00019327 | 44 | 4603 | Unplanned | Third party interference | Truck v Pole - Tai Tapu Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 147 | INCD-61755-K | Tai Tapu Rd | Lincoln Unit 123 | 2024-05-08 08:52 | 2024-05-08 11:05 | 0.12217 | 0.00092244 | 210 | 27812 | Unplanned | Third party interference | Truck v Pole - Tai Tapu Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 148 | INCD-61755-K | Tai Tapu Rd | Lincoln Unit 123 | 2024-05-08 08:52 | 2024-05-08 15:10 | 0.04809 | 0.00012739 | 29 | 10948 | Unplanned | Third party interference | Truck v Pole - Tai Tapu Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 149 | INCD-61767-K | Wards Rd | Darfield Unit 112 | 2024-05-08 11:15 | 2024-05-08 11:57 | 0.00018449 | 4.3926e-06 | 1 | 42 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 150 | INCD-60852-K | Hamptons Rd | Prebbleton Unit 123 | 2024-05-08 12:06 | 2024-05-08 14:19 | 0.0011684 | 8.7852e-06 | 2 | 266 | Planned | Planned interruption | (Fuse Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 151 | INCD-8273-M | Goughs Rd | Duvauchelle Unit 123 | 2024-05-09 08:37 | 2024-05-09 11:08 | 0.0066328 | 4.3926e-05 | 10 | 1510 | Planned | Planned interruption | (Earths New) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 152 | INCD-61833-K | Englishs Rd | Springston Unit 114 | 2024-05-09 09:18 | 2024-05-09 15:14 | 0.0015594 | 4.3926e-06 | 1 | 355 | Unplanned | Defective equipment | Tail off SF - Englishs Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 153 | INCD-61854-K | Glandovey Rd | Fendalton Unit 12 | 2024-05-10 05:27 | 2024-05-10 07:37 | 0.021076 | 0.00016253 | 37 | 4798 | Unplanned | Human error | Construction Error - LV Panel Bolt - Glandovey Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 154 | INCD-61860-K | Waireka Rd | Darfield Unit 111 | 2024-05-10 08:06 | 2024-05-10 09:05 | 0.0018141 | 3.0748e-05 | 7 | 413 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 155 | INCD-8318-M | Selwyn Rd | Springston Unit 113 | 2024-05-10 08:47 | 2024-05-10 15:24 | 0.01045 | 2.6356e-05 | 6 | 2379 | Planned | Planned interruption | (Subdiv) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 156 | INCD-8318-M | Selwyn Rd | Springston Unit 113 | 2024-05-10 08:36 | 2024-05-10 15:31 | 0.0072829 | 1.757e-05 | 4 | 1658 | Planned | Planned interruption | (Subdiv) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 157 | INCD-61242-K | Port Hills Rd | Heathcote Unit 17 | 2024-05-10 12:15 | 2024-05-12 16:50 | 0.013859 | 4.3926e-06 | 1 | 3155 | Planned | Planned interruption | (LV Alterations) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 158 | INCD-22516-L | West Coast Rd | Castle Hill GXP Unit 642 | 2024-05-10 12:28 | 2024-05-10 13:49 | 0.0003558 | 4.3926e-06 | 1 | 81 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 159 | INCD-61890-K | The Lake Rd | Brookside Unit 124 | 2024-05-10 12:40 | 2024-05-10 13:30 | 0.00066328 | 1.3178e-05 | 3 | 151 | Unplanned | Wildlife | Bird Strike - The Lake Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 160 | INCD-8378-M | West Coast Rd | Darfield Unit 111 | 2024-05-11 09:03 | 2024-05-11 14:26 | 0.028407 | 8.7852e-05 | 20 | 6467 | Planned | Planned interruption | (Orange Tag) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 161 | INCD-8378-M | West Coast Rd | Darfield Unit 111 | 2024-05-11 08:41 | 2024-05-11 14:26 | 0.0015154 | 4.3926e-06 | 1 | 345 | Planned | Planned interruption | (Orange Tag) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 162 | INCD-8378-M | West Coast Rd | Darfield Unit 111 | 2024-05-11 08:41 | 2024-05-11 14:26 | 0.0015154 | 4.3926e-06 | 1 | 345 | Planned | Planned interruption | (Orange Tag) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 163 | INCD-8378-M | West Coast Rd | Darfield Unit 111 | 2024-05-11 08:41 | 2024-05-11 14:26 | 0.0075772 | 2.1963e-05 | 5 | 1725 | Planned | Planned interruption | (Orange Tag) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 164 | INCD-8336-M | Quadrant Dr | Shands Rd Unit 123 | 2024-05-11 14:49 | 2024-05-11 15:41 | 0.00022841 | 4.3926e-06 | 1 | 52 | Planned | Planned interruption | (LV Alterations) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 165 | INCD-61908-K | North Tr | Darfield Unit 111 | 2024-05-11 15:02 | 2024-05-11 15:07 | 0.00015374 | 3.0748e-05 | 7 | 35 | Unplanned | Other cause | LV Fault - Knife Switch - North Tr - 11kV Isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 166 | INCD-61950-K | Irwell Rakaia Rd | Killinchy Unit 112 | 2024-05-13 09:38 | 2024-05-13 10:35 | 0.003804 | 6.5889e-05 | 15 | 866 | Unplanned | Defective equipment | Insulator Fault - Irwell Rakaia Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 167 | INCD-61950-K | Irwell Rakaia Rd | Killinchy Unit 112 | 2024-05-13 09:38 | 2024-05-13 10:56 | 0.016925 | 0.00021524 | 49 | 3853 | Unplanned | Defective equipment | Insulator Fault - Irwell Rakaia Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 168 | INCD-61950-K | Irwell Rakaia Rd | Killinchy Unit 112 | 2024-05-13 09:38 | 2024-05-13 11:07 | 0.005482 | 6.1496e-05 | 14 | 1248 | Unplanned | Defective equipment | Insulator Fault - Irwell Rakaia Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 169 | INCD-61950-K | Irwell Rakaia Rd | Killinchy Unit 112 | 2024-05-13 09:38 | 2024-05-13 11:14 | 0.0088818 | 9.2244e-05 | 21 | 2022 | Unplanned | Defective equipment | Insulator Fault - Irwell Rakaia Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 170 | INCD-61950-K | Irwell Rakaia Rd | Killinchy Unit 112 | 2024-05-13 09:38 | 2024-05-13 11:21 | 0.0040763 | 3.9533e-05 | 9 | 928 | Unplanned | Defective equipment | Insulator Fault - Irwell Rakaia Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 171 | INCD-61950-K | Irwell Rakaia Rd | Killinchy Unit 112 | 2024-05-13 09:38 | 2024-05-13 11:55 | 0.012102 | 8.7852e-05 | 20 | 2755 | Unplanned | Defective equipment | Insulator Fault - Irwell Rakaia Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 172 | INCD-61950-K | Irwell Rakaia Rd | Killinchy Unit 112 | 2024-05-13 09:38 | 2024-05-13 12:19 | 0.017729 | 0.00010981 | 25 | 4036 | Unplanned | Defective equipment | Insulator Fault - Irwell Rakaia Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 173 | INCD-61950-K | Irwell Rakaia Rd | Killinchy Unit 112 | 2024-05-13 09:38 | 2024-05-13 14:51 | 0.026167 | 8.3459e-05 | 19 | 5957 | Unplanned | Defective equipment | Insulator Fault - Irwell Rakaia Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 174 | INCD-8276-M | Hunters Rd | Diamond Harbour Unit 111 | 2024-05-14 08:38 | 2024-05-14 12:32 | 0.23538 | 0.0010059 | 229 | 53586 | Planned | Planned interruption | (Defect Maint) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 175 | INCD-61410-K | Sharlands Rd | Te Pirita Unit 112 | 2024-05-14 09:37 | 2024-05-14 13:34 | 0.0062463 | 2.6356e-05 | 6 | 1422 | Planned | Planned interruption | (Tx New) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 176 | INCD-61410-K | Sharlands Rd | Te Pirita Unit 112 | 2024-05-14 09:31 | 2024-05-14 13:34 | 0.0010674 | 4.3926e-06 | 1 | 243 | Planned | Planned interruption | (Tx New) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 177 | INCD-22726-L | Weedons Ross Rd | Weedons Unit 124 | 2024-05-14 19:53 | 2024-05-14 20:11 | 0.00055347 | 3.0748e-05 | 7 | 126 | Unplanned | Third party interference | Vandalism - Earth Cable Stolen - Weedons Ross Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 178 | INCD-62007-K | Kimberley Zone Sub | Kimberley Unit 4902 | 2024-05-14 20:20 | 2024-05-14 20:26 | 0.010916 | 0.0021128 | 481 | 2485 | Unplanned | Human error | Accidental Tripping - T2 - Kimberley Zone Sub - LOS Kimberley ZS | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 179 | INCD-22729-L | Weedons Ross Rd | Weedons Unit 124 | 2024-05-14 20:45 | 2024-05-14 20:59 | 0.00012739 | 8.7852e-06 | 2 | 29 | Unplanned | Third party interference | Vandalism - Earth Cable Stolen - Weedons Ross Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 180 | INCD-8366-M | Silvester St | Portman Unit 1 | 2024-05-15 08:35 | 2024-05-15 15:21 | 0.0035668 | 8.7852e-06 | 2 | 812 | Planned | Planned interruption | (Kiosk New) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 181 | INCD-8339-M | Aylesbury Rd | Highfield Unit 111 | 2024-05-15 09:30 | 2024-05-15 15:40 | 0.0032505 | 8.7852e-06 | 2 | 740 | Planned | Planned interruption | (Vegetation Management) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 182 | INCD-62034-K | Trents Rd | Prebbleton Unit 111 | 2024-05-15 11:57 | 2024-05-15 12:56 | 0.0015374 | 2.6356e-05 | 6 | 350 | Unplanned | Defective equipment | Fuse OH Fault - Trents Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 183 | INCD-62043-K | Goodericks Rd | Springston Unit 111 | 2024-05-15 16:51 | 2024-05-15 23:48 | 0.0018317 | 4.3926e-06 | 1 | 417 | Unplanned | Defective equipment | Tx Fault - Insulation - Goodericks Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 184 | INCD-61224-K | Durey Rd | Waimakariri Unit 9 | 2024-05-16 01:38 | 2024-05-16 02:01 | 0.00020645 | 8.7852e-06 | 2 | 47 | Planned | Planned interruption | (Priv Network - Blackout Test) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 185 | INCD-8372-M | Springs Rd | Prebbleton Unit 111 | 2024-05-16 08:30 | 2024-05-16 13:19 | 0.011425 | 3.9533e-05 | 9 | 2601 | Planned | Planned interruption | (PRP) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 186 | INCD-8372-M | Springs Rd | Prebbleton Unit 111 | 2024-05-16 08:32 | 2024-05-16 13:20 | 0.1265 | 0.00043926 | 100 | 28799 | Planned | Planned interruption | (PRP) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 187 | INCD-61263-K | West Coast Rd | Darfield Unit 114 | 2024-05-16 08:32 | 2024-05-16 12:25 | 0.0081966 | 3.5141e-05 | 8 | 1866 | Planned | Planned interruption | (Demo) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 188 | INCD-61263-K | West Coast Rd | Darfield Unit 114 | 2024-05-16 08:32 | 2024-05-16 12:27 | 0.0020689 | 8.7852e-06 | 2 | 471 | Planned | Planned interruption | (Demo) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 189 | INCD-8369-M | Johns Rd | Waimakariri Unit 14 | 2024-05-16 09:01 | 2024-05-16 15:30 | 0.0068261 | 1.757e-05 | 4 | 1554 | Planned | Planned interruption | (Vegetation Management) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 190 | INCD-22777-L | Drain Rd | Brookside Unit 113 | 2024-05-16 12:35 | 2024-05-16 15:27 | 0.06653 | 0.00038655 | 88 | 15146 | Unplanned | Defective equipment | Tx Fault - Oil Leak - Drain Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 191 | INCD-22777-L | Drain Rd | Brookside Unit 113 | 2024-05-16 12:35 | 2024-05-16 15:27 | 0.0098262 | 5.7104e-05 | 13 | 2237 | Unplanned | Defective equipment | Tx Fault - Oil Leak - Drain Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 192 | INCD-22822-L | Norris St | Prebbleton Unit 112 | 2024-05-16 14:16 | 2024-05-16 15:49 | 0.019283 | 0.00020645 | 47 | 4390 | Unplanned | Defective equipment | Line Clash - Norris St | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 193 | INCD-62076-K | Wairiri Rd | Hororata Unit 112 | 2024-05-16 14:35 | 2024-05-16 15:18 | 0.00075113 | 1.757e-05 | 4 | 171 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 194 | INCD-8321-M | Keens Rd | Annat Unit 111 | 2024-05-17 06:31 | 2024-05-17 19:53 | 0.010577 | 1.3178e-05 | 3 | 2408 | Planned | Planned interruption | (Zone Maint) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 195 | INCD-62112-K | Milton Rd | Greendale Unit 113 | 2024-05-17 09:25 | 2024-05-17 14:31 | 0.013428 | 4.3926e-05 | 10 | 3057 | Unplanned | Third party interference | Tractor v Pole - Milton Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 196 | INCD-62139-K | River Rd | Lincoln Unit 123 | 2024-05-18 16:27 | 2024-05-18 20:49 | 0.089881 | 0.00034262 | 78 | 20462 | Unplanned | Third party interference | Tree v Line - Contractor - River Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 197 | INCD-62145-K | Kimberley Rd | Kimberley Unit 113 | 2024-05-18 18:46 | 2024-05-18 20:37 | 0.0072741 | 6.5889e-05 | 15 | 1656 | Unplanned | Third party interference | Car v Pole - Kimberley Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 198 | INCD-62160-K | Turners Rd | Belfast Unit 19 | 2024-05-19 01:44 | 2024-05-19 02:07 | 0.033985 | 0.0014496 | 330 | 7737 | Unplanned | Vegetation | Branch v Line - Turners Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 199 | INCD-62160-K | Turners Rd | Belfast Unit 19 | 2024-05-19 01:44 | 2024-05-19 02:33 | 0.013468 | 0.00027673 | 63 | 3066 | Unplanned | Vegetation | Branch v Line - Turners Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 200 | INCD-62160-K | Turners Rd | Belfast Unit 19 | 2024-05-19 01:44 | 2024-05-19 02:51 | 0.0008873 | 1.3178e-05 | 3 | 202 | Unplanned | Vegetation | Branch v Line - Turners Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 201 | INCD-62190-K | Dickies Rd | Brookside Unit 124 | 2024-05-20 04:39 | 2024-05-20 05:35 | 0.00073796 | 1.3178e-05 | 3 | 168 | Unplanned | Wildlife | Bird Strike - Dickies Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 202 | INCD-62223-K | Holmes Rd | Prebbleton Unit 113 | 2024-05-20 12:02 | 2024-05-20 12:40 | 0.00033384 | 8.7852e-06 | 2 | 76 | Unplanned | Third party interference | Vandalism - Earth Cable Stolen - Holmes Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 203 | INCD-62241-K | Hudsons Rd | Motukarara Unit 112 | 2024-05-21 05:29 | 2024-05-21 07:14 | 0.016169 | 0.00015374 | 35 | 3681 | Unplanned | Defective equipment | Insulator Fault - Hudsons Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 204 | INCD-62241-K | Hudsons Rd | Motukarara Unit 112 | 2024-05-21 05:29 | 2024-05-21 07:34 | 0.031934 | 0.00025477 | 58 | 7270 | Unplanned | Defective equipment | Insulator Fault - Hudsons Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 205 | INCD-62241-K | Hudsons Rd | Motukarara Unit 112 | 2024-05-21 05:29 | 2024-05-21 07:55 | 0.031952 | 0.00021963 | 50 | 7274 | Unplanned | Defective equipment | Insulator Fault - Hudsons Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 206 | INCD-62241-K | Hudsons Rd | Motukarara Unit 112 | 2024-05-21 05:29 | 2024-05-21 08:29 | 0.065625 | 0.00036459 | 83 | 14940 | Unplanned | Defective equipment | Insulator Fault - Hudsons Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 207 | INCD-62241-K | Hudsons Rd | Motukarara Unit 112 | 2024-05-21 05:29 | 2024-05-21 08:42 | 0.019464 | 0.00010103 | 23 | 4431 | Unplanned | Defective equipment | Insulator Fault - Hudsons Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 208 | INCD-62241-K | Hudsons Rd | Motukarara Unit 112 | 2024-05-21 08:52 | 2024-05-21 08:54 | 0.0018185 | 0.00099273 | 226 | 414 | Unplanned | Defective equipment | Insulator Fault - Hudsons Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 209 | INCD-62241-K | Hudsons Rd | Motukarara Unit 112 | 2024-05-21 05:29 | 2024-05-21 09:01 | 0.04737 | 0.00022402 | 51 | 10784 | Unplanned | Defective equipment | Insulator Fault - Hudsons Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 210 | INCD-62241-K | Hudsons Rd | Motukarara Unit 112 | 2024-05-21 09:27 | 2024-05-21 09:28 | 0.0014715 | 0.00099273 | 226 | 335 | Unplanned | Defective equipment | Insulator Fault - Hudsons Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 211 | INCD-62241-K | Hudsons Rd | Motukarara Unit 112 | 2024-05-21 08:52 | 2024-05-21 13:14 | 0.026426 | 0.00010103 | 23 | 6016 | Unplanned | Defective equipment | Insulator Fault - Hudsons Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 212 | INCD-8471-M | Ferrmead Park Dr | Heathcote Unit 14 | 2024-05-21 08:13 | 2024-05-21 10:01 | 0.0004744 | 4.3926e-06 | 1 | 108 | Planned | Planned interruption | (HV Alterations) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 213 | INCD-62244-K | Homebush Rd | Darfield Unit 114 | 2024-05-21 12:16 | 2024-05-21 12:39 | 0.0025038 | 0.00010981 | 25 | 570 | Unplanned | Vegetation | Branch v Line - Homebush Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 214 | INCD-61572-K | Corson Av | Milton Unit 25 | 2024-05-22 11:06 | 2024-05-22 11:33 | 0.0076783 | 0.00027673 | 63 | 1748 | Planned | Planned interruption | (Tap Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 215 | INCD-62328-K | Dickies Rd | Brookside Unit 124 | 2024-05-22 19:54 | 2024-05-22 20:41 | 0.00061936 | 1.3178e-05 | 3 | 141 | Unplanned | Wildlife | Bird Strike - Swan - Dickies Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 216 | INCD-61512-K | Osterholts Rd | Prebbleton Unit 113 | 2024-05-23 08:32 | 2024-05-23 15:48 | 0.31078 | 0.0007116 | 162 | 70751 | Planned | Planned interruption | (PRP) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 217 | INCD-61512-K | Osterholts Rd | Prebbleton Unit 113 | 2024-05-23 08:32 | 2024-05-23 15:55 | 0.011689 | 2.6356e-05 | 6 | 2661 | Planned | Planned interruption | (PRP) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 218 | INCD-23047-L | Victoria Park | Milton Unit 13 | 2024-05-23 09:10 | 2024-05-23 14:45 | 0.016174 | 4.8319e-05 | 11 | 3682 | Unplanned | Defective equipment | MSU Fault - Corona Discharge - Victoria Park - No Heater - Damp Location | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 219 | INCD-62352-K | Halkett Rd | Weedons Unit 122 | 2024-05-23 11:45 | 2024-05-23 13:07 | 0.001085 | 1.3178e-05 | 3 | 247 | Unplanned | Other cause | LV Fault - DB Fault - Halkett Rd - 11kV Isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 220 | INCD-62421-K | Kinloch Rd | Little River Unit 112 | 2024-05-24 15:22 | 2024-05-24 17:52 | 0.0019855 | 1.3178e-05 | 3 | 452 | Unplanned | Other cause | LV Fault - Bushing - Kinloch Rd - 11kV Isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 221 | INCD-62445-K | Wycola Av | Moffett St Unit 126 | 2024-05-24 18:50 | 2024-05-24 19:37 | 0.16024 | 0.0033735 | 768 | 36480 | Unplanned | Defective equipment | HV Cable Fault - Run - Wycola Av - CD_4783 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 222 | INCD-62445-K | Wycola Av | Moffett St Unit 126 | 2024-05-24 18:50 | 2024-05-24 19:49 | 0.036924 | 0.00062814 | 143 | 8406 | Unplanned | Defective equipment | HV Cable Fault - Run - Wycola Av - CD_4783 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 223 | INCD-23185-L | Old West Coast Rd | Moffett St Unit 114 | 2024-05-25 18:47 | 2024-05-25 21:48 | 0.032545 | 0.0001801 | 41 | 7409 | Unplanned | Third party interference | Vehicle v Pole - Old West Coast Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 224 | INCD-23200-L | Hills Rd | Hills Rd Unit 112 | 2024-05-26 14:36 | 2024-05-26 15:37 | 0.0068832 | 0.00011421 | 26 | 1567 | Unplanned | Defective equipment | Crossarm Fault - Centre Bolt - Hills Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 225 | INCD-62502-K | Neave Rd | Weedons Unit 112 | 2024-05-26 18:10 | 2024-05-26 18:42 | 0.021572 | 0.00068085 | 155 | 4911 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 226 | INCD-62502-K | Neave Rd | Weedons Unit 112 | 2024-05-26 18:10 | 2024-05-26 18:45 | 0.012282 | 0.0003558 | 81 | 2796 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 227 | INCD-62502-K | Neave Rd | Weedons Unit 112 | 2024-05-26 18:10 | 2024-05-26 20:37 | 0.12539 | 0.00085656 | 195 | 28545 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 228 | INCD-62508-K | Sandy Knolls Rd | Rolleston Unit 121 | 2024-05-26 20:07 | 2024-05-26 20:50 | 0.0011553 | 2.6356e-05 | 6 | 263 | Unplanned | Other cause | LV Fault - Fuse OH - Sandy Knolls Rd - 11kV Isolation | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 229 | INCD-61587-K | West Coast Rd | Darfield Unit 114 | 2024-05-27 08:31 | 2024-05-27 08:56 | 0.00032944 | 1.3178e-05 | 3 | 75 | Planned | Planned interruption | (Asset Relocation) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 230 | INCD-61587-K | West Coast Rd | Darfield Unit 114 | 2024-05-27 08:37 | 2024-05-27 14:58 | 0.0050251 | 1.3178e-05 | 3 | 1144 | Planned | Planned interruption | (Asset Relocation) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 231 | INCD-61587-K | West Coast Rd | Darfield Unit 114 | 2024-05-27 08:31 | 2024-05-27 15:05 | 0.005192 | 1.3178e-05 | 3 | 1182 | Planned | Planned interruption | (Asset Relocation) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 232 | INCD-61587-K | West Coast Rd | Darfield Unit 114 | 2024-05-27 08:03 | 2024-05-27 16:34 | 0.002249 | 4.3926e-06 | 1 | 512 | Planned | Planned interruption | (Asset Relocation) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 233 | INCD-62520-K | Leinster Rd | Fendalton Unit 4 | 2024-05-27 08:24 | 2024-05-27 08:50 | 0.037948 | 0.0014539 | 331 | 8639 | Unplanned | Defective equipment | HV Cable Fault - Joint - Leinster Rd - CD_586 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 234 | INCD-62520-K | Leinster Rd | Fendalton Unit 4 | 2024-05-27 08:24 | 2024-05-27 09:03 | 0.015313 | 0.00039094 | 89 | 3486 | Unplanned | Defective equipment | HV Cable Fault - Joint - Leinster Rd - CD_586 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 235 | INCD-62520-K | Leinster Rd | Fendalton Unit 4 | 2024-05-27 08:24 | 2024-05-27 09:24 | 0.0079067 | 0.00013178 | 30 | 1800 | Unplanned | Defective equipment | HV Cable Fault - Joint - Leinster Rd - CD_586 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 236 | INCD-62520-K | Leinster Rd | Fendalton Unit 4 | 2024-05-27 08:24 | 2024-05-27 09:24 | 0.00026356 | 4.3926e-06 | 1 | 60 | Unplanned | Defective equipment | HV Cable Fault - Joint - Leinster Rd - CD_586 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 237 | INCD-62520-K | Leinster Rd | Fendalton Unit 4 | 2024-05-27 08:24 | 2024-05-27 09:34 | 0.0092244 | 0.00013178 | 30 | 2100 | Unplanned | Defective equipment | HV Cable Fault - Joint - Leinster Rd - CD_586 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 238 | INCD-62520-K | Leinster Rd | Fendalton Unit 4 | 2024-05-27 08:24 | 2024-05-27 11:16 | 0.028776 | 0.00016692 | 38 | 6551 | Unplanned | Defective equipment | HV Cable Fault - Joint - Leinster Rd - CD_586 | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 239 | INCD-61758-K | Beach Rd | Motukarara Unit 111 | 2024-05-27 09:25 | 2024-05-27 15:48 | 0.22712 | 0.000593 | 135 | 51705 | Planned | Planned interruption | (Tx Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 240 | INCD-61758-K | Beach Rd | Motukarara Unit 111 | 2024-05-27 09:25 | 2024-05-27 15:54 | 0.037592 | 9.6637e-05 | 22 | 8558 | Planned | Planned interruption | (Tx Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 241 | INCD-61758-K | Beach Rd | Motukarara Unit 111 | 2024-05-27 09:25 | 2024-05-27 16:23 | 0.020197 | 4.8319e-05 | 11 | 4598 | Planned | Planned interruption | (Tx Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 242 | INCD-62586-K | Creyke Rd | Darfield Unit 114 | 2024-05-28 08:31 | 2024-05-28 10:18 | 0.0014056 | 1.3178e-05 | 3 | 320 | Planned | Planned interruption | (Asset Relocation) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 243 | INCD-8468-M | Burnham Rd | Rolleston Unit 111 | 2024-05-28 08:39 | 2024-05-28 13:06 | 0.080969 | 0.00030309 | 69 | 18433 | Planned | Planned interruption | (Reinforcement) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 244 | INCD-61779-K | West Coast Rd | Moffett St Unit 114 | 2024-05-28 10:14 | 2024-05-28 14:07 | 0.0010235 | 4.3926e-06 | 1 | 233 | Planned | Planned interruption | (Fuse Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 245 | INCD-62592-K | Birchs Rd | Prebbleton Unit 113 | 2024-05-28 14:26 | 2024-05-28 15:55 | 0.00078188 | 8.7852e-06 | 2 | 178 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 246 | INCD-62601-K | Norwood St | Milton Unit 25 | 2024-05-28 14:53 | 2024-05-28 15:43 | 0.022863 | 0.00045683 | 104 | 5205 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 247 | INCD-61884-K | Kennedys Bush Rd | Prebbleton Unit 113 | 2024-05-29 08:30 | 2024-05-29 12:59 | 0.14163 | 0.00052711 | 120 | 32244 | Planned | Planned interruption | (PRP) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 248 | INCD-61590-K | Creyke Rd | Darfield Unit 114 | 2024-05-29 08:31 | 2024-05-29 15:26 | 0.0054644 | 1.3178e-05 | 3 | 1244 | Planned | Planned interruption | (Asset Relocation) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 249 | INCD-61599-K | Ashgrove Tr | Milton Unit 13 | 2024-05-29 11:03 | 2024-05-29 11:08 | 0.0026443 | 0.00051833 | 118 | 602 | Planned | Planned interruption | (Tap Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 250 | INCD-61782-K | Shands Rd | Shands Rd Unit 122 | 2024-05-30 09:12 | 2024-05-30 11:49 | 0.00068964 | 4.3926e-06 | 1 | 157 | Planned | Planned interruption | (Tx Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 251 | INCD-8480-M | Martin Av | Milton Unit 25 | 2024-05-30 11:02 | 2024-05-30 11:11 | 0.0020733 | 0.00023281 | 53 | 472 | Planned | Planned interruption | (Tap Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 252 | INCD-23446-L | Weedons Rd | Springston Unit 114 | 2024-05-31 10:39 | 2024-05-31 11:58 | 0.00034701 | 4.3926e-06 | 1 | 79 | Unplanned | Third party interference | Car v Pole - Weedons Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 253 | INCD-62343-K | Purua Port Levy Rd | Diamond Harbour Unit 112 | 2024-06-04 08:34 | 2024-06-04 15:47 | 0.005706 | 1.3178e-05 | 3 | 1299 | Planned | Planned interruption | (Vegetation Management) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 254 | INCD-23566-L | Burkes Bush Rd | Prebbleton Unit 113 | 2024-06-04 11:49 | 2024-06-04 13:13 | 0.00036898 | 4.3926e-06 | 1 | 84 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 255 | INCD-62835-K | Karanga Rd | Greendale Unit 112 | 2024-06-04 13:55 | 2024-06-04 15:25 | 0.001186 | 1.3178e-05 | 3 | 270 | Unplanned | Defective equipment | Fuse OH Fault - Karanga Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 256 | INCD-23584-L | Old South Rd | Dunsandel Unit 121 | 2024-06-04 15:03 | 2024-06-04 16:23 | 0.00035141 | 4.3926e-06 | 1 | 80 | Unplanned | Wildlife | Bird Strike - Old South Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 257 | INCD-62214-K | Spencerville Rd | Belfast Unit 19 | 2024-06-05 09:35 | 2024-06-05 13:24 | 0.0010059 | 4.3926e-06 | 1 | 229 | Planned | Planned interruption | (Tx Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 258 | INCD-8486-M | Kennedys Bush Rd | Prebbleton Unit 113 | 2024-06-06 08:30 | 2024-06-06 12:46 | 0.050603 | 0.00019767 | 45 | 11520 | Planned | Planned interruption | (PRP) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 259 | INCD-61875-K | Old Tai Tapu Rd | Halswell Unit 1 | 2024-06-06 08:31 | 2024-06-06 12:46 | 0.050475 | 0.00019767 | 45 | 11491 | Planned | Planned interruption | (PRP) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 260 | INCD-61875-K | Old Tai Tapu Rd | Halswell Unit 1 | 2024-06-06 08:30 | 2024-06-06 13:02 | 0.089416 | 0.00032944 | 75 | 20356 | Planned | Planned interruption | (PRP) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 261 | INCD-62937-K | Moores Rd | Duvauchelle Unit 124 | 2024-06-06 17:48 | 2024-06-06 19:53 | 0.0021919 | 1.757e-05 | 4 | 499 | Unplanned | Wildlife | Rat v Tx - Moores Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 262 | INCD-23683-L | Old West Coast Rd | Kimberley Unit 113 | 2024-06-06 21:45 | 2024-06-07 01:20 | 0.050989 | 0.0002372 | 54 | 11608 | Unplanned | Third party interference | Car v Pole - Old West Coast Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 263 | INCD-62079-K | Savills Rd | Waimakariri Unit 1 | 2024-06-07 09:01 | 2024-06-07 14:19 | 0.0027893 | 8.7852e-06 | 2 | 635 | Planned | Planned interruption | (PRP) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 264 | INCD-62661-K | Johns Rd | Waimakariri Unit 14 | 2024-06-07 09:02 | 2024-06-07 15:22 | 0.0066767 | 1.757e-05 | 4 | 1520 | Planned | Planned interruption | (Vegetation Management) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 265 | INCD-23698-L | Morgans Rd | Hororata Unit 113 | 2024-06-07 14:19 | 2024-06-07 14:36 | 0.00022402 | 1.3178e-05 | 3 | 51 | Unplanned | Defective equipment | Crossarm Fault - Brace Bolt - Morgans Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 266 | INCD-62985-K | Homebush Rd | Darfield Unit 114 | 2024-06-08 10:03 | 2024-06-08 10:52 | 0.00085656 | 1.757e-05 | 4 | 195 | Unplanned | Wildlife | Bird Strike - Duck - Homebush Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 267 | INCD-62058-K | Deans Av | Addington Unit 2722 | 2024-06-10 08:31 | 2024-06-10 10:38 | 0.0089257 | 7.0281e-05 | 16 | 2032 | Planned | Planned interruption | (MSU Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 268 | INCD-62058-K | Deans Av | Addington Unit 2722 | 2024-06-10 08:31 | 2024-06-10 10:41 | 0.0074235 | 5.7104e-05 | 13 | 1690 | Planned | Planned interruption | (MSU Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 269 | INCD-63024-K | Old Tai Tapu Rd | Lincoln Unit 122 | 2024-06-10 08:38 | 2024-06-10 09:27 | 0.00043047 | 8.7852e-06 | 2 | 98 | Unplanned | Wildlife | Bird Strike - Goose - Old Tai Tapu Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 270 | INCD-63060-K | Adams Rd | Weedons Unit 112 | 2024-06-10 12:27 | 2024-06-10 12:35 | 0.0099404 | 0.0012124 | 276 | 2263 | Unplanned | Defective equipment | Insulator Fault - Adams Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 271 | INCD-63060-K | Adams Rd | Weedons Unit 112 | 2024-06-10 13:30 | 2024-06-10 13:35 | 0.0054161 | 0.0012124 | 276 | 1233 | Unplanned | Defective equipment | Insulator Fault - Adams Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 272 | INCD-63060-K | Adams Rd | Weedons Unit 112 | 2024-06-10 12:27 | 2024-06-10 13:37 | 0.0092332 | 0.00013178 | 30 | 2102 | Unplanned | Defective equipment | Insulator Fault - Adams Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 273 | INCD-63060-K | Adams Rd | Weedons Unit 112 | 2024-06-10 12:27 | 2024-06-10 17:02 | 0.15088 | 0.00054907 | 125 | 34348 | Unplanned | Defective equipment | Insulator Fault - Adams Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 274 | INCD-63087-K | Rakaia Terrace Rd | Te Pirita Unit 112 | 2024-06-10 14:54 | 2024-06-10 15:51 | 0.00025038 | 4.3926e-06 | 1 | 57 | Unplanned | Wildlife | Bird Strike - Starling - Rakaia Terrace Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 275 | INCD-63096-K | Brookside Zone Sub | Brookside Unit 124 | 2024-06-10 23:33 | 2024-06-11 00:01 | 0.033357 | 0.0011948 | 272 | 7594 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 276 | INCD-63096-K | Brookside Zone Sub | Brookside Unit 124 | 2024-06-10 23:33 | 2024-06-11 00:23 | 0.020549 | 0.0004129 | 94 | 4678 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 277 | INCD-63096-K | Brookside Zone Sub | Brookside Unit 124 | 2024-06-10 23:33 | 2024-06-11 00:26 | 0.00023281 | 4.3926e-06 | 1 | 53 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 278 | INCD-63096-K | Brookside Zone Sub | Brookside Unit 124 | 2024-06-10 23:33 | 2024-06-11 00:40 | 0.038031 | 0.00056664 | 129 | 8658 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 279 | INCD-63102-K | Ridgeland Wy | Weedons Unit 122 | 2024-06-11 07:05 | 2024-06-11 07:11 | 0.032259 | 0.0056269 | 1281 | 7344 | Unplanned | Defective equipment | (Subdiv) - Ridgeland Wy - Switching Fault - MSU Misfire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 280 | INCD-63105-K | Ridgeland Wy | Weedons Unit 124 | 2024-06-11 07:05 | 2024-06-11 07:11 | 0.0008302 | 0.00014496 | 33 | 189 | Unplanned | Defective equipment | (Subdiv) - Ridgeland Wy - Switching Fault - MSU Misfire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 281 | INCD-63105-K | Ridgeland Wy | Weedons Unit 124 | 2024-06-11 07:05 | 2024-06-11 07:12 | 0.0015594 | 0.00022841 | 52 | 355 | Unplanned | Defective equipment | (Subdiv) - Ridgeland Wy - Switching Fault - MSU Misfire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 282 | INCD-62121-K | Mount Pleasant Rd | Barnett Park Unit 4 | 2024-06-11 08:31 | 2024-06-11 13:19 | 0.036722 | 0.00012739 | 29 | 8360 | Planned | Planned interruption | (LSW Upgrade) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 283 | INCD-62388-K | Weedons Ross Rd | Weedons Unit 124 | 2024-06-11 08:32 | 2024-06-11 13:58 | 0.012905 | 3.9533e-05 | 9 | 2938 | Planned | Planned interruption | (Subdiv) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 284 | INCD-62388-K | Weedons Ross Rd | Weedons Unit 124 | 2024-06-11 08:32 | 2024-06-11 13:58 | 0.0057367 | 1.757e-05 | 4 | 1306 | Planned | Planned interruption | (Subdiv) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 285 | INCD-62061-K | Deans Av | Addington Unit 2722 | 2024-06-11 08:36 | 2024-06-11 17:34 | 0.030722 | 5.7104e-05 | 13 | 6994 | Planned | Planned interruption | (MSU Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 286 | INCD-62061-K | Deans Av | Addington Unit 2722 | 2024-06-11 08:34 | 2024-06-11 17:34 | 0.037952 | 7.0281e-05 | 16 | 8640 | Planned | Planned interruption | (MSU Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 287 | INCD-62229-K | Clintons Rd | Greendale Unit 114 | 2024-06-11 09:01 | 2024-06-11 15:55 | 0.081922 | 0.00019767 | 45 | 18650 | Planned | Planned interruption | (Vegetation Management) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 288 | INCD-8600-M | West Coast Rd | Darfield Unit 111 | 2024-06-12 08:31 | 2024-06-12 14:20 | 0.04296 | 0.00012299 | 28 | 9780 | Planned | Planned interruption | (LSW Upgrade) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 289 | INCD-62394-K | Weedons Ross Rd | Weedons Unit 124 | 2024-06-12 08:37 | 2024-06-12 16:23 | 0.020443 | 4.3926e-05 | 10 | 4654 | Planned | Planned interruption | (Subdiv) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 290 | INCD-62394-K | Weedons Ross Rd | Weedons Unit 124 | 2024-06-12 08:37 | 2024-06-12 16:45 | 0.010714 | 2.1963e-05 | 5 | 2439 | Planned | Planned interruption | (Subdiv) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 291 | INCD-23920-L | Volckman Rd | Hills Rd Unit 114 | 2024-06-12 14:56 | 2024-06-12 16:23 | 0.015761 | 0.0001801 | 41 | 3588 | Unplanned | Defective equipment | Insulator Fault - Volckman Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 292 | INCD-8663-M | Embankment Rd | Springston Unit 114 | 2024-06-13 08:13 | 2024-06-13 17:41 | 0.027436 | 4.8319e-05 | 11 | 6246 | Planned | Planned interruption | (Vegetation Management) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 293 | INCD-8597-M | Highsted Rd | Waimakariri Unit 13 | 2024-06-13 08:32 | 2024-06-13 15:20 | 0.039415 | 9.6637e-05 | 22 | 8973 | Planned | Planned interruption | (Subdiv) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 294 | INCD-8612-M | Algidus Rd | Coleridge GXP Unit 1022 | 2024-06-13 08:34 | 2024-06-13 12:42 | 0.031684 | 0.00012739 | 29 | 7213 | Planned | Planned interruption | (LSW Upgrade) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 295 | INCD-8657-M | Kaituna Valley Rd | Motukarara Unit 111 | 2024-06-13 09:45 | 2024-06-13 10:57 | 0.0015813 | 2.1963e-05 | 5 | 360 | Planned | Planned interruption | (Non-Sched Maint) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 296 | INCD-63291-K | Springs Rd | Shands Rd Unit 122 | 2024-06-14 03:54 | 2024-06-14 04:58 | 0.010002 | 0.00015813 | 36 | 2277 | Unplanned | Wildlife | Bird Strike - Springs Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 297 | INCD-63291-K | Springs Rd | Shands Rd Unit 122 | 2024-06-14 03:54 | 2024-06-14 05:23 | 0.00078188 | 8.7852e-06 | 2 | 178 | Unplanned | Wildlife | Bird Strike - Springs Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 298 | INCD-62208-K | Gardiners Rd | Waimakariri Unit 14 | 2024-06-14 09:02 | 2024-06-14 12:04 | 0.0039841 | 2.1963e-05 | 5 | 907 | Planned | Planned interruption | (PRP) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 299 | INCD-24025-L | Curraghs Rd | Larcomb Unit 114 | 2024-06-14 14:30 | 2024-06-14 16:15 | 0.010147 | 9.6637e-05 | 22 | 2310 | Unplanned | Defective equipment | Pole Suspect - Red Tag - Curraghs Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 300 | INCD-24127-L | Seabridge Rd | Motukarara Unit 112 | 2024-06-17 13:01 | 2024-06-17 14:53 | 0.00098394 | 8.7852e-06 | 2 | 224 | Unplanned | Wildlife | Bird Strike - Seabridge Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 301 | INCD-24115-L | Tramway Rd | Annat Unit 113 | 2024-06-17 15:57 | 2024-06-17 17:04 | 0.0014803 | 2.1963e-05 | 5 | 337 | Unplanned | Defective equipment | LA Fault - Tramway Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 302 | INCD-62535-K | Spencerville Rd | Belfast Unit 19 | 2024-06-18 09:03 | 2024-06-18 17:00 | 0.094331 | 0.00019767 | 45 | 21475 | Planned | Planned interruption | (Vegetation Management) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 303 | INCD-62289-K | West Coast Rd | Castle Hill GXP Unit 642 | 2024-06-18 09:04 | 2024-06-18 12:08 | 0.010507 | 5.7104e-05 | 13 | 2392 | Planned | Planned interruption | (Tx Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 304 | INCD-63459-K | Steeles Rd | Te Pirita Unit 114 | 2024-06-18 17:39 | 2024-06-18 19:33 | 0.00099712 | 8.7852e-06 | 2 | 227 | Unplanned | Defective equipment | Fuse OH Fault - Steeles Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 305 | INCD-63468-K | West Coast Rd | Moffett St Unit 114 | 2024-06-19 07:45 | 2024-06-19 18:52 | 0.017592 | 2.6356e-05 | 6 | 4005 | Unplanned | Wildlife | Rat v Tx - West Coast Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 306 | INCD-62532-K | Dalethorpe Rd | Annat Unit 112 | 2024-06-19 08:30 | 2024-06-19 13:53 | 0.0056752 | 1.757e-05 | 4 | 1292 | Planned | Planned interruption | (LSW Upgrade) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 307 | INCD-62532-K | Dalethorpe Rd | Annat Unit 112 | 2024-06-19 08:35 | 2024-06-19 14:33 | 0.0015682 | 4.3926e-06 | 1 | 357 | Planned | Planned interruption | (LSW Upgrade) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 308 | INCD-62532-K | Dalethorpe Rd | Annat Unit 112 | 2024-06-19 08:33 | 2024-06-19 14:33 | 0.0015813 | 4.3926e-06 | 1 | 360 | Planned | Planned interruption | (LSW Upgrade) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 309 | INCD-63504-K | Bush Gully Rd | Annat Unit 112 | 2024-06-19 15:45 | 2024-06-19 17:40 | 0.00050515 | 4.3926e-06 | 1 | 115 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 310 | INCD-62745-K | Mcclelland Rd | Larcomb Unit 114 | 2024-06-20 08:17 | 2024-06-20 16:08 | 0.0041422 | 8.7852e-06 | 2 | 943 | Planned | Planned interruption | (Vegetation Management) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 311 | INCD-8771-M | Wards Rd | Darfield Unit 115 | 2024-06-20 08:34 | 2024-06-20 13:10 | 0.015721 | 5.7104e-05 | 13 | 3579 | Planned | Planned interruption | (LSW Upgrade) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 312 | INCD-8771-M | Wards Rd | Darfield Unit 115 | 2024-06-20 08:34 | 2024-06-20 13:10 | 0.014531 | 5.2711e-05 | 12 | 3308 | Planned | Planned interruption | (LSW Upgrade) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 313 | INCD-63084-K | Curletts Rd | Middleton Unit 4 | 2024-06-20 14:07 | 2024-06-20 21:44 | 0.0040148 | 8.7852e-06 | 2 | 914 | Planned | Planned interruption | (Cust Requested) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 314 | INCD-62748-K | Mcclelland Rd | Larcomb Unit 114 | 2024-06-21 08:10 | 2024-06-21 12:18 | 0.0021787 | 8.7852e-06 | 2 | 496 | Planned | Planned interruption | (Vegetation Management) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 315 | INCD-8825-M | Old West Coast Rd | Moffett St Unit 115 | 2024-06-21 08:40 | 2024-06-21 11:46 | 0.0073532 | 3.9533e-05 | 9 | 1674 | Planned | Planned interruption | (Tx Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 316 | INCD-63576-K | Rakaia Selwyn Rd | Brookside Unit 123 | 2024-06-22 13:11 | 2024-06-22 14:20 | 0.0012167 | 1.757e-05 | 4 | 277 | Unplanned | Wildlife | Bird Strike - Rakaia Selwyn Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 317 | INCD-63585-K | Lake Rd | Hills Rd Unit 114 | 2024-06-22 18:17 | 2024-06-22 20:25 | 0.0056357 | 4.3926e-05 | 10 | 1283 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 318 | INCD-62673-K | Ryans Rd | Waimakariri Unit 1 | 2024-06-24 08:39 | 2024-06-24 13:59 | 0.050699 | 0.00015813 | 36 | 11542 | Planned | Planned interruption | (Fuse Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 319 | INCD-24412-L | Johnstons Rd | Hills Rd Unit 114 | 2024-06-24 13:40 | 2024-06-24 14:36 | 0.00024599 | 4.3926e-06 | 1 | 56 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 320 | INCD-62814-K | Leadleys Rd | Prebbleton Unit 113 | 2024-06-25 08:41 | 2024-06-25 14:36 | 0.082616 | 0.00023281 | 53 | 18808 | Planned | Planned interruption | (PRP) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 321 | INCD-63117-K | Bells Rd | Weedons Unit 122 | 2024-06-25 09:13 | 2024-06-25 16:13 | 0.0018449 | 4.3926e-06 | 1 | 420 | Planned | Planned interruption | (Tx Change) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 322 | INCD-62823-K | Te Oka Bay Rd | Little River Unit 112 | 2024-06-25 09:33 | 2024-06-25 11:21 | 0.005236 | 4.8319e-05 | 11 | 1192 | Planned | Planned interruption | (Vegetation Management) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 323 | INCD-63057-K | Walkers Rd | Rolleston Unit 112 | 2024-06-25 10:04 | 2024-06-25 12:27 | 0.0031407 | 2.1963e-05 | 5 | 715 | Planned | Planned interruption | (Metering) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 324 | INCD-63693-K | Greenpark Rd | Springston Unit 114 | 2024-06-25 13:48 | 2024-06-25 15:05 | 0.0010147 | 1.3178e-05 | 3 | 231 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 325 | INCD-62883-K | Racecourse Rd | Sockburn Unit 112 | 2024-06-26 08:55 | 2024-06-26 17:44 | 0.074358 | 0.00014056 | 32 | 16928 | Planned | Planned interruption | (PRP) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 326 | INCD-62877-K | Greendale Rd | Darfield Unit 112 | 2024-06-26 09:26 | 2024-06-26 15:07 | 0.022477 | 6.5889e-05 | 15 | 5117 | Planned | Planned interruption | (LSW Upgrade) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 327 | INCD-62877-K | Greendale Rd | Darfield Unit 112 | 2024-06-26 09:23 | 2024-06-26 15:13 | 0.020013 | 5.7104e-05 | 13 | 4556 | Planned | Planned interruption | (LSW Upgrade) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 328 | INCD-62877-K | Greendale Rd | Darfield Unit 112 | 2024-06-26 09:26 | 2024-06-26 15:18 | 0.06653 | 0.00018888 | 43 | 15146 | Planned | Planned interruption | (LSW Upgrade) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 329 | INCD-24496-L | Buckleys Rd | Brookside Unit 124 | 2024-06-26 13:03 | 2024-06-26 18:00 | 0.096786 | 0.00032505 | 74 | 22034 | Unplanned | Other cause | LV Fault - Suspect Cable Fault - Buckleys Rd - 11kV Isolation - Pole Fire | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 330 | INCD-63741-K | Wards Rd | Darfield Unit 115 | 2024-06-26 15:49 | 2024-06-26 16:16 | 0.056506 | 0.0021084 | 480 | 12864 | Unplanned | Human error | Switching error - Wards Rd - Protection not disabled | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 331 | INCD-63744-K | Wards Rd | Darfield Unit 112 | 2024-06-26 15:49 | 2024-06-26 16:16 | 0.0047045 | 0.0001757 | 40 | 1071 | Unplanned | Human error | Switching error - Wards Rd - Protection not disabled | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 332 | INCD-62901-K | Pigeon Bay Rd | Duvauchelle Unit 121 | 2024-06-27 08:31 | 2024-06-27 14:29 | 0.23092 | 0.00064571 | 147 | 52570 | Planned | Planned interruption | (Vegetation Management) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 333 | INCD-63771-K | Rakaia Terrace Rd | Te Pirita Unit 114 | 2024-06-27 08:33 | 2024-06-27 09:19 | 0.01139 | 0.00024599 | 56 | 2593 | Unplanned | Third party interference | High Load v Line - Rakaia Terrace Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 334 | INCD-63771-K | Rakaia Terrace Rd | Te Pirita Unit 114 | 2024-06-27 08:33 | 2024-06-27 12:53 | 0.0068481 | 2.6356e-05 | 6 | 1559 | Unplanned | Third party interference | High Load v Line - Rakaia Terrace Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 335 | INCD-63831-K | Jowers Rd | Weedons Unit 112 | 2024-06-27 21:01 | 2024-06-27 22:08 | 0.0026487 | 3.9533e-05 | 9 | 603 | Unplanned | Wildlife | Rat v Line - Jowers Rd | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 336 | INCD-63915-K | Bethels Rd | Springston Unit 112 | 2024-06-30 18:56 | 2024-06-30 20:54 | 0.0046342 | 3.9533e-05 | 9 | 1055 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 337 | INCD-62967-K | Maddisons Rd | Weedons Unit 122 | 2024-07-01 09:45 | 2024-07-01 14:32 | 0.0012607 | 4.3926e-06 | 1 | 287 | Planned | Planned interruption | (Subdiv) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 338 | INCD-62967-K | Maddisons Rd | Weedons Unit 122 | 2024-07-01 09:45 | 2024-07-01 15:01 | 0.0013881 | 4.3926e-06 | 1 | 316 | Planned | Planned interruption | (Subdiv) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 339 | INCD-8813-M | Dickies Rd | Brookside Unit 124 | 2024-07-01 10:05 | 2024-07-01 15:34 | 0.0043355 | 1.3178e-05 | 3 | 987 | Planned | Planned interruption | (Non-Sched Maint) | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS
Orion NZ | 2025 |  | 340 | INCD-63993-K | Little River Zone Sub | Little River Unit 111 | 2024-07-02 09:11 | 2024-07-02 10:36 | 0.012343 | 0.00014496 | 33 | 2810 | Unplanned | Unknown | NFF | 10a(i): Raw interruption data | 10.11 | Year end | SCHEDULE 10a: REPORT ON INTERRUPTIONS